## Ignition
Year | Quarter | Date | Time | Date/Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification/Circuit | Other Companies | Transmission or Distribution | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | OutageID | Outage Date | Outage Time | Suspected Initiating Event | Equipment /Facility Failure | Contact Object | Facility Contacted | Contributing Factor | (Internal Use) Cause | Tier | District | FPI | FPI Level
2015 | 1 | 2015-03-19 | 23:50 | 3/19/15 23:50:00 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | S.D. City | P719156 |  | Distribution | 12kV | Conductor | Overhead | Yes | 150319E64881 | 2015-03-19 | 23:50 | Contact From Object |  | Vehicle | Pole | Human Error | Vehicle contact | Tier 2 | NE | 4 | Normal
2015 | 2 | 2015-04-09 | 17:23 | 4/09/15 17:23:00 | 32.7233 | -116.8922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | P171928 |  | Distribution | 12kV | Other | Overhead | No |  |  |  | Unknown |  |  | Electric Facility |  | Undetermined | Tier 3 | EA | 7 | Normal
2015 | 2 | 2015-04-12 | 12:31 | 4/12/15 12:31:00 | 33.0117 | -116.866 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | P214319 |  | Distribution | 12kV | Conductor | Overhead | Yes | 150412E66711 | 2015-04-12 | 12:30 | Contact From Object |  | Other | Electric Facility |  | Other- Outside force/object | Tier 2 | RA | 9 | Normal
2015 | 2 | 2015-04-12 | 14:30 | 4/12/15 14:30:00 | 33.2754 | -117.3306 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Pendleton | P164638 |  | Distribution | 12kV | Lightning Arrestor | Overhead | No |  |  |  | Contact From Object |  | Vehicle | Pole |  | Other- Human related- SDGE | Tier 2 | NC | 9 | Normal
2015 | 2 | 2015-04-13 | 10:50 | 4/13/15 10:50:00 | 32.5859 | -117.0017 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Chula Vista | P81123 |  | Distribution | 12kV | Conductor | Overhead | Yes | 150413E66770 | 2015-04-13 | 10:50 | Contact From Object |  | Vehicle | Electric Facility | Human Error | Vehicle contact | Tier 2 | CM | 8 | Normal
2015 | 2 | 2015-04-28 | 13:30 | 4/28/15 13:30:00 | 32.8917 | -116.8419 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P176657 | none | Distribution | 12kV | Conductor | Overhead | Yes |  | 2015-04-28 | 13:30 | Contact From Object | Conductor | Vehicle | Electric Facility | Human Error | Vehicle contact | Tier 3 | EA | 9 | Normal
2015 | 2 | 2015-04-29 | 12:00 | 4/29/15 12:00:00 | 32.6061 | -116.696 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P175961 | none | Distribution | 12kV | Conductor | Overhead | Yes |  | 2015-04-29 | 12:00 | Contact From Object | Splice/Clamp/Connector | Vegetation | Electric Facility | Unknown | Vegetation | Tier 3 | ME | 10 | Normal
2015 | 3 | 2015-07-17 | 9:48 | 7/17/15 09:48:00 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P213348 |  | Distribution | 12kV | Conductor | Overhead | No | 150717E73913 |  |  | Contact From Object | Protective Relay | Vegetation | Communication Facility | Human Error | Other- Human related- non SDGE | Tier 3 | NE | 12 | Elevated
2015 | 3 | 2015-07-27 | 14:30 | 7/27/15 14:30:00 | 33.0665 | -116.579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P212006 |  | Distribution | 12kV | Conductor | Overhead | Yes | 150727E74823 | 2015-07-27 | 14:30 | Contact From Object | Crossarm | Vegetation | Electric Facility | None | Vegetation | Tier 3 | RA | 12 | Elevated
2015 | 3 | 2015-08-13 | 20:33 | 8/13/15 20:33:00 | 33.2457 | -116.6769 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P19586 |  | Distribution | 12kV | Conductor | Overhead | Yes | 150813E76133 | 2015-08-13 | 20:33 | Unknown | Conductor |  |  | Unknown | Other- Equip Failure | Tier 2 | RA | 12 | Elevated
2015 | 3 | 2015-08-23 | 15:00 | 8/23/15 15:00:00 | 33.2729 | -117.1521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | P415300 |  | Distribution | 12kV | Conductor | Overhead | Yes | 150823E76860 | 2015-08-23 | 15:00 | Contact From Object |  | Vegetation | Electric Facility | Weather | Vegetation | Tier 2 | NE | 14 | Elevated
2015 | 3 | 2015-09-01 | 8:50 | 9/01/15 08:50:00 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P41145 cir. 445 |  | Distribution | 12kV | Conductor | Overhead | Yes | 150901E77579 | 2015-09-01 | 8:50 | Equipment/Facility Failure | Conductor |  |  | None | Other- Equip Failure | Tier 2 | ME | 13 | Elevated
2015 | 3 | 2015-09-08 | 11:45 | 9/08/15 11:45:00 | 33.0726 | -116.7435 | Vegetation | Rural | Less Than .25 Acres | Utility | CAL FIRE | P416995 cir 222 | none | Distribution | 12kV | Switch | Overhead | Yes | 150908E77978 | 2015-09-08 | 11:45 | Equipment/Facility Failure | Switch |  |  | None | Other- Equip Failure | Tier 3 | RA | 13 | Elevated
2015 | 4 | 2015-12-26 | 3:04 | 12/26/15 03:04:00 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Escondido | P218563 |  | Distribution | 12kV | Conductor | Overhead | Yes | 151226E85117 | 2015-12-26 | 3:04 | Contact From Object |  | Vegetation | Electric Facility | Weather | Vegetation | Tier 2 | NE | 10 | Normal
2016 | 1 | 2016-01-31 | 15:00 | 1/31/16 15:00:00 | 33.3217 | -117.156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CALFIRE | P714625 |  | Distribution | 12kV | Conductor | Overhead | Yes | 160131E87336 | 2016-01-31 | 15:00 | Equipment/Facility Failure | Conductor |  | Pole | Weather | Undetermined | Tier 2 | NE | 6 | Normal
2016 | 1 | 2016-02-12 | 19:30 | 2/12/16 19:30:00 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P414015 |  | Distribution | 12kV | Conductor | Overhead | Yes | 160212E88424 | 2016-02-12 | 19:30 | Vandalism/Theft |  |  |  | Outside Force | Other- Human related- non SDGE | Tier 3 | NE | 6 | Normal
2016 | 1 | 2016-02-18 | 14400:00 | 2/18/16 00:00:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P40825 |  | Distribution | 12kV | Conductor | Overhead | Yes | 160218E88690/160218E88828 | 2016-02-18 | 6:00 | Contact From Object | Conductor | Vehicle | Pole | None | Vehicle contact | Tier 3 | ME | 4 | Normal
2016 | 2 | 2016-04-16 | Unknown | 4/16/16 Unknown | 33.2243 | -117.3683 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Unknown | Z29145 (TL 690, C198) |  | Distribution | 12kV | Conductor | Overhead | Yes | 20160416TR01 | 2016-04-16 |  | Contact From Object | Conductor | Vegetation |  | Weather | Vegetation | Tier 2 | NC | 6 | Normal
2016 | 2 | 2016-06-14 | 6:05 | 6/14/16 06:05:00 | 32.8801 | -116.9051 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P370041 | AT&T | Distribution | 12kV | Conductor | Overhead | Yes | 160614E98493 | 2016-06-14 | 6:05 | Contact From Object |  | Vehicle | Pole | Outside Force | Vehicle contact | Tier 2 | EA | 10 | Normal
2016 | 2 | 2016-06-27 | 15:30 | 6/27/16 15:30:00 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P112086 |  | Distribution | 12kV | Other | Overhead | No |  |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Other- Human related- non SDGE | Tier 2 | RA | 13 | Elevated
2016 | 3 | 2016-07-02 | 7:51 | 7/02/16 07:51:00 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P775960 |  | Distribution | 12kV | Capacitor Bank | Overhead | Yes | 160702E99563 | 2016-07-02 | 7:51 | Equipment/Facility Failure | Capacitor Bank |  |  | None | Other- Equip Failure | Tier 2 | EA | 12 | Elevated
2016 | 3 | 2016-07-11 | 10:27 | 7/11/16 10:27:00 | 33.4531 | -117.3044 | Vegetation | Urban | Less Than .25 Acres | Customer | CALFIRE | P228931 C 520 |  | Distribution | 12kV | Conductor | Overhead | Yes | 160711E100064 | 2016-07-11 | 10:27 | Contact From Object | Other | Other | Electric Facility |  | Other- Outside force/object | Tier 2 | NE | 12 | Elevated
2016 | 3 | 2016-07-11 | 13:19 | 7/11/16 13:19:00 | 33.1146 | -116.5843 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | P412648 C221 | None | Distribution | 12kV | Lightning Arrestor | Overhead | Yes | 160711E100085 | 2016-07-11 | 13:19 | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Other- Equip Failure | Tier 3 | RA | 12 | Elevated
2016 | 3 | 2016-07-22 | Unknown | 7/22/16 Unknown | 33.2015 | -116.9352 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P212466 |  | Distribution | 12kV | Transformer | Overhead | No |  |  |  | Equipment/Facility Failure | Other |  |  | Unknown | Other- Human related- SDGE | Tier 3 | NE | 14 | Elevated
2016 | 3 | 2016-07-29 | 10:57 | 7/29/16 10:57:00 | 33.071 | -116.7424 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P416995 |  | Distribution | 12kV | Conductor | Overhead | Yes |  | 2016-07-29 |  | Equipment/Facility Failure | Conductor |  |  |  | Other- Equip Failure | Tier 3 | RA | 13 | Elevated
2016 | 3 | 2016-07-31 | 13:43 | 7/31/16 13:43:00 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Fallbrook Fire | P115869 |  | Distribution | 12kV | Conductor | Overhead | Yes | 160731E101667 | 2016-07-31 | 13:43 | Contact From Object | Recloser | Vegetation | Electric Facility | Unknown | Vegetation | Tier 2 | NE | 12 | Elevated
2016 | 3 | 2016-09-23 | 11:25 | 9/23/16 11:25:00 | 32.7372 | -116.7343 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P101347 |  | Distribution | 12kV | Transformer | Overhead | Yes | 160923E105793/160923E105855 | 2016-09-23 | 11:25 | Equipment/Facility Failure | Transformer |  |  | None | Other- Equip Failure | Tier 3 | EA | 11 | Normal
2016 | 3 | 2016-09-27 | unknown | 9/27/16 unknown | 33.2967 | -117.2079 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE |  |  | Distribution | 12kV | Fuse | Overhead | No | 160926E106015 |  |  | Contact From Object |  | Animal |  | Unknown | Other- Human related- SDGE | Tier 2 | NE | 13 | Elevated
2016 | 4 | 2016-10-21 | 11:20 | 10/21/16 11:20:00 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P114079 |  | Distribution | 12kV | Conductor | Overhead | No |  |  |  | Equipment/Facility Failure | Transformer |  |  |  | Other- Equip Failure | Tier 2 | RA | 14 | Elevated
2016 | 4 | 2016-11-02 | 10:30 | 11/02/16 10:30:00 | 32.8373 | -116.7022 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P175475 |  | Distribution | 12kV | Conductor | Overhead | Yes | 161102E108598 | 2016-11-02 | 10:30 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Other- Equip Failure | Tier 3 | ME | 11 | Normal
2016 | 4 | 2016-11-12 | 20:30 | 11/12/16 20:30:00 | 32.6227 | -116.9388 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Chula Vista Fire | P85952 |  | Distribution | 12kV | Lightning Arrestor | Overhead | Yes |  | 2016-11-12 | 18:34 | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Other- Equip Failure | Tier 2 | CM | 11 | Normal
2017 | 2 | 2017-06-08 | 4:12 | 6/08/17 04:12:00 | 33.0356 | -117.1839 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Rnch Snta Fe | Circuit 307 |  | Distribution | 12kV | Transformer | Padmounted | Yes | 170608E123968 | 2017-06-08 | 4:12 | Contact From Object | Transformer | Vehicle | Electric Facility | Human Error | Vehicle contact | Tier 2 | NC | 9 | Normal
2017 | 2 | 2017-06-12 | 11:20 | 6/12/17 11:20:00 | 32.843 | -116.7111 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Viejas Fire Dept | Circuit 1458 |  | Distribution | 12kV | Conductor | Overhead | No | 170612E124282 |  |  | Contact From Object |  | Other | Electric Facility | Weather | Other- Outside force/object | Tier 3 | ME | 8 | Normal
2017 | 2 | 2017-06-29 | 14:58 | 6/29/17 14:58:00 | 32.6926 | -116.8564 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | Circuit 75 | Communication | Distribution | 12kV | Conductor | Overhead | Yes | 170629E125730 | 2017-06-29 | 14:58 | Contact From Object |  | Vehicle | Electric Facility | None | Vehicle contact | Tier 3 | EA | 10 | Normal
2017 | 3 | 2017-07-28 | 16:31 | 7/28/17 16:31:00 | 32.7802 | -116.8722 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Heartland | P78591/ C228 |  | Distribution | 12kV | Conductor | Overhead | Yes | 170728E127770 |  | 16:31 | Contact From Object | Pole /Conductor | Vehicle | Electric Facility | Outside Force | Vehicle contact | Tier 2 | EA | 12 | Elevated
2017 | 3 | 2017-08-30 | 14:12 | 8/30/17 14:12:00 | 33.3875 | -117.2459 | Vegetation | Urban | Less Than .25 Acres | Fire Agency |  | P214608 |  | Distribution | 12kV | Conductor | Overhead | Yes | 170830E130169 | 8/30/217 | 14:11 | Contact From Object |  | Balloons | Electric Facility | Other | Mylar | Tier 2 | NE | 14 | Elevated
2017 | 3 | 2017-09-05 | 14:49 | 9/05/17 14:49:00 | 32.6191 | -116.6949 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P175945 |  | Distribution | 12kV | Conductor | Overhead | Yes | 170905E130653 | 2017-09-05 | 14:49 | Contact From Object |  | Vegetation | Electric Facility | Unknown | Vegetation | Tier 3 | ME | 13 | Elevated
2017 | 3 | 2017-09-27 | 14:28 | 9/27/17 14:28:00 | 33.2327 | -116.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | Circuit 909 -Z12816 |  | Distribution | 12kV | Conductor | Overhead | Yes | 170927E132482 | 2017-09-27 | 12:43 | Unknown |  |  |  | Unknown | Undetermined | Tier 2 | NE | 14 | Elevated
2017 | 3 | 2017-09-27 | 16:10 | 9/27/17 16:10:00 | 32.7272 | -116.7788 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P877437 |  | Distribution | 12kV | Lightning Arrestor | Overhead | Yes | 170927E132512 | 2017-09-27 | 15:59 | Equipment/Facility Failure | Lightning Arrestor |  |  | None | Other- Equip Failure | Tier 3 | EA | 14 | Elevated
2017 | 4 | 2017-10-07 | 17:40 | 10/07/17 17:40:00 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | P471952 | Communication | Distribution | 12kV | Conductor | Overhead | No |  |  |  | Equipment/Facility Failure | Conductor |  |  | Other | Other- Human related- non SDGE | Tier 3 | ME | 14 | Elevated
2017 | 4 | 2017-10-16 | 10:20 | 10/16/17 10:20:00 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | P112774 / c236 |  | Distribution | 12kV | Conductor | Overhead | No |  |  |  | Contact From Object |  | Balloons | Electric Facility | Other | Mylar | Tier 3 | RA | 14 | Elevated
2017 | 4 | 2017-10-22 | 10:22 | 10/22/17 10:22:00 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Rnch Snta Fe | P250055 Circuit 182 |  | Distribution | 12kV | Conductor | Overhead | Yes | 171022E134440 | 2017-10-22 | 10:22 | Contact From Object |  | Other | Electric Facility | Human Error | Other- Outside force/object | Tier 2 | NE | 15 | Extreme
2017 | 4 | 2017-10-25 | 13:02 | 10/25/17 13:02:00 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CALFIRE | P416197, Circuit 908 |  | Distribution | 12kV | Other | Overhead | No |  |  |  | Equipment/Facility Failure | Other |  |  | Weather | Other- Equip Failure | Tier 2 | NE | 14 | Elevated
2017 | 4 | 2017-12-10 | 5:26 | 12/10/17 05:26:00 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | P32240 |  | Distribution | 12kV | Conductor | Overhead | Yes | 171210E137763 | 2017-12-10 | 5:26 | Contact From Object |  | Vegetation | Electric Facility | Weather | Vegetation | Tier 3 | NE | 16 | Extreme
2018 | 1 | 2018-02-16 | 16:50 | 2/16/18 16:50:00 | 32.6276 | -116.9409 | Vegetation | Urban | Less Than .25 Acres | Utility |  | C-594 |  | Distribution | 12kV | Conductor | Overhead | Yes | 180216E143303 | 2018-02-16 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Outside Force | Mylar | Tier 2 | CM | 10 | Normal
2018 | 2 | 2018-05-22 | 14:23 | 5/22/18 14:23:00 | 33.362 | -117.032 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CALFIRE | P214790 Cir.217 |  | Distribution | 12kV | Conductor | Overhead | Yes | 180522E150424 | 2018-05-22 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | Mylar | Tier 3 | NE | 9 | Normal
2018 | 2 | 2018-06-12 | 9:00 | 6/12/18 09:00:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P44708 Cir. 458 |  | Distribution | 12kV | Conductor | Overhead | Yes | 180612E151825 | 2018-06-12 | 9:00 | Contact From Object |  | Animal | Electric Facility | None | Animal contact | Tier 3 | ME | 13 | Elevated
2018 | 2 | 2018-06-12 | 15:14 | 6/12/18 15:14:00 | 32.864 | -116.747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Fire Agency | P871937 Cir. 357 |  | Distribution | 12kV | Conductor | Overhead | Yes | 180612E151902 | 2018-06-12 | 14:38 | Contact from Object |  | Balloons | Electric Facility | None | Mylar | Tier 3 | EA | 13 | Elevated
2018 | 2 | 2018-06-22 | 9:46 | 6/22/18 09:46:00 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | SDFD | Z100698 Cir. 535 |  | Distribution | 12kV | Switch | Overhead | Yes | 180622E158931/180622E159690 | 2018-06-22 | 9:42 | Equipment/Facility Failure | Switch |  |  | Unknown | Other- Equip Failure | Tier 2 | CM | 11 | Normal
2018 | 3 | 2018-07-06 | 10:26 | 7/06/18 10:26:00 | 32.6203 | -116.7649 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CalFire | P177572, Station 157-825, C157 |  | Distribution | 12kV | Transformer | Overhead | No |  |  |  | Equipment/Facility Failure | Transformer |  |  |  | Other- Equip Failure | Tier 3 | ME | 15 | Extreme
2018 | 3 | 2018-08-19 | 18:35 | 8/19/18 18:35:00 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P254640 Cir 75 |  | Distribution | 12kV | Conductor | Overhead | Yes | 180819E157239 | 2018-07-19 | 18:35 | Contact From Object |  | Balloons | Electric Facility | Other | Mylar | Tier 3 | EA | 13 | Elevated
2018 | 3 | 2018-09-14 | 10:00 | 9/14/18 10:00:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | MVU & NCFPD | P213051 Cir 233 | Telecom/cable | Distribution | 12kV | Conductor | Overhead | No | 180913E159085 |  |  | Contact Between Third Party Facility on Pole and Supply Lines | Other | Vehicle | Communication Facility | Human Error | Vehicle contact | Tier 2 | NE | 13 | Elevated
2018 | 4 | 2018-10-15 | 10:21 | 10/15/18 10:21:00 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P112366 |  | Distribution | 12kV | Conductor | Overhead | Yes | 181015E161501 | 2018-10-15 | 12:02 | Equipment/Facility Failure | Conductor |  |  | None | Other- Equip Failure | Tier 2 | NE | 15 | Extreme
2018 | 4 | 2018-11-26 | 1:51 | 11/26/18 01:51:00 | 33.4314 | -117.5952 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | OCFA | P25325 |  | Distribution | 12kV | Conductor | Overhead | Yes | 181126E164092 | 2018-11-26 | 1:45 | Contact From Object |  | Balloons | Electric Facility |  | Mylar | Tier 2 | OC | 12 | Elevated
2019 | 2 | 2019-06-12 | 22:05 | 6/12/19 22:05:00 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CalFire | W100304 |  | Distribution | 12kV | Switch | Padmounted | Yes | 190612E178337 | 2019-06-12 | 22:17 | Contact From Object |  | Vehicle | Electric Facility | None | Vehicle contact | Tier 2 | RA | 11 | Normal
2019 | 3 | 2019-07-05 | 12:32 | 7/05/19 12:32:00 | 33.1584 | -117.222 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Marcos | P415472 |  | Distribution | 12kV | Conductor | Overhead | Yes | 190705E179972 | 2019-07-05 | 12:19 | Contact From Object |  | Vehicle | Pole | Human Error | Vehicle contact | Tier 2 | NC | 10 | Normal
2019 | 3 | 2019-07-16 | 19:08 | 7/16/19 19:08:00 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Deer Springs | P610712 | Telco | Distribution | 12kV | Conductor | Overhead | Yes | 190716E180726 | 2019-07-16 | 19:08 | Contact Between Third Party Facility on Pole and Supply Lines |  | Vegetation | Electric Facility | Other | Other- Outside force/object | Tier 2 | NE | 13 | Elevated
2019 | 3 | 2019-07-16 | 7:36 | 7/16/19 07:36:00 | 33.1675 | -117.1462 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Marcos | P114649 |  | Distribution | 12kV | Conductor | Overhead | Yes | 190716E180796 | 2019-07-16 | 7:53 | Wire-Wire Contact |  |  |  | Other | Animal contact | Tier 2 | NE | 13 | Elevated
2019 | 3 | 2019-09-10 | 12:59 | 9/10/19 12:59:00 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Diego | P194970 |  | Distribution | 12kV | Switch | Overhead | Yes | 190910E184807 | 2019-09-10 | 12:55 | Equipment/Facility Failure | Switch |  |  | None | Other- Equip Failure | Tier 2 | CM | 10 | Normal
2019 | 3 | 2019-09-11 | 14:17 | 9/11/19 14:17:00 | 33.226 | -117.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CalFire | P228412 |  | Distribution | 12kV | Lightning Arrestor | Overhead | Yes |  | 2019-09-11 | 14:17 | Contact From Object |  | Animal | Electric Facility | None | Animal contact | Tier 2 | NE | 12 | Elevated
2019 | 4 | 2019-10-24 |  | 10/24/19 00:00:00 | 32.8357 | -116.7252 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Alpine FD | P377113 | Telco | Distribution | 12kV | Fuse | Overhead | Yes | 191024E188493 | 2019-10-24 |  | Equipment/Facility Failure | Fuse |  |  | None | Other- Equip Failure | Tier 3 | ME | 14 | Elevated
2019 | 4 | 2019-10-25 |  | 10/25/19 00:00:00 | 33.1195 | -117.1628 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | CalFire | P211697 | Telco | Distribution | 12kV | Other | Overhead | Yes | 191025E188581 | 2019-10-25 |  | Equipment/Facility Failure | Other |  |  | Other | Other- Equip Failure | Tier 2 | NE | 15 | Extreme
2019 | 4 | 2019-11-04 | 15:30 | 11/04/19 15:30:00 | 33.1969 | -116.7121 | Vegetation | Rural | Less Than .25 Acres | Utility | CalFire | P19533 |  | Distribution | 12kV | Conductor | Overhead | Yes | 191104E189566 | 2019-11-04 | 15:30 | Equipment/Facility Failure | Other |  |  |  |  | Tier 3 | RA | 14 | Elevated
2020 | 1 | 2020-02-26 | 0:17 | 2/26/20 00:17:00 | 32.914 | -116.64 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Cal Fire | P972695 |  | Distribution | 12kV | Lightning Arrestor | Overhead | Yes | 200225E197752 | 2020-02-26 | 0:17 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Other- Equip Failure | Tier 3 | ME | 11 | Normal
2020 | 2 | 2020-05-17 | 8:52 | 5/17/20 08:52:00 | 33.2373 | -117.0301 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P515883 |  | Distribution | 12kV | Conductor | Overhead | Yes | 200517E204879 | 2020-05-17 | 8:52 | Contact From Object | Conductor | Balloons |  | Other | Mylar | Tier 2 | NE | 7 | Normal
2020 | 2 | 2020-06-02 | 18:00 | 6/02/20 18:00:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Cal Fire | P111476 |  | Distribution | 12kv | Conductor | Overhead | Yes | 200602E206273 | 2020-06-02 | 18:00 | Contact From Object |  | Vehicle | Pole | Human Error |  | Tier 3 | RA | 10 | Normal
2020 | 2 | 2020-06-03 | 11:17 | 6/03/20 11:17:00 | 33.1234 | -117.025 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Escondido | P714414 |  | Distribution | 12kv | Transformer | Overhead | Yes | 200603E206329 | 2020-06-03 | 11:17 | Contact From Object |  | Animal | Electric Facility | None |  | Tier 3 | NE | 10 | Normal
2020 | 3 | 2020-07-05 | 14:08 | 7/05/20 14:08:00 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SDFR, Cal Fire | P14263 | telco | Distribution | 12kV | Lightning Arrestor | Overhead | Yes | 200705E208873 | 2020-07-05 | 20:55 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown |  | Tier 3 | NE | 12 | Elevated
2020 | 3 | 2020-07-17 | 16:30 | 7/17/20 16:30:00 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P115116 | telco | Distribution | 12kV | Transformer | Overhead | Yes | 200717E209923 | 2020-07-17 |  | Contact From Object |  | Animal | Electric Facility | None |  | Tier 3 | RA | 13 | Elevated
2020 | 3 | 2020-07-29 | 17:14 | 7/29/20 17:14:00 | 32.737 | -116.875 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P678395 |  | Distribution | 12kV | Conductor | Overhead | Yes | 200729E211046 | 2020-07-29 | 17:12 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown |  | Tier 3 | EA | 12 | Elevated
2020 | 3 | 2020-08-01 | 11:11 | 8/01/20 11:11:00 | 32.631 | -116.174 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | P45248 |  | Distribution | 12kV | Other | Overhead | Yes | 200801E211347 | 2020-08-01 | 11:10 | Equipment/Facility Failure | Other |  |  | Unknown |  | Tier 2 | ME | 13 | Elevated
2020 | 3 | 2020-08-22 | 13:38 | 8/22/20 13:38:00 | 33.0744 | -116.5773 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P31591 |  | Distribution | Secondary | Conductor | Overhead | Yes |  | 2020-08-22 | 13:38 | Equipment/Facility Failure | Conductor |  |  | Unknown |  | Tier 3 | RA | 13 | Elevated
2020 | 3 | 2020-09-02 | 19:30 | 9/02/20 19:30:00 | 33.362 | -117.137 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P215301 |  | Distribution | 12kV | Conductor | Overhead | Yes | 200902E214085 | 2020-09-02 | 19:30 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None |  | Tier 3 | NE | 13 | Elevated
2020 | 3 | 2020-09-04 | 20:30 | 9/04/20 20:30:00 | 33.0658 | -116.8592 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P216155 | telco | Distribution | 12kV | Conductor | Overhead | Yes | 200904E214251 | 2020-09-04 | 20:30 | Contact From Object |  | Vehicle | Pole | Other |  | Tier 2 | RA | 14 | Elevated
2020 | 3 | 2020-09-12 | 5:30 | 9/12/20 05:30:00 | 33.1056 | -117.0002 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | P614833 |  | Distribution | 12kv | Lightning Arrestor | Overhead | Yes | 200912E214983 | 2020-09-12 | 5:30 | Equipment/Facility Failure | Lightning Arrestor |  |  | None |  | Tier 3 | NE | 14 | Elevated
2020 | 3 | 2020-09-12 | 7:00 | 9/12/20 07:00:00 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | P14263 |  | Distribution | 12kV | Capacitor Bank | Overhead | Yes | 200912E214983 | 2020-09-12 | 7:00 | Equipment/Facility Failure | Capacitor Bank |  |  | None |  | Tier 3 | NE | 14 | Elevated
2020 | 4 | 2020-10-14 | 15:05 | 10/14/20 15:05:00 | 33.027 | -116.889 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | P612927 | telco | Distribution | 12kv | Lightning Arrestor | Overhead | No |  |  |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown |  | Tier 2 | RA | 14 | Elevated
2020 | 4 | 2020-11-11 | 9:51 | 11/11/20 09:51:00 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CALFIRE | P270154 |  | Distribution | 12kv | Other | Overhead | Yes | 201111E220239 | 2020-11-11 |  | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown |  | Tier 3 | EA | 11 | Normal
2020 | 4 | 2020-11-30 | 9:10 | 11/30/20 09:10:00 | 33.266 | -117.223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | NCFPD | P161627 |  | Distribution | 12kV | Lightning Arrestor | Overhead | Yes | 201130E221367 | 2020-11-30 | 9:10 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown |  | Tier 2 | NE | 12 | Elevated
2020 | 4 | 2020-12-03 | 11:56 | 12/03/20 11:56:00 | 33.176 | -117.1541 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NCFPD | P194669 |  | Distribution | 12kV | Conductor | Overhead | Yes | 201203E223718 | 2020-12-03 | 11:56 | Equipment/Facility Failure | Pole |  |  | Weather |  | Tier 2 | NE | 15 | Extreme
2021 | 1 | 2021-02-28 | 1300.5833 | 2/28/21 14:00:00 | 33.437 | -117.569 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | P227391 |  | Distribution | 12kV | Transformer | Overhead | Yes | 210228E227563 | 2021-02-28 | 1300 | Contact From Object |  | Animal | Electric Facility | Outside Force | SP- Bird nesting material made phase to phase contact with transformer leads | Tier 2 | OC | 11 | Normal
2021 | 2 | 2021-05-07 | 13:10 | 5/07/21 13:10:00 | 33.338 | -117.154 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE/ NCFPD |  |  | Distribution | 12kv | Conductor | Overhead | Yes | 210507E233010 | 2021-05-07 | 1312 | Contact From Object |  | Other | Electric Facility | Outside Force |  | Tier 3 | NE | 8 | Normal
2021 | 2 | 2021-06-13 | 12:00 | 6/13/21 12:00:00 | 33.0265 | -116.858 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ramona CAL FIRE | P107449 |  | Distribution | 12kv | Conductor | Overhead | Yes | 210613E235545 | 2021-06-13 | 12:00 | Contact From Object |  | Balloons | Electric Facility | Other |  | Tier 2 | RA | 13 | Elevated
2021 | 2 | 2021-06-16 | 14:27 | 6/16/21 14:27:00 | 33.3483 | -116.7324 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P239535 |  | Distribution | 12kv | Switch | Overhead | Yes | 210616E235835 | 2021-06-16 | 14:27 | Equipment/Facility Failure | Switch |  |  | Unknown |  | Tier 3 | RA | 13 | Elevated
2021 | 2 | 2021-06-17 | 9:51 | 6/17/21 09:51:00 | 32.6037 | -116.6113 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P176917 |  | Distribution | 12kV | Conductor | Overhead | Yes | 210617E235879 | 2021-06-17 | 9:52 | Equipment/Facility Failure | Conductor |  |  | Unknown |  | Tier 3 | ME | 13 | Elevated
2021 | 3 | 2021-07-01 | 7:42 | 7/01/21 07:42:00 | 33.2806 | -117.1574 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE/ NCFPD | P119250 |  | Distribution | 12kV | Conductor | Overhead | Yes | 210701E236980 | 2007-01-21 | 7:42 | Vandalism/Theft | Conductor |  |  | Outside Force |  | Tier 2 | NE | 12 | Elevated
2021 | 3 | 2021-07-24 | 15:19 | 7/24/21 15:19:00 | 32.7058 | -116.7315 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FiRE/ USFS | P74739 |  | Distribution | 12kv | Other | Overhead | Yes | 210724E238722 | 2021-07-24 |  | Contact From Object |  | Animal | Electric Facility | Outside Force |  | Tier 3 | ME | 13 | Elevated
2021 | 3 | 2021-07-28 | 13:51 | 7/28/21 13:51:00 | 33.2282 | -116.983 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Z16445 |  | Distribution | 12kv | Conductor | Overhead | Yes |  | 2021-07-28 | 13:51 | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Human Error |  | Tier 2 | NE | 12 | Elevated
2021 | 3 | 2021-08-25 | 5:25 | 8/25/21 05:25:00 | 33.0827 | -116.9698 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Diego FD | P11679 |  | Distribution | 12kv | Conductor | Overhead | Yes | 210825E250245 | 2021-08-25 | 5:25 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other |  | Tier 3 | NE | 13 | Elevated
2021 | 4 | 2021-12-03 | 12:20 | 12/03/21 12:20:00 | 32.568 | -116.962 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Diego FD | P226534 |  | Distribution |  | Switch | Overhead | Yes | 211203E248190 | 2012-03-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Outside Force |  | Tier 2 | CM | 10 | Normal
2021 | 4 | 2021-12-06 | 14:13 | 12/06/21 14:13:00 | 32.6762 | -116.7286 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P372261 |  | Distribution | 12kV | Other | Overhead | Yes | 211206E248342 | 2012-06-21 | 14:13 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown |  | Tier 3 | ME | 12 | Elevated
Note on C1: Date the event started (Use MM/DD/YY when inputting dates)
Note on D1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on F1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Material involved in the initial fueling of the fire;
Note on I1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on J1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on K1: Is who suppressed the fire
Note on L1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on M1: Utility’s description of the pole and/or equipment involved.
Note on N1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on P1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on Q1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on R1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on S1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on U1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on V1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on W1: The suspected cause of the ignition;
Note on X1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on Y1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on Z1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AA1: Factors that contributed to the ignition;
Note on Z8: Rottenberg, Michael R:
Note on T90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is new SWP. 241047 is NRO
Note on T91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: THere are lot more steps into this SWP. 248219 has very few steps

## Outages
Cause | Cause Description | Circuit (Filtered)1 | Combined Date/Time1 | FPI | HFTD | Isolating Device | Occurrence | Outage ID | Ignition-Outage? | Outage OH/UG | Protective Device1 | Status | Disable Time | Status diff in Hr | Compare Device | New Struct ID | New Device | Device Operated | Result | SWP
304 | Animal contact | 222 | 2017-10-22 06:00 | Elevated | Tier 3 | 222-1364R | 2017-10-25 07:42 | 171025E134657 | #N/A | OH | 222-1364R | ENABLE | 2017-10-25 15:01 | 81.0133 | TRUE |  |  | Same Recloser | Success | 134657
304 | Animal contact | 222 | 2017-10-22 06:00 | Elevated | Tier 3 | 222-1364R | 2017-10-25 07:42 | 171025E134657 | #N/A | OH | 222-1370R | ENABLE | 2017-10-26 10:35 | 100.5772 | FALSE | #N/A | 222-1364R | Downstream Recloser | Success | 134657
304 | Animal contact | 222 | 2017-10-22 06:04 | Elevated | Tier 3 | 222-1364R | 2017-10-25 07:42 | 171025E134657 | #N/A | OH | 222-7R | ENABLE | 2017-10-25 15:06 | 81.0308 | FALSE | #N/A | 222-1364R | Downstream Recloser | Success | 134657
304 | Animal contact | 240 | 2019-10-23 01:19 | Elevated | Tier 2 | P73973 | 2019-11-01 10:11 | 191101E189371 | #N/A | OH | 240-1028R | ENABLE | 2019-11-01 12:57 | 227.6289 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 189371
304 | Animal contact | 240 | 2019-10-23 01:19 | Elevated | Tier 2 | P73973 | 2019-11-01 10:11 | 191101E189371 | #N/A | OH | 240-1095R | ENABLE | 2019-11-01 12:57 | 227.6347 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 189371
304 | Animal contact | 240 | 2019-10-23 01:19 | Elevated | Tier 2 | P73973 | 2019-11-01 10:11 | 191101E189371 | #N/A | OH | 240-1097R | ENABLE | 2019-11-01 12:57 | 227.6328 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 189371
502 | Arrester (lightning) failure | 1215 | 2017-10-22 05:53 | Elevated | Tier 3 | 1215-12R | 2017-10-25 13:22 | 171025E134715 | #N/A | OH | 1215-10R | ENABLE | 2017-10-26 10:30 | 100.6142 | FALSE | #N/A | 1215-12R | Downstream Recloser | Success | 134715
502 | Arrester (lightning) failure | 1215 | 2017-10-22 05:53 | Elevated | Tier 3 | 1215-12R | 2017-10-25 13:22 | 171025E134715 | #N/A | OH | 1215-12R | ENABLE | 2017-10-25 17:56 | 84.0486 | TRUE |  |  | Same Recloser | Success | 134715
315 | Balloon contact | 176 | 2019-11-16 17:54 | Elevated | Tier 3 | 176-26R | 2019-11-17 10:23 | 191117E190645 | #N/A | OH | 176-58R | ENABLE | 2019-11-17 13:15 | 19.3481 | FALSE | #N/A | #N/A | Downstream Recloser | Success | 190645
315 | Balloon contact | 176 | 2019-11-16 17:59 | Elevated | Tier 3 | 176-26R | 2019-11-17 10:23 | 191117E190645 | #N/A | OH | 176-26R | ENABLE | 2019-11-17 10:35 | 16.6039 | TRUE |  |  | Same Recloser | Success | 190645
315 | Balloon contact | 176 | 2019-11-16 17:59 | Elevated | Tier 3 | 176-26R | 2019-11-17 10:23 | 191117E190645 | #N/A | OH | 176-41R | ENABLE | 2019-11-17 10:34 | 16.5908 | FALSE | #N/A | #N/A | Downstream Recloser | Success | 190645
315 | Balloon contact | 236 | 2017-12-04 04:27 | Elevated | Tier 2 | P214879 | 2017-12-30 07:23 | 171230E138950 | #N/A | OH | 236-10R | ENABLE | 2018-01-02 15:32 | 707.0867 | FALSE | P214879 | #N/A | Downstream Structure | Downstream Fuse | 138950
315 | Balloon contact | 236 | 2017-12-29 10:57 | Elevated | Tier 2 | P214879 | 2017-12-30 07:23 | 171230E138950 | #N/A | OH | 236-38R | ENABLE | 2018-01-02 15:28 | 100.5258 | FALSE | P214879 | #N/A | Downstream Structure | Downstream Fuse | 138950
308 | Bird contact | 237 | 2019-10-10 01:48 | Extreme | Tier 2 | 237-17R | 2019-10-11 12:09 | 191011E187413 | #N/A | OH | 237-17R | ENABLE | 2019-10-11 12:32 | 34.7333 | TRUE |  |  | Same Recloser | Success | 187413
308 | Bird contact | 237 | 2019-10-10 01:49 | Extreme | Tier 2 | 237-17R | 2019-10-11 12:09 | 191011E187413 | #N/A | OH | 237-2R | ENABLE | 2019-10-11 12:28 | 34.6508 | FALSE | #N/A | 237-17R | Downstream Recloser | Success | 187413
308 | Bird contact | 237 | 2019-10-10 02:00 | Extreme | Tier 2 | 237-17R | 2019-10-11 12:09 | 191011E187413 | #N/A | OH | 237-30R | ENABLE | 2019-10-11 12:30 | 34.495 | FALSE | #N/A | 237-17R | Downstream Recloser | Success | 187413
308 | Bird contact | 237 | 2019-10-20 02:27 | Elevated | Tier 2 | 237-17R | 2019-10-21 13:57 | 191021E188157 | #N/A | OH | 237-17R | ENABLE | 2019-10-21 14:01 | 35.5633 | TRUE |  |  | Same Recloser | Success | 188157
308 | Bird contact | 237 | 2019-10-20 02:33 | Elevated | Tier 2 | 237-17R | 2019-10-21 13:57 | 191021E188157 | #N/A | OH | 237-30R | ENABLE | 2019-10-21 14:00 | 35.45 | FALSE | #N/A | 237-17R | Downstream Recloser | Success | 188157
308 | Bird contact | 237 | 2019-10-20 02:33 | Elevated | Tier 2 | 237-17R | 2019-10-21 13:57 | 191021E188157 | #N/A | OH | 237-2R | ENABLE | 2019-10-21 14:03 | 35.4903 | FALSE | #N/A | 237-17R | Downstream Recloser | Success | 188157
308 | Bird contact | 350 | 2020-09-28 01:57 | Elevated | Tier 2 | 350-2196R | 2020-09-29 16:25 | 200929E216478 | #N/A | OH | 350-2196R | ENABLE | 2020-09-29 16:43 | 38.7667 | TRUE |  |  | Same Recloser | Success | 216478
308 | Bird contact | 350 | 2020-09-28 01:58 | Elevated | Tier 2 | 350-2196R | 2020-09-29 16:25 | 200929E216478 | #N/A | OH | 350-41R | ENABLE | 2020-09-29 18:28 | 40.5 | FALSE | #N/A | 350-41R | Downstream Recloser | Success | 216478
308 | Bird contact | 445 | 2017-10-14 06:12 | Elevated | Tier 2 | P41153 | 2017-10-15 07:54 | 171015E133938 | #N/A | OH | 445-23R | ENABLE | 2017-10-18 10:36 | 100.3889 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 133938
308 | Bird contact | 524 | 2019-10-20 00:23 | Elevated | Tier 3 | P74609 | 2019-10-20 18:15 | 191020E188076 | #N/A | OH | 524-50R | ENABLE | 2019-11-01 12:51 | 300.4767 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188076
308 | Bird contact | 524 | 2019-10-20 00:23 | Elevated | Tier 3 | P74609 | 2019-10-27 18:03 | 191027E188704 | #N/A | OH | 524-50R | ENABLE | 2019-11-01 12:51 | 300.4767 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188704
308 | Bird contact | 524 | 2019-10-20 00:23 | Elevated | Tier 3 | P74609 | 2019-10-20 18:15 | 191020E188076 | #N/A | OH | 524-69R | ENABLE | 2019-10-27 09:51 | 177.4761 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188076
308 | Bird contact | 524 | 2019-10-20 16:11 | Elevated | Tier 3 | P74609 | 2019-10-20 18:15 | 191020E188076 | #N/A | OH | 524-46R | ENABLE | 2019-10-27 09:51 | 161.6758 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188076
308 | Bird contact | 524 | 2019-10-20 16:11 | Elevated | Tier 3 | P74609 | 2019-10-20 18:15 | 191020E188076 | #N/A | OH | 524-22R | ENABLE | 2019-10-20 19:20 | 3.1569 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188076
308 | Bird contact | 524 | 2019-10-20 16:13 | Elevated | Tier 3 | P74609 | 2019-10-20 18:15 | 191020E188076 | #N/A | OH | 524-27R | ENABLE | 2019-10-20 19:20 | 3.1236 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188076
308 | Bird contact | 524 | 2019-10-27 14:57 | Elevated | Tier 3 | P74609 | 2019-10-27 18:03 | 191027E188704 | #N/A | OH | 524-69R | ENABLE | 2019-10-29 16:07 | 49.1667 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188704
308 | Bird contact | 524 | 2019-10-27 14:57 | Elevated | Tier 3 | P74609 | 2019-10-27 18:03 | 191027E188704 | #N/A | OH | 524-46R | ENABLE | 2019-10-29 16:07 | 49.1664 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188704
308 | Bird contact | 524 | 2019-10-27 14:57 | Elevated | Tier 3 | P74609 | 2019-10-27 18:03 | 191027E188704 | #N/A | OH | 524-22R | ENABLE | 2019-10-29 16:07 | 49.1672 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188704
308 | Bird contact | 524 | 2019-10-27 15:00 | Elevated | Tier 3 | P74609 | 2019-10-27 18:03 | 191027E188704 | #N/A | OH | 524-27R | ENABLE | 2019-11-01 12:49 | 117.8061 | FALSE | P74609 | #N/A | Downstream Structure | Downstream Fuse | 188704
404 | Circ. Flashover/storm/high winds/undet. | 79 | 2017-10-09 03:21 | Elevated | Tier 3 | 79-679R | 2017-10-09 11:09 | 171009E133448 | #N/A | OH | 79-673R | ENABLE | 2017-10-09 15:06 | 11.7561 | FALSE | #N/A | 79-679R | Downstream Recloser | Success | 133448
404 | Circ. Flashover/storm/high winds/undet. | 79 | 2017-10-09 03:22 | Elevated | Tier 3 | 79-679R | 2017-10-09 11:09 | 171009E133448 | #N/A | OH | 79-685R | ENABLE | 2017-10-10 12:59 | 33.615 | FALSE | #N/A | 79-679R | Downstream Recloser | Success | 133448
404 | Circ. Flashover/storm/high winds/undet. | 79 | 2017-10-09 03:22 | Elevated | Tier 3 | 79-679R | 2017-10-09 11:09 | 171009E133448 | #N/A | OH | 79-679R | ENABLE | 2017-10-09 13:11 | 9.8156 | TRUE |  |  | Same Recloser | Success | 133448
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 03:02 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-678R | ENABLE | 2018-11-13 09:44 | 54.6944 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 03:02 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-650R | ENABLE | 2018-11-13 09:54 | 54.8608 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 03:02 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-680R | ENABLE | 2018-11-13 09:09 | 54.1117 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 03:03 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-628R | ENABLE | 2018-11-13 09:59 | 54.9361 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 03:03 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-638R | ENABLE | 2018-11-13 09:11 | 54.1475 | TRUE |  |  | Same Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 03:03 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-652R | ENABLE | 2018-11-13 09:52 | 54.8236 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 03:03 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-674R | ENABLE | 2018-11-13 10:00 | 54.9622 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 10:05 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-635R | ENABLE | 2018-11-13 09:10 | 47.0739 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 10:58 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-632R | ENABLE | 2018-11-13 09:56 | 46.9689 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 212 | 2018-11-11 10:59 | Extreme | Tier 2 | 212-638R | 2018-11-13 09:02 | 181113E163446 | #N/A | OH | 212-630R | ENABLE | 2018-11-13 09:57 | 46.9722 | FALSE | #N/A | 212-638R | Downstream Recloser | Success | 163446
404 | Circ. Flashover/storm/high winds/undet. | 220 | 2017-12-08 22:41 | Extreme | Tier 3 | 220-288R | 2017-12-10 08:28 | 171210E137773 | #N/A | OH | 220-288R | ENABLE | 2017-12-10 08:34 | 33.8736 | TRUE |  |  | Same Recloser | Success | 137773
404 | Circ. Flashover/storm/high winds/undet. | 220 | 2017-12-08 23:13 | Extreme | Tier 3 | 220-288R | 2017-12-10 08:28 | 171210E137773 | #N/A | OH | 220-294R | ENABLE | 2017-12-10 08:33 | 33.3436 | FALSE | #N/A | 220-288R | Downstream Recloser | Success | 137773
404 | Circ. Flashover/storm/high winds/undet. | 220 | 2017-12-08 23:15 | Extreme | Tier 3 | 220-288R | 2017-12-10 08:28 | 171210E137773 | #N/A | OH | 220-298R | ENABLE | 2017-12-10 08:35 | 33.3325 | FALSE | #N/A | 220-288R | Downstream Recloser | Success | 137773
404 | Circ. Flashover/storm/high winds/undet. | 230 | 2017-12-04 04:23 | Extreme | Tier 2 | Z219397 | 2017-12-07 13:55 | 171207E137629 | #N/A | OH | 230-4R | ENABLE | 2017-12-18 08:57 | 340.5647 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137629
404 | Circ. Flashover/storm/high winds/undet. | 237 | 2018-07-06 05:05 | Extreme | Tier 2 | 237-2R | 2018-07-06 19:13 | 180706E153817 | #N/A | OH | 237-2R | ENABLE | 2018-07-07 08:24 | 27.3081 | TRUE |  |  | Same Recloser | Success | 153817
404 | Circ. Flashover/storm/high winds/undet. | 357 | 2018-10-15 02:11 | Extreme | Tier 2 | 357-45R | 2018-10-15 11:38 | 181015E161499 | #N/A | OH | 357-1147R | ENABLE | 2018-10-15 15:56 | 13.7422 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 161499
404 | Circ. Flashover/storm/high winds/undet. | 441 | 2017-10-14 06:15 | Elevated | Tier 3 | 441-23R | 2017-10-14 09:58 | 171014E133915 | #N/A | OH | 441-23R | ENABLE | 2017-10-14 11:51 | 5.6083 | TRUE |  |  | Same Recloser | Success | 133915
404 | Circ. Flashover/storm/high winds/undet. | 441 | 2017-10-14 06:16 | Elevated | Tier 3 | 441-23R | 2017-10-14 09:58 | 171014E133915 | #N/A | OH | 441-25R | ENABLE | 2017-10-14 11:47 | 5.5281 | FALSE | #N/A | 441-23R | Downstream Recloser | Success | 133915
404 | Circ. Flashover/storm/high winds/undet. | 445 | 2018-07-06 05:02 | Extreme | Tier 2 | 445-23R | 2018-07-06 21:33 | 180706E153832 | #N/A | OH | 445-23R | ENABLE | 2018-07-07 01:14 | 20.1864 | TRUE |  |  | Same Recloser | Success | 153832
404 | Circ. Flashover/storm/high winds/undet. | 445 | 2018-07-07 01:14 | Elevated | Tier 2 | 445-23R | 2018-07-07 02:24 | 180706E153832 | #N/A | OH | 445-23R | ENABLE | 2018-07-07 02:32 | 1.3044 | TRUE |  |  | Same Recloser | Success | 153832
404 | Circ. Flashover/storm/high winds/undet. | 448 | 2017-12-04 03:53 | Extreme | Tier 3 | 448-9R | 2017-12-07 10:21 | 171207E137550 | #N/A | OH | 448-11R | ENABLE | 2017-12-07 10:36 | 78.7178 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 137550
404 | Circ. Flashover/storm/high winds/undet. | 448 | 2017-12-04 03:53 | Extreme | Tier 3 | 448-9R | 2017-12-07 10:21 | 171207E137550 | #N/A | OH | 448-19R | ENABLE | 2017-12-07 10:43 | 78.8275 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 137550
404 | Circ. Flashover/storm/high winds/undet. | 448 | 2017-12-04 03:53 | Extreme | Tier 3 | 448-9R | 2017-12-07 10:21 | 171207E137550 | #N/A | OH | 448-23R | ENABLE | 2017-12-07 10:41 | 78.7933 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 137550
404 | Circ. Flashover/storm/high winds/undet. | 448 | 2017-12-04 03:53 | Extreme | Tier 3 | 448-9R | 2017-12-07 10:21 | 171207E137550 | #N/A | OH | 448-9R | ENABLE | 2017-12-07 10:44 | 78.85 | TRUE |  |  | Same Recloser | Success | 137550
404 | Circ. Flashover/storm/high winds/undet. | 448 | 2017-12-04 03:55 | Extreme | Tier 3 | 448-9R | 2017-12-07 10:21 | 171207E137550 | #N/A | OH | 448-33R | ENABLE | 2017-12-07 11:19 | 79.3931 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 137550
404 | Circ. Flashover/storm/high winds/undet. | 448 | 2017-12-04 03:59 | Extreme | Tier 3 | 448-9R | 2017-12-07 10:21 | 171207E137550 | #N/A | OH | 448-13R | ENABLE | 2017-12-07 11:18 | 79.3192 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 137550
404 | Circ. Flashover/storm/high winds/undet. | 1215 | 2018-07-06 05:03 | Extreme | Tier 3 | 445-23R | 2018-07-06 21:33 | 180706E153832 | #N/A | OH | 1215-10R | ENABLE | 2018-07-07 08:22 | 27.3194 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 153832
404 | Circ. Flashover/storm/high winds/undet. | 1215 | 2018-07-06 05:03 | Extreme | Tier 3 | 445-23R | 2018-07-06 21:33 | 180706E153832 | #N/A | OH | 1215-12R | ENABLE | 2018-07-07 08:22 | 27.3194 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 153832
404 | Circ. Flashover/storm/high winds/undet. | 1233 | 2018-11-11 02:52 | Elevated | Tier 3 | 1233-259R | 2018-11-11 15:08 | 181111E163272 | #N/A | OH | 1233-259R | ENABLE | 2018-11-11 15:41 | 12.8119 | TRUE |  |  | Same Recloser | Success | 163272
404 | Circ. Flashover/storm/high winds/undet. | 1233 | 2018-11-11 02:52 | Elevated | Tier 3 | 1233-259R | 2018-11-11 15:08 | 181111E163272 | #N/A | OH | 1233-252R | ENABLE | 2018-11-11 15:46 | 12.9019 | FALSE | #N/A | 1233-259R | Downstream Recloser | Success | 163272
404 | Circ. Flashover/storm/high winds/undet. | 1234 | 2018-11-11 02:52 | Elevated | Tier 3 | 1234-3R | 2018-11-11 09:53 | 181111E163270 | #N/A | OH | 1234-3R | ENABLE | 2018-11-11 13:58 | 11.1028 | TRUE |  |  | Same Recloser | Success | 163270
402 | Circuit Flashover/fog/foreign object | 243 | 2017-12-04 03:57 | Extreme | Non-HFTD | P873179 | 2017-12-07 09:50 | 171207E137543 | #N/A | OH | 243-14R | ENABLE | 2017-12-27 10:51 | 558.8925 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137543
402 | Circuit Flashover/fog/foreign object | 536 | 2018-11-11 03:00 | Elevated | Tier 2 | 536-150R | 2018-11-13 06:40 | 181113E163402 | #N/A | OH | 536-150R | ENABLE | 2018-11-13 08:09 | 53.1375 | TRUE |  |  | Same Recloser | Success | 163402
510 | Conductor contact/wire slap | 79 | 2017-10-09 03:22 | Elevated | Tier 3 | 79-679R | 2017-10-10 12:45 | 171010E133579 | #N/A | OH | 79-685R | ENABLE | 2017-10-10 12:59 | 33.615 | FALSE | #N/A | 79-679R | Downstream Recloser | Success | 133579
510 | Conductor contact/wire slap | 79 | 2017-10-10 12:10 | Elevated | Tier 3 | 79-679R | 2017-10-10 12:45 | 171010E133579 | #N/A | OH | 79-673R | ENABLE | 2017-10-10 15:48 | 3.6383 | FALSE | #N/A | 79-679R | Downstream Recloser | Success | 133579
510 | Conductor contact/wire slap | 79 | 2017-10-10 12:10 | Elevated | Tier 3 | 79-679R | 2017-10-10 12:45 | 171010E133579 | #N/A | OH | 79-679R | ENABLE | 2017-10-10 12:52 | 0.69778 | TRUE |  |  | Same Recloser | Success | 133579
510 | Conductor contact/wire slap | 907 | 2018-11-11 02:49 | Extreme | Tier 3 | Z12871 | 2018-11-13 06:17 | 181113E163395 | #N/A | OH | 907-1716R | ENABLE | 2018-11-17 12:09 | 153.3361 | FALSE | Z12871 | #N/A | Downstream Structure | Downstream Fuse | 163395
510 | Conductor contact/wire slap | 907 | 2018-11-11 02:49 | Extreme | Tier 3 | Z12871 | 2018-11-13 06:17 | 181113E163395 | #N/A | OH | 907-1702R | ENABLE | 2018-11-17 12:10 | 153.3453 | FALSE | Z12871 | #N/A | Downstream Structure | Downstream Fuse | 163395
513 | Conductor failure/wire down | 448 | 2019-10-09 23:02 | Elevated | Tier 3 | 448-33R | 2019-10-10 09:22 | 191010E187219 | #N/A | OH | 448-37R | ENABLE | 2019-10-12 09:44 | 58.6992 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 187219
513 | Conductor failure/wire down | 448 | 2019-10-09 23:03 | Elevated | Tier 3 | 448-33R | 2019-10-10 09:22 | 191010E187219 | #N/A | OH | 448-9R | ENABLE | 2019-10-10 12:25 | 13.3797 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 187219
513 | Conductor failure/wire down | 448 | 2019-10-09 23:03 | Elevated | Tier 3 | 448-33R | 2019-10-10 09:22 | 191010E187219 | #N/A | OH | 448-11R | ENABLE | 2019-10-12 09:43 | 58.6661 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 187219
513 | Conductor failure/wire down | 448 | 2019-10-09 23:08 | Elevated | Tier 3 | 448-33R | 2019-10-10 09:22 | 191010E187219 | #N/A | OH | 448-33R | ENABLE | 2019-10-10 11:09 | 12.0206 | TRUE |  |  | Same Recloser | Success | 187219
513 | Conductor failure/wire down | 448 | 2019-10-09 23:08 | Elevated | Tier 3 | 448-33R | 2019-10-10 09:22 | 191010E187219 | #N/A | OH | 448-13R | ENABLE | 2019-10-10 09:26 | 10.2936 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 187219
513 | Conductor failure/wire down | 448 | 2019-10-09 23:08 | Elevated | Tier 3 | 448-33R | 2019-10-10 09:22 | 191010E187219 | #N/A | OH | 448-23R | ENABLE | 2019-10-10 09:27 | 10.3147 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 187219
513 | Conductor failure/wire down | 448 | 2019-10-09 23:08 | Elevated | Tier 3 | 448-33R | 2019-10-10 09:22 | 191010E187219 | #N/A | OH | 448-19R | ENABLE | 2019-10-10 09:28 | 10.3225 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 187219
554 | Crossarm failure | 73 | 2017-12-04 03:47 | Extreme | Tier 3 | Z272960 | 2017-12-06 15:51 | 171206E137429 | #N/A | OH | 73-23R | ENABLE | 2017-12-07 07:34 | 75.7908 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137429
554 | Crossarm failure | 79 | 2019-10-20 01:26 | Elevated | Tier 3 | 79-799R | 2019-10-20 10:26 | 191020E188061 | #N/A | OH | 79-714R | ENABLE | 2019-10-24 03:56 | 98.4939 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188061
554 | Crossarm failure | 79 | 2019-10-20 01:27 | Elevated | Tier 3 | 79-799R | 2019-10-20 10:26 | 191020E188061 | #N/A | OH | 79-676R | ENABLE | 2019-10-23 06:52 | 77.4178 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188061
554 | Crossarm failure | 79 | 2019-10-20 01:27 | Elevated | Tier 3 | 79-799R | 2019-10-20 10:26 | 191020E188061 | #N/A | OH | 79-658R | ENABLE | 2019-10-23 06:51 | 77.4047 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188061
554 | Crossarm failure | 79 | 2019-10-20 01:27 | Elevated | Tier 3 | 79-799R | 2019-10-20 10:26 | 191020E188061 | #N/A | OH | 79-685R | ENABLE | 2019-10-25 19:47 | 138.3403 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188061
554 | Crossarm failure | 79 | 2019-10-20 01:29 | Elevated | Tier 3 | 79-799R | 2019-10-20 10:26 | 191020E188061 | #N/A | OH | 79-660R | ENABLE | 2019-10-25 19:26 | 137.9506 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188061
554 | Crossarm failure | 79 | 2019-10-20 01:29 | Elevated | Tier 3 | 79-799R | 2019-10-20 10:26 | 191020E188061 | #N/A | OH | 79-668R | ENABLE | 2019-10-25 21:48 | 140.3044 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188061
554 | Crossarm failure | 214 | 2019-10-20 02:12 | Elevated | Tier 3 | P514970 | 2019-10-23 17:34 | 191023E188379 | #N/A | OH | 214-613R | ENABLE | 2019-10-24 16:54 | 110.7003 | FALSE | P514970 | #N/A | Downstream Structure | Downstream Fuse | 188379
554 | Crossarm failure | 214 | 2019-10-20 02:16 | Elevated | Tier 3 | P514970 | 2019-10-23 17:34 | 191023E188379 | #N/A | OH | 214-1122R | ENABLE | 2019-10-24 20:57 | 114.68 | FALSE | P514970 | #N/A | Downstream Structure | Downstream Fuse | 188379
554 | Crossarm failure | 214 | 2019-10-20 02:21 | Elevated | Tier 3 | P514970 | 2019-10-23 17:34 | 191023E188379 | #N/A | OH | 214-536R | ENABLE | 2019-10-24 17:03 | 110.6997 | FALSE | P514970 | #N/A | Downstream Structure | Downstream Fuse | 188379
554 | Crossarm failure | 214 | 2019-10-23 13:11 | Elevated | Tier 3 | P514970 | 2019-10-23 17:34 | 191023E188379 | #N/A | OH | 214-583R | ENABLE | 2019-10-24 17:01 | 27.8333 | FALSE | P514970 | #N/A | Downstream Structure | Downstream Fuse | 188379
554 | Crossarm failure | 524 | 2017-12-04 03:54 | Extreme | Tier 3 | P274957 | 2017-12-06 16:37 | 171206E137428 | #N/A | OH | 524-69R | ENABLE | 2017-12-12 11:16 | 199.3694 | FALSE | P274957 | #N/A | Downstream Structure | Downstream Fuse | 137428
554 | Crossarm failure | 524 | 2017-12-04 04:00 | Extreme | Tier 3 | P274957 | 2017-12-06 16:37 | 171206E137428 | #N/A | OH | 524-27R | ENABLE | 2017-12-27 10:42 | 558.7006 | FALSE | P274957 | #N/A | Downstream Structure | Downstream Fuse | 137428
554 | Crossarm failure | 1215 | 2017-09-01 17:46 | Elevated | Tier 3 | P46303 | 2017-09-02 09:33 | 170902E130459 | #N/A | OH | 1215-12R | ENABLE | 2017-09-02 12:15 | 18.4906 | FALSE | P46303 | #N/A | Downstream Structure | Downstream Fuse | 130459
554 | Crossarm failure | 1215 | 2017-09-01 17:49 | Elevated | Tier 3 | P46303 | 2017-09-02 09:33 | 170902E130459 | #N/A | OH | 1215-10R | ENABLE | 2017-09-02 12:15 | 18.4425 | FALSE | P46303 | #N/A | Downstream Structure | Downstream Fuse | 130459
518 | Cutout failure | 445 | 2018-10-15 02:11 | Extreme | Tier 2 | P41541 | 2018-10-15 07:08 | 181015E161463 | #N/A | OH | 445-23R | ENABLE | 2018-10-16 20:05 | 41.8992 | FALSE | P41541 | #N/A | Downstream Structure | Downstream Fuse | 161463
518 | Cutout failure | 445 | 2018-10-15 02:12 | Extreme | Tier 2 | P41541 | 2018-10-15 07:08 | 181015E161463 | #N/A | OH | 445-39R | ENABLE | 2018-10-15 12:28 | 10.2697 | FALSE | P41541 | #N/A | Downstream Structure | Downstream Fuse | 161463
518 | Cutout failure | 1243 | 2018-01-27 19:47 | Elevated | Tier 2 | P38955 | 2018-01-29 07:48 | 180129E141114 | #N/A | OH | 1243-45R | ENABLE | 2018-01-30 13:59 | 66.1939 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 141114
206 | Fire | 357 | 2018-07-06 05:04 | Extreme | Tier 2 | 357-45R | 2018-07-06 12:19 | 180706E153777 | #N/A | OH | 357-1147R | ENABLE | 2018-07-07 08:22 | 27.3061 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 153777
206 | Fire/Smoke | 67 | 2020-09-04 22:10 | Elevated | Tier 3 | 67-34R | 2020-09-06 12:20 | 200906E214453 | #N/A | Transmission OH | 67-45R | ENABLE | 2020-09-06 12:28 | 38.2889 | FALSE | #N/A | 67-34R | Downstream Recloser | Success | 214453
206 | Fire/Smoke | 67 | 2020-09-04 22:11 | Elevated | Tier 3 | 67-34R | 2020-09-06 12:20 | 200906E214453 | #N/A | Transmission OH | 67-37R | ENABLE | 2020-09-06 12:29 | 38.3 | FALSE | #N/A | 67-34R | Downstream Recloser | Success | 214453
206 | Fire/Smoke | 67 | 2020-09-04 22:13 | Elevated | Tier 3 | 67-34R | 2020-09-06 12:20 | 200906E214453 | #N/A | Transmission OH | 67-34R | ENABLE | 2020-09-06 12:26 | 38.2222 | TRUE |  |  | Same Recloser | Success | 214453
206 | Fire/Smoke | 67 | 2020-09-05 | Elevated | Tier 3 | 67-34R | 2020-09-06 12:20 | 200906E214453 | #N/A | Transmission OH | 67-24R | ENABLE | 2020-09-09 15:40 | 111.6667 | FALSE | #N/A | 67-34R | Downstream Recloser | Success | 214453
206 | Fire/Smoke | 73 | 2020-09-04 23:18 | Elevated | Tier 3 | 73-643R | 2020-09-05 15:20 | 200905E214290 | #N/A | OH | 73-643R | ENABLE | 2020-09-05 15:24 | 16.1 | TRUE |  |  | Same Recloser | Success | 214290
206 | Fire/Smoke | 79 | 2020-09-04 23:22 | Elevated | Tier 3 | 79-714R | 2020-09-06 12:20 | 200906E214458 | #N/A | Transmission OH | 79-714R | ENABLE | 2020-09-06 19:46 | 44.4053 | TRUE |  |  | Same Recloser | Success | 214458
206 | Fire/Smoke | 79 | 2020-09-04 23:24 | Elevated | Tier 3 | 79-714R | 2020-09-06 12:20 | 200906E214458 | #N/A | Transmission OH | 79-799R | ENABLE | 2020-09-08 20:57 | 93.55 | FALSE | #N/A | 79-714R | Downstream Recloser | Success | 214458
206 | Fire/Smoke | 79 | 2020-09-04 23:25 | Elevated | Tier 3 | 79-714R | 2020-09-06 12:20 | 200906E214458 | #N/A | Transmission OH | 79-685R | ENABLE | 2020-09-06 13:31 | 38.0944 | FALSE | #N/A | 79-714R | Downstream Recloser | Success | 214458
206 | Fire/Smoke | 79 | 2020-09-04 23:28 | Elevated | Tier 3 | 79-714R | 2020-09-06 12:20 | 200906E214458 | #N/A | Transmission OH | 79-668R | ENABLE | 2020-09-06 13:33 | 38.0778 | FALSE | #N/A | 79-714R | Downstream Recloser | Success | 214458
206 | Fire/Smoke | 79 | 2020-09-04 23:29 | Elevated | Tier 3 | 79-714R | 2020-09-06 12:20 | 200906E214458 | #N/A | Transmission OH | 79-660R | ENABLE | 2020-09-06 13:01 | 37.5389 | FALSE | #N/A | 79-714R | Downstream Recloser | Success | 214458
206 | Fire/Smoke | 356 | 2020-09-04 22:45 | Elevated | Tier 2 | 356-16R | 2020-09-06 12:20 | 200906E214452 | #N/A | Transmission OH | 356-19R | ENABLE | 2020-09-06 12:25 | 37.6667 | FALSE | #N/A | 356-16R | Downstream Recloser | Success | 214452
206 | Fire/Smoke | 356 | 2020-09-04 22:46 | Elevated | Tier 2 | 356-16R | 2020-09-06 12:20 | 200906E214452 | #N/A | Transmission OH | 356-16R | ENABLE | 2020-09-06 12:30 | 37.7333 | TRUE |  |  | Same Recloser | Success | 214452
206 | Fire/Smoke | 441 | 2020-09-04 23:34 | Elevated | Tier 3 | 441-23R | 2020-09-06 12:20 | 200906E214461 | #N/A | Transmission OH | 441-30R | ENABLE | 2020-09-06 17:58 | 42.4006 | FALSE | #N/A | 441-23R | Downstream Recloser | Success | 214461
206 | Fire/Smoke | 441 | 2020-09-04 23:35 | Elevated | Tier 3 | 441-23R | 2020-09-06 12:20 | 200906E214461 | #N/A | Transmission OH | 441-27R | ENABLE | 2020-09-06 17:55 | 42.3272 | FALSE | #N/A | 441-23R | Downstream Recloser | Success | 214461
206 | Fire/Smoke | 441 | 2020-09-04 23:36 | Elevated | Tier 3 | 441-23R | 2020-09-06 12:20 | 200906E214461 | #N/A | Transmission OH | 441-25R | ENABLE | 2020-09-10 13:16 | 133.6611 | FALSE | #N/A | 441-23R | Downstream Recloser | Success | 214461
206 | Fire/Smoke | 441 | 2020-09-04 23:37 | Elevated | Tier 3 | 441-23R | 2020-09-06 12:20 | 200906E214461 | #N/A | Transmission OH | 441-23R | ENABLE | 2020-09-06 15:13 | 39.6053 | TRUE |  |  | Same Recloser | Success | 214461
206 | Fire/Smoke | 448 | 2020-09-04 23:49 | Elevated | Tier 3 | 448-19R | 2020-09-06 12:21 | 200906E214454 | #N/A | Transmission OH | 448-23R | ENABLE | 2020-09-06 12:24 | 36.5833 | FALSE | #N/A | 448-13R | Downstream Recloser | Success | 214454
206 | Fire/Smoke | 448 | 2020-09-04 23:50 | Elevated | Tier 3 | 448-19R | 2020-09-06 12:21 | 200906E214454 | #N/A | Transmission OH | 448-19R | ENABLE | 2020-09-06 19:16 | 43.4333 | TRUE |  |  | Same Recloser | Success | 214454
206 | Fire/Smoke | 448 | 2020-09-04 23:50 | Elevated | Tier 3 | 448-19R | 2020-09-06 12:21 | 200906E214454 | #N/A | Transmission OH | 448-11R | ENABLE | 2020-09-06 12:29 | 36.65 | FALSE | #N/A | 448-13R | Downstream Recloser | Success | 214454
206 | Fire/Smoke | 448 | 2020-09-04 23:51 | Elevated | Tier 3 | 448-19R | 2020-09-06 12:21 | 200906E214454 | #N/A | Transmission OH | 448-13R | ENABLE | 2020-09-06 18:34 | 42.7222 | FALSE | #N/A | 448-13R | Downstream Recloser | Success | 214454
206 | Fire/Smoke | 449 | 2020-09-04 23:51 | Elevated | Tier 3 | 449-6R | 2020-09-06 12:20 | 200906E214463 | #N/A | Transmission OH | 449-6R | ENABLE | 2020-09-06 18:30 | 42.65 | TRUE |  |  | Same Recloser | Success | 214463
206 | Fire/Smoke | 449 | 2020-09-04 23:52 | Elevated | Tier 3 | 449-6R | 2020-09-06 12:20 | 200906E214463 | #N/A | Transmission OH | 449-16R | ENABLE | 2020-09-10 13:24 | 133.5333 | FALSE | #N/A | 449-6R | Downstream Recloser | Success | 214463
206 | Fire/Smoke | 449 | 2020-09-04 23:53 | Elevated | Tier 3 | 449-6R | 2020-09-06 12:20 | 200906E214463 | #N/A | Transmission OH | 449-13R | ENABLE | 2020-09-06 19:28 | 43.5833 | FALSE | #N/A | 449-6R | Downstream Recloser | Success | 214463
206 | Fire/Smoke | 524 | 2020-09-04 22:23 | Elevated | Tier 3 | 524-22R | 2020-09-05 19:58 | 200905E214339 | #N/A | OH | 524-69R | ENABLE | 2020-09-10 14:52 | 136.4889 | FALSE | #N/A | 524-22R | Downstream Recloser | Success | 214339
206 | Fire/Smoke | 524 | 2020-09-04 22:24 | Elevated | Tier 3 | 524-22R | 2020-09-05 19:58 | 200905E214339 | #N/A | OH | 524-50R | ENABLE | 2020-09-07 15:28 | 65.0611 | FALSE | #N/A | 524-22R | Downstream Recloser | Success | 214339
206 | Fire/Smoke | 524 | 2020-09-04 22:25 | Elevated | Tier 3 | 524-22R | 2020-09-05 19:58 | 200905E214339 | #N/A | OH | 524-46R | ENABLE | 2020-09-07 15:22 | 64.9506 | FALSE | #N/A | 524-22R | Downstream Recloser | Success | 214339
206 | Fire/Smoke | 524 | 2020-09-04 22:26 | Elevated | Tier 3 | 524-22R | 2020-09-05 19:58 | 200905E214339 | #N/A | OH | 524-27R | ENABLE | 2020-09-07 15:16 | 64.8444 | FALSE | #N/A | 524-22R | Downstream Recloser | Success | 214339
206 | Fire/Smoke | 524 | 2020-09-04 22:26 | Elevated | Tier 3 | 524-22R | 2020-09-05 19:58 | 200905E214339 | #N/A | OH | 524-22R | ENABLE | 2020-09-07 14:32 | 64.0944 | TRUE |  |  | Same Recloser | Success | 214339
206 | Fire/Smoke | 1166 | 2020-09-04 23:02 | Elevated | Tier 3 | 1166-18R | 2020-09-05 17:28 | 200905E214319 | #N/A | OH | 1166-18R | ENABLE | 2020-09-05 21:37 | 22.5889 | TRUE |  |  | Same Recloser | Success | 214319
206 | Fire/Smoke | 1166 | 2020-09-04 23:03 | Elevated | Tier 3 | 1166-18R | 2020-09-05 17:28 | 200905E214319 | #N/A | OH | 1166-15R | ENABLE | 2020-09-10 12:54 | 133.85 | FALSE | #N/A | 1166-18R | Downstream Recloser | Success | 214319
206 | Fire/Smoke | 1215 | 2020-09-04 23:53 | Elevated | Tier 3 | 1215-28R | 2020-09-06 12:20 | 200906E214462 | #N/A | Transmission OH | 1215-32R | ENABLE | 2020-09-07 00:23 | 48.5003 | FALSE | #N/A | 1215-12R | Downstream Recloser | Success | 214462
206 | Fire/Smoke | 1215 | 2020-09-04 23:54 | Elevated | Tier 3 | 1215-28R | 2020-09-06 12:20 | 200906E214462 | #N/A | Transmission OH | 1215-28R | ENABLE | 2020-09-06 23:33 | 47.6444 | TRUE |  |  | Same Recloser | Success | 214462
206 | Fire/Smoke | 1215 | 2020-09-04 23:55 | Elevated | Tier 3 | 1215-28R | 2020-09-06 12:20 | 200906E214462 | #N/A | Transmission OH | 1215-12R | ENABLE | 2020-09-06 19:18 | 43.3833 | FALSE | #N/A | 1215-12R | Downstream Recloser | Success | 214462
206 | Fire/Smoke | 1215 | 2020-09-04 23:55 | Elevated | Tier 3 | 1215-28R | 2020-09-06 12:20 | 200906E214462 | #N/A | Transmission OH | 1215-10R | ENABLE | 2020-09-07 00:30 | 48.5722 | FALSE | #N/A | 1215-12R | Downstream Recloser | Success | 214462
522 | Fuse - overload/inadequate size/fatigue | 221 | 2020-12-05 12:38 | Elevated | Tier 3 | P17908 | 2020-12-05 13:24 | 201205E222502 | #N/A | OH | 221-344R | ENABLE | 2020-12-10 00:29 | 107.8556 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 222502
522 | Fuse - overload/inadequate size/fatigue | 442 | 2020-04-01 11:24 | Elevated | Tier 3 | 442-2R | 2020-06-22 19:07 | 200622E207963 | #N/A | OH | 442-16R | ENABLE | 2020-08-20 08:54 | 3381.5028 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 207963
515 | OH connector failure (jumper/splice/squeeze-on) | 73 | 2018-11-14 15:39 | Extreme | Tier 3 | P876812 | 2018-11-14 23:10 | 181114E163684 | #N/A | OH | 73-49R | ENABLE | 2018-11-17 11:30 | 67.8556 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 163684
515 | OH connector failure (jumper/splice/squeeze-on) | 73 | 2018-11-14 15:40 | Extreme | Tier 3 | P876812 | 2018-11-14 23:10 | 181114E163684 | #N/A | OH | 73-14R | ENABLE | 2018-11-15 20:45 | 29.08 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 163684
515 | OH connector failure (jumper/splice/squeeze-on) | 73 | 2018-11-14 15:43 | Extreme | Tier 3 | P876812 | 2018-11-14 23:10 | 181114E163684 | #N/A | OH | 73-765R | ENABLE | 2018-11-17 11:32 | 67.8244 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 163684
515 | OH connector failure (jumper/splice/squeeze-on) | 73 | 2018-11-14 15:44 | Extreme | Tier 3 | P876812 | 2018-11-14 23:10 | 181114E163684 | #N/A | OH | 73-23R | ENABLE | 2018-11-17 11:33 | 67.8036 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 163684
515 | OH connector failure (jumper/splice/squeeze-on) | 470 | 2019-10-31 00:25 | Extreme | Tier 3 | P112397 | 2019-10-31 11:14 | 191031E189268 | #N/A | OH | 470-47R | ENABLE | 2019-10-31 13:40 | 13.2536 | FALSE | P112397 | #N/A | Downstream Structure | Downstream Fuse | 189268
515 | OH connector failure (jumper/splice/squeeze-on) | 1166 | 2019-09-24 17:47 | Normal | Tier 3 | P971976 | 2019-09-26 01:20 | 190926E186095 | #N/A | OH | 1166-18R | ENABLE | 2019-09-28 00:34 | 78.7781 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 186095
532 | Pole broke/rotted/on fire | 214 | 2019-10-20 02:12 | Elevated | Tier 3 | P617780 | 2019-10-23 10:42 | 191023E188298 | #N/A | OH | 214-613R | ENABLE | 2019-10-24 16:54 | 110.7003 | FALSE | P617780 | #N/A | Downstream Structure | Downstream Fuse | 188298
532 | Pole broke/rotted/on fire | 214 | 2019-10-20 02:16 | Elevated | Tier 3 | P617780 | 2019-10-23 10:42 | 191023E188298 | #N/A | OH | 214-1122R | ENABLE | 2019-10-24 20:57 | 114.68 | FALSE | P617780 | #N/A | Downstream Structure | Downstream Fuse | 188298
532 | Pole broke/rotted/on fire | 214 | 2019-10-20 02:21 | Elevated | Tier 3 | P617780 | 2019-10-23 10:42 | 191023E188298 | #N/A | OH | 214-536R | ENABLE | 2019-10-24 17:03 | 110.6997 | FALSE | P617780 | #N/A | Downstream Structure | Downstream Fuse | 188298
532 | Pole broke/rotted/on fire | 214 | 2019-10-26 11:47 | Elevated | Tier 3 | P617776 | 2019-10-29 12:44 | 191029E188799 | #N/A | OH | 214-536R | ENABLE | 2019-11-01 14:41 | 146.9022 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188799
532 | Pole broke/rotted/on fire | 214 | 2019-10-26 11:47 | Elevated | Tier 3 | P617776 | 2019-10-29 12:44 | 191029E188799 | #N/A | OH | 214-583R | ENABLE | 2019-10-29 13:57 | 74.1656 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188799
532 | Pole broke/rotted/on fire | 214 | 2019-10-26 11:47 | Elevated | Tier 3 | P617776 | 2019-10-29 12:44 | 191029E188799 | #N/A | OH | 214-613R | ENABLE | 2019-10-29 13:49 | 74.0364 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 188799
532 | Pole broke/rotted/on fire | 217 | 2017-12-04 04:21 | Extreme | Tier 2 | P319330 | 2017-12-06 17:30 | 171206E137424 | #N/A | OH | 217-835R | ENABLE | 2017-12-07 05:10 | 72.8136 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137424
532 | Pole broke/rotted/on fire | 217 | 2017-12-04 04:40 | Extreme | Tier 2 | P319330 | 2017-12-06 17:30 | 171206E137424 | #N/A | OH | 217-25R | ENABLE | 2017-12-08 13:42 | 105.0242 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137424
532 | Pole broke/rotted/on fire | 233 | 2017-12-04 04:45 | Extreme | Tier 2 | P614703 | 2017-12-10 12:10 | 171210E137741 | #N/A | OH | 233-41R | ENABLE | 2017-12-10 13:36 | 152.8525 | FALSE | P614703 | #N/A | Downstream Structure | Downstream Fuse | 137741
532 | Pole broke/rotted/on fire | 233 | 2017-12-14 11:55 | Elevated | Tier 2 | P109159 | 2017-12-18 09:18 | 171218E138163 | #N/A | OH | 233-41R | ENABLE | 2017-12-27 11:35 | 311.665 | FALSE | P109159 | #N/A | Downstream Structure | Downstream Fuse | 138163
532 | Pole broke/rotted/on fire | 233 | 2017-12-15 11:11 | Elevated | Tier 2 | P109159 | 2017-12-18 09:18 | 171218E138163 | #N/A | OH | 233-123R | ENABLE | 2017-12-27 11:33 | 288.3619 | FALSE | P109159 | #N/A | Downstream Structure | Downstream Fuse | 138163
532 | Pole broke/rotted/on fire | 524 | 2019-10-20 00:23 | Elevated | Tier 3 | P274763 | 2019-10-29 16:54 | 191029E188854 | #N/A | OH | 524-50R | ENABLE | 2019-11-01 12:51 | 300.4767 | FALSE | P274763 | #N/A | Downstream Structure | Downstream Fuse | 188854
532 | Pole broke/rotted/on fire | 524 | 2019-10-27 15:00 | Elevated | Tier 3 | P274763 | 2019-10-29 16:54 | 191029E188854 | #N/A | OH | 524-27R | ENABLE | 2019-11-01 12:49 | 117.8061 | FALSE | P274763 | #N/A | Downstream Structure | Downstream Fuse | 188854
532 | Pole broke/rotted/on fire | 599 | 2017-12-04 04:27 | Extreme | Tier 2 | P415996 | 2017-12-07 10:59 | 171207E137515 | #N/A | OH | 599-19R | ENABLE | 2017-12-15 10:10 | 269.7136 | FALSE | P415996 | #N/A | Downstream Structure | Downstream Fuse | 137515
532 | Pole broke/rotted/on fire | 1233 | 2017-12-04 04:29 | Extreme | Tier 3 | P238984 | 2017-12-06 16:39 | 171206E137426 | #N/A | OH | 1233-259R | ENABLE | 2017-12-06 17:09 | 60.6653 | FALSE | P238984 | #N/A | Downstream Structure | Downstream Fuse | 137426
532 | Pole broke/rotted/on fire | 1233 | 2017-12-04 04:50 | Extreme | Tier 3 | P238984 | 2017-12-06 16:39 | 171206E137426 | #N/A | OH | 1233-252R | ENABLE | 2017-12-06 17:09 | 60.3144 | FALSE | P238984 | #N/A | Downstream Structure | Downstream Fuse | 137426
534 | Pothead failure | 470 | 2018-11-11 02:41 | Extreme | Tier 3 | P512669J | 2018-11-13 10:51 | 181113E163481 | #N/A | OH | 470-47R | ENABLE | 2018-11-17 11:49 | 153.1411 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 163481
534 | Pothead failure | 908 | 2019-10-30 19:14 | Extreme | Tier 2 | P233588 | 2019-10-31 06:19 | 191031E189311 | #N/A | OH | 908-1236R | ENABLE | 2019-11-01 13:19 | 42.0736 | FALSE | P233588 | #N/A | Downstream Structure | Downstream Fuse | 189311
534 | Pothead failure | 908 | 2019-10-30 19:18 | Extreme | Tier 2 | P233588 | 2019-10-31 06:19 | 191031E189311 | #N/A | OH | 908-1172R | ENABLE | 2019-11-01 13:20 | 42.0361 | FALSE | P233588 | #N/A | Downstream Structure | Downstream Fuse | 189311
534 | Pothead failure | 908 | 2019-10-30 19:18 | Extreme | Tier 2 | P233588 | 2019-10-31 06:19 | 191031E189311 | #N/A | OH | 908-1201R | ENABLE | 2019-10-31 23:29 | 28.1744 | FALSE | P233588 | #N/A | Downstream Structure | Downstream Fuse | 189311
536 | Recloser/service restorer failure/contact | 233 | 2020-09-06 05:36 | Elevated | Tier 2 | 233-123R | 2020-09-06 16:54 | 200906E214500 | #N/A | OH | 233-41R | ENABLE | 2020-09-06 19:32 | 13.9283 | FALSE | #N/A | 233-41R | Downstream Recloser | Success | 214500
536 | Recloser/service restorer failure/contact | 233 | 2020-09-06 05:38 | Elevated | Tier 2 | 233-123R | 2020-09-06 16:54 | 200906E214500 | #N/A | OH | 233-123R | ENABLE | 2020-09-06 19:04 | 13.4333 | TRUE |  |  | Same Recloser | Success | 214500
612 | SDG&E crew error | 442 | 2020-04-01 11:24 | Elevated | Tier 3 | P478778J | 2020-08-11 20:17 | 200811E212120 | #N/A | OH | 442-16R | ENABLE | 2020-08-20 08:54 | 3381.5028 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 212120
544 | Switch faulted/mechanical | 788 | 2018-11-11 02:50 | Extreme | Non-HFTD | 788-34R | 2018-11-12 11:54 | 181112E163351 | #N/A | OH | 788-34R | ENABLE | 2018-11-12 12:10 | 33.3344 | TRUE |  |  | Same Recloser | Success | 163351
550 | Transformer (station) failure/contact | 239 | 2020-09-05 00:18 | Elevated | Tier 2 | D137730 | 2020-09-07 16:02 | 200907E214625 | #N/A | UG | 239-2144R | ENABLE | 2020-09-10 13:35 | 133.2839 | FALSE | D137730 | #N/A | Downstream Structure | Downstream Fuse | 214625
550 | Transformer faulted/mechanical | 78 | 2018-01-27 19:26 | Elevated | Tier 3 | 1458 | 2018-01-28 20:42 | 180128E141084 | #N/A | OH | 78-26R | ENABLE | 2018-01-30 13:38 | 66.1997 | FALSE | #N/A | #N/A | Recloser detected a fault and CB operated | NO Success | 141084
550 | Transformer faulted/mechanical | 235 | 2018-11-11 03:01 | Elevated | Tier 2 | 235-897R | 2018-11-17 02:31 | 181117E163806 | #N/A | OH | 235-899R | ENABLE | 2018-11-17 13:06 | 154.0819 | FALSE | #N/A | 235-897R | Downstream Recloser | Success | 163806
550 | Transformer faulted/mechanical | 235 | 2018-11-11 03:04 | Elevated | Tier 2 | 235-897R | 2018-11-17 02:31 | 181117E163806 | #N/A | OH | 235-897R | ENABLE | 2018-11-17 07:24 | 148.3353 | TRUE |  |  | Same Recloser | Success | 163806
550 | Transformer faulted/mechanical | 445 | 2017-09-01 07:57 | Extreme | Tier 2 | 445-23R | 2017-09-01 14:20 | 170901E130417 | #N/A | OH | 445-23R | ENABLE | 2017-09-01 16:54 | 8.9408 | TRUE |  |  | Same Recloser | Success | 130417
550 | Transformer faulted/mechanical | 470 | 2019-10-10 00:22 | Extreme | Non-HFTD | Z16604 | 2019-10-11 10:24 | 191011E187383 | #N/A | OH | 470-47R | ENABLE | 2019-10-11 12:16 | 35.8983 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 187383
550 | Transformer faulted/mechanical | 859 | 2018-11-11 02:27 | Extreme | Tier 2 | 859-42R | 2018-11-12 13:09 | 181112E163361 | #N/A | OH | 859-42R | ENABLE | 2018-11-12 14:54 | 36.445 | TRUE |  |  | Same Recloser | Success | 163361
550 | Transformer faulted/mechanical | 971 | 2019-10-20 02:35 | Extreme | Tier 3 | P714076 | 2019-10-30 09:40 | 191030E189097 | #N/A | OH | 971-29R | ENABLE | 2019-11-01 14:54 | 300.3167 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 189097
550 | Transformer faulted/mechanical | 971 | 2019-10-25 18:05 | Extreme | Tier 3 | P714076 | 2019-10-30 09:40 | 191030E189097 | #N/A | OH | 971-379R | ENABLE | 2019-11-01 11:09 | 161.0692 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 189097
550 | Transformer faulted/mechanical | 1215 | 2017-09-01 07:57 | Extreme | Tier 2 | 445-23R | 2017-09-01 14:20 | 170901E130417 | #N/A | OH | 1215-10R | ENABLE | 2017-09-01 17:49 | 9.8544 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 130417
550 | Transformer faulted/mechanical | 1215 | 2017-09-01 07:57 | Extreme | Tier 2 | 445-23R | 2017-09-01 14:20 | 170901E130417 | #N/A | OH | 1215-12R | ENABLE | 2017-09-01 17:45 | 9.7942 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 130417
318 | Tree contact due to growth/encroachment | 75 | 2020-09-04 22:18 | Elevated | Tier 3 | 75-32R | 2020-09-05 14:42 | 200905E214281 | #N/A | OH | 75-996R | ENABLE | 2020-09-10 12:43 | 134.4111 | FALSE | #N/A | 75-32R | Downstream Recloser | Success | 214281
318 | Tree contact due to growth/encroachment | 75 | 2020-09-04 22:19 | Elevated | Tier 3 | 75-32R | 2020-09-05 14:42 | 200905E214281 | #N/A | OH | 75-32R | ENABLE | 2020-09-06 16:20 | 42.0111 | TRUE |  |  | Same Recloser | Success | 214281
318 | Tree contact due to growth/encroachment | 75 | 2020-09-04 22:21 | Elevated | Tier 3 | 75-32R | 2020-09-05 14:42 | 200905E214281 | #N/A | OH | 75-1589R | ENABLE | 2020-09-05 14:52 | 16.5111 | FALSE | #N/A | 75-32R | Downstream Recloser | Success | 214281
420 | Tree contact due to storm/high wind | 236 | 2018-11-11 03:01 | Extreme | Tier 2 | P117488 | 2018-11-13 09:52 | 181113E163463 | #N/A | OH | 236-38R | ENABLE | 2018-11-17 13:09 | 154.1311 | FALSE | P117488 | #N/A | Downstream Structure | Downstream Fuse | 163463
420 | Tree contact due to storm/high wind | 236 | 2018-11-11 03:03 | Extreme | Tier 2 | P117488 | 2018-11-13 09:52 | 181113E163463 | #N/A | OH | 236-10R | ENABLE | 2018-11-13 13:56 | 58.8872 | FALSE | P117488 | #N/A | Downstream Structure | Downstream Fuse | 163463
420 | Tree contact due to storm/high wind | 972 | 2018-11-11 02:55 | Extreme | Tier 2 | 972-32R | 2018-11-12 08:03 | 181112E163325 | #N/A | OH | 972-32R | ENABLE | 2018-11-12 15:44 | 36.8192 | TRUE |  |  | Same Recloser | Success | 163325
420 | Tree contact due to storm/high wind | 972 | 2018-11-11 02:55 | Extreme | Tier 2 | 972-32R | 2018-11-12 08:03 | 181112E163325 | #N/A | OH | 972-26R | ENABLE | 2018-11-12 11:09 | 32.2369 | FALSE | #N/A | 972-26R | Downstream Recloser | Success | 163325
420 | Tree contact due to storm/high wind | 1001 | 2018-11-13 00:08 | Extreme | Non-HFTD | 1001-1140R | 2018-11-13 05:33 | 181113E163393 | #N/A | OH | 1001-1130R | ENABLE | 2018-11-13 05:42 | 5.565 | FALSE | #N/A | 1001-1130R | Downstream Recloser | Success | 163393
420 | Tree contact due to storm/high wind | 1001 | 2018-11-13 00:08 | Extreme | Non-HFTD | 1001-1140R | 2018-11-13 05:33 | 181113E163393 | #N/A | OH | 1001-1140R | ENABLE | 2018-11-13 05:41 | 5.5456 | TRUE |  |  | Same Recloser | Success | 163393
322 | Tree fell on line | 307 | 2019-10-23 22:35 | Elevated | Non-HFTD | 307-234R | 2019-10-24 16:43 | 191024E188539 | #N/A | OH | 307-234R | ENABLE | 2019-10-24 16:50 | 18.2508 | TRUE |  |  | Same Recloser | Success | 188539
322 | Tree fell on line | 1166 | 2019-10-05 10:36 | Elevated | Tier 3 | Z272890 | 2019-10-06 13:28 | 191006E186894 | #N/A | OH | 1166-18R | ENABLE | 2019-10-07 06:51 | 44.2436 | FALSE | Z272890 | #N/A | Downstream Structure | Downstream Fuse | 186894
426 | Tree fell on line due to storm/wind | 236 | 2017-12-04 04:24 | Extreme | Tier 2 | P312345 | 2017-12-07 09:37 | 171207E137542 | #N/A | OH | 236-38R | ENABLE | 2017-12-29 09:34 | 605.1619 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137542
426 | Tree fell on line due to storm/wind | 305 | 2018-11-11 02:21 | Extreme | Non-HFTD | 305-32R | 2018-11-13 07:29 | 181113E163412 | #N/A | OH | 305-32R | ENABLE | 2018-11-13 23:19 | 68.9567 | TRUE |  |  | Same Recloser | Success | 163412
426 | Tree fell on line due to storm/wind | 305 | 2018-11-11 02:21 | Extreme | Non-HFTD | 305-32R | 2018-11-13 07:29 | 181113E163412 | #N/A | OH | 305-35R | ENABLE | 2018-11-13 23:18 | 68.9378 | FALSE | #N/A | 305-32R | Downstream Recloser | Success | 163412
100 | Undetermined | 176 | 2018-01-27 19:41 | Elevated | Tier 2 | P316966 | 2018-01-29 00:43 | 180129E141092 | #N/A | OH | 176-26R | ENABLE | 2018-01-29 09:43 | 38.0219 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 141092
100 | Undetermined | 176 | 2018-01-27 19:41 | Elevated | Tier 3 | 176-26R | 2018-01-29 00:22 | 180129E141091 | #N/A | OH | 176-26R | ENABLE | 2018-01-29 09:43 | 38.0219 | TRUE |  |  | Same Recloser | Success | 141091
100 | Undetermined | 198 | 2019-10-17 09:26 | Normal | Non-HFTD | P138697 | 2019-10-19 14:27 | 191019E188058 | #N/A | UG | 198-37R | ENABLE | 2019-10-19 15:48 | 54.3697 | FALSE | P138697 | #N/A | Downstream Structure | Downstream Fuse | 188058
100 | Undetermined | 206 | 2019-10-23 21:54 | Elevated | Non-HFTD | 206-953R | 2019-10-24 00:10 | 191024E188394 | #N/A | OH | 206-953R | ENABLE | 2019-10-24 00:18 | 2.3981 | TRUE |  |  | Same Recloser | Success | 188394
100 | Undetermined | 211 | 2020-12-04 11:08 | Elevated | Tier 2 | P312016 | 2020-12-05 16:30 | 201205E221901 | #N/A | OH | 211-279R | ENABLE | 2020-12-07 23:06 | 83.9722 | FALSE | P312016 | #N/A | Downstream Structure | Downstream Fuse | 221901
100 | Undetermined | 211 | 2020-12-04 11:08 | Elevated | Tier 2 | P312016 | 2020-12-05 16:30 | 201205E221901 | #N/A | OH | 211-280R | ENABLE | 2020-12-07 23:11 | 84.0436 | FALSE | P312016 | #N/A | Downstream Structure | Downstream Fuse | 221901
100 | Undetermined | 217 | 2017-10-22 06:02 | Extreme | Tier 2 | 217-835R | 2017-10-24 12:34 | 171024E134614 | #N/A | OH | 217-835R | ENABLE | 2017-10-24 16:02 | 58.0022 | TRUE |  |  | Same Recloser | Success | 134614
100 | Undetermined | 217 | 2020-09-28 00:01 | Elevated | Tier 2 | 217-972R | 2020-09-28 16:16 | 200928E216362 | #N/A | OH | 217-983R | ENABLE | 2020-09-28 16:24 | 16.3889 | FALSE | #N/A | 217-837R | Downstream Recloser | Success | 216362
100 | Undetermined | 217 | 2020-09-28 00:01 | Elevated | Tier 2 | 217-972R | 2020-09-28 16:16 | 200928E216362 | #N/A | OH | 217-835R | ENABLE | 2020-09-28 16:24 | 16.3722 | FALSE | #N/A | 217-837R | Downstream Recloser | Success | 216362
100 | Undetermined | 217 | 2020-09-28 00:01 | Elevated | Tier 2 | 217-972R | 2020-09-28 16:16 | 200928E216362 | #N/A | OH | 217-837R | ENABLE | 2020-09-28 16:28 | 16.4444 | FALSE | #N/A | 217-837R | Downstream Recloser | Success | 216362
100 | Undetermined | 217 | 2020-09-28 01:54 | Elevated | Tier 2 | 217-972R | 2020-09-28 16:16 | 200928E216362 | #N/A | OH | 217-972R | ENABLE | 2020-09-28 16:27 | 14.5611 | TRUE |  |  | Same Recloser | Success | 216362
100 | Undetermined | 221 | 2019-10-20 02:53 | Elevated | Tier 3 | 221-31R | 2019-10-22 11:57 | 191022E188270 | #N/A | OH | 221-344R | ENABLE | 2019-10-22 12:03 | 57.1556 | FALSE | #N/A | 221-31R | Downstream Recloser | Success | 188270
100 | Undetermined | 221 | 2019-10-20 02:56 | Elevated | Tier 3 | 221-31R | 2019-10-22 11:57 | 191022E188270 | #N/A | OH | 221-19R | ENABLE | 2019-10-22 12:09 | 57.2244 | FALSE | #N/A | 221-31R | Downstream Recloser | Success | 188270
100 | Undetermined | 221 | 2019-10-20 14:44 | Elevated | Tier 3 | 221-31R | 2019-10-22 11:57 | 191022E188270 | #N/A | OH | 221-31R | ENABLE | 2019-10-22 12:02 | 45.2975 | TRUE |  |  | Same Recloser | Success | 188270
100 | Undetermined | 222 | 2017-12-11 15:51 | Elevated | Tier 3 | P619905 | 2018-01-02 05:01 | 180102E138963 | #N/A | UG | 222-1433R | ENABLE | 2018-01-02 15:28 | 527.6128 | FALSE | P619905 | #N/A | Downstream Structure | Downstream Fuse | 138963
100 | Undetermined | 222 | 2017-12-11 15:51 | Elevated | Tier 3 | P619905 | 2018-01-02 05:01 | 180102E138963 | #N/A | UG | 222-1441R | ENABLE | 2018-01-02 15:28 | 527.6083 | FALSE | P619905 | #N/A | Downstream Structure | Downstream Fuse | 138963
100 | Undetermined | 222 | 2017-12-11 15:54 | Elevated | Tier 3 | P619905 | 2018-01-02 05:01 | 180102E138963 | #N/A | UG | 222-7R | ENABLE | 2018-01-02 15:33 | 527.6464 | FALSE | P619905 | #N/A | Downstream Structure | Downstream Fuse | 138963
100 | Undetermined | 222 | 2017-12-17 17:06 | Elevated | Tier 3 | P619905 | 2018-01-02 05:01 | 180102E138963 | #N/A | UG | 222-1364R | ENABLE | 2018-01-02 10:27 | 377.3583 | FALSE | P619905 | #N/A | Downstream Structure | Downstream Fuse | 138963
100 | Undetermined | 222 | 2017-12-20 14:28 | Elevated | Tier 3 | P619905 | 2018-01-02 05:01 | 180102E138963 | #N/A | UG | 222-1401R | ENABLE | 2018-01-02 15:28 | 312.9969 | FALSE | P619905 | #N/A | Downstream Structure | Downstream Fuse | 138963
100 | Undetermined | 222 | 2017-12-20 14:28 | Elevated | Tier 3 | P619905 | 2018-01-02 05:01 | 180102E138963 | #N/A | UG | 222-1370R | ENABLE | 2018-01-02 15:28 | 312.9922 | FALSE | P619905 | #N/A | Downstream Structure | Downstream Fuse | 138963
100 | Undetermined | 236 | 2015-09-18 11:56 | Elevated | Tier 2 | 236-10R | 2015-09-20 17:34 | 150920E79127 | #N/A | OH | 236-10R | ENABLE | 2015-12-01 07:55 | 1771.9853 | TRUE |  |  | Same Recloser | Success | 79127
100 | Undetermined | 236 | 2015-09-18 11:56 | Elevated | Tier 2 | 236-10R | 2015-09-20 19:54 | 150920E79127 | #N/A | OH | 236-10R | ENABLE | 2015-12-01 07:55 | 1771.9853 | TRUE |  |  | Same Recloser | Success | 79127
100 | Undetermined | 236 | 2015-09-18 11:56 | Elevated | Tier 2 | 236-10R | 2015-09-20 20:43 | 150920E79127 | #N/A | OH | 236-10R | ENABLE | 2015-12-01 07:55 | 1771.9853 | TRUE |  |  | Same Recloser | Success | 79127
100 | Undetermined | 237 | 2018-07-06 05:05 | Extreme | Tier 3 | P317990 | 2018-07-06 23:58 | 180706E153845 | #N/A | OH | 237-2R | ENABLE | 2018-07-07 08:24 | 27.3081 | FALSE | P317990 | #N/A | Downstream Structure | Downstream Fuse | 153845
100 | Undetermined | 239 | 2020-12-02 16:22 | Elevated | Tier 3 | 239-89R | 2020-12-09 09:21 | 201209E222143 | #N/A | OH | 239-2144R | ENABLE | 2020-12-09 09:30 | 161.1392 | FALSE | #N/A | 239-89R | Downstream Recloser | Success | 222143
100 | Undetermined | 239 | 2020-12-06 10:45 | Elevated | Tier 3 | 239-89R | 2020-12-09 09:21 | 201209E222143 | #N/A | OH | 239-89R | ENABLE | 2020-12-09 09:32 | 70.7889 | TRUE |  |  | Same Recloser | Success | 222143
100 | Undetermined | 243 | 2020-09-28 01:24 | Elevated | Non-HFTD | 243-14R | 2020-09-29 17:22 | 200929E216483 | #N/A | OH | 243-14R | ENABLE | 2020-09-29 17:23 | 39.9722 | TRUE |  |  | Same Recloser | Success | 216483
100 | Undetermined | 350 | 2017-12-04 04:24 | Elevated | Tier 2 | 350-33R | 2017-12-04 08:25 | 171204E137207 | #N/A | OH | 350-41R | ENABLE | 2017-12-04 11:42 | 7.2914 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137207
100 | Undetermined | 350 | 2017-12-04 04:25 | Elevated | Tier 2 | 350-33R | 2017-12-04 08:25 | 171204E137207 | #N/A | OH | 350-33R | ENABLE | 2017-12-04 10:59 | 6.5808 | TRUE |  |  | Same Recloser | Success | 137207
100 | Undetermined | 350 | 2017-12-04 04:25 | Elevated | Tier 2 | 350-33R | 2017-12-04 08:25 | 171204E137207 | #N/A | OH | 350-46R | ENABLE | 2017-12-04 11:43 | 7.3022 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137207
100 | Undetermined | 350 | 2017-12-04 04:27 | Elevated | Tier 2 | 350-33R | 2017-12-04 08:25 | 171204E137207 | #N/A | OH | 350-15R | ENABLE | 2017-12-04 11:44 | 7.2786 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137207
100 | Undetermined | 350 | 2017-12-04 04:28 | Elevated | Tier 2 | 350-33R | 2017-12-04 08:25 | 171204E137207 | #N/A | OH | 350-684R | ENABLE | 2017-12-04 11:44 | 7.2642 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 137207
100 | Undetermined | 442 | 2020-04-01 11:24 | Normal | Tier 3 | 442-2R | 2020-05-06 14:01 | 200506E203868 | #N/A | OH | 442-16R | ENABLE | 2020-08-20 08:54 | 3381.5028 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 203868
100 | Undetermined | 445 | 2017-12-11 11:33 | Elevated | Tier 2 | 445-24R | 2017-12-11 11:41 | 171211E137860 | #N/A | OH | 445-39R | ENABLE | 2017-12-11 14:30 | 2.9486 | FALSE | #N/A | 445-24R | Downstream Recloser | Success | 137860
100 | Undetermined | 445 | 2017-12-11 11:34 | Elevated | Tier 2 | 445-24R | 2017-12-11 11:41 | 171211E137860 | #N/A | OH | 445-23R | ENABLE | 2017-12-11 14:33 | 2.9925 | FALSE | #N/A | 445-24R | Downstream Recloser | Success | 137860
100 | Undetermined | 445 | 2017-12-11 11:34 | Elevated | Tier 2 | 445-24R | 2017-12-11 11:41 | 171211E137860 | #N/A | OH | 445-24R | ENABLE | 2017-12-11 14:35 | 3.0117 | TRUE |  |  | Same Recloser | Success | 137860
100 | Undetermined | 445 | 2018-10-31 00:41 | Elevated | Tier 2 | P45697 | 2018-10-31 04:39 | 181031E162599 | #N/A | OH | 445-23R | ENABLE | 2018-10-31 17:11 | 16.5111 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 162599
100 | Undetermined | 445 | 2020-09-08 12:28 | Extreme | Tier 2 | 445-24R | 2020-09-09 08:24 | 200909E214739 | #N/A | OH | 445-24R | ENABLE | 2020-09-09 08:30 | 20.0275 | TRUE |  |  | Same Recloser | Success | 214739
100 | Undetermined | 445 | 2020-09-08 12:30 | Extreme | Tier 2 | 445-24R | 2020-09-09 08:24 | 200909E214739 | #N/A | OH | 445-19R | ENABLE | 2020-09-10 07:20 | 42.8272 | FALSE | #N/A | 445-24R | Downstream Recloser | Success | 214739
100 | Undetermined | 445 | 2020-09-08 12:35 | Extreme | Tier 2 | 445-24R | 2020-09-09 08:24 | 200909E214739 | #N/A | OH | 445-17R | ENABLE | 2020-09-10 07:21 | 42.7667 | FALSE | #N/A | 445-24R | Downstream Recloser | Success | 214739
100 | Undetermined | 450 | 2017-12-04 04:25 | Elevated | Non-HFTD | 450 | 2017-12-17 03:36 | 171217E138258 | #N/A | OH | 450-50R | ENABLE | 2017-12-27 11:57 | 559.5311 | FALSE | #N/A | #N/A | Recloser detected a fault and CB operated | NO Success | 138258
100 | Undetermined | 520 | 2017-12-20 15:49 | Elevated | Tier 3 | P119022 | 2017-12-23 17:37 | 171223E138564 | #N/A | OH | 520-18R | ENABLE | 2017-12-27 11:58 | 164.1447 | FALSE | P119022 | #N/A | Downstream Structure | Downstream Fuse | 138564
100 | Undetermined | 520 | 2017-12-20 15:49 | Elevated | Tier 3 | P119022 | 2017-12-23 17:37 | 171223E138564 | #N/A | OH | 520-33R | ENABLE | 2017-12-27 11:58 | 164.1467 | FALSE | P119022 | #N/A | Downstream Structure | Downstream Fuse | 138564
100 | Undetermined | 520 | 2017-12-23 14:04 | Elevated | Tier 3 | P119022 | 2017-12-23 17:37 | 171223E138564 | #N/A | OH | 520-26R | ENABLE | 2017-12-27 11:58 | 93.8933 | FALSE | P119022 | #N/A | Downstream Structure | Downstream Fuse | 138564
100 | Undetermined | 520 | 2017-12-23 14:05 | Elevated | Tier 3 | P119022 | 2017-12-23 17:37 | 171223E138564 | #N/A | OH | 520-10R | ENABLE | 2017-12-27 11:58 | 93.8814 | FALSE | P119022 | #N/A | Downstream Structure | Downstream Fuse | 138564
100 | Undetermined | 520 | 2017-12-23 14:05 | Elevated | Tier 3 | P119022 | 2017-12-23 17:37 | 171223E138564 | #N/A | OH | 520-22R | ENABLE | 2017-12-27 11:58 | 93.8844 | FALSE | P119022 | #N/A | Downstream Structure | Downstream Fuse | 138564
100 | Undetermined | 520 | 2020-12-05 12:06 | Elevated | Tier 2 | P214168 | 2020-12-07 04:38 | 201207E221932 | #N/A | OH | 520-10R | ENABLE | 2020-12-07 07:12 | 43.1056 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 221932
100 | Undetermined | 521 | 2019-10-22 15:14 | Extreme | Tier 2 | 521-700R | 2019-10-30 08:32 | 191030E189093 | #N/A | OH | 521-14R | ENABLE | 2019-11-01 14:06 | 238.8719 | FALSE | #N/A | 521-700R | Downstream Recloser | Success | 189093
100 | Undetermined | 521 | 2019-10-27 23:40 | Extreme | Tier 2 | 521-700R | 2019-10-30 08:32 | 191030E189093 | #N/A | OH | 521-29R | ENABLE | 2019-10-31 14:09 | 86.4814 | FALSE | #N/A | 521-700R | Downstream Recloser | Success | 189093
100 | Undetermined | 521 | 2019-10-27 23:40 | Extreme | Tier 2 | 521-700R | 2019-10-30 08:32 | 191030E189093 | #N/A | OH | 521-700R | ENABLE | 2019-10-30 10:09 | 58.4714 | TRUE |  |  | Same Recloser | Success | 189093
100 | Undetermined | 521 | 2019-10-29 16:26 | Extreme | Tier 2 | 521-700R | 2019-10-30 08:32 | 191030E189093 | #N/A | OH | 521-27R | ENABLE | 2019-11-01 14:06 | 69.6672 | FALSE | #N/A | 521-700R | Downstream Recloser | Success | 189093
100 | Undetermined | 524 | 2018-11-11 03:10 | Extreme | Non-HFTD | 524-22R | 2018-11-12 21:33 | 181112E163383 | #N/A | OH | 524-69R | ENABLE | 2018-11-12 21:58 | 42.8017 | FALSE | #N/A | 524-22R | Downstream Recloser | Success | 163383
100 | Undetermined | 524 | 2018-11-11 03:10 | Extreme | Non-HFTD | 524-22R | 2018-11-12 21:33 | 181112E163383 | #N/A | OH | 524-46R | ENABLE | 2018-11-12 21:55 | 42.7411 | FALSE | #N/A | 524-22R | Downstream Recloser | Success | 163383
100 | Undetermined | 524 | 2018-11-11 03:15 | Extreme | Non-HFTD | 524-22R | 2018-11-12 21:33 | 181112E163383 | #N/A | OH | 524-22R | ENABLE | 2018-11-12 21:53 | 42.6369 | TRUE |  |  | Same Recloser | Success | 163383
100 | Undetermined | 591 | 2019-10-27 22:52 | Elevated | Non-HFTD | 591-1129R | 2019-10-28 06:44 | 191028E188714 | #N/A | OH | 591-1129R | ENABLE | 2019-10-28 06:48 | 7.9367 | TRUE |  |  | Same Recloser | Success | 188714
100 | Undetermined | 599 | 2017-12-04 04:27 | Elevated | Tier 2 | 599-19R | 2017-12-15 08:47 | 171215E138145 | #N/A | OH | 599-19R | ENABLE | 2017-12-15 10:10 | 269.7136 | TRUE |  |  | Same Recloser | Success | 138145
100 | Undetermined | 971 | 2019-10-20 02:33 | Elevated | Tier 2 | 971-26R | 2019-10-21 00:40 | 191021E188092 | #N/A | OH | 971-26R | ENABLE | 2019-10-21 00:47 | 22.2439 | TRUE |  |  | Same Recloser | Success | 188092
100 | Undetermined | 971 | 2019-10-20 02:35 | Elevated | Tier 2 | 971-26R | 2019-10-21 00:40 | 191021E188092 | #N/A | OH | 971-29R | ENABLE | 2019-11-01 14:54 | 300.3167 | FALSE | #N/A | #N/A | Downstream Recloser | Success | 188092
100 | Undetermined | 971 | 2019-10-20 02:43 | Elevated | Tier 2 | 971-26R | 2019-10-21 00:40 | 191021E188092 | #N/A | OH | 971-379R | ENABLE | 2019-10-21 00:48 | 22.0811 | FALSE | #N/A | #N/A | Downstream Recloser | Success | 188092
100 | Undetermined | 1030 | 2017-12-11 13:58 | Normal | Tier 3 | P117171 | 2017-12-21 11:03 | 171221E138475 | #N/A | OH | 1030-18R | ENABLE | 2017-12-27 12:03 | 382.0706 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 138475
100 | Undetermined | 1215 | 2017-10-14 06:13 | Elevated | Tier 3 | 1215-10R | 2017-10-16 05:03 | 171016E133968 | #N/A | OH | 1215-10R | ENABLE | 2017-10-16 08:06 | 49.8822 | TRUE |  |  | Same Recloser | Success | 133968
100 | Undetermined | 1215 | 2017-10-14 06:13 | Elevated | Tier 3 | 1215-10R | 2017-10-16 05:03 | 171016E133968 | #N/A | OH | 1215-12R | ENABLE | 2017-10-16 09:49 | 51.6017 | FALSE | #N/A | 1215-10R | Downstream Recloser | Success | 133968
100 | Undetermined | 1215 | 2017-12-11 11:26 | Elevated | Tier 3 | 1215-10R | 2017-12-11 11:43 | 171211E137849 | #N/A | OH | 1215-10R | ENABLE | 2017-12-11 12:49 | 1.3872 | TRUE |  |  | Same Recloser | Success | 137849
100 | Undetermined | 1215 | 2017-12-11 11:26 | Elevated | Tier 3 | 1215-10R | 2017-12-11 11:43 | 171211E137849 | #N/A | OH | 1215-12R | ENABLE | 2017-12-11 12:48 | 1.3669 | FALSE | #N/A | 1215-10R | Downstream Recloser | Success | 137849
100 | Undetermined | 1215 | 2017-12-11 11:26 | Elevated | Tier 3 | 1215-10R | 2017-12-11 11:43 | 171211E137849 | #N/A | OH | 1215-28R | ENABLE | 2017-12-15 02:35 | 87.1386 | FALSE | #N/A | 1215-10R | Downstream Recloser | Success | 137849
100 | Undetermined | 1215 | 2017-12-11 11:27 | Elevated | Tier 3 | 1215-10R | 2017-12-11 11:43 | 171211E137849 | #N/A | OH | 1215-32R | ENABLE | 2017-12-15 02:38 | 87.1872 | FALSE | #N/A | 1215-10R | Downstream Recloser | Success | 137849
100 | Undetermined | 1233 | 2019-10-10 01:03 | Elevated | Tier 3 | 1233-259R | 2019-10-10 01:32 | 191010E187196 | #N/A | OH | 1233-259R | ENABLE | 2019-10-10 01:36 | 0.55778 | TRUE |  |  | Same Recloser | Success | 187196
100 | Undetermined | 1233 | 2019-10-10 01:03 | Elevated | Tier 3 | 1233-259R | 2019-10-10 01:32 | 191010E187196 | #N/A | OH | 1233-252R | ENABLE | 2019-10-10 01:38 | 0.58417 | FALSE | #N/A | 1233-259R | Downstream Recloser | Success | 187196
100 | Undetermined | 1234 | 2019-10-10 13:24 | Extreme | Tier 3 | 1234-3R | 2019-10-11 12:09 | 191011E187411 | #N/A | OH | 1234-3R | ENABLE | 2019-10-11 12:32 | 23.1208 | TRUE |  |  | Same Recloser | Success | 187411
404 | Undetermined (weather related) | 78 | 2020-09-04 23:21 | Elevated | Tier 3 | 78-26R | 2020-09-05 15:21 | 200905E214335 | #N/A | OH | 78-26R | ENABLE | 2020-09-05 19:28 | 20.1281 | TRUE |  |  | Same Recloser | Success | 214335
404 | Undetermined (weather related) | 78 | 2020-09-04 23:59 | Elevated | Tier 3 | 78-26R | 2020-09-05 15:21 | 200905E214335 | #N/A | OH | 78-404R | ENABLE | 2020-09-05 19:31 | 19.5389 | FALSE | #N/A | 78-26R | Downstream Recloser | Success | 214335
404 | Undetermined (weather related) | 182 | 2020-09-06 05:28 | Elevated | Non-HFTD | P212396 | 2020-09-06 23:29 | 200906E214558 | #N/A | OH | 182-356R | ENABLE | 2020-09-10 06:48 | 97.3394 | FALSE | P212396 | #N/A | Downstream Structure | Downstream Fuse | 214558
404 | Undetermined (weather related) | 217 | 2020-09-29 13:07 | Elevated | Tier 2 | 217-972R | 2020-09-29 15:21 | 200929E216473 | #N/A | OH | 217-983R | ENABLE | 2020-09-29 15:32 | 2.4167 | FALSE | #N/A | 217-837R | Downstream Recloser | Success | 216473
404 | Undetermined (weather related) | 217 | 2020-09-29 13:08 | Elevated | Tier 2 | 217-972R | 2020-09-29 15:21 | 200929E216473 | #N/A | OH | 217-837R | ENABLE | 2020-09-29 15:35 | 2.4506 | FALSE | #N/A | 217-837R | Downstream Recloser | Success | 216473
404 | Undetermined (weather related) | 217 | 2020-09-29 13:09 | Elevated | Tier 2 | 217-972R | 2020-09-29 15:21 | 200929E216473 | #N/A | OH | 217-835R | ENABLE | 2020-09-29 15:30 | 2.35 | FALSE | #N/A | 217-837R | Downstream Recloser | Success | 216473
404 | Undetermined (weather related) | 217 | 2020-09-29 13:09 | Elevated | Tier 2 | 217-972R | 2020-09-29 15:21 | 200929E216473 | #N/A | OH | 217-972R | ENABLE | 2020-09-29 15:27 | 2.295 | TRUE |  |  | Same Recloser | Success | 216473
404 | Undetermined (weather related) | 237 | 2020-09-05 02:22 | Elevated | Tier 3 | 237-30R | 2020-09-05 14:18 | 200905E214276 | #N/A | OH | 237-17R | ENABLE | 2020-09-05 18:03 | 15.6722 | FALSE | #N/A | 237-2R | Downstream Recloser | Success | 214276
404 | Undetermined (weather related) | 237 | 2020-09-05 02:23 | Elevated | Tier 3 | 237-30R | 2020-09-05 14:18 | 200905E214276 | #N/A | OH | 237-2R | ENABLE | 2020-09-05 18:01 | 15.6389 | FALSE | #N/A | 237-2R | Downstream Recloser | Success | 214276
404 | Undetermined (weather related) | 237 | 2020-09-05 02:30 | Elevated | Tier 3 | 237-30R | 2020-09-05 14:18 | 200905E214276 | #N/A | OH | 237-30R | ENABLE | 2020-09-05 14:35 | 12.0781 | TRUE |  |  | Same Recloser | Success | 214276
404 | Undetermined (weather related) | 307 | 2020-09-05 19:03 | Elevated | Non-HFTD | 307-234R | 2020-09-05 19:04 | 200905E214333 | #N/A | OH | 307-234R | ENABLE | 2020-09-05 19:15 | 0.2 | TRUE |  |  | Same Recloser | Success | 214333
404 | Undetermined (weather related) | 350 | 2020-09-05 00:20 | Elevated | Tier 2 | 350-2192R | 2020-09-06 18:28 | 200906E214514 | #N/A | OH | 350-2201R | ENABLE | 2020-09-10 13:36 | 133.2611 | FALSE | #N/A | 350-41R | Downstream Recloser | Success | 214514
404 | Undetermined (weather related) | 350 | 2020-09-06 05:41 | Elevated | Tier 2 | 350-2192R | 2020-09-06 18:28 | 200906E214514 | #N/A | OH | 350-2196R | ENABLE | 2020-09-10 07:36 | 97.9111 | FALSE | #N/A | 350-41R | Downstream Recloser | Success | 214514
404 | Undetermined (weather related) | 350 | 2020-09-06 05:43 | Elevated | Tier 2 | 350-2192R | 2020-09-06 18:28 | 200906E214514 | #N/A | OH | 350-41R | ENABLE | 2020-09-07 08:51 | 27.1389 | FALSE | #N/A | 350-41R | Downstream Recloser | Success | 214514
404 | Undetermined (weather related) | 350 | 2020-09-06 05:44 | Elevated | Tier 2 | 350-2192R | 2020-09-06 18:28 | 200906E214514 | #N/A | OH | 350-2192R | ENABLE | 2020-09-07 11:17 | 29.5611 | TRUE |  |  | Same Recloser | Success | 214514
404 | Undetermined (weather related) | 353 | 2020-09-06 05:51 | Elevated | Tier 2 | 353-904R | 2020-09-06 16:45 | 200906E214499 | #N/A | OH | 353-904R | ENABLE | 2020-09-06 18:47 | 12.9389 | TRUE |  |  | Same Recloser | Success | 214499
404 | Undetermined (weather related) | 411 | 2020-09-27 23:24 | Elevated | Tier 2 | 411-30R | 2020-09-29 17:09 | 200929E216482 | #N/A | OH | 411-14R | ENABLE | 2020-09-29 17:10 | 41.7617 | FALSE | #N/A | 411-14R | Downstream Recloser | Success | 216482
404 | Undetermined (weather related) | 411 | 2020-09-27 23:24 | Elevated | Tier 2 | 411-30R | 2020-09-29 17:09 | 200929E216482 | #N/A | OH | 411-30R | ENABLE | 2020-09-29 17:10 | 41.7617 | TRUE |  |  | Same Recloser | Success | 216482
404 | Undetermined (weather related) | 445 | 2020-09-04 23:45 | Elevated | Tier 2 | 445-39R | 2020-09-05 15:02 | 200905E214285 | #N/A | OH | 445-39R | ENABLE | 2020-09-05 15:04 | 15.3278 | TRUE |  |  | Same Recloser | Success | 214285
404 | Undetermined (weather related) | 445 | 2020-09-27 23:48 | Elevated | Tier 2 | 445-39R | 2020-09-28 00:28 | 200928E216269 | #N/A | OH | 445-39R | ENABLE | 2020-09-28 03:52 | 4.0667 | TRUE |  |  | Same Recloser | Success | 216269
404 | Undetermined (weather related) | 445 | 2020-09-28 09:36 | Elevated | Tier 2 | 445-17R | 2020-09-28 12:26 | 200928E216335 | #N/A | OH | 445-19R | ENABLE | 2020-09-29 17:49 | 32.2111 | FALSE | #N/A | 445-17R | Downstream Recloser | Success | 216335
404 | Undetermined (weather related) | 445 | 2020-09-28 09:38 | Elevated | Tier 2 | 445-17R | 2020-09-28 12:26 | 200928E216335 | #N/A | OH | 445-17R | ENABLE | 2020-09-28 14:17 | 4.6556 | TRUE |  |  | Same Recloser | Success | 216335
404 | Undetermined (weather related) | 445 | 2020-11-26 12:10 | Elevated | Tier 2 | 445-39R | 2020-11-27 05:44 | 201127E221307 | #N/A | OH | 445-39R | ENABLE | 2020-11-27 06:03 | 17.8769 | TRUE |  |  | Same Recloser | Success | 221307
404 | Undetermined (weather related) | 445 | 2020-11-26 12:10 | Elevated | Tier 2 | 445-39R | 2020-11-27 05:44 | 201127E221307 | #N/A | OH | 445-17R | ENABLE | 2020-11-27 05:56 | 17.7611 | FALSE | #N/A | 445-39R | Downstream Recloser | Success | 221307
404 | Undetermined (weather related) | 445 | 2020-11-26 12:11 | Elevated | Tier 2 | 445-39R | 2020-11-27 05:44 | 201127E221307 | #N/A | OH | 445-19R | ENABLE | 2020-11-27 06:04 | 17.8833 | FALSE | #N/A | 445-39R | Downstream Recloser | Success | 221307
404 | Undetermined (weather related) | 445 | 2020-11-26 12:11 | Elevated | Tier 2 | 445-39R | 2020-11-27 05:44 | 201127E221307 | #N/A | OH | 445-894R | ENABLE | 2020-11-27 06:07 | 17.9233 | FALSE | #N/A | 445-39R | Downstream Recloser | Success | 221307
404 | Undetermined (weather related) | 448 | 2020-09-27 23:49 | Elevated | Tier 3 | 448-33R | 2020-09-28 16:26 | 200928E216364 | #N/A | OH | 448-33R | ENABLE | 2020-09-28 16:52 | 17.0556 | TRUE |  |  | Same Recloser | Success | 216364
404 | Undetermined (weather related) | 448 | 2020-09-27 23:50 | Elevated | Tier 3 | 448-33R | 2020-09-28 16:26 | 200928E216364 | #N/A | OH | 448-19R | ENABLE | 2020-09-28 16:42 | 16.8778 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 216364
404 | Undetermined (weather related) | 448 | 2020-09-27 23:50 | Elevated | Tier 3 | 448-33R | 2020-09-28 16:26 | 200928E216364 | #N/A | OH | 448-23R | ENABLE | 2020-09-28 16:42 | 16.8672 | FALSE | #N/A | 448-9R | Downstream Recloser | Success | 216364
404 | Undetermined (weather related) | 450 | 2020-09-06 07:16 | Elevated | Non-HFTD | 450-50R | 2020-09-06 14:43 | 200906E214477 | #N/A | OH | 450-50R | ENABLE | 2020-09-06 16:07 | 8.85 | TRUE |  |  | Same Recloser | Success | 214477
404 | Undetermined (weather related) | 524 | 2020-09-04 22:23 | Elevated | Tier 2 | D138823 | 2020-09-07 16:31 | 200907E214630 | #N/A | UG | 524-69R | ENABLE | 2020-09-10 14:52 | 136.4889 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 214630
404 | Undetermined (weather related) | 907 | 2020-09-05 01:09 | Elevated | Tier 3 | 907-1716R | 2020-09-05 16:51 | 200905E214312 | #N/A | OH | 907-1716R | ENABLE | 2020-09-05 17:03 | 15.8889 | TRUE |  |  | Same Recloser | Success | 214312
404 | Undetermined (weather related) | 907 | 2020-09-05 01:10 | Elevated | Tier 3 | 907-1716R | 2020-09-05 16:51 | 200905E214312 | #N/A | OH | 907-1702R | ENABLE | 2020-09-05 17:11 | 16.0164 | FALSE | #N/A | 907-1716R | Downstream Recloser | Success | 214312
404 | Undetermined (weather related) | 975 | 2020-09-05 01:09 | Elevated | Tier 3 | 975-22R | 2020-09-05 18:05 | 200905E214326 | #N/A | OH | 975-22R | ENABLE | 2020-09-05 18:08 | 16.9778 | TRUE |  |  | Same Recloser | Success | 214326
404 | Undetermined (weather related) | 1030 | 2020-09-05 01:11 | Elevated | Tier 2 | 1030-23R | 2020-09-05 14:58 | 200905E214284 | #N/A | OH | 1030-989R | ENABLE | 2020-09-05 15:13 | 14.0389 | FALSE | #N/A | 1030-23R | Downstream Recloser | Success | 214284
404 | Undetermined (weather related) | 1030 | 2020-09-05 01:11 | Elevated | Tier 2 | 1030-23R | 2020-09-05 14:58 | 200905E214284 | #N/A | OH | 1030-23R | ENABLE | 2020-09-05 15:00 | 13.8056 | TRUE |  |  | Same Recloser | Success | 214284
404 | Undetermined (weather related) | 1030 | 2020-09-05 01:12 | Elevated | Tier 2 | 1030-23R | 2020-09-05 14:58 | 200905E214284 | #N/A | OH | 1030-20R | ENABLE | 2020-09-05 15:10 | 13.9669 | FALSE | #N/A | 1030-23R | Downstream Recloser | Success | 214284
404 | Undetermined (weather related) | 1030 | 2020-09-05 01:13 | Elevated | Tier 2 | 1030-23R | 2020-09-05 14:58 | 200905E214284 | #N/A | OH | 1030-18R | ENABLE | 2020-09-05 15:08 | 13.9281 | FALSE | #N/A | 1030-23R | Downstream Recloser | Success | 214284
404 | Undetermined (weather related) | 1458 | 2020-09-04 22:55 | Elevated | Tier 2 | D2476184146 | 2020-09-07 04:06 | 200907E214577 | #N/A | UG | 1458-565 | ENABLE | 2020-09-10 07:16 | 128.35 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 214577
404 | Undetermined (weather related) | RB1 | 2020-09-05 00:31 | Elevated | Tier 3 | RB1-30R | 2020-09-06 11:10 | 200906E214436 | #N/A | OH | RB1-19R | ENABLE | 2020-09-06 11:12 | 34.6833 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 214436
710 | Vehicle contact | 78 | 2016-10-19 02:05 | Elevated | Tier 3 | P176547 | 2016-10-20 15:29 | 161020E107709 | #N/A | UG | 78-26R | ENABLE | 2016-10-20 20:03 | 41.9622 | FALSE | P176547 | #N/A | Downstream Structure | Downstream Fuse | 107709
710 | Vehicle contact | 206 | 2017-12-04 04:34 | Elevated | Non-HFTD | D119469 | 2017-12-18 03:26 | 171218E138270 | #N/A | UG | 206-953R | ENABLE | 2017-12-27 11:06 | 558.5325 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 138270
710 | Vehicle contact | 212 | 2017-10-14 06:22 | Extreme | Tier 3 | P616190 | 2017-10-14 13:03 | 171014E133931 | #N/A | OH | 212-638R | ENABLE | 2017-10-16 07:15 | 48.8711 | FALSE | P616190 | #N/A | Downstream Structure | Downstream Fuse | 133931
710 | Vehicle contact | 212 | 2017-10-14 06:23 | Extreme | Tier 3 | P616190 | 2017-10-14 13:03 | 171014E133931 | #N/A | OH | 212-674R | ENABLE | 2017-10-16 07:15 | 48.8531 | FALSE | P616190 | #N/A | Downstream Structure | Downstream Fuse | 133931
710 | Vehicle contact | 212 | 2017-10-14 06:24 | Extreme | Tier 3 | P616190 | 2017-10-14 13:03 | 171014E133931 | #N/A | OH | 212-652R | ENABLE | 2017-10-18 10:58 | 100.5675 | FALSE | P616190 | #N/A | Downstream Structure | Downstream Fuse | 133931
710 | Vehicle contact | 240 | 2019-10-20 00:25 | Elevated | Tier 2 | 240 | 2019-10-21 23:19 | 191021E188199 | #N/A | OH | 240-1028R | ENABLE | 2019-10-21 23:24 | 46.9803 | FALSE | #N/A | #N/A | Recloser detected a fault and CB operated | Success | 188199
710 | Vehicle contact | 240 | 2019-10-20 00:26 | Elevated | Tier 2 | 240 | 2019-10-21 23:19 | 191021E188199 | #N/A | OH | 240-1095R | ENABLE | 2019-10-21 23:24 | 46.9622 | FALSE | #N/A | #N/A | Recloser detected a fault and CB operated | Success | 188199
710 | Vehicle contact | 240 | 2019-10-20 11:04 | Elevated | Tier 2 | 240 | 2019-10-21 23:19 | 191021E188199 | #N/A | OH | 240-1097R | ENABLE | 2019-10-21 23:29 | 36.4125 | FALSE | #N/A | #N/A | Recloser detected a fault and CB operated | Success | 188199
710 | Vehicle contact | 246 | 2017-12-04 03:54 | Elevated | Tier 2 | P177371 | 2017-12-15 06:25 | 171215E138128 | #N/A | OH | 246-34R | ENABLE | 2017-12-27 10:45 | 558.8436 | FALSE | #N/A | #N/A | Upstream Fault | Upstream/Non Related Fault | 138128
710 | Vehicle contact | 470 | 2019-10-31 15:01 | Elevated | Tier 2 | 470 | 2019-11-01 05:48 | 191101E189327 | #N/A | OH | 470-47R | ENABLE | 2019-11-01 05:56 | 14.9169 | FALSE | #N/A | #N/A | Recloser detected a fault and CB operated | NO Success | 189327
710 | Vehicle contact | 520 | 2020-10-25 12:08 | Normal | Tier 2 | 520-26R | 2020-10-25 21:44 | 201025E218693 | #N/A | OH | 520-26R | ENABLE | 2020-10-25 22:16 | 10.1325 | TRUE |  |  | Same Recloser | Success | 218693
710 | Vehicle contact | 521 | 2020-10-25 12:12 | Normal | Tier 2 | 521-14R | 2020-10-25 21:44 | 201025E218693 | #N/A | OH | 521-27R | ENABLE | 2020-10-25 21:59 | 9.7936 | FALSE | #N/A | 521-14R | Downstream Recloser | Success | 218693
710 | Vehicle contact | 521 | 2020-10-25 12:14 | Normal | Tier 2 | 521-14R | 2020-10-25 21:44 | 201025E218693 | #N/A | OH | 521-14R | ENABLE | 2020-10-25 21:58 | 9.7342 | TRUE |  |  | Same Recloser | Success | 218693
710 | Vehicle contact | 521 | 2020-10-25 15:57 | Normal | Tier 2 | 521-14R | 2020-10-25 21:44 | 201025E218693 | #N/A | OH | 521-18R | ENABLE | 2020-10-27 18:46 | 50.8222 | FALSE | #N/A | 521-14R | Downstream Recloser | Success | 218693
710 | Vehicle contact | 521 | 2020-10-25 15:58 | Normal | Tier 2 | 521-14R | 2020-10-25 21:44 | 201025E218693 | #N/A | OH | 521-32R | ENABLE | 2020-10-27 18:49 | 50.8611 | FALSE | #N/A | 521-14R | Downstream Recloser | Success | 218693
710 | Vehicle contact | 973 | 2018-11-11 02:55 | Extreme | Tier 3 | D208807 | 2018-11-14 15:33 | 181114E163598 | #N/A | UG | 973-649R | ENABLE | 2018-11-17 13:36 | 154.6767 | FALSE | D208807 | #N/A | Downstream Structure | Downstream Fuse | 163598
710 | Vehicle contact | 973 | 2018-11-11 02:55 | Extreme | Tier 3 | D208807 | 2018-11-14 15:33 | 181114E163598 | #N/A | UG | 973-630R | ENABLE | 2018-11-14 18:17 | 87.3678 | FALSE | D208807 | #N/A | Downstream Structure | Downstream Fuse | 163598
710 | Vehicle contact | 973 | 2018-11-11 02:55 | Extreme | Tier 3 | D208807 | 2018-11-14 15:33 | 181114E163598 | #N/A | UG | 973-626R | ENABLE | 2018-11-17 13:37 | 154.6964 | FALSE | D208807 | #N/A | Downstream Structure | Downstream Fuse | 163598
412 | Wind - wires slap/pole down | 440 | 2018-01-27 19:36 | Elevated | Tier 3 | 440-13R | 2018-01-29 02:47 | 180129E141093 | #N/A | OH | 440-13R | ENABLE | 2018-01-29 02:50 | 31.2392 | TRUE |  |  | Same Recloser | Success | 141093
510 | Conductor contact/failure/overload/wire slap | 67 | 2021-01-18 20:56 | Elevated | Tier 3 | 67-45R | 2021-01-19 13:38 | 210119E224390 | #N/A | OH | 67-45R | ENABLE | 2021-01-19 13:44 | 16.7906 | TRUE |  |  | Same Recloser | Success
510 | Conductor contact/failure/overload/wire slap | 67 | 2021-01-18 20:57 | Elevated | Tier 3 | 67-45R | 2021-01-19 13:38 | 210119E224390 | #N/A | OH | 67-24R | ENABLE | 2021-01-19 20:07 | 23.1739 | FALSE | #N/A | 67-45R | Downstream Recloser | Success
510 | Conductor contact/failure/overload/wire slap | 445 | 2021-01-18 23:55 | Elevated | Tier 2 | 445-24R | 2021-01-19 13:03 | 210119E224531 | #N/A | OH | 445-894R | ENABLE | 2021-01-19 22:50 | 22.9217 | FALSE | #N/A | 445-24R | Downstream Recloser | Success
510 | Conductor contact/failure/overload/wire slap | 445 | 2021-01-18 23:55 | Elevated | Tier 2 | 445-24R | 2021-01-19 13:03 | 210119E224531 | #N/A | OH | 445-19R | ENABLE | 2021-01-19 22:52 | 22.9442 | FALSE | #N/A | 445-24R | Downstream Recloser | Success
508 | Flashover due to contamination/overload/tracking | 445 | 2021-01-18 23:55 | Elevated | Tier 2 | 445-24R | 2021-01-19 10:10 | 210119E224360 | #N/A | OH | 445-894R | ENABLE | 2021-01-19 22:50 | 22.9217 | FALSE | #N/A | 445-24R | Downstream Recloser | Success
508 | Flashover due to contamination/overload/tracking | 445 | 2021-01-18 23:55 | Elevated | Tier 2 | 445-24R | 2021-01-19 10:10 | 210119E224360 | #N/A | OH | 445-19R | ENABLE | 2021-01-19 22:52 | 22.9442 | FALSE | #N/A | 445-24R | Downstream Recloser | Success
410 | Lightning/arrester/xfmr failure (weather related) | 221 | 2021-11-24 13:56 | Elevated | Non-HFTD | P478446 | 2021-11-25 04:02 | 211125E247617 | #N/A | OH | 221-344R | ENABLE | 2021-11-26 22:30 | 56.5586 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
410 | Lightning/arrester/xfmr failure (weather related) | 221 | 2021-11-24 13:58 | Elevated | Non-HFTD | P478446 | 2021-11-25 04:02 | 211125E247617 | #N/A | OH | 221-782R | ENABLE | 2021-11-26 22:32 | 56.5753 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
515 | OH connector failure (jumper/splice/squeeze-on) | 521 | 2021-01-18 21:52 | Elevated | Tier 2 | P919091 | 2021-01-19 16:42 | 210119E224424 | #N/A | OH | 521-32R | ENABLE | 2021-01-19 21:02 | 23.1689 | FALSE | P919091 | #N/A | Downstream Structure | Downstream Fuse
515 | OH connector failure (jumper/splice/squeeze-on) | 521 | 2021-01-18 21:52 | Elevated | Tier 2 | P919091 | 2021-01-19 16:42 | 210119E224424 | #N/A | OH | 521-27R | ENABLE | 2021-01-19 21:02 | 23.1672 | FALSE | P919091 | #N/A | Downstream Structure | Downstream Fuse
515 | OH connector failure (jumper/splice/squeeze-on) | 521 | 2021-01-18 21:53 | Elevated | Tier 2 | P919091 | 2021-01-19 16:42 | 210119E224424 | #N/A | OH | 521-14R | ENABLE | 2021-01-19 21:04 | 23.1744 | FALSE | P919091 | #N/A | Downstream Structure | Downstream Fuse
515 | OH connector failure (jumper/splice/squeeze-on) | 521 | 2021-01-18 21:55 | Elevated | Tier 2 | P919091 | 2021-01-19 16:42 | 210119E224424 | #N/A | OH | 521-18R | ENABLE | 2021-01-19 21:03 | 23.1464 | FALSE | P919091 | #N/A | Downstream Structure | Downstream Fuse
515 | OH connector failure (jumper/splice/squeeze-on) | 521 | 2021-01-18 21:55 | Elevated | Tier 2 | P919091 | 2021-01-19 16:42 | 210119E224424 | #N/A | OH | 521-700R | ENABLE | 2021-01-19 21:04 | 23.16 | FALSE | P919091 | #N/A | Downstream Structure | Downstream Fuse
532 | Pole - contact/damage/broke/rotted/on fire | 357 | 2021-11-24 15:20 | Elevated | Tier 2 | P677795 | 2021-11-24 20:25 | 211124E247696 | #N/A | OH | 357-1147R | ENABLE | 2021-11-26 19:21 | 52.0078 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
532 | Pole - contact/damage/broke/rotted/on fire | 357 | 2021-11-24 15:21 | Elevated | Tier 2 | P677795 | 2021-11-24 20:25 | 211124E247696 | #N/A | OH | 357-50R | ENABLE | 2021-11-25 08:06 | 16.7544 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
532 | Pole - contact/damage/broke/rotted/on fire | 357 | 2021-11-24 15:22 | Elevated | Tier 2 | P677795 | 2021-11-24 20:25 | 211124E247696 | #N/A | OH | 357-1299R | ENABLE | 2021-11-25 06:02 | 14.6697 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
100 | Undetermined | 75 | 2021-11-24 12:07 | Elevated | Non-HFTD | 75-996R | 2021-11-25 20:11 | 211125E247740 | #N/A | OH | 75-32R | ENABLE | 2021-11-25 20:21 | 32.2183 | FALSE | #N/A | 75-996R | Downstream Recloser | Success
100 | Undetermined | 75 | 2021-11-24 12:08 | Elevated | Non-HFTD | 75-996R | 2021-11-25 20:11 | 211125E247740 | #N/A | OH | 75-996R | ENABLE | 2021-11-25 20:21 | 32.2122 | TRUE |  |  | Same Recloser | Success
100 | Undetermined | 212 | 2021-11-24 15:00 | Elevated | Tier 2 | 212-734R | 2021-11-25 15:44 | 211125E247736 | #N/A | OH | 212-734R | ENABLE | 2021-11-25 15:54 | 24.9089 | TRUE |  |  | Same Recloser | Success
100 | Undetermined | 212 | 2021-11-24 15:01 | Elevated | Tier 2 | 212-734R | 2021-11-25 15:44 | 211125E247736 | #N/A | OH | 212-652R | ENABLE | 2021-11-25 15:49 | 24.8078 | FALSE | #N/A | 212-734R | Downstream Recloser | Success
100 | Undetermined | 212 | 2021-11-24 15:01 | Elevated | Tier 2 | 212-734R | 2021-11-25 15:44 | 211125E247736 | #N/A | OH | 212-773R | ENABLE | 2021-11-25 15:51 | 24.8317 | FALSE | #N/A | 212-734R | Downstream Recloser | Success
100 | Undetermined | 212 | 2021-11-24 15:02 | Elevated | Tier 2 | 212-734R | 2021-11-25 15:44 | 211125E247736 | #N/A | OH | 212-638R | ENABLE | 2021-11-26 20:45 | 53.7122 | FALSE | #N/A | 212-734R | Downstream Recloser | Success
100 | Undetermined | 212 | 2021-11-24 15:03 | Elevated | Tier 2 | 212-734R | 2021-11-25 15:44 | 211125E247736 | #N/A | OH | 212-650R | ENABLE | 2021-11-25 15:48 | 24.7481 | FALSE | #N/A | 212-734R | Downstream Recloser | Success
100 | Undetermined | 214 | 2021-01-18 22:05 | Elevated | Tier 3 | P812593 | 2021-01-19 15:33 | 210119E224409 | #N/A | OH | 214-613R | ENABLE | 2021-01-19 21:18 | 23.2139 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
100 | Undetermined | 214 | 2021-01-18 22:05 | Elevated | Tier 3 | P812593 | 2021-01-19 15:33 | 210119E224409 | #N/A | OH | 214-583R | ENABLE | 2021-01-19 21:18 | 23.2158 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
100 | Undetermined | 214 | 2021-01-18 22:05 | Elevated | Tier 3 | P812593 | 2021-01-19 15:33 | 210119E224409 | #N/A | OH | 214-4R | ENABLE | 2021-01-19 21:26 | 23.3483 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
100 | Undetermined | 214 | 2021-01-18 22:05 | Elevated | Tier 3 | P812593 | 2021-01-19 15:33 | 210119E224409 | #N/A | OH | 214-536R | ENABLE | 2021-01-19 21:26 | 23.3383 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
100 | Undetermined | 221 | 2021-11-24 13:56 | Elevated | Tier 2 | 221-6R | 2021-11-25 02:22 | 211125E247718 | #N/A | OH | 221-344R | ENABLE | 2021-11-26 22:30 | 56.5586 | FALSE | #N/A | 221-6R | Downstream Recloser | Success
100 | Undetermined | 221 | 2021-11-24 13:58 | Elevated | Tier 2 | 221-6R | 2021-11-25 02:22 | 211125E247718 | #N/A | OH | 221-782R | ENABLE | 2021-11-26 22:32 | 56.5753 | FALSE | #N/A | 221-6R | Downstream Recloser | Success
100 | Undetermined | 221 | 2021-11-24 14:56 | Elevated | Tier 2 | 221-6R | 2021-11-25 02:22 | 211125E247718 | #N/A | OH | 221-6R | ENABLE | 2021-11-25 02:41 | 11.7556 | TRUE |  |  | Same Recloser | Success
100 | Undetermined | 520 | 2021-01-18 21:51 | Elevated | Tier 3 | 520-35R | 2021-01-19 18:15 | 210119E224420 | #N/A | OH | 520-10R | ENABLE | 2021-01-19 18:28 | 20.615 | FALSE | #N/A | 520-35R | Downstream Recloser | Success
100 | Undetermined | 520 | 2021-01-18 21:52 | Elevated | Tier 3 | 520-35R | 2021-01-19 18:15 | 210119E224420 | #N/A | OH | 520-35R | ENABLE | 2021-01-19 18:25 | 20.5556 | TRUE |  |  | Same Recloser | Success
100 | Undetermined | 520 | 2021-01-18 23:59 | Elevated | Tier 3 | 520-35R | 2021-01-19 18:15 | 210119E224420 | #N/A | OH | 520-18R | ENABLE | 2021-01-19 22:54 | 22.9222 | FALSE | #N/A | 520-35R | Downstream Recloser | Success
100 | Undetermined | 520 | 2021-11-24 13:32 | Elevated | Tier 3 | 520-35R | 2021-11-25 14:54 | 211125E247735 | #N/A | OH | 520-10R | ENABLE | 2021-11-25 15:06 | 25.5533 | FALSE | #N/A | 520-35R | Downstream Recloser | Success
100 | Undetermined | 520 | 2021-11-24 13:32 | Elevated | Tier 3 | 520-35R | 2021-11-25 14:54 | 211125E247735 | #N/A | OH | 520-35R | ENABLE | 2021-11-25 15:04 | 25.5261 | TRUE |  |  | Same Recloser | Success
404 | Undetermined (weather related) | 217 | 2021-01-18 22:09 | Elevated | Tier 3 | 217-837R | 2021-01-19 16:18 | 210119E224415 | #N/A | OH | 217-983R | ENABLE | 2021-01-19 16:31 | 18.3594 | FALSE | #N/A | 217-837R | Downstream Recloser | Success
404 | Undetermined (weather related) | 217 | 2021-01-18 22:10 | Elevated | Tier 3 | 217-837R | 2021-01-19 16:18 | 210119E224415 | #N/A | OH | 217-837R | ENABLE | 2021-01-19 16:25 | 18.2478 | TRUE |  |  | Same Recloser | Success
404 | Undetermined (weather related) | 217 | 2021-01-18 22:10 | Elevated | Tier 3 | 217-837R | 2021-01-19 16:18 | 210119E224415 | #N/A | OH | 217-835R | ENABLE | 2021-01-19 16:28 | 18.3033 | FALSE | #N/A | 217-837R | Downstream Recloser | Success
404 | Undetermined (weather related) | 220 | 2021-01-18 22:23 | Elevated | Tier 3 | 220-288R | 2021-01-19 10:07 | 210119E224361 | #N/A | OH | 220-288R | ENABLE | 2021-01-19 10:26 | 12.0475 | TRUE |  |  | Same Recloser | Success
404 | Undetermined (weather related) | 220 | 2021-01-18 22:23 | Elevated | Tier 3 | 220-288R | 2021-01-19 10:07 | 210119E224361 | #N/A | OH | 220-298R | ENABLE | 2021-01-19 10:26 | 12.0503 | FALSE | #N/A | 220-288R | Downstream Recloser | Success
404 | Undetermined (weather related) | 220 | 2021-01-18 22:23 | Elevated | Tier 3 | 220-288R | 2021-01-19 10:07 | 210119E224361 | #N/A | OH | 220-294R | ENABLE | 2021-01-19 10:25 | 12.0272 | FALSE | #N/A | 220-288R | Downstream Recloser | Success
404 | Undetermined (weather related) | 221 | 2021-11-24 13:56 | Elevated | Non-HFTD | 221-1251R | 2021-11-25 00:47 | 211125E247642 | #N/A | OH | 221-344R | ENABLE | 2021-11-26 22:30 | 56.5586 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
404 | Undetermined (weather related) | 221 | 2021-11-24 13:56 | Elevated | Non-HFTD | P478446 | 2021-11-26 13:09 | 211126E247839 | #N/A | OH | 221-344R | ENABLE | 2021-11-26 22:30 | 56.5586 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
404 | Undetermined (weather related) | 221 | 2021-11-24 13:58 | Elevated | Non-HFTD | 221-1251R | 2021-11-25 00:47 | 211125E247642 | #N/A | OH | 221-782R | ENABLE | 2021-11-26 22:32 | 56.5753 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
404 | Undetermined (weather related) | 221 | 2021-11-24 13:58 | Elevated | Non-HFTD | P478446 | 2021-11-26 13:09 | 211126E247839 | #N/A | OH | 221-782R | ENABLE | 2021-11-26 22:32 | 56.5753 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
404 | Undetermined (weather related) | 221 | 2021-11-24 14:56 | Elevated | Non-HFTD | 221-1251R | 2021-11-25 00:47 | 211125E247642 | #N/A | OH | 221-6R | ENABLE | 2021-11-25 02:41 | 11.7556 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
404 | Undetermined (weather related) | 1166 | 2021-01-18 20:56 | Elevated | Tier 3 | 1166-15R | 2021-01-19 11:44 | 210119E224373 | #N/A | OH | 1166-15R | ENABLE | 2021-01-19 11:47 | 14.855 | TRUE |  |  | Same Recloser | Success
404 | Undetermined (weather related) | 1166 | 2021-01-18 20:56 | Elevated | Tier 3 | 1166-15R | 2021-01-19 11:44 | 210119E224373 | #N/A | OH | 1166-18R | ENABLE | 2021-01-19 20:06 | 23.1667 | FALSE | #N/A | 1166-15R | Downstream Recloser | Success
710 | Vehicle contact | 233 | 2021-11-24 14:51 | Elevated | Tier 2 | 233-81F | 2021-11-24 21:03 | 211124E247713 | #N/A | OH | 233-123R | ENABLE | 2021-11-26 20:19 | 53.46 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
710 | Vehicle contact | 233 | 2021-11-24 14:51 | Elevated | Tier 2 | 233-81F | 2021-11-24 21:03 | 211124E247713 | #N/A | OH | 233-41R | ENABLE | 2021-11-26 20:20 | 53.4778 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
710 | Vehicle contact | 524 | 2021-11-26 11:44 | Elevated | Tier 3 | P876479 | 2021-11-26 12:26 | 211126E247742 | #N/A | OH | 524-69R | ENABLE | 2021-11-26 20:02 | 8.2856 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
710 | Vehicle contact | 524 | 2021-11-26 11:45 | Elevated | Tier 3 | P876479 | 2021-11-26 12:26 | 211126E247742 | #N/A | OH | 524-50R | ENABLE | 2021-11-26 20:01 | 8.2619 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
710 | Vehicle contact | 524 | 2021-11-26 11:47 | Elevated | Tier 3 | P876479 | 2021-11-26 12:26 | 211126E247742 | #N/A | OH | 524-46R | ENABLE | 2021-11-26 20:01 | 8.2328 | FALSE | #N/A | #N/A |  | Upstream/Non Related Fault
412 | Wire slap/pole down/wire down (weather related) | 215 | 2021-01-18 22:08 | Elevated | Tier 2 | 215-38R | 2021-01-19 12:16 | 210119E224377 | #N/A | OH | 215-38R | ENABLE | 2021-01-19 12:28 | 14.3308 | TRUE |  |  | Same Recloser | Success
412 | Wire slap/pole down/wire down (weather related) | 215 | 2021-01-19 00:05 | Elevated | Tier 2 | 215-38R | 2021-01-19 12:16 | 210119E224377 | #N/A | OH | 215-1531R | ENABLE | 2021-01-19 12:28 | 12.3906 | FALSE | #N/A | 215-38R | Downstream Recloser | Success
412 | Wire slap/pole down/wire down (weather related) | 215 | 2021-01-19 00:05 | Elevated | Tier 2 | 215-38R | 2021-01-19 12:16 | 210119E224377 | #N/A | OH | 215-1534R | ENABLE | 2021-01-19 12:28 | 12.3833 | FALSE | #N/A | 215-38R | Downstream Recloser | Success
412 | Wire slap/pole down/wire down (weather related) | 220 | 2021-01-19 17:58 | Elevated | Tier 3 | 220-288R | 2021-01-19 18:46 | 210119E224421 | #N/A | OH | 220-294R | ENABLE | 2021-01-19 18:48 | 0.83833 | FALSE | #N/A | 220-288R | Downstream Recloser | Success
412 | Wire slap/pole down/wire down (weather related) | 220 | 2021-01-19 18:00 | Elevated | Tier 3 | 220-288R | 2021-01-19 18:46 | 210119E224421 | #N/A | OH | 220-288R | ENABLE | 2021-01-19 18:48 | 0.81111 | TRUE |  |  | Same Recloser | Success
412 | Wire slap/pole down/wire down (weather related) | 220 | 2021-01-19 18:00 | Elevated | Tier 3 | 220-288R | 2021-01-19 18:46 | 210119E224421 | #N/A | OH | 220-298R | ENABLE | 2021-01-19 18:48 | 0.78556 | FALSE | #N/A | 220-288R | Downstream Recloser | Success
Note on J168: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TST mentioned these are not outages associated with SRP. CB operated in this case and SRP enabled device was far from CB. CB has it's own reclosing capacity so not to include this outage.

## Pivot outages
Result | Success
Occurrence | (Multiple Items)
HFTD | (All)
Row Labels
170901E130417
171009E133448
171010E133579
171014E133915
171016E133968
171024E134614
171025E134657
171025E134715
171204E137207
171207E137550
171210E137773
171211E137849
171211E137860
171215E138145
171217E138258
180128E141084
180129E141091
180129E141093
180706E153817
180706E153832
181111E163270
181111E163272
181112E163325
181112E163351
181112E163361
181112E163383
181113E163393
181113E163402
181113E163412
181113E163446
181117E163806
191010E187196
191010E187219
191011E187411
191011E187413
191021E188092
191021E188157
191021E188199
191022E188270
191024E188394
191024E188539
191028E188714
191030E189093
191101E189327
191117E190645
200905E214276
200905E214281
200905E214284
200905E214285
200905E214290
200905E214312
200905E214319
200905E214326
200905E214333
200905E214335
200905E214339
200906E214452
200906E214453
200906E214454
200906E214458
200906E214461
200906E214462
200906E214463
200906E214477
200906E214499
200906E214500
200906E214514
200909E214739
200928E216269
200928E216335
200928E216362
200928E216364
200929E216473
200929E216478
200929E216482
200929E216483
201025E218693
201127E221307
201209E222143
210119E224390
210119E224531
210119E224360
211125E247740
211125E247736
211125E247718
210119E224420
211125E247735
210119E224415
210119E224361
210119E224373
210119E224377
210119E224421

## Final Analysis
Profile 3 Analysis: |  | System(HFTD) Analysis
2015-2021 |  | 2015-2021
Total Faults: | 119 | Total Faults: | 3010
Faults isolated by fuses | 29
Tier 2 | 12 | Total Ignitions(HFTD Dist): | 91
Tier 3 | 17
Faults isolated by profile 3 enabled devices | 90 | % Ignition: | 3.023%
Tier 2 | 50
Tier 3 | 40 | % Decrease in ignition after profile 3: | 61.44%
Total Ignitions* : | 0 | % Decrease in ignition after profile 3: | 100%
%Ignition | 0%
Note on G3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 437+372+424+381+483+415+499