## Cover
Policy 001-PP
MAINTENANCE INTERVALS FOR APPARATUS, RELAYS, METERS,
LINE PATROL/INSPECTIONS AND COMMUNICATIONS EQUIPMENT
Pacific Power Asset Management Policy 001
Date | Revision no. | Notes
2021-06-21 | 0 | First version of Policy 001 specific to Pacific Power
Updated Communications man hours. Removed WMA maintenance task
2022-06-20 | 1 | Added local transmission infrared line inspections (wires tab)
Updated to include distribution breaker overhaul plans for large customers (apparatus tab)
Added grid resilience equipment/storage facility inspection and maintenance task (apparatus tab)
RAS SPS1 maintenance interval changed from four years to six years (relay tab)
Added B1_B2 maintenance to RAS SPS1 maintenance tasks (relay tab)
Local transmission infrared testing - removed Washington; pertains to OR/CA only. (wires tab)
Author: various contributors; updated by Sheila Andreatta
Approval: Jonathon Connelly
Authoring Department: Asset Management
Approved Location: J:\Publications\FPP\DIS\POL
File Number-Name: PP-001-Maintenance Intervals.xlsx
Revision number: | 1
Revision date: | 2022-06-20
The most current version of this document is posted to engineering's policy websites.
Revisions to this document must be approved by the authoring department and processed by engineering publications, eampub@pacificorp.com

## Column Definitions & Notes
Column Definitions
Column Name | Column Definition
Equipment Type | Type of equipment or facility maintenance plan applies to.
Equipment Description | Further information to describe equipment or facility in more detail.
Equipment Use | Application equipment or facility is used for.
Business Unit | Company business unit that oversees equipment or facility.
**Equipment Model | Information that describes a particular model or type of equipment.
**Voltage | Equipment or facility rating.
Requires Commissioning | Indicates if equipment requires start up commissioning.
Equip.Code | SAP Code that identifies equipment category.
Maintenance Task | Maintenance task description.
Maintenance ID | ID used in SAP to identify maintenance task. First three letters identify business unit, next four letters represent equipment and maintenance task, next three numbers indicate interval between maintenance in months
Interval | Scheduled Time period in-between consecutive maintenance tasks***.
Counter (Ops/Fault) | Numbers of recorded equipment operations or faults before maintenance order is called
EC PM MAT | ID used to identify maintenance material activity type for distribution equipment.
EC Repair MAT | ID used to identify repair material activity type for distribution equipment.
MG/LOC PM MAT | ID used to identify maintenance material activity type for transmission equipment.
MG/LOC Repair MAT | ID used to identify repair material activity type for transmission equipment.
Notes | Any applicable notes.
**This information is only provided on the worksheet if the specific information impacts plan frequency or counter operations. If cell is blank it can be assumed that all types are included.
*** See maintenance basis discussion for clarification of time period/intervals and how they are applied to determine maintenance due dates. Intervals for tasks and asset associated with NERC Reliability Standards and Oregon / California Inspection programs and other regulatory requirements are firm intervals unless otherwise modified in the individual asset maintenance policies. Intervals for other assets and maintenance tasks are recommended and may be revised or modified during course of operations.

## Maintenance Basis
Maintenance Basis
PROTECTION SYSTEMS (Relay Equipment and Batteries) | See policies 270 and 277
APPARATUS | Apparatus maintenance intervals for PacifiCorp are based on a combination of manufacturer recommendations, failure and corrective maintenance history and experience, and the opinions of PacifiCorp subject matter experts. The maintenance intervals are either time-based or are based on operations counts or other triggers.
The following pertains to apparatus equipment designated as a component of a WECC critical path: 1) time intervals are developed assuming the required preventive maintenance work will be performed within the calendar year the order is generated with the stated interval being defined as calendar years. 2) For equipment on work that is triggered by an operational counter, the work shall be performed within the calendar year following the counter trigger date. 3) For time intervals less than one year (i.e. 3 mo., 4 mo., etc) the preventive maintenance work will be performed within the cycle time period.
Testing or maintenance activities that call for operation of the equipment may be satisfied if an actual real-time operation of that device can be documented during the last maintenance cycle.
Maintenance intervals and requirements are reviewed on a periodic basis and adjusted based on failure or maintenance issues, industry trends and manufacturer recommendations.
COMMUNICATIONS EQUIPMENT | See policies 270 and 277
MAINTENANCE DEFERRAL FOR CONSTRUCTION | Apparatus maintenance due in a given calendar year may be deferred if an approved capital replacement project for the equipment is scheduled for the following calendar year. The maintenance order will be closed when the replaced equipment is placed in service and a new maintenance plan will be assigned to the replaced equipment.
Non-WECC relay maintenance due in a given calendar year may be deferred if an approved capital or maintenance project is scheduled for the following calendar year that will require replacement of the existing equipment. Upon completion of the change in settings or relay replacement, the testing of the relay maintenance will be satisfied and the maintenance order will be closed or a new maintenance policy will be created.
Non-WECC communications maintenance due in a given calendar year may be deferred if an approved capital or maintenance project is scheduled for the following calendar year that will require performance of the necessary maintenance work or equipment replacement. Upon completion of the settings or equipment replacement, the communications maintenance will be satisfied and the maintenance order will be closed.
NEW OR REVISED MAINTENANCE POLICIES | Upon creation or revision of a maintenance policy, the determination of when the new maintenance activity will commence on an individual piece of equipment will be determined by asset management. Equipment will not be considered non-compliant with the new or revised maintenance policy interval if the work required per this policy is completed within the calendar year of the initial call date that was assigned to that equipment by asset management.

## Wires
Equipment Type | Equipment Description | Equipment Use | Equipment Model or Manufacturer | State | Maintenance Task | Equipment Code | Maintenance ID | Interval Calendar Year | Notes
DISTRIBUTION | Overhead distribution circuit |  |  | OR and WA | Visual Assurance Inspection | Map String | Standing Order | 2 | NOTE: Does not apply to FHCA areas in OR or WA
| Overhead distribution circuit |  |  | CA | Visual Assurance Inspection | Map String | Standing Order | 2 | NOTE: Maximum interval is 2 years plus 3 calendar months from the previous inspection for Non-Tier and Tier 1 areas.
| Overhead distribution circuit | Tier 2/3 FHCA |  | CA, OR and WA | Visual Assurance Inspection | Map String | Standing Order | 1 | NOTE: Maximum interval is 1 year plus 3 calendar months from the previous inspection for Tier 2 and Tier 3 areas in CA. NOTE: OH Distribution Visual Assurance Inspections in OR and WA moving to 1-yr cycle within the FHCA beginning in 2020.
| Overhead distribution circuit | Tier 2/3 FHCA |  | CA, OR and WA | Detail Inspection | Map String | Standing Order | 5 | NOTE: Maximum interval in CA is 5 years plus 3 calendar months from the previous detail inspection. NOTE: OH Distribution Detailed Inspections in OR and WA moving to 5 yr cycle within the FHCA beginning in 2020.
| Overhead distribution circuit |  |  | WA | Detail Inspection | Map String | Standing Order | 10 | NOTE: OH Distribution Detailed Inspections in WA moving to 10 yr cycle outside the FHCA beginning in 2021.
| Overhead distribution circuit |  |  | OR | Detail Pole Test and Treat | Map String | Standing Order | 10
| Overhead distribution circuit |  |  | CA | Pole Test and Treat Inspection | Map String | Standing Order | 20 | NOTE: If detail and test and treat are combined in one task, the combined inspection must be performed no later than 5 years and 3 months from the previous detail inspection. Maximum interval between test and treat inspections is 20 calendar years. NOTE: Alturas is on 10-year interval, due to the few number of map strings and sections.
| Overhead distribution circuit |  |  | WA | Detail Pole Test | Map String | Standing Order | 20
| Underground distribution circuit |  |  | CA | Visual Assurance Inspection | Map String | Standing Order | 2 | NOTE: Maximum interval is 2 years plus 3 calendar months from the previous inspection.
| Underground distribution circuit |  |  | CA | Detail Inspection | Map String | Standing Order | 4 | Open cabinet or padmount (secondary pedestals are not considered to be equipment and do not need to be inspected). Note: Maximum interval is 4 years plus 3 calendar months from previous inspection.
| Underground distribution circuit |  |  | OR | Detail Inspection | Map String | Standing Order | 10 | Open cabinet
| Underground distribution circuit |  |  | WA | Detail Inspection | Map String | Standing Order | 20
LOCAL TRANSMISSION | Overhead transmission line | Tier 2/3 FHCA |  | CA or OR | Infrared Inspection | Plant Locality Number | LOC-IR | 1 | Applies to Tier 2/3 and FHCA identified lines
| Overhead transmission line |  |  | OR and WA | Visual Assurance Inspection | Plant Locality Number | LOC-ISA | 2 | NOTE: Does not apply to FHCA areas in OR or WA
| Overhead transmission line |  |  | CA, OR and WA | Visual Assurance Inspection | Plant Locality Number | LOC-ISA | 1 | Specific lines, where annual visual assurance recommended.
| Overhead transmission line | Tier 2/3 FHCA |  | CA, OR and WA | Visual Assurance Inspection | Plant Locality Number | LOC-ISA | 1 | NOTE: For All CA locations as well as locations within the FHCA in OR and WA NOTE: OH local transmission visual assurance inspections in OR and WA moving to 1-yr cycle within the FHCA beginning in 2020.
| Overhead transmission line | Tier 2/3 FHCA |  | CA, OR and WA | Detail Inspection | Plant Locality Number | LOC-IFA | 5 | NOTE: For All CA locations as well as locations within the FHCA in OR and WA.
LOCAL TRANSMISSION (cont'd) | Overhead transmission line |  |  | CA, OR and WA | Detail Pole Test and Treat Inspection | Plant Locality Number | LOC-PTT | 10
| Overhead transmission line |  |  | CA, OR and WA | Hold Down Inspection | Plant Locality Number | LOC-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction.
| Overhead transmission line |  |  | CA, OR and WA | Hold Down Inspection | Plant Locality Number | LOC-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction
MAIN GRID TRANSMISSION | Overhead transmission line |  |  | CA, OR and WA | Visual Assurance Inspection | Plant Locality Number | MGT-AIR | 1
| Overhead transmission line |  |  | CA, OR and WA | Detail Inspection | Plant Locality Number | MGT-PAT | 2
| Overhead transmission line |  |  | CA, OR and WA | Pole Test and Treat Inspection | Plant Locality Number | MGT-PTT | 10
| Overhead transmission line |  |  | CA, OR and WA | Hold Down Inspection | Plant Locality Number | MGT-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction.
| Overhead transmission line |  |  | CA, OR and WA | Hold Down Inspection | Plant Locality Number | MGT-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction.
LINE RECLOSER/PROTECTION DEVICES | Distribution transfer switch − U/G | No relay protection |  |  | Operate MO | Vault / FP number | DST-DTSW-060 | 5 | Work coordinated by Wires
| Distribution recloser controller | Circuits |  | CA, OR and WA | Recloser Controller Mtc and Battery Replacement | DRCL | DST-DRCL-036 | 3 | Line reclosers/controller maintained by substation operations.
| Distribution recloser controller | Circuits | GandW Viper w/351R -0, -1, -2 controllers | CA, OR and WA | Recloser Controller Mtc and Battery Replacement | DRCL | DST-DRCL-024 | 2 | Line reclosers/controller maintained by substation operations.
| Distribution fuse saver | Circuits |  | CA, OR and WA | Battery Replacement | FSBT | DST-FSBT-060 | 5
UNDERGROUND VAULTS |  | Portland |  | OR | Vault Inspection | Plant Locality Number | DST-UGIN-006 (012) | 6 / 12
|  | Portland |  | OR | Air-Cooled Transformers Cleaned and Tested | Plant Locality Number | DST-UGTC-084 | 7
|  | Portland |  | OR | River Crossing Sign Inspection | Plant Locality Number | DST-UGRC-001 | monthly | Monthly inspection of the river crossing sign, required by City of Portland.
LINE FAULT INDICATORS | Fault indicators | Circuits and transmission lines | Joslyn or Fisher Pierce | CA, OR and WA | Fault Indicator Battery Replacement | FLI | XXX-FIBT-108 | 9
|  |  | Navigator or unknown | CA, OR and WA | Fault Indicator Battery Replacement | FLI | XXX-FIBT-096 | 8
LINE HIGH-VOLTAGE SWITCHES | Transmission high-voltage switches | Transmission lines | Motor Operator switches | CA, OR and WA | High-Voltage Switch Battery Replacement | SWBT | XXX-SWBT-036 | 3 | Replace batteries in high-voltage switches − performed by substation operations.
FII SUBSTATION INSPECTIONS |  |  |  | OR |  | FII-SBIN | XXX-FII-SBIN-001 | monthly | Periodic security and operational inspection. NOTE: Inspections shall be performed monthly, with no longer than 45 calendar days between consecutive inspections.
|  |  |  | CA and WA |  | FII-SBIN | XXX-FII-SBIN-001 | monthly | Periodic security and operational inspection. NOTE: Company policy requires a minimum of 7 inspections be performed annually, with no more than 120 days between consecutive monthly or 180 days between the more detail major inspections.
WEATHER STATIONS | Weather Stations − All RAWS and Microstations |  | RAWS and Microstation | CA, OR and WA | Maintenance/ Inspection | WEA | XXX-WSIN-012 | 1 (May) | Perform calibration, visual inspection, dowel replacement (with fuel moisture sensor only), cleaning and sensor check.

## Apparatus
Equipment Type | Equipment Description | Equipment Use | Equipment Model or Manufacturer | Operating Ratings | Maintenance Task | Equip. Code | Maintenance ID | Interval Years (months) | Interval Months | Counters (Ops/Fault) | Notes | Group Counter
BATTERIES | Vented or NiCad (VLA) | WECC - Bulk Electrical System | All |  | Battery Inspection | BAT | XXX-BTTI-004 | 4 months | 4 |  | Battery inspection | 1
| Valve Regulated (VRLA) | WECC - Bulk Electrical System | All |  | Battery Maintenance | BAT | XXX-BTTM-004 | 4 months | 4 |  | Battery impedance test | 1
| Vented or NiCad (VLA) | WECC - Bulk Electrical System | All |  | Battery Maintenance | BAT | XXX-BTTM-018 | 18 months | 18 |  | Battery impedance test | 1
| All | Transmission and distribution (Non-WECC) | All |  | Battery Maintenance | BAT | XXX-BTTM-024 | 2 | 24 |  | Battery impedance test
CIRCUIT BREAKERS | Breaker battery |  | With UPS |  | Circuit Breaker Battery Replacement | CKB | XXX-BKBT-036 | 3 | 36 |  | Circuit Breaker battery replacement
| Recloser battery |  |  |  | Recloser Battery Replacement | CKB | XXX-RCBT-036 | 3 | 36 |  | Recloser battery replacement
| Recloser battery |  | G&W Viper w/351R -0, -1, -2 controllers |  | Recloser Battery Replacement | CKB | XXX-RCBT-024 | 2 | 24 |  | Recloser battery replacement
| All types |  |  | 115kV and above | Warranty Inspection | CKB | XXX-WARR-048 | 4 | 48 |  | Inspect equipment for warranty problems. Schedule based on manufacture date. One time only plan.
| All types | All applications except transformer low side circuit breakers with no bypass, or 35kV and below cap bank switches and others as approved by Asset Management. |  | All voltages | Exercise Breaker | CKB | XXX-BIOA-012 | 1 | 12 |  | Yearly operational test. May be fulfilled by documentation of actual operation. | 1
| Air | Breakers selected by Pacific Power Asset Management (LGCU) |  |  | Minor Maintenance | CKB | DST-BMMA-036 | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed.
| Air | Breakers selected by Pacific Power Asset Management (LGCU) | All |  | Overhaul | CKB | DST-BOHA-108 | 9 | 108
| Air | All applications except bus, cap and low side transformer |  | 35kV and below | Overhaul | CKB | DST-BOHA-CTR |  |  | 50-Fault | Counters applied per Asset Management. | 1
| Air | Tertiary-fed reactor, cap bank, station service, synchronous condenser | All | 13kv and above | Overhaul | CKB | XXX-BOHA-072 | 6 | 72 |  |  | 2
| SF6 gas | Breakers selected by Pacific Power Asset Management (LGCU) |  | All voltages | Minor Maintenance | CKB | XXX-BMMS-036 | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed.
| SF6 gas | Capacitor/reactor without zero crossing | All | 40kv and above | Minor Maintenance | CKB | XXX-BMMS-096 | 8 | 96 | Capacitors 2,000-Ops Reactors 1,000-Ops | Time/ductor inspect mechanism
| SF6 gas | Reactor with zero crossing controls | All | 40kv and above | Minor Maintenance | CKB | XXX-BMMS-072 | 6 | 72 |  | Time/ductor inspect mechanism
| SF6 gas | Reactor with zero crossing controls | All | 40kV and above | Control System Download | CKB | XXX-BXRT-024 | 2 | 24 |  | Meter/relay to download oscillograph data and forward to Apparatus Tech Support for review of proper timing.
CIRCUIT BREAKERS (cont'd) | SF6 gas puffer | Line, transformer, bus |  | 40kV & above | Minor Maintenance | CKB | XXX-BMMS-120 | 10 | 120
| SF6 gas, dual pressure | Line, transformer, bus | All | 40kv and above | Minor Maintenance | CKB | XXX-BMMS-048 | 4 | 48 |  | Time/ductor inspect mechanism | 1
| SF6 gas, dual pressure |  | ITE model GA | 230kV- 500kV | Overhaul | CKB | XXX-BOHS-072 | 6 | 72 |  | These models have overhaul only, no minor maintenance | 1
| SF6 gas, dual pressure |  | Westinghouse model 2300-SF-15000 | 230kV | Overhaul | CKB | XXX-BOHS-072 | 6 | 72 |  | These models have overhaul only, no minor maintenance
| SF6 gas, dual pressure |  | Westinghouse model SFA | 230-500kV | Overhaul | CKB | XXX-BOHS-096 | 8 | 96 |  | These models have overhaul only, no minor maintenance | 2
| SF6 gas bottles | Breakers selected by Pacific Power Asset Management (LGCU) |  |  | Minor Maintenance | CKB | DST-BMMS-036 | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed.
| SF6 gas | Breakers selected by Pacific Power Asset Management (LGCU) |  |  | Overhaul | CKB | DST-BOHS-108 | 9 | 108
| SF6 gas bottles (sealed module) | All applications except bus, cap and low side transformer |  | 35kv and below | Overhaul | CKB | DST-BOHS-CTR |  |  | 50-Fault | Counters applied per Asset Management. Pacific Power ONLY.
| Oil | Breakers selected by Pacific Power Asset Management (LGCU) |  |  | Minor Maintenance | CKB | DST-BMMO-036 | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed.
| Oil | Capacitor or reactor |  | 40kv and above | Minor Maintenance | CKB | XXX-BMMO-072 | 6 | 72 | 1,000-Ops |  | 1
| Oil | Breakers selected by Pacific Power Asset Management (LGCU) |  |  | Overhaul | CKB | XXX-BOHO-108 | 6 | 72
| Oil | All applications except bus, cap and low side transformer |  | 35kv and below | Overhaul | CKB | DST-BOHO-CTR |  |  | 30-Fault | Counters applied per Asset Management. | 1
| Oil | Line transformer, bus |  | 40kV & above | Minor Maintenance | CKB | XXX-BMMO-072 | 6 | 72 | Set-up as Multi-ctr. No counter pts. | Unless cap bank, bus tie, transformer, or reactor CKB | 1
| Vacuum | Breakers selected by Pacific Power Asset Management (LGCU) |  |  | Minor Maintenance | CKB | DST-BMMV-036 | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed.
| Vacuum | Breakers selected by Pacific Power Asset Management (LGCU) |  |  | Overhaul | CKB | DST-BOHV-108 | 9 | 108
| Vacuum | All applications except bus, cap and low side transformer |  | 35kV and below | Overhaul | CKB | DST-BOHV-CTR |  |  | 50-Fault | Counters applied per Asset Management.
| Vacuum | Tertiary-fed reactor, cap bank | All | 13kv and above | Overhaul | CKB | XXX-BOHV-096 | 8 | 96
CIRCUIT BREAKERS (cont'd) | Vacuum | Tertiary-fed SVC, wind site breakers | All | 13kv and above | Overhaul | CKB | XXX-BOHV-120 | 10 | 120
| Vacuum | Synchronous condenser | All | 13kv and above | Overhaul | CKB | XXX-BOHV-072 | 6 | 72
CIRCIT SWITCHERS | Gas | Reactive switching or transformer with 100kV or above low side | S&C Type G, Mark Series , Siemens Linebacker | Reactive Switching, 100kV and above line switching and transformer with 100kV or above low side applications | Inspect and Operate | CSW | XXX-CSIO-060 | 5 | 60 |  | Inspect and test
| Gas | All applications | No physical counter | All voltages | Overhaul | CSW | XXX-CSOH-096 | Contact AM | 96 |  | Review with Risk and Strategy department
| Gas | All applications | S&C 2000 Series | All voltages | Overhaul | CSW | XXX-CSOH-CTR |  |  | 3,000-Ops
| Gas | All applications | S&C Type G, Mark Series (excluding Mark V- pre 1983), Siemens Linebacker, Siemens CPV2, CSV | All voltages | Overhaul | CSW | XXX-CSOH-CTR |  |  | 1,500-Ops
| Gas | All applications | S&C Mark V − pre-1983 | All voltages | Overhaul | CSW | XXX-CSOH-CTR |  |  | 1,000-Ops
FUSE | All spare power transformer fuses |  | S&C and SMD fuses |  | Air Flow Test |  | XXX-FUSE-060 | 5 | 60 |  | Air flow test
GENERATOR | Emergency |  |  |  | Annual Inspection | EPU | XXX-EPUA-012 | 1 | 12 |  |  | 1
GRID RESILIENCE STORAGE FACILITY | Grid resilience facility |  |  |  | GR Equipment/Bldg Inspection |  | XXX-GRID-004 | 4 months | 3 |  | Inspection of grid resilience equipment and storage facility
HVAC | Air conditioners, heating |  | HVAC system units |  | Inspect and Operate | HVAC | XXX-HVAC-012 | 1 | 12 |  | Annual maintenance of heating and AC system (no maintenance on wall or window units, unless specified by operations manager).
REACTORS | All types |  |  | 115kV and above | Warranty Inspection | XRT | XXX-WARR-048 | 4 | 48 |  | Inspect equipment for warranty problems. Schedule based on manufacture date. One-time only plan.
| Substation | Oil-filled |  |  | DGA and Oil Quality Tests | XRT | XXX-XROS-012 | 1 | 12 |  | DGA and oil quality for reactor tank.
| Substation |  | ABB | 345kV, 500kV | DGA and Oil Quality Tests | XRT | XXX-XROS-004 | 4 months | 4 |  | DGA and oil quality for reactor tank. NOTE: Work orders generated every 4 months, a minimum of 2 tests shall be performed in a calendar year. | 1
REGULATOR | 1-phase |  |  |  |  | REG |  |  |  |  | No plan or order. Enter counter reads only. | 1
| 3-phase − non-vacuum |  |  |  | Overhaul | REG | XXX-RGOH-048 | 4 | 48 |  | Inspect contacts and filter oil | 1
| 3-phase vacuum LTC |  | V2A |  | Overhaul | REG | XXX-RGOH-096 | 8 | 96 |  | Inspect contacts & filter oil
REGULATOR (cont'd) | 3-phase − LTC in Tank |  | AFR,AFR300 kva,SFR,TMLT32 | All | DGA and Oil Quality Tests | REG | XXX-RGOS-004 | 4 months | 4 |  | DGA and oil quality for regulator main tank. NOTE: Work orders generated every 4 months, a minimum of 2 tests shall be performed in a calendar year.
| 3-phase − LTC in separate tank |  | GE-MLT32, LR83 COOPER-550BLS, SVR WESTINGHOUSE-URS,URT,UTT | All | DGA and Oil Quality Tests | REG | XXX-RGOS-012 | 1 | 12 |  | DGA and oil quality for regulator main tank.
REGULATOR LTC | 3-phase vacuum LTC |  | V2A | All | DGA Tests | REG | XXX-TCOS-012 | 1 | 12 |  | DGA for LTC Tank
| 3-phase non-vacuum with separate LTC tank |  | GE-MLT32, LR83 COOPER-550BLS, SVR WESTINGHOUSE-URS,URT,UTT | All | DGA Tests | REG | XXX-TCOS-004 | 4 months | 4 |  | DGA for LTC Tank NOTE: Work orders generated every 4 months, a minimum of 2 tests shall be performed in a calendar year.
SERIES CAPACITOR | Under 10 years old |  | All | All | Inspection | SCAP | XXX-SCIN-048 | 4 | 48 |  | On platform inspection − equipment OOS.
| Over 10 years old |  | All | All | Inspection | SCAP | XXX-SCIN-024 | 2 | 24 |  | On platform inspection − equipment OOS.
| With air gap trigger |  | N/A | n/a | Air Gap Injection | SCAP | MGT-ARGP-CTR |  |  | 25 Operations | Pacific Power only at Burns Reactor sub.
SYNCHRONOUS VAR CONTROLLER (SVC) | Thyristor switched |  | All | All | Inspection/Checkout | SVC | XXX-SVCI-024 | 2 | 24 |  | De-energized inspection/checkout per SVC maintenance checklist. | 1
SUBSTATION | Substations − WECC |  |  |  | Sub Safety/Operational Inspection |  | XXX-SBIN-001 | monthly | 1 |  | Periodic substation security and operational inspection, load and counter reads/minor/major scope performed periodically. NOTE: Substations associated with WECC critical paths (WECC - FAC-501), a minimum of 10 monthly inspections shall be performed annually, with 3 of these monthly inspections being the more detailed "major." The maximum interval between the monthly inspections shall be 65 days, with 180 days the maximum interval between a major inspection.
| Substations − Oregon | Oregon only |  |  | Sub Safety/Operational Inspection |  | XXX-SBIN-001 | monthly | 1 |  | Periodic substation security and operational inspection, load and counter reads/minor/major scope performed periodically. NOTE: Inspections shall be performed monthly, with no longer than 45 calendar days between consecutive inspections.
| Substations − all others Including Mobiles |  |  |  | Sub Safety/Operational Inspection |  | XXX-SBIN-001 | monthly | 1 |  | Periodic substation security and operational inspection, load and counter reads/minor/major scope performed periodically. NOTE: Company policy requires a minimum of 7 inspections be performed annually, with no more than 120 days between consecutive monthly or 180 days between the more detail major inspections. | 1
| Pole mount/other facility with no electrical exposure, fence requirement. Excludes FII sites. |  |  |  | Facility Safety/ Operational Inspection |  | XXX-OFIN-xxx | varies |  |  | Interval determined by Asset Management. Inspect pole mounts, collector sites (4 months) or other facilities with no electrical exposure/fence requirement. | 2
| Distribution substation |  |  |  | Infrared Testing |  | XXX-SINF-024 | 2 | 24 |  | Infrared testing of substation bus, switches and major equipment. | 2
| Transmission substation WECC substations |  |  |  | Infrared Testing |  | XXX-SINF-012 | 1 | 12 |  | Infrared testing of substation bus, switches and major equipment.
| Substation security system (WECC only) |  |  |  | Inspection | SSS | XXX-SSSI-036 | 3 | 36 |  | AVTEC security contracted to inspect system. Company required to chaperone AVTEC during inspection.
SUBSTATION (cont'd) | Wood poles |  |  |  | Detail Pole Test and Treat | WOOD | XXX-WOOD-120 | 10 | 120 |  | Wood pole within substation fence will be inspected, tested or treated per company's PTT policies. Inspections completed by OSMOSE and coordinated with sub-operations staff.
TANK | Oil/fuel storage tank |  |  |  | Inspection | TANK | XXX-TKIN-012 | 1 | 12 |  | Inspection of oil or fuel storage and trailer mounted tanks.
| Oil/fuel storage tank, above ground |  |  |  | Certified Tank Inspection | TANK | XXX-TKTS-240 | 20 | 240 |  | Certified tank inspection performed by STI certified tank inspector per PacifiCorp policy 216 and Steel Tank Institute(STI) document SP001 Section 4.
| SF6 cylinder trailers/carts |  |  |  | Inspection | SF6C | XXX-SF6C-060 | 5 | 60 |  | Hammer or ring test SF6 cylinders on handcart and trailers.
TECH OPS BUILDING | Strategic spare equipment |  |  |  | Spare Equipment Inspection |  | XXX-SPAR-004 | 4 months | 4 |  | Inspection of strategic spares in yard
TRANSFORMER | All types |  |  | 115kV and above (low side) | Warranty Inspection | TRF | XXX-WARR-048 | 4 | 48 |  | Inspect equipment for warranty problems. Schedule based on manufacture date. One-time only plan.
| 1-phase | 1 phase |  | Below 230kV and 2.5-59MVA | DGA and Oil Quality Tests | TRF | XXX-TROS-036 | 3 | 36 |  | DGA and oil quality for transformer tank. | 2
| 3-phase | 3 phase |  | Below 230kV and 5-59MVA | DGA and Oil Quality Tests | TRF | XXX-TROS-036 | 3 | 36 |  | DGA and oil quality for transformer tank. | 3
| 1 or 3-phase |  |  | 230kV & above or 60MVA & above | DGA and Oil Quality Tests | TRF | XXX-TROS-012 | 1 | 12 |  | DGA and oil quality for transformer tank. | 2
| Over 40 years old |  |  | Over 40 years of age regardless of size or voltage | DGA and Oil Quality Tests | TRF | XXX-TROS-012 | 1 | 12 |  | Over 40 years old. DGA and oil quality for transformer tank.
| Mobile |  |  |  | DGA and Oil Quality Tests | TRF | XXX-TROS-012 | 1 | 12 |  | DGA and oil quality for transformer tank.
| Designated/strategic spare |  |  |  | Oil Quality Tests | TRF | XXX-TROS-024 | 2 | 24 |  | Oil quality for transformer tank of strategic spares.
TRANSFORMER LTC | All types except vacuum |  |  | All Voltages | DGA Tests | TRF | XXX-TCOS-004 | 4 months | 4 |  | DGA for load tap changer only. NOTE: Work orders generated every 4 months, a minimum of 2 tests shall be performed in a calendar year.
| Vacuum |  | Reinhausen RMV & VR, or Cooper V1 & V2, or LRT -200 & 500 | All voltages | DGA Tests | TRF | XXX-TCOS-012 | 1 | 12 |  | DGA for load tap changer only. | 1
| Reactive with or without filter |  | TC-525, 546 (Fed. Pacific) 550 |  | Overhaul LTC | TRF | XXX-TCOH-036 | 3 | 36 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. | 2
| Reactive without filter |  | UTT, URT, URS, LRT32, MA, UT,THL-21, 496B |  | Overhaul LTC | TRF | XXX-TCOH-036 | 3 | 36 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. | 2
| Reactive with filter, distribution only |  | UTT, URT, URS, LRT32, MA, UT,THL-21, 496B |  | Overhaul LTC | TRF | XXX-TCOH-072 | 6 | 72 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment.
TRANSFORMER LTC (cont'd) | Reactive with filter, transmission only |  | UTT, URT, URS, LRT32, MA, UT,THL-21, 496B |  | Overhaul LTC | TRF | XXX-TCOH-036 | 3 | 36 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. | 4
| Resistive without filter |  | UZD,UZE,UZF,TYPE-M or T |  | Overhaul LTC | TRF | XXX-TCOH-072 | 6 | 72 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. | 4
| Resistive with filter, distribution only |  | UZD,UZE,UZF,TYPE-M or T |  | Overhaul LTC | TRF | XXX-TCOH-108 | 9 | 108 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment.
| Resistive with filter, transmission only |  | UZD,UZE,UZF,TYPE-M or T |  | Overhaul LTC | TRF | XXX-TCOH-072 | 6 | 72 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. | 5
| Vacuum |  | Reinhausen RMV, or Cooper V1 & V2 |  | Overhaul LTC | TRF | XXX-TCOH-144 | 12 | 144 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. | 5
| Vacuum |  | Reinhausen VR |  | Overhaul LTC | TRF | XXX-TCOH-CTR |  |  | 300,000-Ops | NOTE: Overhaul will be based on operational count per manufacturer recommendations.
| Vacuum |  | LRT-200 & 500 |  | Overhaul LTC | TRF | XXX-TCOH-096 | 8 | 96 |  | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment.
| Mobile |  |  | All voltages | Overhaul LTC | TRF | XXX-TCOH-XXX |  |  |  | Same time-based interval as it would be if it was not a mobile LTC.

## Relay
Equipment Type | Equipment Description | Equipment Use | Maintenance Task | Equip. Code | Interval Years | Procedures | Notes
WECC − BULK ELECTRIC SYSTEM
WECC/BES RELAY PACKAGE | Microprocessor relay protection system Monitored and alarming to SCADA | BES (WECC) line, bus or apparatus protection | Major and Control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | B1 | 12 | MAJ/CTRL/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B2 equip code. B2 is scheduled first − 6 years after commissioning.
|  |  | Minor: settings, test auxiliaries, verify inputs | B2 | 12 | MIN | Verify inputs and settings, download history − maintain non-monitored relays per procedures, trip coils if 2 coils present. NOTE: Maintenance shall be scheduled 6 years offset from B1 Equip Code. B2 is scheduled first − 6 years after commissioning.
| Microprocessor relay protection system Not monitored | BES (WECC) line, bus or apparatus protection | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | B3 | 12 | MAJ/CTRL/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B4 Equip Code. B4 is scheduled first − 6 years after commissioning.
|  |  | Major: test and calibrate relays, auxiliaries, verify inputs | B4 | 12 | MAJ/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, auxiliary relays, per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B3 Equip Code. B4 is scheduled first − 6 years after commissioning.
| Primary microprocessor with electromechanical or electronic backup relay | BES (WECC) line, bus or apparatus protection | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | B5 | 12 | MAJ/CTRL/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B6 Equip Code. B6 is scheduled first − 6 years after commissioning.
|  |  | Major: test and calibrate relays, auxiliaries, verify inputs | B6 | 12 | MAJ/INSRVC | Test overall protection package including sudden press if present, CT/ PTs, auxiliary relays, per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B5 Equip Code. B6 is scheduled first − 6 years after commissioning.
| Electronic or electromechanical relay protection system | BES (WECC) line, bus or apparatus protection | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | B7 | 12 | MAJ/CTRL/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B8 Equip Code. B8 is scheduled first − 6 years after commissioning;
|  |  | Major: test and calibrate relays, auxiliaries, verify inputs | B8 | 12 | MAJ/INSRVC | Test overall protection package including sudden press if present, CT/ PTs, auxiliary relays, per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B7 Equip Code. B8 is scheduled first − 6 years after commissioning.
| Programmable Logic Controller (PLC)-based protection systems for series capacitor banks or other devices | BES (WECC) line, bus or apparatus protection | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | B9 | 6 | MAJ/CTRL | Test overall protection package, CT/PTs, auxiliary relays, control wiring per procedures, trip coils if 2 present.
WECC/BES RELAY PACKAGE (cont'd) | Transmission protection with reclosing relay per PRC-005-4 Monitored and alarming to SCADA | BES (WECC) line, bus or apparatus protection | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | BR1 | 12 | MAJ/CTRL/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from BR2 Equip Code. BR2 is scheduled first − 6 years after commissioning.
|  |  | Minor: settings, test auxiliaries, verify inputs | BR2 | 12 | MIN | Verify inputs and settings, download history − Maintain non-monitored relays per procedures, trip coils if 2 coils present. NOTE: Maintenance shall be scheduled 6 years offset from BR1 Equip Code. BR2 is scheduled first − 6 years after commissioning.
| Transmission protection with reclosing relay per PRC-005-4 Not monitored | BES (WECC) line, bus or apparatus protection | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | BR3 | 12 | MAJ/CTRL/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from BR2 Equip Code. BR4 is scheduled first − 6 years after commissioning.
|  |  | Major: test and calibrate relays, auxiliaries, verify inputs | BR4 | 12 | MAJ/INSRVC | Test overall relay package including sudden press if present, CT/ PTs, auxiliary relays, per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B3 Equip Code. BR4 is scheduled first − 6 years after commissioning.
WECC − UNDER-FREQUENCY AND UNDER-VOLTAGE
WECC UF/UV RELAY PACKAGE | Microprocessor relay protection system Monitored and Alarming to SCADA | WECC - Distributed, All UFLS or UVLS | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | U1 | 12 | MAJ/CTRL/INSRVC | Test overall relay package, CT/ PTs, alarm path, auxiliary relays, control wiring per procedures, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from U2 Equip Code. U2 is scheduled first − 6 years after commissioning.
|  |  | Minor: A/D, settings, auxiliaries | U2 | 12 | MIN | Verify inputs and settings, download history − maintain non-monitored auxiliary relays per procedures. NOTE: Maintenance shall be scheduled 6 years offset from U1 Equip Code. U2 is scheduled first − 6 years after commissioning.
| Microprocessor relay protection system Not Monitored | WECC - Distributed, All UFLS or UVLS | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | U3 | 6 | MAJ/CTRL/INSRVC | Test overall relay package, CT/PTs, control wiring.
| Electronic or electromechanical relay protection system − load shed | WECC - Distributed, All UFLS or UVLS | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | U4 | 6 | MAJ/CTRL/INSRVC | Test overall relay package, CT/PTs, control wiring.
TRANSMISSION
TRANSMISSION RELAY PACKAGE | Microprocessor relay protection system | Non-BES (WECC) transmission line, bus or apparatus protection | Major and control: test and calibrate overall relay package, control circuitry, CTs and PTs and control circuitry | T1 | 12 | MAJ/CTRL | Functional test overall relay package, operate lockouts if feasible. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes. NOTE: Maintenance shall be scheduled 6 years offset from T2 Equip Code. T2 is scheduled first − 6 years after commissioning.
|  |  | Minor: A/D, settings, auxiliaries | T2 | 12 | MIN | Verify inputs and settings, download history − maintain non-monitored relays per procedures. NOTE: Maintenance shall be scheduled 6 years offset from T1 Equip Code. T2 is scheduled first − 6 years after commissioning.
| Primary microprocessor with electrical mechanical or electronic backup relay | Non-BES (WECC) transmission line, bus or apparatus protection | Major and Control: Test and Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | T3 | 6 | MAJ / CTRL | MP diagnostic, perform relay functional test and element testing of EM/EE relays, operate lockouts if feasible. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes.
| Electromechanical or electronic relay protection system | Non-BES (WECC) transmission line, bus or apparatus protection | Major and Control: Test and Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | T4 | 6 | MAJ / CTRL | Perform relay functional test and element testing of EM/EE relays, operate lockouts if feasible. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes.
| Transmission auto-throwover | Any transmission line throwover relay package ( Excludes Automated Subs) | Perform relay functional test and decouple and operate motor operators. | T5 | 6 | ATOS | Not subject to PRC-005 standard requirements
DISTRIBUTION
DISTRIBUTION RELAY PACKAGE | Microprocessor relay protection system | Distribution - Non UFLS / UVLS - all applications | Test and Calibrate Relay Package and components | D1 | 12 | MAJ/CTRL | Functional test overall relay package. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes.
| Electromechanical or electronic relay protection system | Distribution - Non UFLS / UVLS - all applications | Test and Calibrate Relay Package and components | D3 | 12 | MAJ/CTRL | Functional test overall relay package. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes.
AUXILIARY RELAYS | Fuse-protected | Transformer | Test and Calibrate Relays/Devices | D4 | 12 | CTRL | Test thermal/other relays
DISTRIBUTION RELAY PACKAGE | Electromechanical or electronic relay with capacitive components protection system | Transformer | Test and Calibrate Relay Package and components | D5 | 6 | MAJ/CTRL | Perform relay element testing of EM/EE relays/test auxiliary relays. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes.
HMI AND WECC − REMEDIAL ACTION SCHEMES
RELAY − HMI | Automated substation | Substation | Replace CPU Battery | S3 | 5 | N/A | Replace CPU battery
RELAY − REMEDIAL ACTION SCHEME | Remedial Action Scheme and components | Remedial Action Scheme components | Remedial Action Scheme functional testing | SPS1* | 6 | Functional testing | Maintain per PRC-005 requirements
|  |  | Major and Control: test and calibrate overall relay package, control circuitry, CTs, PTs and control circuitry | B1* | 12 | MAJ/CTRL/INSRVC | Test overall relay package including sudden pressure if present, CT/ PTs, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B2 Equip Code. B2 is scheduled first, 6 years after commissioning.
|  |  | Minor: settings, test auxiliaries, verify inputs | B2* | 12 | MIN | Verify inputs and settings, download history. Maintain non-monitored relays per procedures, trip coils if 2 coils present. NOTE: Maintenance shall be scheduled 6 years offset from B1 Equip Code. B2 is scheduled first, 6 years after commissioning.
*SPS1 maintenance to be completed with B1 and B2 maintenance based on schedule outlined above.
DOBLE TEST EQUIPMENT
Relay - Doble Test Equip | Doble F6150 test equipment | Relay Test Equip | Test and calibrate relay test set | TST | 12 | N/A | Perform annual calibration of Doble F6150

## Meter
Equipment | Equipment Types | Equipment Use | Witness | Form(s) to Submit | Equip. Code | Maintenance Type | Interval Years | Maintenance ID | Notes
Meter Package | Intertie Meters (Interchange Meter as Defined by NERC Bal-005) | PAC-owned WECC | YES | Form 129F | MTR | M1 | 2 | XXX-M1-024 | Test document 129F must have the NERC/WECC portion populated on at least one meter in package.
| Intertie Meters (Interchange Meter as defined by NERC Bal-005) | Foreign-owned | YES | Foreign Utility Test Form and Form 130F | MTR | M2 | Varies | XXX-M2-XXX | Interval determined by other utility.
| Borderline or PAC gen meters | PAC-owned Non-WECC | YES | Form 129F | MTR | M3 | 2 | XXX-M3-024
| Borderline or cust gen meters | Foreign-owned Non-WECC | YES | Foreign Utility Test Form and Form 130F | MTR | M4 | Varies | XXX-M4-XXX | Interval determined by other utility.
| Borderline, gen retail, PAC gen or load meters | PAC-owned Non-WECC | NO | Form 129F | MTR | M5 | 2 | XXX-M5-024 | Load - meters used for retail loads that provide SCADA to the EMS.
| Check or Stateline Meters | PAC-owned Non-WECC | NO | Form 129F | MTR | M6 | 5 | XXX-M6-060
| Retail | PAC-owned Non-WECC | NO | None | MTR | N/A | Varies | Maintained in CSS | Retail - Meter used for retail load outside of a substation.
| CAISO/EIM Meters | PAC-owned | NO | Form 129F | MTR | Various | 2 | Various
| CAISO/EIM Meters | Foreign-owned | YES | Foreign Utility Test Form and Form 130F | MTR | Various | 2 | Various

## Communications
Equip Code | Equipment Type | Equipment Description | Requires Commissioning see note 4 | Equipment Use | Equipment Model Examples | Maintenance Task | Maintenance ID | Interval Calendar Year | Man Hours | Notes | EC PM MAT | EC Repair MAT | MG/LOC PM MAT | MG/LOC Repair MAT
ASR | Antenna structure registration | FCC number attached to a tower and cleared with the FAA | No | Non-BES | Number attached to the tower | Check tower for FCC antenna registration number | GMP6004 | 4 | 1 | Antenna structure meets FAA and FCC requirements | CSM 579 | CSR 580 | CSM 887 | CSR 888
BAS | Base radio | Mobile radio system base station | Yes | Non-BES | TAIT | Testing | GMP6301 | 1 | 8 | Radio meets FCC requirements | RDM 585 | RDR 586 | RDM 895 | RDR 896
BAS/MCL | Base radio control link | Point to point mobile radio system | Yes | Non-BES |  | Testing | GMP6301 | 2 | 5 | Radio meets FCC requirements | RDM 585 | RDR 586 | RDM 895 | RDR 896
BAT | Power supply | Battery and charger | Yes | Non-BES | All non-BES | Inspect and maintain | GMP6502 | 1 | 5 | Battery impedance test | BAM 588 | BAF 589 | BAM 828 | BAF 829
| Substation site/vented lead acid | Battery and charger | Yes | BES (WECC) | Alcad, Fiamm, Hoppecke | Battery inspection | GMP6504 | 4 month | 5 | Battery inspection test | BAM 588 | BAF 589 | BAM 828 | BAF 829
| Substation site/valve regulated | Battery and charger | Yes | BES (WECC) | East Penn, C&D | Battery maintenance | GMP6503 | 4 month | 5 | Battery impedance test | BAM 588 | BAF 589 | BAM 828 | BAF 829
| Substation site/vented lead acid | Battery and charger | Yes | BES (WECC) | Alcad, Fiamm, Hoppecke | Battery maintenance | GMP6505 | 18 month | 5 | Battery impedance test | BAM 588 | BAF 589 | BAM 828 | BAF 829
DCS | Digital cross connect system | Digital cross connect system | Yes | Non-BES | DNX-88, Titan 532L, V4150 | Testing | GMP6450 | 1 | 3 | Verify high-speed module protection | DCM 608 | DCR 609 | DCM 908 | DCR 910
EPUy | Generator (comm.) | LP gas engine generator | Yes | Non-BES | Generac, Onan, Kohler | Inspect and maintain | GMP6512 | 1 | 5 | Pre-winter LOF and inspection | GPM 596 | GPR 597 | GPM 834 | GPR 835
EPUm | Generator (comm.) | Diesel generator only | Yes | Non-BES | Caterpillar | Inspect | GMP6513 | 1 month | 1 | Monthly startup/inspection. Diesel only. | GPM 596 | GPR 597 | GPM 834 | GPR 835
FAC | Communication site | Property and equipment | Yes | Non-BES | Various | Inspection | GMP6001 | 6 month | 5 | Semi-annual check of facility and peripheral equipment | CSM 579 | CSR 580 | CSM 887 | CSR 888
FOT | Fiber optics terminal | FO multiplex equipment | Yes | Non-BES | Larus FT2, ATT DDM 1000, NEC RC28D, DMXplore | Test and maintain | GMP6402 | 4 | 4 | Perform tests | FOM 602 | FOR 603 | FOM 830 | FOR 831
DMX FOT | DMX Ffber optics terminal | FO multiplex equipment | Yes | Non-BES | DMX, DMXtend | Inspect | GMP6403 | 1 | 4 | Change filter | FOM 602 | FOR 603 | FOM 830 | FOR 831
MAS | Radio (MAS) Master all/Transmission only for remotes | SCADA radio | Yes | Non-BES | Darcomm, MDS, Alligator | Testing | GMP6332 | 1 | 4 | Perform tests. Radio meets FCC requirements. | RDM 585 | RDR 586 | RDM 895 | RDR 896
MAS/MCL | MAS radio control link | Point to point SCADA radio system | Yes | Non-BES | Darcomm, Alligator, Optaphone | Testing | GMP6332 | 1 | 4 | Perform tests. Radio meets FCC requirements. | RDM 585 | RDR 586 | RDM 895 | RDR 896
MWD | Radio (digital) | Digital microwave | Yes | Non-BES | Alcatel MDR-6706, Harris Constellation, IRU600 | Testing | GMP6312 | 1 | 4 | Perform tests on Digital MW | CTM 590 | CTR 591 | CTM 898 | CTR 899
OTN | Optical transport network |  | Yes | Non-BES | Ciena 6500 | Testing | GMP6405 | 1 | 3 | Perform tests
PLC | Power line carrier | On/off PLC terminal | Yes | BES (WECC) | Westinghouse TC10B | Inspect | GMP 6104 | 4 month | 6 | Function verification | PLM 593 | PLR 594 | PLM 832 | PLR 833
| Power line carrier | PLC terminal | Yes | BES (WECC) | GE Type 51, 61, 71, TCF-10B | Maintenance | GMP6102 | 2 see note 3 | 6 | Check levels and operate. Perform test. | PLM 593 | PLR 594 | PLM 832 | PLR 833
RTU | Remote terminal unit/transmission only | SCADA remote | Yes | Non-BES, except Jim Bridger SEL RTU's | Harris D-20, L&G 5700 | Inspection | GMP6342 | 1 | 4 | Inspect | RTR 583 | RTR 584 | RTM 893 | RTR 894
RTU | GE N60 | Logic controller | Yes | CIP | GE N60 | Test | GMP6345 | 5 | 8 | Perform test | RTR 583 | RTR 584 | RTM 893 | RTR 894
RCC | Monarch comm. channels | SCADA | No | Non-BES | Monarch | Inspection | GMP6343 | 4 month | 3 | PCC and SCC communications channel switchover | RTR 583 | RTR 584 | RTM 893 | RTR 894
TON | Tone relay | Tone relay terminal | Yes | BES (WECC) | GE Type 30, GE Type 40, RFL 6745 | Test and maintain | GMP6202 | 1 see note 1 | 4 | Check levels and operate. Perform test. | TOM 598 | TOR 599 | TOM 836 | TOR 837
| Tone relay | Tone relay terminal | Yes | BES (WECC) | 9745 | Test and maintain | GMP6204 | 4 see note 2 | 4 | Check levels and operate. Perform test. | TOM 598 | TOR 599 | TOM 836 | TOR 837
TOWg | Tower (guyed) | Tower | Yes | Non-BES | All | Inspect and maintain | GMP6005 | 3 | 4 | Contracted inspection of guyed towers | CSM 579 | CSR 580 | CSM 887 | CSR 888
TOWs | Tower(steel) | Tower | Yes | Non-BES | Sabre, Microflect, Valmont | Inspect and maintain | GMP6002 | 5 | 4 | Contracted inspection of steel towers | CSM 579 | CSR 580 | CSM 887 | CSR 888
1) Interval shown is the preferred interval. Work orders will be generated every calendar year with a PM performed no longer than 18 calendar months between consecutive tests.
2) Interval shown is the preferred interval. Work orders will be generated every 4 calendar years with a PM performed no longer than 60 calendar months between consecutive tests.
3) Interval shown is the preferred interval. Work orders will be generated every 2 calendar years with an interval of no longer than 36 calendar months between consecutive tests.
4) Other equipment requiring commissioning would include, HVAC, digital mux, charger, DRI, DFI, fiber optic cable, network equipment, satellite equipment, and telemetery equipment.

##  (hidden)
Equipment Type
Meter Package -