## Sheet1
**This Data Request Summary reflects Data Requests completed each Thursday | [5 empty] | LSPGC 2023-2025 WMP Request Log
Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Responses | Requestor | Date Rec'd | Final Due Date | Date Sent | Links | Number of Atchs | NDA required | WMP Section | Category | Subcategory | Confidential (Yes)
1 | OEIS | 2023-01 | P-WMP_2023-LSP-001 | 1 | 01-OEIS-P-WMP_2023-LSP-001 Q. 01 Answer | Regarding Vegetation Management On page 120 of its WMP, LS Power states “Operations personnel and qualified contractors will perform patrol inspections by visually inspecting vegetation around the facility and equipment.” a. What are the qualifications of the contractors who will perform the vegetation inspection around the facility? b. What are the qualifications of the contractor or personnel who will assess trees that are tall enough to strike the facility? | a. Response: Once operational, LSPGC substation personnel will perform monthly substation inspections which include inspection of vegetation in and around the facilities. Table 8-11 in the WMP describes the expected qualifications of these yet-to-be hired individuals. While it is unlikely that they will posses an arborist or forestry background, they will be trained on the specific hazards and protocols related to LSPGC facilities including the substation defensive space. b. Response: Ahead of operations, LSPGC expects to engage an ISA Certified Arborist Utility Specialist to conduct a survey around the facilities and inform of any trees outside of the substation defensible space that may require ongoing monitoring. Please note that LSPGC facilities planned for the current WMP cycle include no transmission lines. | OEIS | 2023-09-13 | 2023-09-18 | 2023-09-18 | N/A | N/A | No | 8.2 | Wildfire Mitigations | Vegetation Management and inspetions
2 | OEIS | 2023-02 | P-WMP_2023-LSP-002 | 1 | 01-OEIS-P-WMP_2023-LSP-002 Q. 01 Answer | a. Describe LS Power’s plans, including a timeline, for developing its PSPS Protocols | Response: LSPGC anticipates developing PSPS Protocols ahead of commercial operation of the company’s first transmission line assets which are currently scheduled for December 2027. | OEIS | 2023-09-15 | 2023-09-20 | 2023-09-20 | N/A | N/A | No | 9.2 | Public Safety Power Shutoff | Protocols on PSPS
3 | OEIS | 2023-02 | P-WMP_2023-LSP-002 | 2 | 02-OEIS-P-WMP_2023-LSP-002 Q. 02 Answer | a. In Table 8-5 of LS Power’s WMP, LS Power lists a projection of two grid inspection findings in 2025. Explain how LS Power calculated and determined this projection. | Response: 2025 is expected to be the first full year of operations for LSPGC’s Orchard and Fern Rd. substations. As such, and as newly constructed facilities without operating history, it was determined that one grid inspection finding per location was a reasonable projection based on LSPGC affiliates’ operations and the aforementioned factors. | OEIS | 2023-09-15 | 2023-09-20 | 2023-09-20 | N/A | N/A | No | 8.1 | Wildfire Mitigations | Grid Design, Operations, and Maintenance
4 | OEIS | 2024-01 | OEIS-P-WMP_2024-LSP-001 | 1 | 01-OEIS-P-WMP_2024-LSP-001 Q. 01 Answer | Regarding 2025 Vegetation Inspection Quarterly Targets (LSP-04): In its 2025 WMP Update, LS Power defines the 2025 vegetation inspection targets as 6 for the end of Q2, 9 for the end of Q3, and 15 for the end of the year.1 LS Power’s 2023-2025 Base WMP redline indicates that vegetation inspections will occur “monthly and ahead of extreme weather events (RFW).” a. Clarify if LS Power intends to use inspections ahead of extreme weather events to also meet monthly inspection commitments. b. Will LS Power meet the target of 15 inspections regardless of the number of extreme weather events? i. If so, when would these additional three inspections beyond the 12 that are conducted monthly occur and what would be their purpose? c. How will LS Power approach vegetation inspections ahead of extreme weather events if the target of 15 inspections has already been met? d. Explain how monthly inspections are scheduled (e.g., occurring at a regular cadence or scheduled as extreme weather events are anticipated). | a) Response: Additional vegetation inspections may occur ahead of extreme weather events such as Red Flag Warnings (RFWs) or other warnings such as fire weather watches, high wind advisories, and fuels and fire behavior advisories for the area in which the substations are located. Potential inspections due to extreme weather events were not included in the yearly targets. b) Response: LS Power will meet the target of 15 inspections regardless of extreme weather occurrences, subject to project in-service dates. The targets were based on expected in-service of the Orchard Substation throughout 2025 and in-service of the Fern Road Substation in Q4 2025. Both of these in-service dates are subject to change. This would be 12 inspections (once monthly) for Orchard and 3 inspections for Fern Road (once monthly starting Oct.). c) Response: LSPGC does not consider the target to be a limit on inspections and will inspect facilities as needed. d) Response: Monthly inspections will occur on regularly scheduled cadence and additional inspections will be conducted if deemed necessary ahead of extreme weather events. | OEIS | 2024-07-25 | 2024-07-30 | 2024-07-30 | N/A | N/A | No | 8.1 & 8.2 | Wildfire Mitigations | Grid Design, Operations, and Maintenance & Vegetation Management and inspetions
5 | OEIS | 2024-02 | OEIS-P-WMP_2024-LSP-002 | 1 | 01-OEIS-P-WMP_2024-LSP-002 Q. 01 Answer | Regarding Integration of StormGeo: On page 6 of its 2025 WMP Update, LS Power states that its objective completion date for integrating StormGeo (LSP-05) has shifted from December 2024 to Q1 2025. LS Power provides a justification for this change, stating that its first substation was previously scheduled to be operational in June 2024 but has now shifted to January 2025. i. Confirm that the reason for delays in StormGeo integration (December 2024 to Q1 2025) is due to delays in scheduled substation operation (June 2024 to January 2025). 1. If this is incorrect, please explain the reason(s) for delays in StormGeo integration. ii. Provide and explain the reason(s) for the delay in substation operation shifting from June 2024 to January 2025. iii. Explain how the data derived from StormGeo will be used in daily operations (e.g., Fire Potential Index, staffing levels, decision points for maintenance, etc.). |  | OEIS | 2024-08-14 | 2024-08-19 |  | N/A | N/A | No | 8.3 | Wildfire Mitigations | Situational Awareness and Forecasting
6 | OEIS | 2024-02 | OEIS-P-WMP_2024-LSP-002 | 2 | 02-OEIS-P-WMP_2024-LSP-002 Q. 02 Answer | Regarding Weather Station Deployment: a. On page 9 of its 2025 WMP Update, LS Power discusses a new program to include dedicated weather stations on site at all LS Power substations. i. Provide the total number, type, and location (latitude/longitude) of all weather stations that will be deployed throughout LS Power’s service territory. ii. Include an annual maintenance and calibration schedule for all weather stations. |  | OEIS | 2024-08-14 | 2024-08-19 |  | N/A | N/A | No | 8.3 | Wildfire Mitigations | Situational Awareness and Forecasting