## Decision Framework AT
| Circuit Name (1 miles) |  | No System Hardening | Overhead Hardening | Under-Grounding | Hybrid | Circuit Name - Zone - PM #
| Project Scope Risk Reduced After Mitigation |  | - | 0.9 | 0.99 | 0.945
| Project Scope Residual Risk Value |  | 1 | 0.1 | 0.01 | 0.055
| Overall Miles Installed |  | 1 Existing OH | 1 | 1 | 1 | OH | UG | Hybrid
| Overall Miles Removed |  | - | - | - | -
| OH System Hardening Cost | $1M/risk-mile | - | $1.2M | - | $0.6M (0.5 mi) | 1.2 |  | 0.6
| UG System Hardening Cost | $2.8M/risk-mile | - | - | $2.8M | $1.4M (0.5 mi) |  | 2.8 | 1.4
| Line Removal Cost | $106k/risk-mile | - | - | - | - | 0 | 0 | 0
| Total Capital Cost (AACE Class 5) |  |  | $1.2M | $2.8M | $2M | 0 | 0 | 0
| Average O&M Cost (per year) |  |  | $15k | $3k | $9k
| NPV @ 6.8% discount rate |  |  | ($1.3M) | ($2.9M) | ($2.1M)
Primary Filter | $ NPV per unit of rise (RSE) |  |  | ($1.48M) 1st | ($2.89M) 3rd | ($2.21M) 2nd | -1479.693 | -2885.3242 | -2214.7344
| PSS Preference (Ingress/egress/fire history) |  |  | Satisfactory | Satisfactory | Satisfactory | 1st | 3rd | 2nd | Select One | Preferred | Satisfactory | Non-satisfactory
Secondary Filter | Strike Tree Potential |  | High Fall-In Risk | Low Fall-In Risk | No Fall-In Risk | No Fall-In Risk
| Ingress / Egress |  | Non-satisfactory | Satisfactory | Preferred | Satisfactory |  |  |  | Select One | No Fall-In Risk | Low Fall-In Risk | Moderate Fall-In Risk | High Fall-In Risk
PSPS Mitigation (# custs * # event)
| Execution timeline (2021, 2022, 2022+) |  |  | 2021 | 2022+ | 2022+
Other (Operational Considerations, etc.)
Recommended
NEEDS MANUAL SELECTION
NEEDS MANUAL SELECTION
NEEDS MANUAL SELECTION
NEEDS MANUAL ENTRY (if necessary)
NEEDS MANUAL ENTRY
Do NOT make any changes to anything in this section. It is automatically updated when you make changes to the "Inputs" & "Risks" tabs

## Decision Framework
| Circuit Name (1 miles) |  | No System Hardening | Overhead Hardening | Under-Grounding | Hybrid | Circuit Name - Zone - PM #
| Project Scope Risk Reduced After Mitigation |  | - | 0.72 | 0.99 | 0.855
| Project Scope Residual Risk Value |  | 1 | 0.28 | 0.01 | 0.145
| Overall Miles Installed |  | 1 Existing OH | 1 | 1 | 1 | OH | UG | Hybrid
| Overall Miles Removed |  | - | - | - | -
| OH System Hardening Cost | $1M/risk-mile | - | $1M | - | $0.5M (0.5 mi) | 1 |  | 0.5
| UG System Hardening Cost | $2.8M/risk-mile | - | - | $2.8M | $1.4M (0.5 mi) |  | 2.8 | 1.4
| Line Removal Cost | $106k/risk-mile | - | - | - | - | 0 | 0 | 0
| Total Capital Cost (AACE Class 5) |  |  | $1M | $2.8M | $1.9M | 0 | 0 | 0
| Average O&M Cost (per year) |  |  | $15k | $3k | $9k
| NPV @ 6.8% discount rate |  |  | ($1.3M) | ($2.9M) | ($2.1M)
Primary Filter | $ NPV per unit of rise (RSE) |  |  | ($1.85M) 1st | ($2.89M) 3rd | ($2.45M) 2nd | -1849.6163 | -2885.3242 | -2447.8644
| PSS Preference (Ingress/egress/fire history) |  |  | Non-satisfactory | Satisfactory | Satisfactory | 1st | 3rd | 2nd | Select One | Preferred | Satisfactory | Non-satisfactory
Secondary Filter | Strike Tree Potential |  | High Fall-In Risk | Moderate Fall-In Risk | No Fall-In Risk | Low Fall-In Risk
| Ingress / Egress |  | Non-satisfactory | Non-satisfactory | Preferred | Satisfactory |  |  |  | Select One | No Fall-In Risk | Low Fall-In Risk | Moderate Fall-In Risk | High Fall-In Risk
PSPS Mitigation (# custs * # event)
| Execution timeline (2021, 2022, 2022+) |  |  | 2021 | 2022+ | 2022+
Other (Operational Considerations, etc.)
Recommended
NEEDS MANUAL SELECTION
NEEDS MANUAL SELECTION
NEEDS MANUAL SELECTION
NEEDS MANUAL ENTRY (if necessary)
NEEDS MANUAL ENTRY
Do NOT make any changes to anything in this section. It is automatically updated when you make changes to the "Inputs" & "Risks" tabs

## Inputs
Overhead (OH) vs. Underground (UG) Electric Distribution Analysis
Blue Inputs (in yellow cream boxes), Black Formulas | [8 empty] | RESULTS ($000's)
Project Description | Work Type - Circuit Name - Zone - PM # |  | Study Period (i.e. 30-50 yrs) |  | 45 |  |  |  | Hybrid | If All Overhead | If All Underground
| Install | Remove
All Overhead Miles | 1 | 0 | Discount Rate |  | 6.8% |  |  | Cap Ex | 1869.0497 | 974.869 | 2763.2303
All Underground Miles | 1 | 0 | Inflation Rate |  | 2.5% |  |  | Op Ex/Yr. | 8.8536 | 14.7926 | 2.9146 | Hybrid Cost by Type
Hybrid OH Miles | 0.5 |  | Project Risk Value |  | 1 |  |  | $/Mile Mitigated | 1869.0497 | 974.869 | 2763.2303 | 487.4345 | OH Cost | 72% | OH Realistic Harden in Place Risk Reduction
Hybrid UG Miles | 0.5 |  | Existing HFTD Project Miles |  | 1 | [6 empty] | 1381.6152 | UG Cost | 99% | UG Harden Risk Reduction
Hybrid Total Miles | 1 |  | Service Life - Overhead |  | 45 |  |  | NPV Note 1 | -2092.924 | -1331.7237 | -2856.4709 | 487.4345 | $/OH Mile Mitgated | 100% | Line Removal Risk Reduction
Tree Count (avg. trees/mile) | 0 |  | Service Life - Underground |  | 47 | [6 empty] | 1381.6152 | $/UG Mile Mitigated
In Service Year | 2021 |  | Cap Ex Assumption (Select from drop down) |  | Detailed Cost Input |  |  | System Risk Reduction | 0.855 | 0.72 | 0.99
Current year | 2022 |  | Tier |  | 3 |  |  | NPV/Risk Reduced | -2447.8644 | -1849.6163 | -2885.3242
[8 empty] | Remaining Risk | 0.145 | 0.28 | 0.01
[8 empty] | PVRR | 2906.177 | 1849.1951 | 3966.4173
Detailed Capital Expenditures (Cap Ex) ($2021) |  | Overhead | Underground | Hybrid |  | TOTALS ($000's)
Capital Cost Category | Detailed Description | $000/Mile | $000/Mile | $000/Mile |  | Hybrid | If All Overhead | If All Underground | Source | Notes
Planning & Prep | Cost | 44.271 | 63.1867 | 63.1867 |  | 53.7288 | 44.271 | 63.1867 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
Land and Regulatory | Cost | 35.771 | 148.3613 | 148.3613 |  | 92.0662 | 35.771 | 148.3613 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
ConstructionNote 2 | Cost | 578.01 | 2185.5514 | 2185.5514 |  | 1381.7807 | 578.01 | 2185.5514 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
| Line Removal | 0 | 0 | 0 |  | 0 | 0 | 0
Administrative & General | Cost | 316.817 | 366.131 | 366.131 |  | 341.474 | 316.817 | 366.131 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
Detailed Cost Input | Total From Above | 974.869 | 2763.2303 | 2763.2303 |  | 1869.0497 | 974.869 | 2763.2303
[5 empty] | $/Mile | 1869.0497 | 974.869 | 2763.2303
Detailed Operating Expenses (Op Ex)Annual($2021) |  | Overhead | Underground |  |  | TOTALS ($000's)
Expense Cost Category | Detailed Description | $000/Mile | $000/Mile |  |  | Project as Planned | If All Overhead | If All Underground | Source | Notes
Patrols & inspections |  | 3.6816 | 0.70393 |  |  | 2.1927 | 3.6816 | 0.70393 | Business Finance
Outage and Emergency |  | 7.7838 | 1.1148 |  |  | 4.4493 | 7.7838 | 1.1148 | Business Finance
Maintenance & repair |  | 0.78238 | 0.59666 |  |  | 0.68952 | 0.78238 | 0.59666 | Business Finance
Supervision & engg |  | 0.49921 | 0.49921 |  |  | 0.49921 | 0.49921 | 0.49921 | Business Finance
PSPS |  | 2.0456 |  |  |  | 1.0228 | 2.0456 |  | Business Finance
Veg management | Depends on trees per mile | 0 |  |  |  | 0 | 0 |  | EO Veg mgmt
Detailed Cost | Total From Above | 14.7926 | 2.9146 |  |  | 8.8536 | 14.7926 | 2.9146
Ongoing Capital |  | 8.7895 | 4.9647 |  |  | 6.8771 | 8.7895 | 4.9647 | Business Finance
Note 1: The alternatives have been compared to determine which is in the best interest of customers using a net present value of cash flows (NPV). NPV measures the after-tax value created by a project. A project is economically attractive if its NPV is positive or greater than that of all other project alternatives. NPV is calculated by determining the expected cash inflows and outflows for each project and then discounting them to a present value. Under (perfect) cost-of-service-ratemaking, the NPV for an investment will always be zero, assuming full regulatory recovery of project cost at the authorized rate of return. For purposes of this NPV analysis, revenues are ignored, to isolate the lowest cost to customers .
Note 2. Labor - trenching & conduit refers to trenching, boring, backfilling, conduit installation, etc.; Labor – electrical refers to cable pulling, splicing, cable termination, etc.
Cost taxonomy derived from PG&E GRC, stakeholder interviews, and PG&E Field Accounting Handbook
The capital part of the O&M is treated as capital to be added in EASOP as ongoing capital costs. The rest of the O&M which was categorized as expense, was treated as operating expense. For additional O&M costs applied as capital please see the "Unit O&M inputs" tab.

## Inputs AT
Overhead (OH) vs. Underground (UG) Electric Distribution Analysis
Blue Inputs (in yellow cream boxes), Black Formulas | [8 empty] | RESULTS ($000's)
Project Description | Work Type - Circuit Name - Zone - PM # |  | Study Period (i.e. 30-50 yrs) |  | 45 |  |  |  | Hybrid | If All Overhead | If All Underground
| Install | Remove
All Overhead Miles | 1 | 0 | Discount Rate |  | 6.8% |  |  | Cap Ex | 2019.0497 | 1174.869 | 2763.2303
All Underground Miles | 1 | 0 | Inflation Rate |  | 2.5% |  |  | Op Ex/Yr. | 8.8536 | 14.7926 | 2.9146 | Hybrid Cost by Type
Hybrid OH Miles | 0.5 |  | Project Risk Value |  | 1 |  |  | $/Mile Mitigated | 2019.0497 | 1174.869 | 2763.2303 | 587.4345 | OH Cost | 90% | OH Realistic Harden in Place Risk Reduction
Hybrid UG Miles | 0.5 |  | Existing HFTD Project Miles |  | 1 | [6 empty] | 1431.6152 | UG Cost | 99% | UG Harden Risk Reduction
Hybrid Total Miles | 1 |  | Service Life - Overhead |  | 45 |  |  | NPV Note 1 | -2092.924 | -1331.7237 | -2856.4709 | 587.4345 | $/OH Mile Mitgated | 100% | Line Removal Risk Reduction
Tree Count (avg. trees/mile) | 0 |  | Service Life - Underground |  | 47 | [6 empty] | 1431.6152 | $/UG Mile Mitigated
In Service Year | 2021 |  | Cap Ex Assumption (Select from drop down) |  | Detailed Cost Input |  |  | System Risk Reduction | 0.945 | 0.9 | 0.99
Current year | 2022 |  | Tier |  | 3 |  |  | NPV/Risk Reduced | -2214.7344 | -1479.693 | -2885.3242
[8 empty] | Remaining Risk | 0.055 | 0.1 | 0.01
[8 empty] | PVRR | 2906.177 | 1849.1951 | 3966.4173
Detailed Capital Expenditures (Cap Ex) ($2021) |  | Overhead | Underground | Hybrid |  | TOTALS ($000's)
Capital Cost Category | Detailed Description | $000/Mile | $000/Mile | $000/Mile |  | Hybrid | If All Overhead | If All Underground | Source | Notes
Planning & Prep | Cost | 44.271 | 63.1867 | 63.1867 |  | 53.7288 | 44.271 | 63.1867 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
Land and Regulatory | Cost | 35.771 | 148.3613 | 148.3613 |  | 92.0662 | 35.771 | 148.3613 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
ConstructionNote 2 | Cost | 578.01 | 2185.5514 | 2185.5514 |  | 1381.7807 | 578.01 | 2185.5514 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
| Line Removal | 0 | 0 | 0 |  | 0 | 0 | 0
Administrative & General | Cost | 316.817 | 366.131 | 366.131 |  | 341.474 | 316.817 | 366.131 | Business Finance | See "Unit Capital Inputs" sheet
| Risk | 0 | 0 | 0 |  | 0 | 0 | 0 |  | See Risk Worksheet
REFLCL/AT |  | 200 | 0 | 100 |  | 150 | 200 | 0
Detailed Cost Input | Total From Above | 974.869 | 2763.2303 | 2763.2303 |  | 2019.0497 | 1174.869 | 2763.2303
[5 empty] | $/Mile | 2019.0497 | 1174.869 | 2763.2303
Detailed Operating Expenses (Op Ex)Annual($2021) |  | Overhead | Underground |  |  | TOTALS ($000's)
Expense Cost Category | Detailed Description | $000/Mile | $000/Mile |  |  | Project as Planned | If All Overhead | If All Underground | Source | Notes
Patrols & inspections |  | 3.6816 | 0.70393 |  |  | 2.1927 | 3.6816 | 0.70393 | Business Finance
Outage and Emergency |  | 7.7838 | 1.1148 |  |  | 4.4493 | 7.7838 | 1.1148 | Business Finance
Maintenance & repair |  | 0.78238 | 0.59666 |  |  | 0.68952 | 0.78238 | 0.59666 | Business Finance
Supervision & engg |  | 0.49921 | 0.49921 |  |  | 0.49921 | 0.49921 | 0.49921 | Business Finance
PSPS |  | 2.0456 |  |  |  | 1.0228 | 2.0456 |  | Business Finance
Veg management | Depends on trees per mile | 0 |  |  |  | 0 | 0 |  | EO Veg mgmt
Detailed Cost | Total From Above | 14.7926 | 2.9146 |  |  | 8.8536 | 14.7926 | 2.9146
Ongoing Capital |  | 8.7895 | 4.9647 |  |  | 6.8771 | 8.7895 | 4.9647 | Business Finance
Note 1: The alternatives have been compared to determine which is in the best interest of customers using a net present value of cash flows (NPV). NPV measures the after-tax value created by a project. A project is economically attractive if its NPV is positive or greater than that of all other project alternatives. NPV is calculated by determining the expected cash inflows and outflows for each project and then discounting them to a present value. Under (perfect) cost-of-service-ratemaking, the NPV for an investment will always be zero, assuming full regulatory recovery of project cost at the authorized rate of return. For purposes of this NPV analysis, revenues are ignored, to isolate the lowest cost to customers .
Note 2. Labor - trenching & conduit refers to trenching, boring, backfilling, conduit installation, etc.; Labor – electrical refers to cable pulling, splicing, cable termination, etc.
Cost taxonomy derived from PG&E GRC, stakeholder interviews, and PG&E Field Accounting Handbook
The capital part of the O&M is treated as capital to be added in EASOP as ongoing capital costs. The rest of the O&M which was categorized as expense, was treated as operating expense. For additional O&M costs applied as capital please see the "Unit O&M inputs" tab.

## Risks
Risk Details ($000/mile) |  | OH System Hardening Cost ($1M/risk-mile mitigated) |  | $1M
Purpose: User Input Worksheet to quantify project risks |  |  |  |  | $2.8M
Input In Yellow Area, or Select from Drop Down
Cap Ex Risk Adjustment Detail ($2020) |  | Hybrid | Overhead | Underground
Area of Risk | Alternatives | Adjustment | Adjustment | Adjustment | Detailed Description of Cost Variance | Source | Additional Comments
|  | ($000/Mile) | ($000/Mile) | ($000/Mile)
Planning and Prep Areas of Risk
Cal Trans - DSDD |  |  |  |  | $100k/mile for OH in CalTrans ROW |  | Enter additional comments to support risk
Cal Trans - Stamped Civil Drawings |  |  |  |  | $100k/mile if 1 mile or less. $50k/mile if more than a mile. Required when UG in CalTrans ROW |  | Enter additional comments to support risk
Base Map Creation |  |  |  |  | $20k/mile for non-Bay Area & $50k/mile for Bay Area. Required for UG and only required for OH if DSDD included |  | Enter additional comments to support risk
Land and Regulatory
Asset Terrain (Select One) | Average (No Adjustment) | 0 |  | 0 | Assets are along a paved or gravel road |  | Enter additional comments to support risk
Dedicated Street Easement? (Select) | 100% (No Adjustment) | 0 |  | 0 | 5280'/200 x $6300 = $166,320/mile assumed |  | Enter additional comments to support risk
Retaining Walls |  |  |  |  | Assume one retaining wall (R.W.) for every box/substructure per 800' of UG line runnning along slope + a R.W. for TX's ($30k/R.W.) - ($30k/0.15 steep mile or $660k/steep mile) |  | Enter additional comments to support risk
Eminent Domain |  |  |  |  | For every 8 easements needed expect 1 hold out. $40K for hold out. |  | Enter additional comments to support risk
Soil: Granite/Hard Rock |  |  |  |  | Contingency Plan: $330K cost impact is based on added an additional construction crew and equipment for 30 days. Assume 10 days per mile of hard soil conditions (or $110k/mile) • 4 man Crew: @ $7,615.97/Day • Equipment: @ 3,500/day (soil conditions on private properties away from franchise increase likelihood from 33%). |  | Enter additional comments to support risk
Soil: Waterways Crossings |  |  |  |  | Bore rig setup, develop plan. $50k per waterway crossing ($25k/hole - hole each side of waterway) |  | Enter additional comments to support risk
Soil: Bio, Cultural & Environmental |  |  |  |  | Standard costs, Additional Clearing, Delays ($5k flat if issues present for all alternatives) |  | Enter additional comments to support risk
Cross-bore (additional cleaning, delays) |  |  |  |  | Contingency Plan: $147K/mile cost impact is based on added an additional construction crew and equipment for 15 days. • 4 man Crew: @ $7,615.97/Day • Equipment: @ 2,196.57/day (3x miles increased likelihood from 15% - 45%) |  | Enter additional comments to support risk
Open Trench |  |  |  |  | Extensive asphalt restoration, Off-haul/inport, Traffic Control/plating. Cost impact is based on added an additional construction crew, flaggers, equipment, etc. • 5 man Crew can do 75'/day = 70 days/mile @$9519.96/Day= $670k/mile (hand digging can add %50 or $1M/mile total) |  | Enter additional comments to support risk
UG Tap in same trench as Main |  |  |  |  | Assume 75% cost reduction for Cable in same trench |  | Enter additional comments to support risk
Asbestos |  |  |  |  | $100k/mile if open trench & $50k/mile if bore/OH if asbestos present |  | Enter additional comments to support risk
Construction
Scope Changes (Select) | 100% (No Adjustment) | 0 |  | 0 |  |  | Enter additional comments to support risk
Weather Delays | [6 empty] | Enter additional comments to support risk
Vegetation Removal |  |  |  |  | Vegetation Trimming Costs $57/ft ($300k/mi) |  | Enter additional comments to support risk
Remote Generation |  |  |  |  | $270k + ($70k * kVA * 0.8) where kVA is demand |  | Enter additional comments to support risk
Line Removal |  |  |  |  | $106k/mile |  | Enter additional comments to support risk
Administrative & General
Drop Down Input Details - Cap Ex Risk Adjustment |  | Hybrid | Overhead | Underground
Area of Risk | Alternatives | Adjustment | Adjustment | Adjustment | Detailed Description of Cost Variance | Source | Additional Comments
|  | ($000/Mile) | ($000/Mile) | ($000/Mile)
Asset Terrain | Average (No Adjustment) |  |  | 0 | Assets are along a paved or gravel road
| Better (+10%) |  |  | -420 | Natural terrain with low vegetation impact |  | Due to savings in traffic control, assume boring, minimize restoration, spoils removals etc..
| Worse (-50%) |  |  | 2100 | Natural terrain, heavy veg, gradual elevation |  | Assets are along natural terrain, heavy vegetation, and gradual elevation changes (+50%; $6.3M/mile)
| UG is Not Viable |  |  | 16800 | UG not viable due to terrrain, etc. |  | Route not viable due to soil conditions, natural terrain, waterways, creeks, environmental, or land rights
Success Rate in Dedicated Street Easement | 100% (No Adjustment) |  |  | 0 | 5280'/200 x $6300 = $166,320/mile assumed |  | Cost to run primary UG through a private parcel. Easement required underground/pad-mounted equipment, overhead rights exist.
| 90% Success Rate | 182.952 |  | 182.952 | 10% adder x $166,320 |  | $6300 per easement granted for box placement and minimal UG
| 75% Success Rate | 207.9 |  | 207.9 | 25% adder x $166,320
| 50% Success Rate | 249.48 |  | 249.48 | 50% adder x $166,320
Scope Changes | 100% (No Adjustment) |  |  | 0 | Assume $XXX/mile
| 5% Cost Adder |  |  | 0.05 | 5% adder x $xxx
| 10% Cost Adder |  |  | 0.1 | 10% adder x $xxx
| 20% Cost Adder |  |  | 0.2 | 20% adder x $xxx
Delays Due to Weather, protected species,

## NPV Summary
Results of Economic Evaluation Over 45-Year Study Period ($000)
Underground vs. Overhead Analysis
Study Period: |  | 45 years |  |  | First Year of Study: | 2021 |  | Name of Analyst, Phone #
Discount Rate: |  | 6.8% |  |  | Cost Estimate Year: | 2022 |  | EASOP 2020 | MaxCap | Edition
[6 empty] | Cash Flow Measures |  |  | B/C
Alternatives (enter titles to see financial results) | [5 empty] | NPV | ROE | Payback | Ratio | PVRR
1 | Hybrid |  |  |  |  | -2092.924 | - | - | - | 2906.177
2 | All Overhead |  |  |  |  | -1331.7237 | n/a | 0 | n/a | 1849.1951
3 | All Underground |  |  |  |  | -2856.4709 | n/a | never | 0.098914 | 3966.4173
4
5
6
Net present value and present value of revenue requirements are the primary financial measures.
Return on equity, payback period, and benefit-cost ratio are measured relative to status quo.
|  |  | Annual Cash Flow ($000) | [7 empty] | Cumulative NPV | [7 empty] | Annual Cash Flow Relative to SQ | [5 empty] | Cumulative NPV Relative to SQ | [6 empty] | Find Discounted Payback Relative to SQ
| End of Year * |  | S.Q. | Alt A | Alt B | Alt C | Alt D | Alt E |  |  | S.Q. | Alt A | Alt B | Alt C | Alt D | Alt E | Proj |  | Alt A | Alt B | Alt C | Alt D | Alt E | Proj | Alt A | Alt B | Alt C | Alt D | Alt E | Proj |  | Alt A | Alt B | Alt C | Alt D | Alt E | Proj | sp indx
Initial Expenditures |  |  | -1823.4631 | -951.0917 | -2695.8345 | 0 | 0 | 0 |  |  | -1823.4631 | -951.0917 | -2695.8345 | 0 | 0 | 0 | -3646.9262 |  | 872.3714 | -872.3714 | 1823.4631 | 1823.4631 | 1823.4631 | -1823.4631 | 872.3714 | -872.3714 | 1823.4631 | 1823.4631 | 1823.4631 | -1823.4631 | [7 empty] | 1
| 2021 |  | -35.3477 | -33.9803 | -48.2704 | 0 | 0 | 0 |  |  | -1856.5602 | -982.9085 | -2741.0315 | 0 | 0 | 0 | -3723.94 |  | 1.3674 | -12.9227 | 35.3477 | 35.3477 | 35.3477 | -46.903 | 873.6517 | -884.4712 | 1856.5602 | 1856.5602 | 1856.5602 | -1867.3798 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 50 years
| 2022 |  | -31.3842 | -31.7057 | -40.3169 | 0 | 0 | 0 |  |  | -1884.0752 | -1010.7053 | -2776.3778 | 0 | 0 | 0 | -3787.0831 |  | -0.32146 | -8.9326 | 31.3842 | 31.3842 | 31.3842 | -40.6383 | 873.3699 | -892.3026 | 1884.0752 | 1884.0752 | 1884.0752 | -1903.0079 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 49 years
| 2023 |  | 33.8286 | 10.8743 | 81.8574 | 0 | 0 | 0 |  |  | -1856.3056 | -1001.7787 | -2709.1817 | 0 | 0 | 0 | -3710.9604 |  | -22.9543 | 48.0288 | -33.8286 | -33.8286 | -33.8286 | 58.9031 | 854.5269 | -852.8761 | 1856.3056 | 1856.3056 | 1856.3056 | -1854.6548 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 48 years
| 2024 |  | -9.349 | -17.6788 | 1.5391 | 0 | 0 | 0 |  |  | -1863.4915 | -1015.367 | -2707.9987 | 0 | 0 | 0 | -3723.3657 |  | -8.3298 | 10.8881 | 9.349 | 9.349 | 9.349 | -6.7906 | 848.1244 | -844.5072 | 1863.4915 | 1863.4915 | 1863.4915 | -1859.8743 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 47 years
| 2025 |  | -10.9691 | -19.0185 | -1.0346 | 0 | 0 | 0 |  |  | -1871.3858 | -1029.0544 | -2708.7433 | 0 | 0 | 0 | -3737.7977 |  | -8.0494 | 9.9345 | 10.9691 | 10.9691 | 10.9691 | -9.084 | 842.3314 | -837.3575 | 1871.3858 | 1871.3858 | 1871.3858 | -1866.4119 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 46 years
| 2026 |  | -12.4981 | -20.309 | -3.4203 | 0 | 0 | 0 |  |  | -1879.8078 | -1042.7399 | -2711.0481 | 0 | 0 | 0 | -3753.788 |  | -7.8108 | 9.0778 | 12.4981 | 12.4981 | 12.4981 | -11.2311 | 837.0679 | -831.2403 | 1879.8078 | 1879.8078 | 1879.8078 | -1873.9802 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 45 years
| 2027 |  | -13.9439 | -21.5553 | -5.6327 | 0 | 0 | 0 |  |  | -1888.6059 | -1056.3404 | -2714.6021 | 0 | 0 | 0 | -3770.9425 |  | -7.6113 | 8.3112 | 13.9439 | 13.9439 | 13.9439 | -13.244 | 832.2655 | -825.9962 | 1888.6059 | 1888.6059 | 1888.6059 | -1882.3366 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 44 years
| 2028 |  | -15.3137 | -22.7621 | -7.6853 | 0 | 0 | 0 |  |  | -1897.653 | -1069.7879 | -2719.1425 | 0 | 0 | 0 | -3788.9304 |  | -7.4484 | 7.6284 | 15.3137 | 15.3137 | 15.3137 | -15.1337 | 827.8651 | -821.4895 | 1897.653 | 1897.653 | 1897.653 | -1891.2774 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 43 years
| 2029 |  | -15.7677 | -23.3769 | -8.012 | 0 | 0 | 0 |  |  | -1906.3752 | -1082.7193 | -2723.5745 | 0 | 0 | 0 | -3806.2938 |  | -7.6092 | 7.7557 | 15.7677 | 15.7677 | 15.7677 | -15.6212 | 823.6559 | -817.1993 | 1906.3752 | 1906.3752 | 1906.3752 | -1899.9186 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 42 years
| 2030 |  | -16.0487 | -23.8861 | -8.0028 | 0 | 0 | 0 |  |  | -1914.6876 | -1095.0911 | -2727.7195 | 0 | 0 | 0 | -3822.8106 |  | -7.8374 | 8.046 | 16.0487 | 16.0487 | 16.0487 | -15.8401 | 819.5965 | -813.0319 | 1914.6876 | 1914.6876 | 1914.6876 | -1908.123 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 41 years
| 2031 |  | -16.3392 | -24.4092 | -7.9984 | 0 | 0 | 0 |  |  | -1922.6117 | -1106.9289 | -2731.5985 | 0 | 0 | 0 | -3838.5274 |  | -8.07 | 8.3408 | 16.3392 | 16.3392 | 16.3392 | -16.0684 | 815.6828 | -808.9868 | 1922.6117 | 1922.6117 | 1922.6117 | -1915.9157 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 40 years
| 2032 |  | -16.6393 | -24.9466 | -7.9991 | 0 | 0 | 0 |  |  | -1930.1675 | -1118.2569 | -2735.2309 | 0 | 0 | 0 | -3853.4878 |  | -8.3073 | 8.6402 | 16.6393 | 16.6393 | 16.6393 | -16.3064 | 811.9105 | -805.0634 | 1930.1675 | 1930.1675 | 1930.1675 | -1923.3203 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 39 years
| 2033 |  | -16.9493 | -25.4987 | -8.005 | 0 | 0 | 0 |  |  | -1937.374 | -1129.0985 | -2738.6344 | 0 | 0 | 0 | -3867.7329 |  | -8.5493 | 8.9444 | 16.9493 | 16.9493 | 16.9493 | -16.5543 | 808.2755 | -801.2604 | 1937.374 | 1937.374 | 1937.374 | -1930.3589 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 38 years
| 2034 |  | -17.2695 | -26.0658 | -8.0161 | 0 | 0 | 0 |  |  | -1944.2492 | -1139.4755 | -2741.8257 | 0 | 0 | 0 | -3881.3012 |  | -8.7962 | 9.2534 | 17.2695 | 17.2695 | 17.2695 | -16.8123 | 804.7737 | -797.5765 | 1944.2492 | 1944.2492 | 1944.2492 | -1937.052 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 37 years
| 2035 |  | -17.6001 | -26.6483 | -8.0326 | 0 | 0 | 0 |  |  | -1950.8098 | -1149.409 | -2744.8199 | 0 | 0 | 0 | -3894.2289 |  | -9.0482 | 9.5675 | 17.6001 | 17.6001 | 17.6001 | -17.0808 | 801.4009 | -794.0101 | 1950.8098 | 1950.8098 | 1950.8098 | -1943.4191 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 36 years
| 2036 |  | -17.9414 | -27.2466 | -8.0547 | 0 | 0 | 0 |  |  | -1957.0718 | -1158.9188 | -2747.6312 | 0 | 0 | 0 | -3906.55 |  | -9.3052 | 9.8867 | 17.9414 | 17.9414 | 17.9414 | -17.3599 | 798.1531 | -790.5594 | 1957.0718 | 1957.0718 | 1957.0718 | -1949.4782 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 35 years
| 2037 |  | -18.2936 | -27.8611 | -8.0824 | 0 | 0 | 0 |  |  | -1963.0503 | -1168.0239 | -2750.2726 | 0 | 0 | 0 | -3918.2965 |  | -9.5675 | 10.2112 | 18.2936 | 18.2936 | 18.2936 | -17.6499 | 795.0264 | -787.2223 | 1963.0503 | 1963.0503 | 1963.0503 | -1955.2462 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 34 years
| 2038 |  | -18.657 | -28.4922 | -8.116 | 0 | 0 | 0 |  |  | -1968.7593 | -1176.7424 | -2752.7561 | 0 | 0 | 0 | -3929.4985 |  | -9.8352 | 10.541 | 18.657 | 18.657 | 18.657 | -17.9512 | 792.0168 | -783.9968 | 1968.7593 | 1968.7593 | 1968.7593 | -1960.7393 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 33 years
| 2039 |  | -19.0319 | -29.1403 | -8.1556 | 0 | 0 | 0 |  |  | -1974.2122 | -1185.0915 | -2755.0928 | 0 | 0 | 0 | -3940.1843 |  | -10.1084 | 10.8763 | 19.0319 | 19.0319 | 19.0319 | -18.2639 | 789.1206 | -780.8806 | 1974.2122 | 1974.2122 | 1974.2122 | -1965.9721 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 32 years
| 2040 |  | -19.4186 | -29.8058 | -8.2012 | 0 | 0 | 0 |  |  | -1979.4216 | -1193.0876 | -2757.2929 | 0 | 0 | 0 | -3950.3805 |  | -10.3872 | 11.2174 | 19.4186 | 19.4186 | 19.4186 | -18.5885 | 786.334 | -777.8713 | 1979.4216 | 1979.4216 | 1979.4216 | -1970.9589 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 31 years
| 2041 |  | -26.5888 | -34.9447 | -20.8821 | 0 | 0 | 0 |  |  | -1986.1005 | -1201.8654 | -2762.5383 | 0 | 0 | 0 | -3964.4037 |  | -8.3559 | 5.7067 | 26.5888 | 26.5888 | 26.5888 | -29.238 | 784.2351 | -776.4378 | 1986.1005 | 1986.1005 | 1986.1005 | -1978.3032 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 30 years
| 2042 |  | -33.8037 | -40.1431 | -33.5926 | 0 | 0 | 0 |  |  | -1994.051 | -1211.307 | -2770.4392 | 0 | 0 | 0 | -3981.7462 |  | -6.3394 | 0.21103 | 33.8037 | 33.8037 | 33.8037 | -39.9321 | 782.7441 | -776.3882 | 1994.051 | 1994.051 | 1994.051 | -1987.6951 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 29 years
| 2043 |  | -34.2927 | -40.947 | -33.7047 | 0 | 0 | 0 |  |  | -2001.6031 | -1220.3244 | -2777.8617 | 0 | 0 | 0 | -3998.1861 |  | -6.6543 | 0.58802 | 34.2927 | 34.2927 | 34.2927 | -40.359 | 781.2787 | -776.2587 | 2001.6031 | 2001.6031 | 2001.6031 | -1996.5831 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 28 years
| 2044 |  | -34.7964 | -41.7722 | -33.8247 | 0 | 0 | 0 |  |  | -2008.7781 | -1228.9378 | -2784.8364 | 0 | 0 | 0 | -4013.7743 |  | -6.9758 | 0.97169 | 34.7964 | 34.7964 | 34.7964 | -40.8005 | 779.8402 | -776.0583 | 2008.7781 | 2008.7781 | 2008.7781 | -2004.9962 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 27 years
| 2045 |  | -35.3151 | -42.6193 | -33.9528 | 0 | 0 | 0 |  |  | -2015.5964 | -1237.1664 | -2791.3917 | 0 | 0 | 0 | -4028.5582 |  | -7.3042 | 1.3622 | 35.3151 | 35.3151 | 35.3151 | -41.257 | 778.43 | -775.7953 | 2015.5964 | 2015.5964 | 2015.5964 | -2012.9617 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 26 years
| 2046 |  | -35.8491 | -43.4888 | -34.0893 | 0 | 0 | 0 |  |  | -2022.0772 | -1245.0283 | -2797.5544 | 0 | 0 | 0 | -4042.5826 |  | -7.6396 | 1.7598 | 35.8491 | 35.8491 | 35.8491 | -41.7289 | 777.0489 | -775.4772 | 2022.0772 | 2022.0772 | 2022.0772 | -2020.5054 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 25 years
| 2047 |  | -36.3989 | -44.3812 | -34.2343 | 0 | 0 | 0 |  |  | -2028.2384 | -1252.5406 | -2803.3492 | 0 | 0 | 0 | -4055.8898 |  | -7.9823 | 2.1646 | 36.3989 | 36.3989 | 36.3989 | -42.2166 | 775.6978 | -775.1108 | 2028.2384 | 2028.2384 | 2028.2384 | -2027.6514 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 24 years
| 2048 |  | -36.9649 | -45.2972 | -34.3881 | 0 | 0 | 0 |  |  | -2034.097 | -1259.7198 | -2808.7994 | 0 | 0 | 0 | -4068.5192 |  | -8.3323 | 2.5768 | 36.9649 | 36.9649 | 36.9649 | -42.7204 | 774.3772 | -774.7024 | 2034.097 | 2034.097 | 2034.097 | -2034.4222 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 23 years
| 2049 |  | -37.5474 | -46.2373 | -34.5509 | 0 | 0 | 0 |  |  | -2039.669 | -1266.5814 | -2813.9267 | 0 | 0 | 0 | -4080.5082 |  | -8.6899 | 2.9966 | 37.5474 | 37.5474 | 37.5474 | -43.2408 | 773.0876 | -774.2577 | 2039.669 | 2039.669 | 2039.669 | -2040.8391 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 22 years
| 2050 |  | -38.1469 | -47.2022 | -34.7228 | 0 | 0 | 0 |  |  | -2044.9696 | -1273.1402 | -2818.7515 | 0 | 0 | 0 | -4091.8917 |  | -9.0553 | 3.4241 | 38.1469 | 38.1469 | 38.1469 | -43.7781 | 771.8294 | -773.7819 | 2044.9696 | 2044.9696 | 2044.9696 | -2046.9221 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 21 years
| 2051 |  | -38.7638 | -48.1924 | -34.9042 | 0 | 0 | 0 |  |  | -2050.0129 | -1279.4103 | -2823.2927 | 0 | 0 | 0 | -4102.703 |  | -9.4286 | 3.8596 | 38.7638 | 38.7638 | 38.7638 | -44.3329 | 770.6027 | -773.2798 | 2050.0129 | 2050.0129 | 2050.0129 | -2052.69 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 20 years
| 2052 |  | -39.2902 | -49.1374 | -34.8933 | 0 | 0 | 0 |  |  | -2054.7993 | -1285.3962 | -2827.5434 | 0 | 0 | 0 | -4112.9396 |  | -9.8472 | 4.3969 | 39.2902 | 39.2902 | 39.2902 | -44.7405 | 769.4031 | -772.7441 | 2054.7993 | 2054.7993 | 2054.7993 | -2058.1403 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 19 years
| 2053 |  | -39.7261 | -50.0371 | -34.69 | 0 | 0 | 0 |  |  | -2059.3306 | -1291.1036 | -2831.5003 | 0 | 0 | 0 | -4122.6039 |  | -10.311 | 5.0361 | 39.7261 | 39.7261 | 39.7261 | -45.0009 | 768.227 | -772.1697 | 2059.3306 | 2059.3306 | 2059.3306 | -2063.2733 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 18 years
| 2054 |  | -40.1796 | -50.9627 | -34.496 | 0 | 0 | 0 |  |  | -2063.6218 | -1296.5465 | -2835.1845 | 0 | 0 | 0 | -4131.731 |  | -10.7831 | 5.6836 | 40.1796 | 40.1796 | 40.1796 | -45.2791 | 767.0753 | -771.5627 | 2063.6218 | 2063.6218 | 2063.6218 | -2068.1092 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 17 years
| 2055 |  | -40.6513 | -51.915 | -34.3117 | 0 | 0 | 0 |  |  | -2067.687 | -1301.7381 | -2838.6157 | 0 | 0 | 0 | -4140.3538 |  | -11.2636 | 6.3396 | 40.6513 | 40.6513 | 40.6513 | -45.5753 | 765.9489 | -770.9287 | 2067.687 | 2067.687 | 2067.687 | -2072.6668 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 16 years
| 2056 |  | -41.1416 | -52.8945 | -34.1373 | 0 | 0 | 0 |  |  | -2071.5393 | -1306.6908 | -2841.8121 | 0 | 0 | 0 | -4148.503 |  | -11.7529 | 7.0043 | 41.1416 | 41.1416 | 41.1416 | -45.8902 | 764.8485 | -770.2728 | 2071.5393 | 2071.5393 | 2071.5393 | -2076.9637 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 15 years
| 2057 |  | -41.6509 | -53.902 | -33.973 | 0 | 0 | 0 |  |  | -2075.1909 | -1311.4166 | -2844.7906 | 0 | 0 | 0 | -4156.2072 |  | -12.2511 | 7.678 | 41.6509 | 41.6509 | 41.6509 | -46.2241 | 763.7744 | -769.5997 | 2075.1909 | 2075.1909 | 2075.1909 | -2081.0163 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 14 years
| 2058 |  | -42.1798 | -54.9382 | -33.8191 | 0 | 0 | 0 |  |  | -2078.6535 | -1315.9265 | -2847.5669 | 0 | 0 | 0 | -4163.4933 |  | -12.7584 | 8.3607 | 42.1798 | 42.1798 | 42.1798 | -46.5775 | 762.727 | -768.9134 | 2078.6535 | 2078.6535 | 2078.6535 | -2084.8398 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 13 years
| 2059 |  | -25.1529 | -56.0038 | -33.6758 | 0 | 0 | 0 |  |  | -2080.5868 | -1320.2311 | -2850.1553 | 0 | 0 | 0 | -4170.3864 |  | -30.8508 | -8.5228 | 25.1529 | 25.1529 | 25.1529 | -64.5266 | 760.3557 | -769.5685 | 2080.5868 | 2080.5868 | 2080.5868 | -2089.7996 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 12 years
| 2060 |  | 0 | -34.0748 | -20.5379 | 0 | 0 | 0 |  |  | -2080.5868 | -1322.6835 | -2851.6334 | 0 | 0 | 0 | -4174.3169 |  | -34.0748 | -20.5379 | 0 | 0 | 0 | -54.6127 | 757.9034 | -771.0466 | 2080.5868 | 2080.5868 | 2080.5868 | -2093.73 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 11 years
| 2061 |  | 0 | -34.2738 | -19.8928 | 0 | 0 | 0 |  |  | -2080.5868 | -1324.9931 | -2852.9739 | 0 | 0 | 0 | -4177.967 |  | -34.2738 | -19.8928 | 0 | 0 | 0 | -54.1666 | 755.5937 | -772.3871 | 2080.5868 | 2080.5868 | 2080.5868 | -2097.3802 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 10 years
| 2062 |  | 0 | -34.5513 | -19.2856 | 0 | 0 | 0 |  |  | -2080.5868 | -1327.1732 | -2854.1908 | 0 | 0 | 0 | -4181.364 |  | -34.5513 | -19.2856 | 0 | 0 | 0 | -53.8369 | 753.4137 | -773.604 | 2080.5868 | 2080.5868 | 2080.5868 | -2100.7771 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 9 years
| 2063 |  | 0 | -35.8848 | -19.2683 | 0 | 0 | 0 |  |  | -2080.5868 | -1329.2932 | -2855.3292 | 0 | 0 | 0 | -4184.6224 |  | -35.8848 | -19.2683 | 0 | 0 | 0 | -55.1531 | 751.2936 | -774.7423 | 2080.5868 | 2080.5868 | 2080.5868 | -2104.0355 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 8 years
| 2064 |  | 0 | -36.5693 | -18.8777 | 0 | 0 | 0 |  |  | -2080.5868 | -1331.3162 | -2856.3734 | 0 | 0 | 0 | -4187.6896 |  | -36.5693 | -18.8777 | 0 | 0 | 0 | -55.4471 | 749.2707 | -775.7866 | 2080.5868 | 2080.5868 | 2080.5868 | -2107.1028 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 7 years
| 2065 |  | 0 | -7.8689 | -1.8822 | 0 | 0 | 0 |  |  | -2080.5868 | -1331.7237 | -2856.4709 | 0 | 0 | 0 | -4188.1947 |  | -7.8689 | -1.8822 | 0 | 0 | 0 | -9.7512 | 748.8631 | -775.8841 | 2080.5868 | 2080.5868 | 2080.5868 | -2107.6078 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 6 years
| 2066 |  | -25.0143 | 0 | 0 | 0 | 0 | 0 |  |  | -2081.8 | -1331.7237 | -2856.4709 | 0 | 0 | 0 | -4188.1947 |  | 25.0143 | 25.0143 | 25.0143 | 25.0143 | 25.0143 | 25.0143 | 750.0762 | -774.6709 | 2081.8 | 2081.8 | 2081.8 | -2106.3947 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 5 years
| 2067 |  | -24.9324 | 0 | 0 | 0 | 0 | 0 |  |  | -2082.9322 | -1331.7237 | -2856.4709 | 0 | 0 | 0 | -4188.1947 |  | 24.9324 | 24.9324 | 24.9324 | 24.9324 | 24.9324 | 24.9324 | 751.2084 | -773.5388 | 2082.9322 | 2082.9322 | 2082.9322 | -2105.2625 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 4 years
| 2068 |  | -25.6534 | 0 | 0 | 0 | 0 | 0 |  |  | -2084.0229 | -1331.7237 | -2856.4709 | 0 | 0 | 0 | -4188.1947 |  | 25.6534 | 25.6534 | 25.6534 | 25.6534 | 25.6534 | 25.6534 | 752.2992 | -772.448 | 2084.0229 | 2084.0229 | 2084.0229 | -2104.1718 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 3 years
| 2069 |  | -25.8757 | 0 | 0 | 0 | 0 | 0 |  |  | -2085.0531 | -1331.7237 | -2856.4709 | 0 | 0 | 0 | -4188.1947 |  | 25.8757 | 25.8757 | 25.8757 | 25.8757 | 25.8757 | 25.8757 | 753.3293 | -771.4179 | 2085.0531 | 2085.0531 | 2085.0531 | -2103.1416 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 2 years
| 2070 |  | -26.0948 | 0 | 0 | 0 | 0 | 0 |  |  | -2086.0258 | -1331.7237 | -2856.4709 | 0 | 0 | 0 | -4188.1947 |  | 26.0948 | 26.0948 | 26.0948 | 26.0948 | 26.0948 | 26.0948 | 754.3021 | -770.4451 | 2086.0258 | 2086.0258 | 2086.0258 | -2102.1689 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 1 year
* | Project expenditures are assumed to occur beginning of year, so shown at end of the previous year. | [16 empty] | Sum | 451.5642 | -597.6538 | 2954.4076 | 2954.4076 | 2954.4076 | -3100.4972 | [6 empty] | Payback | 0 | never | 0 | 0 | 0 | never | 45
| Annual operating expenses and revenues are assumed to occur at the end of the year. | [16 empty] | Trial ROE | #NUM! | -10.44% | #NUM! | #NUM! | #NUM! | #NUM!
[18 empty] | ROE | n/a | n/a | n/a | n/a | n/a | n/a | [6 empty] | NPVcap | -1122.9598 | -2815.3387 | 0 | 0 | 0 | -3938.2986
|  |  | Earnings Available for Common Stock ($000) * | [28 empty] | n/a | 0.098914 | #REF! | #REF! | #REF!
| Calendar Year |  | S.Q. | Alt A | Alt B | Alt C | Alt D | Alt E | [22 empty] | B/C Ratio | n/a | 0.098914 | n/a | n/a | n/a
| 2021 |  | -109.9933 | -64.6984 | -155.2883 | 0 | 0 | 0
| 2022 |  | -109.0982 | -64.7103 | -153.4861 | 0 | 0 | 0
| 2023 |  | -108.2114 | -64.7344 | -151.6883 | 0 | 0 | 0
| 2024 |  | -107.333 | -64.771 | -149.8951 | 0 | 0 | 0
| 2025 |  | -106.4634 | -64.8204 | -148.1065 | 0 | 0 | 0
* | Earnings are estimated using simplified accounting assumptions and no cost recovery.
Earnings estimates for projects over $100 million should be reviewed by Economic and Project Analysis.
Note on B5: Choose the expected service life of the project considering future changes in business and technology. Suggested study periods: . Years Small computer projects 5 Large computer systems 10 Transformation projects 10 Distribution projects 20 Transmission projects 30
Note on F5: Enter the beginning of the study period, which should be the first year there are differences in costs or benefits between alternatives. It will usually be the first year expenses are incurred or new capital assets become operational. It should never be a year from the past unless you are trying to replicate an analysis done in the past.
Note on B6: Enter the after-tax, weighted average cost of capital. The default value is up-to-date in current versions of EASOP, or consult the EconNet website.
Note on F6: Enter the base year that should be used to escalate future expenditures. Since most estimates are made in today's dollars, the cost estimate year will usually be the current year.
Note on I6: Select: "Standard" for analysis of up to 6 project expenditures per alternative "ExtraCap" for analysis of up to 20 project expenditures per alternative "MaxCap" for analysis of up to 40 project expenditures per alternative

## NPV Summary AT
Results of Economic Evaluation Over 45-Year Study Period ($000)
Underground vs. Overhead Analysis
Study Period: |  | 45 years |  |  | First Year of Study: | 2021 |  | Name of Analyst, Phone #
Discount Rate: |  | 6.8% |  |  | Cost Estimate Year: | 2022 |  | EASOP 2020 | MaxCap | Edition
[6 empty] | Cash Flow Measures |  |  | B/C
Alternatives (enter titles to see financial results) | [5 empty] | NPV | ROE | Payback | Ratio | PVRR
1 | Hybrid |  |  |  |  | -1711.0124 | - | - | - | 2375.865
2 | All Overhead |  |  |  |  | -1528.8727 | n/a | 0 | n/a | 2122.9508
3 | All Underground |  |  |  |  | -2856.4709 | n/a | never | 0.098914 | 3966.4173
4
5
6
Net present value and present value of revenue requirements are the primary financial measures.
Return on equity, payback period, and benefit-cost ratio are measured relative to status quo.
|  |  | Annual Cash Flow ($000) | [7 empty] | Cumulative NPV | [7 empty] | Annual Cash Flow Relative to SQ | [5 empty] | Cumulative NPV Relative to SQ | [6 empty] | Find Discounted Payback Relative to SQ
| End of Year * |  | S.Q. | Alt A | Alt B | Alt C | Alt D | Alt E |  |  | S.Q. | Alt A | Alt B | Alt C | Alt D | Alt E | Proj |  | Alt A | Alt B | Alt C | Alt D | Alt E | Proj | Alt A | Alt B | Alt C | Alt D | Alt E | Proj |  | Alt A | Alt B | Alt C | Alt D | Alt E | Proj | sp indx
Initial Expenditures |  |  | -1445.4782 | -1146.2137 | -2695.8345 | 0 | 0 | 0 |  |  | -1445.4782 | -1146.2137 | -2695.8345 | 0 | 0 | 0 | -3842.0481 |  | 299.2646 | -1250.3563 | 1445.4782 | 1445.4782 | 1445.4782 | -2396.5699 | 299.2646 | -1250.3563 | 1445.4782 | 1445.4782 | 1445.4782 | -2396.5699 | [7 empty] | 1
| 2021 |  | -35.3477 | -36.9629 | -48.2704 | 0 | 0 | 0 |  |  | -1478.5754 | -1180.8231 | -2741.0315 | 0 | 0 | 0 | -3921.8546 |  | -1.6151 | -12.9227 | 35.3477 | 35.3477 | 35.3477 | -49.8855 | 297.7523 | -1262.4561 | 1478.5754 | 1478.5754 | 1478.5754 | -2443.2792 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 50 years
| 2022 |  | -31.3842 | -34.0942 | -40.3169 | 0 | 0 | 0 |  |  | -1506.0903 | -1210.7139 | -2776.3778 | 0 | 0 | 0 | -3987.0917 |  | -2.71 | -8.9326 | 31.3842 | 31.3842 | 31.3842 | -43.0269 | 295.3764 | -1270.2875 | 1506.0903 | 1506.0903 | 1506.0903 | -2481.0014 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 49 years
| 2023 |  | 33.8286 | 17.3462 | 81.8574 | 0 | 0 | 0 |  |  | -1478.3207 | -1196.4746 | -2709.1817 | 0 | 0 | 0 | -3905.6563 |  | -16.4824 | 48.0288 | -33.8286 | -33.8286 | -33.8286 | 65.375 | 281.8461 | -1230.861 | 1478.3207 | 1478.3207 | 1478.3207 | -2427.3356 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 48 years
| 2024 |  | -9.349 | -17.0184 | 1.5391 | 0 | 0 | 0 |  |  | -1485.5066 | -1209.5554 | -2707.9987 | 0 | 0 | 0 | -3917.5541 |  | -7.6694 | 10.8881 | 9.349 | 9.349 | 9.349 | -6.1303 | 275.9512 | -1222.4921 | 1485.5066 | 1485.5066 | 1485.5066 | -2432.0475 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 47 years
| 2025 |  | -10.9691 | -18.5319 | -1.0346 | 0 | 0 | 0 |  |  | -1493.4009 | -1222.8926 | -2708.7433 | 0 | 0 | 0 | -3931.6358 |  | -7.5628 | 9.9345 | 10.9691 | 10.9691 | 10.9691 | -8.5974 | 270.5083 | -1215.3424 | 1493.4009 | 1493.4009 | 1493.4009 | -2438.2349 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 46 years
| 2026 |  | -12.4981 | -19.9819 | -3.4203 | 0 | 0 | 0 |  |  | -1501.8229 | -1236.3577 | -2711.0481 | 0 | 0 | 0 | -3947.4058 |  | -7.4838 | 9.0778 | 12.4981 | 12.4981 | 12.4981 | -10.9041 | 265.4653 | -1209.2252 | 1501.8229 | 1501.8229 | 1501.8229 | -2445.5828 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 45 years
| 2027 |  | -13.9439 | -21.3746 | -5.6327 | 0 | 0 | 0 |  |  | -1510.621 | -1249.8442 | -2714.6021 | 0 | 0 | 0 | -3964.4463 |  | -7.4307 | 8.3112 | 13.9439 | 13.9439 | 13.9439 | -13.0634 | 260.7768 | -1203.9811 | 1510.621 | 1510.621 | 1510.621 | -2453.8253 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 44 years
| 2028 |  | -15.3137 | -22.7156 | -7.6853 | 0 | 0 | 0 |  |  | -1519.6681 | -1263.2643 | -2719.1425 | 0 | 0 | 0 | -3982.4067 |  | -7.4019 | 7.6284 | 15.3137 | 15.3137 | 15.3137 | -15.0872 | 256.4039 | -1199.4744 | 1519.6681 | 1519.6681 | 1519.6681 | -2462.7386 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 43 years
| 2029 |  | -15.7677 | -23.3391 | -8.012 | 0 | 0 | 0 |  |  | -1528.3903 | -1276.1748 | -2723.5745 | 0 | 0 | 0 | -3999.7493 |  | -7.5714 | 7.7557 | 15.7677 | 15.7677 | 15.7677 | -15.5834 | 252.2156 | -1195.1842 | 1528.3903 | 1528.3903 | 1528.3903 | -2471.3589 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 42 years
| 2030 |  | -16.0487 | -23.8322 | -8.0028 | 0 | 0 | 0 |  |  | -1536.7028 | -1288.5187 | -2727.7195 | 0 | 0 | 0 | -4016.2382 |  | -7.7835 | 8.046 | 16.0487 | 16.0487 | 16.0487 | -15.7863 | 248.1841 | -1191.0167 | 1536.7028 | 1536.7028 | 1536.7028 | -2479.5354 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 41 years
| 2031 |  | -16.3392 | -24.3393 | -7.9984 | 0 | 0 | 0 |  |  | -1544.6268 | -1300.3225 | -2731.5985 | 0 | 0 | 0 | -4031.921 |  | -8.0001 | 8.3408 | 16.3392 | 16.3392 | 16.3392 | -15.9985 | 244.3043 | -1186.9717 | 1544.6268 | 1544.6268 | 1544.6268 | -2487.2943 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 40 years
| 2032 |  | -16.6393 | -24.8607 | -7.9991 | 0 | 0 | 0 |  |  | -1552.1826 | -1311.6116 | -2735.2309 | 0 | 0 | 0 | -4046.8424 |  | -8.2214 | 8.6402 | 16.6393 | 16.6393 | 16.6393 | -16.2205 | 240.571 | -1183.0483 | 1552.1826 | 1552.1826 | 1552.1826 | -2494.6599 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 39 years
| 2033 |  | -16.9493 | -25.3967 | -8.005 | 0 | 0 | 0 |  |  | -1559.3891 | -1322.4098 | -2738.6344 | 0 | 0 | 0 | -4061.0442 |  | -8.4474 | 8.9444 | 16.9493 | 16.9493 | 16.9493 | -16.4523 | 236.9794 | -1179.2453 | 1559.3891 | 1559.3891 | 1559.3891 | -2501.6551 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 38 years
| 2034 |  | -17.2695 | -25.9478 | -8.0161 | 0 | 0 | 0 |  |  | -1566.2643 | -1332.7398 | -2741.8257 | 0 | 0 | 0 | -4074.5655 |  | -8.6782 | 9.2534 | 17.2695 | 17.2695 | 17.2695 | -16.6943 | 233.5245 | -1175.5614 | 1566.2643 | 1566.2643 | 1566.2643 | -2508.3012 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 37 years
| 2035 |  | -17.6001 | -26.5142 | -8.0326 | 0 | 0 | 0 |  |  | -1572.8249 | -1342.6233 | -2744.8199 | 0 | 0 | 0 | -4087.4432 |  | -8.9141 | 9.5675 | 17.6001 | 17.6001 | 17.6001 | -16.9467 | 230.2016 | -1171.995 | 1572.8249 | 1572.8249 | 1572.8249 | -2514.6183 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 36 years
| 2036 |  | -17.9414 | -27.0965 | -8.0547 | 0 | 0 | 0 |  |  | -1579.087 | -1352.0807 | -2747.6312 | 0 | 0 | 0 | -4099.712 |  | -9.1551 | 9.8867 | 17.9414 | 17.9414 | 17.9414 | -17.2098 | 227.0062 | -1168.5443 | 1579.087 | 1579.087 | 1579.087 | -2520.625 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 35 years
| 2037 |  | -18.2936 | -27.695 | -8.0824 | 0 | 0 | 0 |  |  | -1585.0654 | -1361.1316 | -2750.2726 | 0 | 0 | 0 | -4111.4042 |  | -9.4014 | 10.2112 | 18.2936 | 18.2936 | 18.2936 | -17.4838 | 223.9338 | -1165.2072 | 1585.0654 | 1585.0654 | 1585.0654 | -2526.3388 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 34 years
| 2038 |  | -18.657 | -28.31 | -8.116 | 0 | 0 | 0 |  |  | -1590.7744 | -1369.7944 | -2752.7561 | 0 | 0 | 0 | -4122.5504 |  | -9.653 | 10.541 | 18.657 | 18.657 | 18.657 | -17.769 | 220.98 | -1161.9817 | 1590.7744 | 1590.7744 | 1590.7744 | -2531.7761 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 33 years
| 2039 |  | -19.0319 | -28.9421 | -8.1556 | 0 | 0 | 0 |  |  | -1596.2273 | -1378.0867 | -2755.0928 | 0 | 0 | 0 | -4133.1794 |  | -9.9102 | 10.8763 | 19.0319 | 19.0319 | 19.0319 | -18.0657 | 218.1406 | -1158.8655 | 1596.2273 | 1596.2273 | 1596.2273 | -2536.9521 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 32 years
| 2040 |  | -19.4186 | -29.5916 | -8.2012 | 0 | 0 | 0 |  |  | -1601.4368 | -1386.0253 | -2757.2929 | 0 | 0 | 0 | -4143.3182 |  | -10.173 | 11.2174 | 19.4186 | 19.4186 | 19.4186 | -18.3742 | 215.4115 | -1155.8562 | 1601.4368 | 1601.4368 | 1601.4368 | -2541.8814 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 31 years
| 2041 |  | -26.5888 | -35.6285 | -20.8821 | 0 | 0 | 0 |  |  | -1608.1156 | -1394.9748 | -2762.5383 | 0 | 0 | 0 | -4157.5131 |  | -9.0397 | 5.7067 | 26.5888 | 26.5888 | 26.5888 | -29.9217 | 213.1408 | -1154.4227 | 1608.1156 | 1608.1156 | 1608.1156 | -2549.3975 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 30 years
| 2042 |  | -33.8037 | -41.7249 | -33.5926 | 0 | 0 | 0 |  |  | -1616.0662 | -1404.7884 | -2770.4392 | 0 | 0 | 0 | -4175.2276 |  | -7.9212 | 0.21103 | 33.8037 | 33.8037 | 33.8037 | -41.5139 | 211.2778 | -1154.3731 | 1616.0662 | 1616.0662 | 1616.0662 | -2559.1614 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 29 years
| 2043 |  | -34.2927 | -42.5127 | -33.7047 | 0 | 0 | 0 |  |  | -1623.6182 | -1414.1506 | -2777.8617 | 0 | 0 | 0 | -4192.0124 |  | -8.22 | 0.58802 | 34.2927 | 34.2927 | 34.2927 | -41.9247 | 209.4675 | -1154.2436 | 1623.6182 | 1623.6182 | 1623.6182 | -2568.3942 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 28 years
| 2044 |  | -34.7964 | -43.3219 | -33.8247 | 0 | 0 | 0 |  |  | -1630.7932 | -1423.0837 | -2784.8364 | 0 | 0 | 0 | -4207.9201 |  | -8.5255 | 0.97169 | 34.7964 | 34.7964 | 34.7964 | -42.3502 | 207.7096 | -1154.0432 | 1630.7932 | 1630.7932 | 1630.7932 | -2577.1268 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 27 years
| 2045 |  | -35.3151 | -44.1529 | -33.9528 | 0 | 0 | 0 |  |  | -1637.6116 | -1431.6083 | -2791.3917 | 0 | 0 | 0 | -4223.0001 |  | -8.8379 | 1.3622 | 35.3151 | 35.3151 | 35.3151 | -42.7907 | 206.0032 | -1153.7802 | 1637.6116 | 1637.6116 | 1637.6116 | -2585.3885 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 26 years
| 2046 |  | -35.8491 | -45.0064 | -34.0893 | 0 | 0 | 0 |  |  | -1644.0923 | -1439.7445 | -2797.5544 | 0 | 0 | 0 | -4237.2989 |  | -9.1573 | 1.7598 | 35.8491 | 35.8491 | 35.8491 | -43.2466 | 204.3478 | -1153.462 | 1644.0923 | 1644.0923 | 1644.0923 | -2593.2066 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 25 years
| 2047 |  | -36.3989 | -45.8828 | -34.2343 | 0 | 0 | 0 |  |  | -1650.2535 | -1447.5111 | -2803.3492 | 0 | 0 | 0 | -4250.8602 |  | -9.4839 | 2.1646 | 36.3989 | 36.3989 | 36.3989 | -43.7182 | 202.7425 | -1153.0956 | 1650.2535 | 1650.2535 | 1650.2535 | -2600.6067 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 24 years
| 2048 |  | -36.9649 | -46.7828 | -34.3881 | 0 | 0 | 0 |  |  | -1656.1121 | -1454.9257 | -2808.7994 | 0 | 0 | 0 | -4263.7251 |  | -9.8178 | 2.5768 | 36.9649 | 36.9649 | 36.9649 | -44.206 | 201.1864 | -1152.6872 | 1656.1121 | 1656.1121 | 1656.1121 | -2607.613 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 23 years
| 2049 |  | -37.5474 | -47.7068 | -34.5509 | 0 | 0 | 0 |  |  | -1661.6842 | -1462.0054 | -2813.9267 | 0 | 0 | 0 | -4275.9321 |  | -10.1594 | 2.9966 | 37.5474 | 37.5474 | 37.5474 | -44.7103 | 199.6788 | -1152.2426 | 1661.6842 | 1661.6842 | 1661.6842 | -2614.248 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 22 years
| 2050 |  | -38.1469 | -48.6557 | -34.7228 | 0 | 0 | 0 |  |  | -1666.9847 | -1468.7662 | -2818.7515 | 0 | 0 | 0 | -4287.5177 |  | -10.5088 | 3.4241 | 38.1469 | 38.1469 | 38.1469 | -45.2316 | 198.2186 | -1151.7668 | 1666.9847 | 1666.9847 | 1666.9847 | -2620.5329 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 21 years
| 2051 |  | -38.7638 | -49.6298 | -34.9042 | 0 | 0 | 0 |  |  | -1672.0281 | -1475.2232 | -2823.2927 | 0 | 0 | 0 | -4298.5159 |  | -10.8661 | 3.8596 | 38.7638 | 38.7638 | 38.7638 | -45.7703 | 196.8048 | -1151.2646 | 1672.0281 | 1672.0281 | 1672.0281 | -2626.4878 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 20 years
| 2052 |  | -39.2902 | -50.5441 | -34.8933 | 0 | 0 | 0 |  |  | -1676.8144 | -1481.3805 | -2827.5434 | 0 | 0 | 0 | -4308.9239 |  | -11.2539 | 4.3969 | 39.2902 | 39.2902 | 39.2902 | -46.1472 | 195.4339 | -1150.729 | 1676.8144 | 1676.8144 | 1676.8144 | -2632.1095 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 19 years
| 2053 |  | -39.7261 | -51.3985 | -34.69 | 0 | 0 | 0 |  |  | -1681.3457 | -1487.2432 | -2831.5003 | 0 | 0 | 0 | -4318.7435 |  | -11.6725 | 5.0361 | 39.7261 | 39.7261 | 39.7261 | -46.3624 | 194.1025 | -1150.1546 | 1681.3457 | 1681.3457 | 1681.3457 | -2637.3978 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 18 years
| 2054 |  | -40.1796 | -52.2789 | -34.496 | 0 | 0 | 0 |  |  | -1685.637 | -1492.8267 | -2835.1845 | 0 | 0 | 0 | -4328.0112 |  | -12.0993 | 5.6836 | 40.1796 | 40.1796 | 40.1796 | -46.5953 | 192.8103 | -1149.5475 | 1685.637 | 1685.637 | 1685.637 | -2642.3742 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 17 years
| 2055 |  | -40.6513 | -53.1859 | -34.3117 | 0 | 0 | 0 |  |  | -1689.7022 | -1498.1454 | -2838.6157 | 0 | 0 | 0 | -4336.7611 |  | -12.5346 | 6.3396 | 40.6513 | 40.6513 | 40.6513 | -46.8463 | 191.5568 | -1148.9136 | 1689.7022 | 1689.7022 | 1689.7022 | -2647.0589 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 16 years
| 2056 |  | -41.1416 | -54.1202 | -34.1373 | 0 | 0 | 0 |  |  | -1693.5544 | -1503.2129 | -2841.8121 | 0 | 0 | 0 | -4345.025 |  | -12.9785 | 7.0043 | 41.1416 | 41.1416 | 41.1416 | -47.1158 | 190.3415 | -1148.2577 | 1693.5544 | 1693.5544 | 1693.5544 | -2651.4706 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 15 years
| 2057 |  | -41.6509 | -55.0824 | -33.973 | 0 | 0 | 0 |  |  | -1697.2061 | -1508.0421 | -2844.7906 | 0 | 0 | 0 | -4352.8327 |  | -13.4315 | 7.678 | 41.6509 | 41.6509 | 41.6509 | -47.4044 | 189.164 | -1147.5846 | 1697.2061 | 1697.2061 | 1697.2061 | -2655.6267 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 14 years
| 2058 |  | -42.1798 | -56.0733 | -33.8191 | 0 | 0 | 0 |  |  | -1700.6686 | -1512.6452 | -2847.5669 | 0 | 0 | 0 | -4360.212 |  | -13.8935 | 8.3607 | 42.1798 | 42.1798 | 42.1798 | -47.7126 | 188.0235 | -1146.8982 | 1700.6686 | 1700.6686 | 1700.6686 | -2659.5434 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 13 years
| 2059 |  | -25.1529 | -57.0936 | -33.6758 | 0 | 0 | 0 |  |  | -1702.602 | -1517.0336 | -2850.1553 | 0 | 0 | 0 | -4367.1889 |  | -31.9406 | -8.5228 | 25.1529 | 25.1529 | 25.1529 | -65.6164 | 185.5684 | -1147.5533 | 1702.602 | 1702.602 | 1702.602 | -2664.5869 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 12 years
| 2060 |  | 0 | 0 | -20.5379 | 0 | 0 | 0 |  |  | -1702.602 | -1517.0336 | -2851.6334 | 0 | 0 | 0 | -4368.667 |  | 0 | -20.5379 | 0 | 0 | 0 | -20.5379 | 185.5684 | -1149.0314 | 1702.602 | 1702.602 | 1702.602 | -2666.065 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 11 years
| 2061 |  | 0 | 0 | -19.8928 | 0 | 0 | 0 |  |  | -1702.602 | -1517.0336 | -2852.9739 | 0 | 0 | 0 | -4370.0075 |  | 0 | -19.8928 | 0 | 0 | 0 | -19.8928 | 185.5684 | -1150.372 | 1702.602 | 1702.602 | 1702.602 | -2667.4056 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 10 years
| 2062 |  | 0 | 0 | -19.2856 | 0 | 0 | 0 |  |  | -1702.602 | -1517.0336 | -2854.1908 | 0 | 0 | 0 | -4371.2244 |  | 0 | -19.2856 | 0 | 0 | 0 | -19.2856 | 185.5684 | -1151.5888 | 1702.602 | 1702.602 | 1702.602 | -2668.6224 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 9 years
| 2063 |  | 0 | 0 | -19.2683 | 0 | 0 | 0 |  |  | -1702.602 | -1517.0336 | -2855.3292 | 0 | 0 | 0 | -4372.3627 |  | 0 | -19.2683 | 0 | 0 | 0 | -19.2683 | 185.5684 | -1152.7272 | 1702.602 | 1702.602 | 1702.602 | -2669.7608 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 8 years
| 2064 |  | 0 | 0 | -18.8777 | 0 | 0 | 0 |  |  | -1702.602 | -1517.0336 | -2856.3734 | 0 | 0 | 0 | -4373.407 |  | 0 | -18.8777 | 0 | 0 | 0 | -18.8777 | 185.5684 | -1153.7715 | 1702.602 | 1702.602 | 1702.602 | -2670.8051 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 7 years
| 2065 |  | 0 | -35.1193 | -1.8822 | 0 | 0 | 0 |  |  | -1702.602 | -1518.8526 | -2856.4709 | 0 | 0 | 0 | -4375.3235 |  | -35.1193 | -1.8822 | 0 | 0 | 0 | -37.0015 | 183.7494 | -1153.869 | 1702.602 | 1702.602 | 1702.602 | -2672.7216 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 6 years
| 2066 |  | -25.0143 | -35.273 | 0 | 0 | 0 | 0 |  |  | -1703.8151 | -1520.5633 | -2856.4709 | 0 | 0 | 0 | -4377.0342 |  | -10.2587 | 25.0143 | 25.0143 | 25.0143 | 25.0143 | -10.2587 | 183.2518 | -1152.6558 | 1703.8151 | 1703.8151 | 1703.8151 | -2673.2191 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 5 years
| 2067 |  | -24.9324 | -35.5053 | 0 | 0 | 0 | 0 |  |  | -1704.9473 | -1522.1756 | -2856.4709 | 0 | 0 | 0 | -4378.6465 |  | -10.5728 | 24.9324 | 24.9324 | 24.9324 | 24.9324 | -10.5728 | 182.7717 | -1151.5236 | 1704.9473 | 1704.9473 | 1704.9473 | -2673.6992 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 4 years
| 2068 |  | -25.6534 | -36.7935 | 0 | 0 | 0 | 0 |  |  | -1706.038 | -1523.74 | -2856.4709 | 0 | 0 | 0 | -4380.2109 |  | -11.1401 | 25.6534 | 25.6534 | 25.6534 | 25.6534 | -11.1401 | 182.2981 | -1150.4329 | 1706.038 | 1706.038 | 1706.038 | -2674.1729 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 3 years
| 2069 |  | -25.8757 | -37.4327 | 0 | 0 | 0 | 0 |  |  | -1707.0682 | -1525.2302 | -2856.4709 | 0 | 0 | 0 | -4381.7012 |  | -11.557 | 25.8757 | 25.8757 | 25.8757 | 25.8757 | -11.557 | 181.838 | -1149.4027 | 1707.0682 | 1707.0682 | 1707.0682 | -2674.633 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 2 years
| 2070 |  | -26.0948 | -8.6871 | 0 | 0 | 0 | 0 |  |  | -1708.0409 | -1525.5541 | -2856.4709 | 0 | 0 | 0 | -4382.025 |  | 17.4077 | 26.0948 | 26.0948 | 26.0948 | 26.0948 | 17.4077 | 182.4869 | -1148.43 | 1708.0409 | 1708.0409 | 1708.0409 | -2673.9841 |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 1 year
* | Project expenditures are assumed to occur beginning of year, so shown at end of the previous year. | [16 empty] | Sum | -148.5825 | -975.6387 | 2576.4227 | 2576.4227 | 2576.4227 | -3700.6439 | [6 empty] | Payback | 0 | never | 0 | 0 | 0 | never | 45
| Annual operating expenses and revenues are assumed to occur at the end of the year. | [16 empty] | Trial ROE | 0.4061% | -12.22% | #NUM! | #NUM! | #NUM! | #NUM!
[18 empty] | ROE | n/a | n/a | n/a | n/a | n/a | n/a | [6 empty] | NPVcap | -1122.9598 | -2815.3387 | 0 | 0 | 0 | -3938.2986
|  |  | Earnings Available for Common Stock ($000) * | [28 empty] | n/a | 0.098914 | #REF! | #REF! | #REF!
| Calendar Year |  | S.Q. | Alt A | Alt B | Alt C | Alt D | Alt E | [22 empty] | B/C Ratio | n/a | 0.098914 | n/a | n/a | n/a
| 2021 |  | -88.5146 | -75.7861 | -155.2883 | 0 | 0 | 0
| 2022 |  | -87.919 | -75.6434 | -153.4861 | 0 | 0 | 0
| 2023 |  | -87.3318 | -75.5128 | -151.6883 | 0 | 0 | 0
| 2024 |  | -86.7531 | -75.3947 | -149.8951 | 0 | 0 | 0
| 2025 |  | -86.1831 | -75.2894 | -148.1065 | 0 | 0 | 0
* | Earnings are estimated using simplified accounting assumptions and no cost recovery.
Earnings estimates for projects over $100 million should be reviewed by Economic and Project Analysis.
Note on B5: Choose the expected service life of the project considering future changes in business and technology. Suggested study periods: . Years Small computer projects 5 Large computer systems 10 Transformation projects 10 Distribution projects 20 Transmission projects 30
Note on F5: Enter the beginning of the study period, which should be the first year there are differences in costs or benefits between alternatives. It will usually be the first year expenses are incurred or new capital assets become operational. It should never be a year from the past unless you are trying to replicate an analysis done in the past.
Note on B6: Enter the after-tax, weighted average cost of capital. The default value is up-to-date in current versions of EASOP, or consult the EconNet website.
Note on F6: Enter the base year that should be used to escalate future expenditures. Since most estimates are made in today's dollars, the cost estimate year will usually be the current year.
Note on I6: Select: "Standard" for analysis of up to 6 project expenditures per alternative "ExtraCap" for analysis of up to 20 project expenditures per alternative "MaxCap" for analysis of up to 40 project expenditures per alternative

## 1 Hybrid AT
Underground vs. Overhead Analysis
Alternative 1 - Hybrid
Project Expenditures Over 45 Years (2021-2065) in $000 * | [7 empty] | Salvage% |  |  | Escalated | [47 empty] | life | salvage | ITC | BD
Year |  | Description |  | Cost | Esc% | Type | Life | Input | Calcd |  | Cost | NPV | boy | cap1 | cap2 | cap3 | cap4 | cap5 | cap6 | cap7 | cap8 | cap9 | cap10 | cap11 | cap12 | cap13 | cap14 | cap15 | cap16 | cap17 | cap18 | cap19 | cap20 | cap21 | cap22 | cap23 | cap24 | cap25 | cap26 | cap27 | cap28 | cap29 | cap30 | cap31 | cap32 | cap33 | cap34 | cap35 | cap36 | cap37 | cap38 | cap39 | cap40 | exp a | exp b | exp c | exp d | total acf | error | error | Check | Error
2021 | Capital OH |  |  | 100 | 2.5 | ed | 45 | 0 |  | 0 | 97.561 | -98.5745 | 2021 | -97.561 | -1347.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1445.4782 | 0 | 0 | 0 | 0
2021 | Capital UG |  |  | 1381.6152 | 2.5 | ed | 47 | 0 |  | 0 | 1347.9172 | -1361.9202 | 2022 | -1.4913 | -20.6034 | -6.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.376 | 0 | 0 | 0 | -35.3477 | 0 | 0 | 0 | 0
2022 | Ongoing capital |  |  | 6.8771 | 0 | ed | 45 | 0 |  | 0 | 6.8771 | -6.5047 | 2023 | -1.1943 | -16.5004 | -0.10512 | -7.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5354 | 0 | 0 | 0 | -31.3842 | 0 | 0 | 0 | 0
2023 | Ongoing capital |  |  | 7.049 | 0 | ed | 45 | 0 |  | 0 | 7.049 | -6.2413 | 2024 | 3.236 | 44.7086 | -0.084185 | -0.10775 | -7.2252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6988 | 0 | 0 | 0 | 33.8286 | 0 | 0 | 0 | 0
2024 | Ongoing capital |  |  | 7.2252 | 0 | ed | 45 | 0 |  | 0 | 7.2252 | -5.9884 | 2025 | 0.33017 | 4.5616 | 0.2281 | -0.08629 | -0.11044 | -7.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8663 | 0 | 0 | 0 | -9.349 | 0 | 0 | 0 | 0
2025 | Ongoing capital |  |  | 7.4059 | 0 | ed | 45 | 0 |  | 0 | 7.4059 | -5.7455 | 2026 | 0.24328 | 3.3612 | 0.023274 | 0.23381 | -0.088447 | -0.1132 | -7.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.038 | 0 | 0 | 0 | -10.9691 | 0 | 0 | 0 | 0
2026 | Ongoing capital |  |  | 7.591 | 0 | ed | 45 | 0 |  | 0 | 7.591 | -5.5123 | 2027 | 0.16351 | 2.2591 | 0.017149 | 0.023855 | 0.23965 | -0.090658 | -0.11603 | -7.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2139 | 0 | 0 | 0 | -12.4981 | 0 | 0 | 0 | 0
2027 | Ongoing capital |  |  | 7.7808 | 0 | ed | 45 | 0 |  | 0 | 7.7808 | -5.2884 | 2028 | 0.090326 | 1.248 | 0.011526 | 0.017578 | 0.024452 | 0.24564 | -0.092925 | -0.11893 | -7.9753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3942 | 0 | 0 | 0 | -13.9439 | 0 | 0 | 0 | 0
2028 | Ongoing capital |  |  | 7.9753 | 0 | ed | 45 | 0 |  | 0 | 7.9753 | -5.0733 | 2029 | 0.023232 | 0.32097 | 0.0063671 | 0.011814 | 0.018017 | 0.025063 | 0.25178 | -0.095248 | -0.12191 | -8.1747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5791 | 0 | 0 | 0 | -15.3137 | 0 | 0 | 0 | 0
2029 | Ongoing capital |  |  | 8.1747 | 0 | ed | 45 | 0 |  | 0 | 8.1747 | -4.8667 | 2030 | 0.0189 | 0.26113 | 0.0016376 | 0.0065263 | 0.012109 | 0.018467 | 0.02569 | 0.25808 | -0.097629 | -0.12495 | -8.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7686 | 0 | 0 | 0 | -15.7677 | 0 | 0 | 0 | 0
2030 | Ongoing capital |  |  | 8.3791 | 0 | ed | 45 | 0 |  | 0 | 8.3791 | -4.6683 | 2031 | 0.026921 | 0.37195 | 0.0013323 | 0.0016786 | 0.0066894 | 0.012412 | 0.018929 | 0.026332 | 0.26453 | -0.10007 | -0.12808 | -8.5886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9628 | 0 | 0 | 0 | -16.0487 | 0 | 0 | 0 | 0
2031 | Ongoing capital |  |  | 8.5886 | 0 | ed | 45 | 0 |  | 0 | 8.5886 | -4.4777 | 2032 | 0.034942 | 0.48276 | 0.0018977 | 0.0013656 | 0.0017205 | 0.0068567 | 0.012722 | 0.019402 | 0.02699 | 0.27114 | -0.10257 | -0.13128 | -8.8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1619 | 0 | 0 | 0 | -16.3392 | 0 | 0 | 0 | 0
2032 | Ongoing capital |  |  | 8.8033 | 0 | ed | 45 | 0 |  | 0 | 8.8033 | -4.2947 | 2033 | 0.042963 | 0.59358 | 0.0024631 | 0.0019451 | 0.0013997 | 0.0017635 | 0.0070281 | 0.013041 | 0.019887 | 0.027665 | 0.27792 | -0.10514 | -0.13456 | -9.0233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3659 | 0 | 0 | 0 | -16.6393 | 0 | 0 | 0 | 0
2033 | Ongoing capital |  |  | 9.0233 | 0 | ed | 45 | 0 |  | 0 | 9.0233 | -4.1188 | 2034 | 0.050983 | 0.7044 | 0.0030284 | 0.0025246 | 0.0019937 | 0.0014347 | 0.0018076 | 0.0072038 | 0.013367 | 0.020385 | 0.028357 | 0.28487 | -0.10776 | -0.13792 | -9.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.5751 | 0 | 0 | 0 | -16.9493 | 0 | 0 | 0 | 0
2034 | Ongoing capital |  |  | 9.2489 | 0 | ed | 45 | 0 |  | 0 | 9.2489 | -3.9498 | 2035 | 0.059004 | 0.81521 | 0.0035938 | 0.0031042 | 0.0025878 | 0.0020436 | 0.0014706 | 0.0018528 | 0.0073839 | 0.013701 | 0.020894 | 0.029065 | 0.29199 | -0.11046 | -0.14137 | -9.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7894 | 0 | 0 | 0 | -17.2695 | 0 | 0 | 0 | 0
2035 | Ongoing capital |  |  | 9.4802 | 0 | ed | 45 | 0 |  | 0 | 9.4802 | -3.7875 | 2036 | 0.067025 | 0.92603 | 0.0041592 | 0.0036837 | 0.0031818 | 0.0026524 | 0.0020947 | 0.0015074 | 0.0018991 | 0.0075685 | 0.014043 | 0.021417 | 0.029792 | 0.29929 | -0.11322 | -0.14491 | -9.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.0092 | 0 | 0 | 0 | -17.6001 | 0 | 0 | 0 | 0
2036 | Ongoing capital |  |  | 9.7172 | 0 | ed | 45 | 0 |  | 0 | 9.7172 | -3.6315 | 2037 | 0.075046 | 1.0368 | 0.0047246 | 0.0042632 | 0.0037758 | 0.0032613 | 0.0027188 | 0.002147 | 0.001545 | 0.0019466 | 0.0077577 | 0.014394 | 0.021952 | 0.030537 | 0.30677 | -0.11605 | -0.14853 | -9.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.2344 | 0 | 0 | 0 | -17.9414 | 0 | 0 | 0 | 0
2037 | Ongoing capital |  |  | 9.9601 | 0 | ed | 45 | 0 |  | 0 | 9.9601 | -3.4816 | 2038 | 0.083067 | 1.1477 | 0.00529 | 0.0048427 | 0.0043698 | 0.0038702 | 0.0033428 | 0.0027867 | 0.0022007 | 0.0015837 | 0.0019953 | 0.0079516 | 0.014754 | 0.022501 | 0.0313 | 0.31444 | -0.11895 | -0.15224 | -10.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4653 | 0 | 0 | 0 | -18.2936 | 0 | 0 | 0 | 0
2038 | Ongoing capital |  |  | 10.2091 | 0 | ed | 45 | 0 |  | 0 | 10.2091 | -3.3375 | 2039 | 0.091087 | 1.2585 | 0.0058554 | 0.0054223 | 0.0049638 | 0.004479 | 0.0039669 | 0.0034264 | 0.0028564 | 0.0022557 | 0.0016233 | 0.0020452 | 0.0081504 | 0.015123 | 0.023063 | 0.032083 | 0.32231 | -0.12193 | -0.15605 | -10.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7019 | 0 | 0 | 0 | -18.657 | 0 | 0 | 0 | 0
2039 | Ongoing capital |  |  | 10.4643 | 0 | ed | 45 | 0 |  | 0 | 10.4643 | -3.1989 | 2040 | 0.099108 | 1.3693 | 0.0064208 | 0.0060018 | 0.0055578 | 0.0050879 | 0.004591 | 0.0040661 | 0.0035121 | 0.0029278 | 0.0023121 | 0.0016638 | 0.0020963 | 0.0083542 | 0.015501 | 0.02364 | 0.032885 | 0.33036 | -0.12497 | -0.15995 | -10.7259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.9444 | 0 | 0 | 0 | -19.0319 | 0 | 0 | 0 | 0
2040 | Ongoing capital |  |  | 10.7259 | 0 | ed | 45 | 0 |  | 0 | 10.7259 | -3.0657 | 2041 | 0.10713 | 1.4801 | 0.0069862 | 0.0065813 | 0.0061518 | 0.0056968 | 0.0052151 | 0.0047058 | 0.0041677 | 0.0035999 | 0.003001 | 0.0023699 | 0.0017054 | 0.0021487 | 0.0085631 | 0.015889 | 0.024231 | 0.033707 | 0.33862 | -0.1281 | -0.16395 | -10.9941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.1931 | 0 | 0 | 0 | -19.4186 | 0 | 0 | 0 | 0
2041 | Ongoing capital |  |  | 10.9941 | 0 | ed | 45 | 0 |  | 0 | 10.9941 | -2.9376 | 2042 | -0.34188 | -4.7235 | 0.0075516 | 0.0071608 | 0.0067458 | 0.0063056 | 0.0058392 | 0.0053455 | 0.0048234 | 0.0042719 | 0.0036899 | 0.003076 | 0.0024292 | 0.0017481 | 0.0022024 | 0.0087771 | 0.016286 | 0.024837 | 0.03455 | 0.34709 | -0.1313 | -0.16805 | -11.2689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.4479 | 0 | 0 | 0 | -26.5888 | 0 | 0 | 0 | 0
2042 | Ongoing capital |  |  | 11.2689 | 0 | ed | 45 | 0 |  | 0 | 11.2689 | -2.8143 | 2043 | -0.7909 | -10.9272 | -0.024099 | 0.0077403 | 0.0073398 | 0.0069145 | 0.0064633 | 0.0059852 | 0.0054791 | 0.004944 | 0.0043787 | 0.0037821 | 0.0031529 | 0.0024899 | 0.0017918 | 0.0022575 | 0.0089966 | 0.016693 | 0.025458 | 0.035413 | 0.35576 | -0.13458 | -0.17225 | -11.5506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.7091 | 0 | 0 | 0 | -33.8037 | 0 | 0 | 0 | 0
2043 | Ongoing capital |  |  | 11.5506 | 0 | ed | 45 | 0 |  | 0 | 11.5506 | -2.6958 | 2044 | -0.78288 | -10.8163 | -0.055751 | -0.024702 | 0.0079338 | 0.0075233 | 0.0070873 | 0.0066248 | 0.0061348 | 0.0056161 | 0.0050676 | 0.0044882 | 0.0038767 | 0.0032318 | 0.0025522 | 0.0018366 | 0.0023139 | 0.0092215 | 0.01711 | 0.026094 | 0.036299 | 0.36466 | -0.13795 | -0.17656 | -11.8394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.9768 | 0 | 0 | 0 | -34.2927 | 0 | 0 | 0 | 0
2044 | Ongoing capital |  |  | 11.8394 | 0 | ed | 45 | 0 |  | 0 | 11.8394 | -2.5817 | 2045 | -0.77486 | -10.7055 | -0.055185 | -0.057144 | -0.02532 | 0.0081322 | 0.0077114 | 0.0072645 | 0.0067905 | 0.0062881 | 0.0057565 | 0.0051943 | 0.0046004 | 0.0039736 | 0.0033125 | 0.002616 | 0.0018825 | 0.0023718 | 0.009452 | 0.017538 | 0.026746 | 0.037206 | 0.37378 | -0.1414 | -0.18097 | -12.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.2512 | 0 | 0 | 0 | -34.7964 | 0 | 0 | 0 | 0
2045 | Ongoing capital |  |  | 12.1354 | 0 | ed | 45 | 0 |  | 0 | 12.1354 | -2.4718 | 2046 | -0.76683 | -10.5947 | -0.05462 | -0.056565 | -0.058573 | -0.025953 | 0.0083355 | 0.0079042 | 0.0074461 | 0.0069602 | 0.0064454 | 0.0059004 | 0.0053242 | 0.0047154 | 0.0040729 | 0.0033954 | 0.0026814 | 0.0019295 | 0.002431 | 0.0096883 | 0.017976 | 0.027415 | 0.038136 | 0.38312 | -0.14493 | -0.18549 | -12.4388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.5325 | 0 | 0 | 0 | -35.3151 | 0 | 0 | 0 | 0
2046 | Ongoing capital |  |  | 12.4388 | 0 | ed | 45 | 0 |  | 0 | 12.4388 | -2.3658 | 2047 | -0.75881 | -10.4839 | -0.054054 | -0.055985 | -0.057979 | -0.060037 | -0.026601 | 0.0085439 | 0.0081018 | 0.0076323 | 0.0071342 | 0.0066065 | 0.0060479 | 0.0054573 | 0.0048333 | 0.0041748 | 0.0034802 | 0.0027484 | 0.0019778 | 0.0024918 | 0.0099305 | 0.018426 | 0.0281 | 0.03909 | 0.3927 | -0.14855 | -0.19013 | -12.7498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.8208 | 0 | 0 | 0 | -35.8491 | 0 | 0 | 0 | 0
2047 | Ongoing capital |  |  | 12.7498 | 0 | ed | 45 | 0 |  | 0 | 12.7498 | -2.2634 | 2048 | -0.75079 | -10.3731 | -0.053489 | -0.055406 | -0.057385 | -0.059428 | -0.061538 | -0.027266 | 0.0087575 | 0.0083044 | 0.0078231 | 0.0073126 | 0.0067716 | 0.0061991 | 0.0055937 | 0.0049541 | 0.0042791 | 0.0035672 | 0.0028171 | 0.0020272 | 0.0025541 | 0.010179 | 0.018887 | 0.028803 | 0.040067 | 0.40251 | -0.15227 | -0.19488 | -13.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.1163 | 0 | 0 | 0 | -36.3989 | 0 | 0 | 0 | 0
2048 | Ongoing capital |  |  | 13.0685 | 0 | ed | 45 | 0 |  | 0 | 13.0685 | -2.1642 | 2049 | -0.74277 | -10.2623 | -0.052924 | -0.054826 | -0.056791 | -0.058819 | -0.060914 | -0.063077 | -0.027948 | 0.0089764 | 0.008512 | 0.0080187 | 0.0074954 | 0.0069409 | 0.0063541 | 0.0057335 | 0.005078 | 0.0043861 | 0.0036564 | 0.0028875 | 0.0020779 | 0.002618 | 0.010433 | 0.019359 | 0.029523 | 0.041069 | 0.41258 | -0.15607 | -0.19976 | -13.3952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.4192 | 0 | 0 | 0 | -36.9649 | 0 | 0 | 0 | 0
2049 | Ongoing capital |  |  | 13.3952 | 0 | ed | 45 | 0 |  | 0 | 13.3952 | -2.0682 | 2050 | -0.73475 | -10.1514 | -0.052358 | -0.054247 | -0.056197 | -0.058211 | -0.06029 | -0.062437 | -0.064653 | -0.028647 | 0.0092008 | 0.0087248 | 0.0082191 | 0.0076828 | 0.0071145 | 0.0065129 | 0.0058769 | 0.0052049 | 0.0044958 | 0.0037478 | 0.0029597 | 0.0021299 | 0.0026834 | 0.010694 | 0.019843 | 0.030261 | 0.042095 | 0.42289 | -0.15998 | -0.20475 | -13.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.7297 | 0 | 0 | 0 | -37.5474 | 0 | 0 | 0 | 0
2050 | Ongoing capital |  |  | 13.7301 | 0 | ed | 45 | 0 |  | 0 | 13.7301 | -1.9751 | 2051 | -0.72673 | -10.0406 | -0.051793 | -0.053667 | -0.055603 | -0.057602 | -0.059666 | -0.061797 | -0.063998 | -0.06627 | -0.029363 | 0.0094309 | 0.0089429 | 0.0084246 | 0.0078748 | 0.0072923 | 0.0066758 | 0.0060238 | 0.0053351 | 0.0046081 | 0.0038415 | 0.0030337 | 0.0021831 | 0.0027505 | 0.010961 | 0.020339 | 0.031018 | 0.043148 | 0.43346 | -0.16398 | -0.20987 | -14.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.048 | 0 | 0 | 0 | -38.1469 | 0 | 0 | 0 | 0
2051 | Ongoing capital |  |  | 14.0733 | 0 | ed | 45 | 0 |  | 0 | 14.0733 | -1.8848 | 2052 | -0.71871 | -9.9298 | -0.051227 | -0.053088 | -0.055009 | -0.056993 | -0.059042 | -0.061158 | -0.063342 | -0.065598 | -0.067927 | -0.030097 | 0.0096666 | 0.0091665 | 0.0086352 | 0.0080717 | 0.0074746 | 0.0068426 | 0.0061744 | 0.0054684 | 0.0047233 | 0.0039376 | 0.0031096 | 0.0022377 | 0.0028193 | 0.011235 | 0.020847 | 0.031793 | 0.044227 | 0.4443 | -0.16808 | -0.21512 | -14.4252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.3742 | 0 | 0 | 0 | -38.7638 | 0 | 0 | 0 | 0
2052 | Ongoing capital |  |  | 14.4252 | 0 | ed | 45 | 0 |  | 0 | 14.4252 | -1.7972 | 2053 | -0.70338 | -9.718 | -0.050662 | -0.052508 | -0.054415 | -0.056384 | -0.058418 | -0.060518 | -0.062686 | -0.064926 | -0.067238 | -0.069625 | -0.030849 | 0.0099083 | 0.0093956 | 0.0088511 | 0.0082735 | 0.0076615 | 0.0070137 | 0.0063288 | 0.0056052 | 0.0048414 | 0.004036 | 0.0031873 | 0.0022936 | 0.0028897 | 0.011516 | 0.021368 | 0.032588 | 0.045332 | 0.45541 | -0.17228 | -0.22049 | -14.7858 | 0 | 0 | 0 | 0 | 0 | 0 | -13.7085 | 0 | 0 | 0 | -39.2902 | 0 | 0 | 0 | 0
2053 | Ongoing capital |  |  | 14.7858 | 0 | ed | 45 | 0 |  | 0 | 14.7858 | -1.7121 | 2054 | -0.68074 | -9.4052 | -0.049581 | -0.051929 | -0.053821 | -0.055775 | -0.057794 | -0.059878 | -0.062031 | -0.064254 | -0.066549 | -0.068919 | -0.071365 | -0.031621 | 0.010156 | 0.0096305 | 0.0090724 | 0.0084803 | 0.007853 | 0.0071891 | 0.006487 | 0.0057453 | 0.0049625 | 0.0041369 | 0.003267 | 0.002351 | 0.002962 | 0.011804 | 0.021903 | 0.033403 | 0.046466 | 0.46679 | -0.17658 | -0.22601 | -15.1554 | 0 | 0 | 0 | 0 | 0 | -14.0512 | 0 | 0 | 0 | -39.7261 | 0 | 0 | 0 | 0
2054 | Ongoing capital |  |  | 15.1554 | 0 | ed | 45 | 0 |  | 0 | 15.1554 | -1.6293 | 2055 | -0.6581 | -9.0924 | -0.047986 | -0.050821 | -0.053227 | -0.055166 | -0.05717 | -0.059238 | -0.061375 | -0.063582 | -0.06586 | -0.068213 | -0.070642 | -0.073149 | -0.032411 | 0.01041 | 0.0098713 | 0.0092992 | 0.0086924 | 0.0080494 | 0.0073688 | 0.0066491 | 0.0058889 | 0.0050865 | 0.0042403 | 0.0033487 | 0.0024097 | 0.003036 | 0.012099 | 0.02245 | 0.034238 | 0.047627 | 0.47846 | -0.181 | -0.23166 | -15.5343 | 0 | 0 | 0 | 0 | -14.4025 | 0 | 0 | 0 | -40.1796 | 0 | 0 | 0 | 0
2055 | Ongoing capital |  |  | 15.5343 | 0 | ed | 45 | 0 |  | 0 | 15.5343 | -1.5487 | 2056 | -0.63546 | -8.7796 | -0.04639 | -0.049185 | -0.052091 | -0.054557 | -0.056545 | -0.058599 | -0.060719 | -0.062909 | -0.065171 | -0.067506 | -0.069918 | -0.072408 | -0.074978 | -0.033221 | 0.01067 | 0.010118 | 0.0095317 | 0.0089097 | 0.0082506 | 0.007553 | 0.0068154 | 0.0060361 | 0.0052137 | 0.0043463 | 0.0034324 | 0.00247 | 0.0031119 | 0.012402 | 0.023011 | 0.035094 | 0.048818 | 0.49043 | -0.18552 | -0.23745 | -15.9227 | 0 | 0 | 0 | -14.7626 | 0 | 0 | 0 | -40.6513 | 0 | 0 | 0 | 0
2056 | Ongoing capital |  |  | 15.9227 | 0 | ed | 45 | 0 |  | 0 | 15.9227 | -1.4701 | 2057 | -0.61282 | -8.4668 | -0.044794 | -0.047549 | -0.050415 | -0.053394 | -0.055921 | -0.057959 | -0.060064 | -0.062237 | -0.064482 | -0.0668 | -0.069194 | -0.071666 | -0.074218 | -0.076853 | -0.034052 | 0.010937 | 0.010371 | 0.00977 | 0.0091324 | 0.0084569 | 0.0077418 | 0.0069858 | 0.006187 | 0.005344 | 0.004455 | 0.0035182 | 0.0025317 | 0.0031897 | 0.012712 | 0.023587 | 0.035971 | 0.050038 | 0.50269 | -0.19016 | -0.24338 | -16.3208 | 0 | 0 | -15.1316 | 0 | 0 | 0 | -41.1416 | 0 | 0 | 0 | 0
2057 | Ongoing capital |  |  | 16.3208 | 0 | ed | 45 | 0 |  | 0 | 16.3208 | -1.3934 | 2058 | -0.59018 | -8.1541 | -0.043198 | -0.045914 | -0.048738 | -0.051675 | -0.054729 | -0.057319 | -0.059408 | -0.061565 | -0.063793 | -0.066094 | -0.06847 | -0.070924 | -0.073457 | -0.076073 | -0.078774 | -0.034903 | 0.01121 | 0.01063 | 0.010014 | 0.0093607 | 0.0086683 | 0.0079354 | 0.0071604 | 0.0063417 | 0.0054776 | 0.0045664 | 0.0036061 | 0.002595 | 0.0032695 | 0.01303 | 0.024176 | 0.03687 | 0.051289 | 0.51525 | -0.19492 | -0.24947 | -16.7288 | 0 | -15.5099 | 0 | 0 | 0 | -41.6509 | 0 | 0 | 0 | 0
2058 | Ongoing capital |  |  | 16.7288 | 0 | ed | 45 | 0 |  | 0 | 16.7288 | -1.3185 | 2059 | -0.56754 | -7.8413 | -0.041602 | -0.044278 | -0.047062 | -0.049957 | -0.052967 | -0.056097 | -0.058752 | -0.060893 | -0.063104 | -0.065388 | -0.067747 | -0.070182 | -0.072697 | -0.075294 | -0.077975 | -0.080743 | -0.035776 | 0.011491 | 0.010896 | 0.010265 | 0.0095947 | 0.008885 | 0.0081338 | 0.0073394 | 0.0065003 | 0.0056146 | 0.0046805 | 0.0036963 | 0.0026599 | 0.0033512 | 0.013355 | 0.024781 | 0.037792 | 0.052571 | 0.52813 | -0.19979 | -0.2557 | -17.147 | -15.8977 | 0 | 0 | 0 | -42.1798 | 0 | 0 | 0 | 0
2059 | Ongoing capital |  |  | 17.147 | 0 | ed | 45 | 0 |  | 0 | 17.147 | -1.2452 | 2060 | -0.5449 | -7.5285 | -0.040006 | -0.042642 | -0.045385 | -0.048238 | -0.051206 | -0.054291 | -0.057499 | -0.060221 | -0.062416 | -0.064682 | -0.067023 | -0.06944 | -0.071937 | -0.074515 | -0.077176 | -0.079925 | -0.082762 | -0.03667 | 0.011778 | 0.011168 | 0.010521 | 0.0098346 | 0.0091071 | 0.0083371 | 0.0075229 | 0.0066628 | 0.0057549 | 0.0047976 | 0.0037887 | 0.0027264 | 0.003435 | 0.013689 | 0.0254 | 0.038737 | 0.053886 | 0.54134 | -0.20478 | -0.2621 | -16.2951 | 0 | 0 | 0 | -25.1529 | 0 | 0 | 0 | 0
2060 | Ongoing capital |  |  | 17.5757 | 0 | ed | 45 | 0 |  |  | 17.5757 | -1.2452
2061 | Ongoing capital |  |  | 18.0151 | 0 | ed | 45 | 0 |  |  | 18.0151 | -1.2452
2062 | Ongoing capital |  |  | 18.4654 | 0 | ed | 45 | 0 |  |  | 18.4654 | -1.2452
2063 | Ongoing capital |  |  | 18.9271 | 0 | ed | 45 | 0 |  |  | 18.9271 | -1.2452
2064 | Ongoing capital |  |  | 19.4003 | 0 | ed | 45 | 0 |  |  | 19.4003 | -1.2452
2065 | Ongoing capital |  |  | 19.8853 | 0 | ed | 45 | 0 |  |  | 19.8853 | -1.2452
* Life and salvage fields ignored when expenditure is an expense (type exp or atx). |  |  |  | 20.3824 | [6 empty] | 1873.4213 | -1586.0644 | 2061 | -0.52227 | -7.2157 | -0.03841 | -0.041006 | -0.043708 | -0.04652 | -0.049444 | -0.052486 | -0.055649 | -0.058937 | -0.061727 | -0.063976 | -0.066299 | -0.068698 | -0.071176 | -0.073735 | -0.076377 | -0.079106 | -0.081923 | -0.084831 | -0.037587 | 0.012072 | 0.011448 | 0.010784 | 0.01008 | 0.0093348 | 0.0085455 | 0.007711 | 0.0068293 | 0.0058988 | 0.0049175 | 0.0038834 | 0.0027946 | 0.0035209 | 0.014032 | 0.026035 | 0.039705 | 0.055233 | 0.55487 | -0.2099 | -16.7025 | 0 | 0 | 0 | -25.0143 | 0 | 0 | 0 | 0
[13 empty] | 2062 | -0.49963 | -6.9029 | -0.036815 | -0.039371 | -0.042032 | -0.044801 | -0.047683 | -0.05068 | -0.053798 | -0.05704 | -0.06041 | -0.06327 | -0.065575 | -0.067957 | -0.070416 | -0.072956 | -0.075578 | -0.078287 | -0.081083 | -0.083971 | -0.086952 | -0.038527 | 0.012374 | 0.011734 | 0.011054 | 0.010332 | 0.0095682 | 0.0087592 | 0.0079037 | 0.0070001 | 0.0060463 | 0.0050404 | 0.0039805 | 0.0028644 | 0.0036089 | 0.014382 | 0.026686 | 0.040698 | 0.056614 | 0.56874 | -17.1201 | 0 | 0 | 0 | -24.9324
Operating Expenses (+) and Revenues (-) Over 45 Years (2021-2065) in $000 | [12 empty] | 2063 | -0.47699 | -6.5901 | -0.035219 | -0.037735 | -0.040355 | -0.043082 | -0.045921 | -0.048875 | -0.051947 | -0.055143 | -0.058466 | -0.06192 | -0.064852 | -0.067215 | -0.069656 | -0.072176 | -0.07478 | -0.077468 | -0.080244 | -0.08311 | -0.08607 | -0.089126 | -0.03949 | 0.012683 | 0.012027 | 0.01133 | 0.010591 | 0.0098074 | 0.0089781 | 0.0081013 | 0.0071751 | 0.0061974 | 0.0051664 | 0.00408 | 0.002936 | 0.0036991 | 0.014742 | 0.027353 | 0.041715 | 0.058029 | -17.5481 | 0 | 0 | 0 | -25.6534
Year | a | b | c | d |  |  | Description |  |  |  | Esc% | NPV | 2064 | -0.45435 | -6.2773 | -0.033623 | -0.036099 | -0.038678 | -0.041364 | -0.044159 | -0.047069 | -0.050096 | -0.053246 | -0.056521 | -0.059927 | -0.063468 | -0.066473 | -0.068895 | -0.071397 | -0.073981 | -0.076649 | -0.079405 | -0.08225 | -0.085188 | -0.088222 | -0.091354 | -0.040477 | 0.013001 | 0.012328 | 0.011613 | 0.010856 | 0.010053 | 0.0092026 | 0.0083039 | 0.0073545 | 0.0063524 | 0.0052956 | 0.004182 | 0.0030094 | 0.0037916 | 0.01511 | 0.028037 | 0.042758 | -17.9868 | 0 | 0 | 0 | -25.8757
2021 | 8.8536 |  |  |  | a. | Annual Operations and Maintenance |  |  |  |  | 2.5 | -124.948 | 2065 | -0.43171 | -5.9645 | -0.032027 | -0.034463 | -0.037002 | -0.039645 | -0.042398 | -0.045263 | -0.048246 | -0.051349 | -0.054577 | -0.057934 | -0.061426 | -0.065055 | -0.068135 | -0.070618 | -0.073182 | -0.07583 | -0.078565 | -0.08139 | -0.084306 | -0.087318 | -0.090427 | -0.093638 | -0.041489 | 0.013326 | 0.012636 | 0.011904 | 0.011127 | 0.010304 | 0.0094327 | 0.0085115 | 0.0075383 | 0.0065112 | 0.005428 | 0.0042866 | 0.0030847 | 0.0038864 | 0.015488 | 0.028738 | -18.4364 | 0 | 0 | 0 | -26.0948
2022 | 8.8536 |  |  |  | b. | [5 empty] | 2.5 | 0 | 2066 | -0.40907 | -5.6518 | -0.030431 | -0.032828 | -0.035325 | -0.037927 | -0.040636 | -0.043458 | -0.046395 | -0.049452 | -0.052633 | -0.055941 | -0.059383 | -0.062961 | -0.066681 | -0.069838 | -0.071655 | -0.072027 | -0.070842 | -0.067986 | -0.063335 | -0.056762 | -0.048132 | -0.037304 | -0.024131 | 0.048392 | 0.18469 | 0.32968 | 0.48377 | 0.64736 | 0.82089 | 1.0048 | 1.1995 | 1.4056 | 1.6235 | 1.8538 | 2.0969 | 2.3535 | 2.6262 | 2.9268 | -18.8974 | 0 | 0 | 0 | -6.5488
2023 | 8.8536 |  |  |  | c. | [5 empty] | 2.5 | 0 | 2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 8.8536 |  |  |  | d. | [5 empty] | 2.5 | 0 | 2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 8.8536 | [10 empty] | -124.948 | 2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 8.8536 | [11 empty] | 2070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 8.8536 | [11 empty] | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 8.8536 | [7 empty] | Total NPV ($000) |  |  | -1711.0124 | 45 | MaxCap
2029 | 8.8536 | [11 empty] | 0 | cap error
2030 | 8.8536 | [11 empty] | 0 | exp error
2031 | 8.8536 | [11 empty] | 0 | tot errors
2032 | 8.8536 | [9 empty] | Comments (press alt+enter to skip to new line)
2033 | 8.8536
2034 | 8.8536
2035 | 8.8536 | [11 empty] | 1 | -5.5438 | -76.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.376 | 0 | 0 | 0 | -88.5146
2036 | 8.8536 | [11 empty] | 2 | -5.4665 | -75.5263 | -0.39079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5354 | 0 | 0 | 0 | -87.919
2037 | 8.8536 | [11 empty] | 3 | -5.3892 | -74.4579 | -0.38534 | -0.40056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6988 | 0 | 0 | 0 | -87.3318
2038 | 8.8536 | [11 empty] | 4 | -5.3119 | -73.3895 | -0.37989 | -0.39497 | -0.41057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8663 | 0 | 0 | 0 | -86.7531
2039 | 8.8536 | [11 empty] | 5 | -5.2345 | -72.3211 | -0.37443 | -0.38938 | -0.40484 | -0.42084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.038 | 0 | 0 | 0 | -86.1831
2040 | 8.8536
2041 | 8.8536
2042 | 8.8536
2043 | 8.8536
2044 | 8.8536
2045 | 8.8536
2046 | 8.8536
2047 | 8.8536
2048 | 8.8536
2049 | 8.8536
2050 | 8.8536
2051 | 8.8536
2052 | 8.8536
2053 | 8.8536
2054 | 8.8536
2055 | 8.8536
2056 | 8.8536
2057 | 8.8536
2058 | 8.8536
2059 | 8.8536
2060 | 8.8536
2061 | 8.8536
2062 | 8.8536
2063 | 8.8536
2064 | 8.8536
2065 | 8.8536
2066
2067
2068
2069
2070
Note on BK6: Jonathan: Starting in 2018, bonus depreciation no longer available to public utilities
Note on A7: Enter year of operation for capital, or year of occurrence for expenses. Timing is assumed to be beginning-of-year. Amounts entered outside of study period are ignored.
Note on C7: Enter project expenditures required to implement this alternative. Amounts already spent on a proposed project should be included as part of the project cost in the alternative that completes the project. In competing alternatives where the project is abandoned (such as status quo), any amounts already spent should be shown as an expense in the year the project is written off.
Note on E7: Enter cost in financial dollars, including contingency and overheads. For multi-year construction projects, enter cost for each expenditure type as lump sum in year of operation.
Note on F7: Accept default escalation rate, enter a different rate, or enter zero if cost is already escalated to year of expenditure (as it would be in a job estimate).
Note on G7: Capital Type Life ¦ Capital Type Life Buildings bldg 50 ¦ Power Plants: Communication equip comm 15 ¦ Combined cycle cc 30 Computer hardware comp 5 ¦ Combustion turbine ct 25 Computer software soft 5 ¦ Micro turbine mt 10 Electric dist (<69kV) ed 45 ¦ Hydro hyd 50 Electric trans (69kV+) et 55 ¦ Hydro additions hyda 20 Electric smart meter em 20 ¦ Nuclear nuc 15 Gas distribution gasd 55 ¦ Nuclear additions nuca 7 Gas meters gm 30 ¦ Biomass bio 25 Gas trans & storage gast 55 ¦ Fuel cell fcl 8 Gas held for resale gasc 99 ¦ Geothermal geo 25 Land easement ease 99 ¦ Solar photovoltaic pv 20 Land purchase land 99 ¦ Solar thermal st 25 Motor vehicles mv 10 ¦ Tidal or wave tdl 10 Office furniture furn 20 ¦ Waste wst 25 Electricity Storage bat 15 ¦ Wind wnd 25 Expense exp ¦ Expense, after-tax atx This is a partial listing of expenditure types. See EASOP Help tab or Economic Guide for additional guidance in selecting expenditure types.
Note on H7: Enter the expected life for each capital asset, even if it extends beyond the study period. EASOP retires each asset at the end of its life or the end of the study period, whichever occurs first, at the salvage specified.
Note on I7: Accept zero as default salvage value, enter a different value, or delete entry to use value calculated by EASOP. For most analyses, use 100% for land and 0% for all other expenditures.
Note on BK8: =IF(OR(AND(A8>2011,RIGHT(G8,3)="sbd"),AND(A8>2012,RIGHT(G8,2)="bd")),1,0)
Note on BK9: =IF(OR(AND(A9>2011,RIGHT(G9,3)="sbd"),AND(A9>2012,RIGHT(G9,2)="bd")),1,0)
Note on BK10: =IF(OR(AND(A10>2011,RIGHT(G10,3)="sbd"),AND(A10>2012,RIGHT(G10,2)="bd")),1,0)
Note on BK11: =IF(OR(AND(A11>2011,RIGHT(G11,3)="sbd"),AND(A11>2012,RIGHT(G11,2)="bd")),1,0)
Note on BK12: =IF(OR(AND(A12>2011,RIGHT(G12,3)="sbd"),AND(A12>2012,RIGHT(G12,2)="bd")),1,0)
Note on BK13: =IF(OR(AND(A13>2011,RIGHT(G13,3)="sbd"),AND(A13>2012,RIGHT(G13,2)="bd")),1,0)
Note on BK14: =IF(OR(AND(A14>2011,RIGHT(G14,3)="sbd"),AND(A14>2012,RIGHT(G14,2)="bd")),1,0)
Note on BK15: =IF(OR(AND(A15>2011,RIGHT(G15,3)="sbd"),AND(A15>2012,RIGHT(G15,2)="bd")),1,0)
Note on BK16: =IF(OR(AND(A16>2011,RIGHT(G16,3)="sbd"),AND(A16>2012,RIGHT(G16,2)="bd")),1,0)
Note on BK17: =IF(OR(AND(A17>2011,RIGHT(G17,3)="sbd"),AND(A17>2012,RIGHT(G17,2)="bd")),1,0)
Note on BK18: =IF(OR(AND(A18>2011,RIGHT(G18,3)="sbd"),AND(A18>2012,RIGHT(G18,2)="bd")),1,0)
Note on BK19: =IF(OR(AND(A19>2011,RIGHT(G19,3)="sbd"),AND(A19>2012,RIGHT(G19,2)="bd")),1,0)
Note on BK20: =IF(OR(AND(A20>2011,RIGHT(G20,3)="sbd"),AND(A20>2012,RIGHT(G20,2)="bd")),1,0)
Note on BK21: =IF(OR(AND(A21>2011,RIGHT(G21,3)="sbd"),AND(A21>2012,RIGHT(G21,2)="bd")),1,0)
Note on BK22: =IF(OR(AND(A22>2011,RIGHT(G22,3)="sbd"),AND(A22>2012,RIGHT(G22,2)="bd")),1,0)
Note on BK23: =IF(OR(AND(A23>2011,RIGHT(G23,3)="sbd"),AND(A23>2012,RIGHT(G23,2)="bd")),1,0)
Note on BK24: =IF(OR(AND(A24>2011,RIGHT(G24,3)="sbd"),AND(A24>2012,RIGHT(G24,2)="bd")),1,0)
Note on BK25: =IF(OR(AND(A25>2011,RIGHT(G25,3)="sbd"),AND(A25>2012,RIGHT(G25,2)="bd")),1,0)
Note on BK26: =IF(OR(AND(A26>2011,RIGHT(G26,3)="sbd"),AND(A26>2012,RIGHT(G26,2)="bd")),1,0)
Note on BK27: =IF(OR(AND(A27>2011,RIGHT(G27,3)="sbd"),AND(A27>2012,RIGHT(G27,2)="bd")),1,0)
Note on BK28: =IF(OR(AND(A28>2011,RIGHT(G28,3)="sbd"),AND(A28>2012,RIGHT(G28,2)="bd")),1,0)
Note on BK29: =IF(OR(AND(A29>2011,RIGHT(G29,3)="sbd"),AND(A29>2012,RIGHT(G29,2)="bd")),1,0)
Note on BK30: =IF(OR(AND(A30>2011,RIGHT(G30,3)="sbd"),AND(A30>2012,RIGHT(G30,2)="bd")),1,0)
Note on BK31: =IF(OR(AND(A31>2011,RIGHT(G31,3)="sbd"),AND(A31>2012,RIGHT(G31,2)="bd")),1,0)
Note on BK32: =IF(OR(AND(A32>2011,RIGHT(G32,3)="sbd"),AND(A32>2012,RIGHT(G32,2)="bd")),1,0)
Note on BK33: =IF(OR(AND(A33>2011,RIGHT(G33,3)="sbd"),AND(A33>2012,RIGHT(G33,2)="bd")),1,0)
Note on BK34: =IF(OR(AND(A34>2011,RIGHT(G34,3)="sbd"),AND(A34>2012,RIGHT(G34,2)="bd")),1,0)
Note on BK35: =IF(OR(AND(A35>2011,RIGHT(G35,3)="sbd"),AND(A35>2012,RIGHT(G35,2)="bd")),1,0)
Note on BK36: =IF(OR(AND(A36>2011,RIGHT(G36,3)="sbd"),AND(A36>2012,RIGHT(G36,2)="bd")),1,0)
Note on BK37: =IF(OR(AND(A37>2011,RIGHT(G37,3)="sbd"),AND(A37>2012,RIGHT(G37,2)="bd")),1,0)
Note on BK38: =IF(OR(AND(A38>2011,RIGHT(G38,3)="sbd"),AND(A38>2012,RIGHT(G38,2)="bd")),1,0)
Note on BK39: =IF(OR(AND(A39>2011,RIGHT(G39,3)="sbd"),AND(A39>2012,RIGHT(G39,2)="bd")),1,0)
Note on BK40: =IF(OR(AND(A40>2011,RIGHT(G40,3)="sbd"),AND(A40>2012,RIGHT(G40,2)="bd")),1,0)
Note on BK41: =IF(OR(AND(A41>2011,RIGHT(G41,3)="sbd"),AND(A41>2012,RIGHT(G41,2)="bd")),1,0)
Note on BK42: =IF(OR(AND(A42>2011,RIGHT(G42,3)="sbd"),AND(A42>2012,RIGHT(G42,2)="bd")),1,0)
Note on BK43: =IF(OR(AND(A43>2011,RIGHT(G43,3)="sbd"),AND(A43>2012,RIGHT(G43,2)="bd")),1,0)
Note on BK44: =IF(OR(AND(A44>2011,RIGHT(G44,3)="sbd"),AND(A44>2012,RIGHT(G44,2)="bd")),1,0)
Note on BK45: =IF(OR(AND(A45>2011,RIGHT(G45,3)="sbd"),AND(A45>2012,RIGHT(G45,2)="bd")),1,0)
Note on BK46: =IF(OR(AND(A46>2011,RIGHT(G46,3)="sbd"),AND(A46>2012,RIGHT(G46,2)="bd")),1,0)
Note on BK47: =IF(OR(AND(A47>2011,RIGHT(G47,3)="sbd"),AND(A47>2012,RIGHT(G47,2)="bd")),1,0)
Note on A57: Timing of operating expenses and revenues is assumed to be end-of-year. Amounts entered beyond study period are ignored.
Note on H57: Enter recurring expenses and revenues (assuming no cost-of-service regulation) for this alternative. If a project will result in savings, enter them as a cost under status quo or as a savings under the proposed project, but not as both in the same evaluation.
Note on L57: Accept default escalation rate, enter a different rate, or enter zero if cost or revenue stream already includes escalation.

## 1 Hybrid
Underground vs. Overhead Analysis
Alternative 1 - Hybrid
Project Expenditures Over 45 Years (2021-2065) in $000 * | [7 empty] | Salvage% |  |  | Escalated | [47 empty] | life | salvage | ITC | BD
Year |  | Description |  | Cost | Esc% | Type | Life | Input | Calcd |  | Cost | NPV | boy | cap1 | cap2 | cap3 | cap4 | cap5 | cap6 | cap7 | cap8 | cap9 | cap10 | cap11 | cap12 | cap13 | cap14 | cap15 | cap16 | cap17 | cap18 | cap19 | cap20 | cap21 | cap22 | cap23 | cap24 | cap25 | cap26 | cap27 | cap28 | cap29 | cap30 | cap31 | cap32 | cap33 | cap34 | cap35 | cap36 | cap37 | cap38 | cap39 | cap40 | exp a | exp b | exp c | exp d | total acf | error | error | Check | Error
2021 | Capital OH |  |  | 487.4345 | 2.5 | ed | 45 | 0 |  | 0 | 475.5459 | -480.4861 | 2021 | -475.5459 | -1347.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1823.4631 | 0 | 0 | 0 | 0
2021 | Capital UG |  |  | 1381.6152 | 2.5 | ed | 47 | 0 |  | 0 | 1347.9172 | -1361.9202 | 2022 | -7.2689 | -20.6034 | -6.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.376 | 0 | 0 | 0 | -41.1254 | 0 | 0 | 0 | 0
2022 | Ongoing capital |  |  | 6.8771 | 0 | ed | 45 | 0 |  | 0 | 6.8771 | -6.5047 | 2023 | -5.8213 | -16.5004 | -0.10512 | -7.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5354 | 0 | 0 | 0 | -36.0113 | 0 | 0 | 0 | 0
2023 | Ongoing capital |  |  | 7.049 | 0 | ed | 45 | 0 |  | 0 | 7.049 | -6.2413 | 2024 | 15.7732 | 44.7086 | -0.084185 | -0.10775 | -7.2252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6988 | 0 | 0 | 0 | 46.3658 | 0 | 0 | 0 | 0
2024 | Ongoing capital |  |  | 7.2252 | 0 | ed | 45 | 0 |  | 0 | 7.2252 | -5.9884 | 2025 | 1.6093 | 4.5616 | 0.2281 | -0.08629 | -0.11044 | -7.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8663 | 0 | 0 | 0 | -8.0698 | 0 | 0 | 0 | 0
2025 | Ongoing capital |  |  | 7.4059 | 0 | ed | 45 | 0 |  | 0 | 7.4059 | -5.7455 | 2026 | 1.1858 | 3.3612 | 0.023274 | 0.23381 | -0.088447 | -0.1132 | -7.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.038 | 0 | 0 | 0 | -10.0265 | 0 | 0 | 0 | 0
2026 | Ongoing capital |  |  | 7.591 | 0 | ed | 45 | 0 |  | 0 | 7.591 | -5.5123 | 2027 | 0.79701 | 2.2591 | 0.017149 | 0.023855 | 0.23965 | -0.090658 | -0.11603 | -7.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2139 | 0 | 0 | 0 | -11.8646 | 0 | 0 | 0 | 0
2027 | Ongoing capital |  |  | 7.7808 | 0 | ed | 45 | 0 |  | 0 | 7.7808 | -5.2884 | 2028 | 0.44028 | 1.248 | 0.011526 | 0.017578 | 0.024452 | 0.24564 | -0.092925 | -0.11893 | -7.9753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.3942 | 0 | 0 | 0 | -13.594 | 0 | 0 | 0 | 0
2028 | Ongoing capital |  |  | 7.9753 | 0 | ed | 45 | 0 |  | 0 | 7.9753 | -5.0733 | 2029 | 0.11324 | 0.32097 | 0.0063671 | 0.011814 | 0.018017 | 0.025063 | 0.25178 | -0.095248 | -0.12191 | -8.1747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5791 | 0 | 0 | 0 | -15.2237 | 0 | 0 | 0 | 0
2029 | Ongoing capital |  |  | 8.1747 | 0 | ed | 45 | 0 |  | 0 | 8.1747 | -4.8667 | 2030 | 0.092127 | 0.26113 | 0.0016376 | 0.0065263 | 0.012109 | 0.018467 | 0.02569 | 0.25808 | -0.097629 | -0.12495 | -8.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7686 | 0 | 0 | 0 | -15.6945 | 0 | 0 | 0 | 0
2030 | Ongoing capital |  |  | 8.3791 | 0 | ed | 45 | 0 |  | 0 | 8.3791 | -4.6683 | 2031 | 0.13122 | 0.37195 | 0.0013323 | 0.0016786 | 0.0066894 | 0.012412 | 0.018929 | 0.026332 | 0.26453 | -0.10007 | -0.12808 | -8.5886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9628 | 0 | 0 | 0 | -15.9444 | 0 | 0 | 0 | 0
2031 | Ongoing capital |  |  | 8.5886 | 0 | ed | 45 | 0 |  | 0 | 8.5886 | -4.4777 | 2032 | 0.17032 | 0.48276 | 0.0018977 | 0.0013656 | 0.0017205 | 0.0068567 | 0.012722 | 0.019402 | 0.02699 | 0.27114 | -0.10257 | -0.13128 | -8.8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1619 | 0 | 0 | 0 | -16.2038 | 0 | 0 | 0 | 0
2032 | Ongoing capital |  |  | 8.8033 | 0 | ed | 45 | 0 |  | 0 | 8.8033 | -4.2947 | 2033 | 0.20941 | 0.59358 | 0.0024631 | 0.0019451 | 0.0013997 | 0.0017635 | 0.0070281 | 0.013041 | 0.019887 | 0.027665 | 0.27792 | -0.10514 | -0.13456 | -9.0233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3659 | 0 | 0 | 0 | -16.4728 | 0 | 0 | 0 | 0
2033 | Ongoing capital |  |  | 9.0233 | 0 | ed | 45 | 0 |  | 0 | 9.0233 | -4.1188 | 2034 | 0.24851 | 0.7044 | 0.0030284 | 0.0025246 | 0.0019937 | 0.0014347 | 0.0018076 | 0.0072038 | 0.013367 | 0.020385 | 0.028357 | 0.28487 | -0.10776 | -0.13792 | -9.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.5751 | 0 | 0 | 0 | -16.7518 | 0 | 0 | 0 | 0
2034 | Ongoing capital |  |  | 9.2489 | 0 | ed | 45 | 0 |  | 0 | 9.2489 | -3.9498 | 2035 | 0.28761 | 0.81521 | 0.0035938 | 0.0031042 | 0.0025878 | 0.0020436 | 0.0014706 | 0.0018528 | 0.0073839 | 0.013701 | 0.020894 | 0.029065 | 0.29199 | -0.11046 | -0.14137 | -9.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7894 | 0 | 0 | 0 | -17.0409 | 0 | 0 | 0 | 0
2035 | Ongoing capital |  |  | 9.4802 | 0 | ed | 45 | 0 |  | 0 | 9.4802 | -3.7875 | 2036 | 0.3267 | 0.92603 | 0.0041592 | 0.0036837 | 0.0031818 | 0.0026524 | 0.0020947 | 0.0015074 | 0.0018991 | 0.0075685 | 0.014043 | 0.021417 | 0.029792 | 0.29929 | -0.11322 | -0.14491 | -9.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.0092 | 0 | 0 | 0 | -17.3404 | 0 | 0 | 0 | 0
2036 | Ongoing capital |  |  | 9.7172 | 0 | ed | 45 | 0 |  | 0 | 9.7172 | -3.6315 | 2037 | 0.3658 | 1.0368 | 0.0047246 | 0.0042632 | 0.0037758 | 0.0032613 | 0.0027188 | 0.002147 | 0.001545 | 0.0019466 | 0.0077577 | 0.014394 | 0.021952 | 0.030537 | 0.30677 | -0.11605 | -0.14853 | -9.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.2344 | 0 | 0 | 0 | -17.6506 | 0 | 0 | 0 | 0
2037 | Ongoing capital |  |  | 9.9601 | 0 | ed | 45 | 0 |  | 0 | 9.9601 | -3.4816 | 2038 | 0.4049 | 1.1477 | 0.00529 | 0.0048427 | 0.0043698 | 0.0038702 | 0.0033428 | 0.0027867 | 0.0022007 | 0.0015837 | 0.0019953 | 0.0079516 | 0.014754 | 0.022501 | 0.0313 | 0.31444 | -0.11895 | -0.15224 | -10.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4653 | 0 | 0 | 0 | -17.9718 | 0 | 0 | 0 | 0
2038 | Ongoing capital |  |  | 10.2091 | 0 | ed | 45 | 0 |  | 0 | 10.2091 | -3.3375 | 2039 | 0.44399 | 1.2585 | 0.0058554 | 0.0054223 | 0.0049638 | 0.004479 | 0.0039669 | 0.0034264 | 0.0028564 | 0.0022557 | 0.0016233 | 0.0020452 | 0.0081504 | 0.015123 | 0.023063 | 0.032083 | 0.32231 | -0.12193 | -0.15605 | -10.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7019 | 0 | 0 | 0 | -18.3041 | 0 | 0 | 0 | 0
2039 | Ongoing capital |  |  | 10.4643 | 0 | ed | 45 | 0 |  | 0 | 10.4643 | -3.1989 | 2040 | 0.48309 | 1.3693 | 0.0064208 | 0.0060018 | 0.0055578 | 0.0050879 | 0.004591 | 0.0040661 | 0.0035121 | 0.0029278 | 0.0023121 | 0.0016638 | 0.0020963 | 0.0083542 | 0.015501 | 0.02364 | 0.032885 | 0.33036 | -0.12497 | -0.15995 | -10.7259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.9444 | 0 | 0 | 0 | -18.6479 | 0 | 0 | 0 | 0
2040 | Ongoing capital |  |  | 10.7259 | 0 | ed | 45 | 0 |  | 0 | 10.7259 | -3.0657 | 2041 | 0.52218 | 1.4801 | 0.0069862 | 0.0065813 | 0.0061518 | 0.0056968 | 0.0052151 | 0.0047058 | 0.0041677 | 0.0035999 | 0.003001 | 0.0023699 | 0.0017054 | 0.0021487 | 0.0085631 | 0.015889 | 0.024231 | 0.033707 | 0.33862 | -0.1281 | -0.16395 | -10.9941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.1931 | 0 | 0 | 0 | -19.0035 | 0 | 0 | 0 | 0
2041 | Ongoing capital |  |  | 10.9941 | 0 | ed | 45 | 0 |  | 0 | 10.9941 | -2.9376 | 2042 | -1.6665 | -4.7235 | 0.0075516 | 0.0071608 | 0.0067458 | 0.0063056 | 0.0058392 | 0.0053455 | 0.0048234 | 0.0042719 | 0.0036899 | 0.003076 | 0.0024292 | 0.0017481 | 0.0022024 | 0.0087771 | 0.016286 | 0.024837 | 0.03455 | 0.34709 | -0.1313 | -0.16805 | -11.2689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.4479 | 0 | 0 | 0 | -27.9134 | 0 | 0 | 0 | 0
2042 | Ongoing capital |  |  | 11.2689 | 0 | ed | 45 | 0 |  | 0 | 11.2689 | -2.8143 | 2043 | -3.8551 | -10.9272 | -0.024099 | 0.0077403 | 0.0073398 | 0.0069145 | 0.0064633 | 0.0059852 | 0.0054791 | 0.004944 | 0.0043787 | 0.0037821 | 0.0031529 | 0.0024899 | 0.0017918 | 0.0022575 | 0.0089966 | 0.016693 | 0.025458 | 0.035413 | 0.35576 | -0.13458 | -0.17225 | -11.5506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.7091 | 0 | 0 | 0 | -36.8679 | 0 | 0 | 0 | 0
2043 | Ongoing capital |  |  | 11.5506 | 0 | ed | 45 | 0 |  | 0 | 11.5506 | -2.6958 | 2044 | -3.816 | -10.8163 | -0.055751 | -0.024702 | 0.0079338 | 0.0075233 | 0.0070873 | 0.0066248 | 0.0061348 | 0.0056161 | 0.0050676 | 0.0044882 | 0.0038767 | 0.0032318 | 0.0025522 | 0.0018366 | 0.0023139 | 0.0092215 | 0.01711 | 0.026094 | 0.036299 | 0.36466 | -0.13795 | -0.17656 | -11.8394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.9768 | 0 | 0 | 0 | -37.3258 | 0 | 0 | 0 | 0
2044 | Ongoing capital |  |  | 11.8394 | 0 | ed | 45 | 0 |  | 0 | 11.8394 | -2.5817 | 2045 | -3.7769 | -10.7055 | -0.055185 | -0.057144 | -0.02532 | 0.0081322 | 0.0077114 | 0.0072645 | 0.0067905 | 0.0062881 | 0.0057565 | 0.0051943 | 0.0046004 | 0.0039736 | 0.0033125 | 0.002616 | 0.0018825 | 0.0023718 | 0.009452 | 0.017538 | 0.026746 | 0.037206 | 0.37378 | -0.1414 | -0.18097 | -12.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.2512 | 0 | 0 | 0 | -37.7985 | 0 | 0 | 0 | 0
2045 | Ongoing capital |  |  | 12.1354 | 0 | ed | 45 | 0 |  | 0 | 12.1354 | -2.4718 | 2046 | -3.7378 | -10.5947 | -0.05462 | -0.056565 | -0.058573 | -0.025953 | 0.0083355 | 0.0079042 | 0.0074461 | 0.0069602 | 0.0064454 | 0.0059004 | 0.0053242 | 0.0047154 | 0.0040729 | 0.0033954 | 0.0026814 | 0.0019295 | 0.002431 | 0.0096883 | 0.017976 | 0.027415 | 0.038136 | 0.38312 | -0.14493 | -0.18549 | -12.4388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.5325 | 0 | 0 | 0 | -38.2861 | 0 | 0 | 0 | 0
2046 | Ongoing capital |  |  | 12.4388 | 0 | ed | 45 | 0 |  | 0 | 12.4388 | -2.3658 | 2047 | -3.6987 | -10.4839 | -0.054054 | -0.055985 | -0.057979 | -0.060037 | -0.026601 | 0.0085439 | 0.0081018 | 0.0076323 | 0.0071342 | 0.0066065 | 0.0060479 | 0.0054573 | 0.0048333 | 0.0041748 | 0.0034802 | 0.0027484 | 0.0019778 | 0.0024918 | 0.0099305 | 0.018426 | 0.0281 | 0.03909 | 0.3927 | -0.14855 | -0.19013 | -12.7498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.8208 | 0 | 0 | 0 | -38.789 | 0 | 0 | 0 | 0
2047 | Ongoing capital |  |  | 12.7498 | 0 | ed | 45 | 0 |  | 0 | 12.7498 | -2.2634 | 2048 | -3.6596 | -10.3731 | -0.053489 | -0.055406 | -0.057385 | -0.059428 | -0.061538 | -0.027266 | 0.0087575 | 0.0083044 | 0.0078231 | 0.0073126 | 0.0067716 | 0.0061991 | 0.0055937 | 0.0049541 | 0.0042791 | 0.0035672 | 0.0028171 | 0.0020272 | 0.0025541 | 0.010179 | 0.018887 | 0.028803 | 0.040067 | 0.40251 | -0.15227 | -0.19488 | -13.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.1163 | 0 | 0 | 0 | -39.3078 | 0 | 0 | 0 | 0
2048 | Ongoing capital |  |  | 13.0685 | 0 | ed | 45 | 0 |  | 0 | 13.0685 | -2.1642 | 2049 | -3.6205 | -10.2623 | -0.052924 | -0.054826 | -0.056791 | -0.058819 | -0.060914 | -0.063077 | -0.027948 | 0.0089764 | 0.008512 | 0.0080187 | 0.0074954 | 0.0069409 | 0.0063541 | 0.0057335 | 0.005078 | 0.0043861 | 0.0036564 | 0.0028875 | 0.0020779 | 0.002618 | 0.010433 | 0.019359 | 0.029523 | 0.041069 | 0.41258 | -0.15607 | -0.19976 | -13.3952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.4192 | 0 | 0 | 0 | -39.8427 | 0 | 0 | 0 | 0
2049 | Ongoing capital |  |  | 13.3952 | 0 | ed | 45 | 0 |  | 0 | 13.3952 | -2.0682 | 2050 | -3.5814 | -10.1514 | -0.052358 | -0.054247 | -0.056197 | -0.058211 | -0.06029 | -0.062437 | -0.064653 | -0.028647 | 0.0092008 | 0.0087248 | 0.0082191 | 0.0076828 | 0.0071145 | 0.0065129 | 0.0058769 | 0.0052049 | 0.0044958 | 0.0037478 | 0.0029597 | 0.0021299 | 0.0026834 | 0.010694 | 0.019843 | 0.030261 | 0.042095 | 0.42289 | -0.15998 | -0.20475 | -13.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.7297 | 0 | 0 | 0 | -40.3941 | 0 | 0 | 0 | 0
2050 | Ongoing capital |  |  | 13.7301 | 0 | ed | 45 | 0 |  | 0 | 13.7301 | -1.9751 | 2051 | -3.5423 | -10.0406 | -0.051793 | -0.053667 | -0.055603 | -0.057602 | -0.059666 | -0.061797 | -0.063998 | -0.06627 | -0.029363 | 0.0094309 | 0.0089429 | 0.0084246 | 0.0078748 | 0.0072923 | 0.0066758 | 0.0060238 | 0.0053351 | 0.0046081 | 0.0038415 | 0.0030337 | 0.0021831 | 0.0027505 | 0.010961 | 0.020339 | 0.031018 | 0.043148 | 0.43346 | -0.16398 | -0.20987 | -14.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.048 | 0 | 0 | 0 | -40.9625 | 0 | 0 | 0 | 0
2051 | Ongoing capital |  |  | 14.0733 | 0 | ed | 45 | 0 |  | 0 | 14.0733 | -1.8848 | 2052 | -3.5032 | -9.9298 | -0.051227 | -0.053088 | -0.055009 | -0.056993 | -0.059042 | -0.061158 | -0.063342 | -0.065598 | -0.067927 | -0.030097 | 0.0096666 | 0.0091665 | 0.0086352 | 0.0080717 | 0.0074746 | 0.0068426 | 0.0061744 | 0.0054684 | 0.0047233 | 0.0039376 | 0.0031096 | 0.0022377 | 0.0028193 | 0.011235 | 0.020847 | 0.031793 | 0.044227 | 0.4443 | -0.16808 | -0.21512 | -14.4252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.3742 | 0 | 0 | 0 | -41.5483 | 0 | 0 | 0 | 0
2052 | Ongoing capital |  |  | 14.4252 | 0 | ed | 45 | 0 |  | 0 | 14.4252 | -1.7972 | 2053 | -3.4285 | -9.718 | -0.050662 | -0.052508 | -0.054415 | -0.056384 | -0.058418 | -0.060518 | -0.062686 | -0.064926 | -0.067238 | -0.069625 | -0.030849 | 0.0099083 | 0.0093956 | 0.0088511 | 0.0082735 | 0.0076615 | 0.0070137 | 0.0063288 | 0.0056052 | 0.0048414 | 0.004036 | 0.0031873 | 0.0022936 | 0.0028897 | 0.011516 | 0.021368 | 0.032588 | 0.045332 | 0.45541 | -0.17228 | -0.22049 | -14.7858 | 0 | 0 | 0 | 0 | 0 | 0 | -13.7085 | 0 | 0 | 0 | -42.0153 | 0 | 0 | 0 | 0
2053 | Ongoing capital |  |  | 14.7858 | 0 | ed | 45 | 0 |  | 0 | 14.7858 | -1.7121 | 2054 | -3.3182 | -9.4052 | -0.049581 | -0.051929 | -0.053821 | -0.055775 | -0.057794 | -0.059878 | -0.062031 | -0.064254 | -0.066549 | -0.068919 | -0.071365 | -0.031621 | 0.010156 | 0.0096305 | 0.0090724 | 0.0084803 | 0.007853 | 0.0071891 | 0.006487 | 0.0057453 | 0.0049625 | 0.0041369 | 0.003267 | 0.002351 | 0.002962 | 0.011804 | 0.021903 | 0.033403 | 0.046466 | 0.46679 | -0.17658 | -0.22601 | -15.1554 | 0 | 0 | 0 | 0 | 0 | -14.0512 | 0 | 0 | 0 | -42.3635 | 0 | 0 | 0 | 0
2054 | Ongoing capital |  |  | 15.1554 | 0 | ed | 45 | 0 |  | 0 | 15.1554 | -1.6293 | 2055 | -3.2078 | -9.0924 | -0.047986 | -0.050821 | -0.053227 | -0.055166 | -0.05717 | -0.059238 | -0.061375 | -0.063582 | -0.06586 | -0.068213 | -0.070642 | -0.073149 | -0.032411 | 0.01041 | 0.0098713 | 0.0092992 | 0.0086924 | 0.0080494 | 0.0073688 | 0.0066491 | 0.0058889 | 0.0050865 | 0.0042403 | 0.0033487 | 0.0024097 | 0.003036 | 0.012099 | 0.02245 | 0.034238 | 0.047627 | 0.47846 | -0.181 | -0.23166 | -15.5343 | 0 | 0 | 0 | 0 | -14.4025 | 0 | 0 | 0 | -42.7294 | 0 | 0 | 0 | 0
2055 | Ongoing capital |  |  | 15.5343 | 0 | ed | 45 | 0 |  | 0 | 15.5343 | -1.5487 | 2056 | -3.0975 | -8.7796 | -0.04639 | -0.049185 | -0.052091 | -0.054557 | -0.056545 | -0.058599 | -0.060719 | -0.062909 | -0.065171 | -0.067506 | -0.069918 | -0.072408 | -0.074978 | -0.033221 | 0.01067 | 0.010118 | 0.0095317 | 0.0089097 | 0.0082506 | 0.007553 | 0.0068154 | 0.0060361 | 0.0052137 | 0.0043463 | 0.0034324 | 0.00247 | 0.0031119 | 0.012402 | 0.023011 | 0.035094 | 0.048818 | 0.49043 | -0.18552 | -0.23745 | -15.9227 | 0 | 0 | 0 | -14.7626 | 0 | 0 | 0 | -43.1133 | 0 | 0 | 0 | 0
2056 | Ongoing capital |  |  | 15.9227 | 0 | ed | 45 | 0 |  | 0 | 15.9227 | -1.4701 | 2057 | -2.9871 | -8.4668 | -0.044794 | -0.047549 | -0.050415 | -0.053394 | -0.055921 | -0.057959 | -0.060064 | -0.062237 | -0.064482 | -0.0668 | -0.069194 | -0.071666 | -0.074218 | -0.076853 | -0.034052 | 0.010937 | 0.010371 | 0.00977 | 0.0091324 | 0.0084569 | 0.0077418 | 0.0069858 | 0.006187 | 0.005344 | 0.004455 | 0.0035182 | 0.0025317 | 0.0031897 | 0.012712 | 0.023587 | 0.035971 | 0.050038 | 0.50269 | -0.19016 | -0.24338 | -16.3208 | 0 | 0 | -15.1316 | 0 | 0 | 0 | -43.5159 | 0 | 0 | 0 | 0
2057 | Ongoing capital |  |  | 16.3208 | 0 | ed | 45 | 0 |  | 0 | 16.3208 | -1.3934 | 2058 | -2.8768 | -8.1541 | -0.043198 | -0.045914 | -0.048738 | -0.051675 | -0.054729 | -0.057319 | -0.059408 | -0.061565 | -0.063793 | -0.066094 | -0.06847 | -0.070924 | -0.073457 | -0.076073 | -0.078774 | -0.034903 | 0.01121 | 0.01063 | 0.010014 | 0.0093607 | 0.0086683 | 0.0079354 | 0.0071604 | 0.0063417 | 0.0054776 | 0.0045664 | 0.0036061 | 0.002595 | 0.0032695 | 0.01303 | 0.024176 | 0.03687 | 0.051289 | 0.51525 | -0.19492 | -0.24947 | -16.7288 | 0 | -15.5099 | 0 | 0 | 0 | -43.9375 | 0 | 0 | 0 | 0
2058 | Ongoing capital |  |  | 16.7288 | 0 | ed | 45 | 0 |  | 0 | 16.7288 | -1.3185 | 2059 | -2.7664 | -7.8413 | -0.041602 | -0.044278 | -0.047062 | -0.049957 | -0.052967 | -0.056097 | -0.058752 | -0.060893 | -0.063104 | -0.065388 | -0.067747 | -0.070182 | -0.072697 | -0.075294 | -0.077975 | -0.080743 | -0.035776 | 0.011491 | 0.010896 | 0.010265 | 0.0095947 | 0.008885 | 0.0081338 | 0.0073394 | 0.0065003 | 0.0056146 | 0.0046805 | 0.0036963 | 0.0026599 | 0.0033512 | 0.013355 | 0.024781 | 0.037792 | 0.052571 | 0.52813 | -0.19979 | -0.2557 | -17.147 | -15.8977 | 0 | 0 | 0 | -44.3786 | 0 | 0 | 0 | 0
2059 | Ongoing capital |  |  | 17.147 | 0 | ed | 45 | 0 |  | 0 | 17.147 | -1.2452 | 2060 | -2.6561 | -7.5285 | -0.040006 | -0.042642 | -0.045385 | -0.048238 | -0.051206 | -0.054291 | -0.057499 | -0.060221 | -0.062416 | -0.064682 | -0.067023 | -0.06944 | -0.071937 | -0.074515 | -0.077176 | -0.079925 | -0.082762 | -0.03667 | 0.011778 | 0.011168 | 0.010521 | 0.0098346 | 0.0091071 | 0.0083371 | 0.0075229 | 0.0066628 | 0.0057549 | 0.0047976 | 0.0037887 | 0.0027264 | 0.003435 | 0.013689 | 0.0254 | 0.038737 | 0.053886 | 0.54134 | -0.20478 | -0.2621 | -16.2951 | 0 | 0 | 0 | -27.2641 | 0 | 0 | 0 | 0
2060 | Ongoing capital |  |  | 17.5757 | 0 | ed | 45 | 0 |  |  | 17.5757 | -1.2452
2061 | Ongoing capital |  |  | 18.0151 | 0 | ed | 45 | 0 |  |  | 18.0151 | -1.2452
2062 | Ongoing capital |  |  | 18.4654 | 0 | ed | 45 | 0 |  |  | 18.4654 | -1.2452
2063 | Ongoing capital |  |  | 18.9271 | 0 | ed | 45 | 0 |  |  | 18.9271 | -1.2452
2064 | Ongoing capital |  |  | 19.4003 | 0 | ed | 45 | 0 |  |  | 19.4003 | -1.2452
2065 | Ongoing capital |  |  | 19.8853 | 0 | ed | 45 | 0 |  |  | 19.8853 | -1.2452
* Life and salvage fields ignored when expenditure is an expense (type exp or atx). |  |  |  | 20.3824 | [6 empty] | 2251.4062 | -1967.976 | 2061 | -2.5457 | -7.2157 | -0.03841 | -0.041006 | -0.043708 | -0.04652 | -0.049444 | -0.052486 | -0.055649 | -0.058937 | -0.061727 | -0.063976 | -0.066299 | -0.068698 | -0.071176 | -0.073735 | -0.076377 | -0.079106 | -0.081923 | -0.084831 | -0.037587 | 0.012072 | 0.011448 | 0.010784 | 0.01008 | 0.0093348 | 0.0085455 | 0.007711 | 0.0068293 | 0.0058988 | 0.0049175 | 0.0038834 | 0.0027946 | 0.0035209 | 0.014032 | 0.026035 | 0.039705 | 0.055233 | 0.55487 | -0.2099 | -16.7025 | 0 | 0 | 0 | -27.0377 | 0 | 0 | 0 | 0
[13 empty] | 2062 | -2.4353 | -6.9029 | -0.036815 | -0.039371 | -0.042032 | -0.044801 | -0.047683 | -0.05068 | -0.053798 | -0.05704 | -0.06041 | -0.06327 | -0.065575 | -0.067957 | -0.070416 | -0.072956 | -0.075578 | -0.078287 | -0.081083 | -0.083971 | -0.086952 | -0.038527 | 0.012374 | 0.011734 | 0.011054 | 0.010332 | 0.0095682 | 0.0087592 | 0.0079037 | 0.0070001 | 0.0060463 | 0.0050404 | 0.0039805 | 0.0028644 | 0.0036089 | 0.014382 | 0.026686 | 0.040698 | 0.056614 | 0.56874 | -17.1201 | 0 | 0 | 0 | -26.8681
Operating Expenses (+) and Revenues (-) Over 45 Years (2021-2065) in $000 | [12 empty] | 2063 | -2.325 | -6.5901 | -0.035219 | -0.037735 | -0.040355 | -0.043082 | -0.045921 | -0.048875 | -0.051947 | -0.055143 | -0.058466 | -0.06192 | -0.064852 | -0.067215 | -0.069656 | -0.072176 | -0.07478 | -0.077468 | -0.080244 | -0.08311 | -0.08607 | -0.089126 | -0.03949 | 0.012683 | 0.012027 | 0.01133 | 0.010591 | 0.0098074 | 0.0089781 | 0.0081013 | 0.0071751 | 0.0061974 | 0.0051664 | 0.00408 | 0.002936 | 0.0036991 | 0.014742 | 0.027353 | 0.041715 | 0.058029 | -17.5481 | 0 | 0 | 0 | -27.5014
Year | a | b | c | d |  |  | Description |  |  |  | Esc% | NPV | 2064 | -2.2146 | -6.2773 | -0.033623 | -0.036099 | -0.038678 | -0.041364 | -0.044159 | -0.047069 | -0.050096 | -0.053246 | -0.056521 | -0.059927 | -0.063468 | -0.066473 | -0.068895 | -0.071397 | -0.073981 | -0.076649 | -0.079405 | -0.08225 | -0.085188 | -0.088222 | -0.091354 | -0.040477 | 0.013001 | 0.012328 | 0.011613 | 0.010856 | 0.010053 | 0.0092026 | 0.0083039 | 0.0073545 | 0.0063524 | 0.0052956 | 0.004182 | 0.0030094 | 0.0037916 | 0.01511 | 0.028037 | 0.042758 | -17.9868 | 0 | 0 | 0 | -27.636
2021 | 8.8536 |  |  |  | a. | Annual Operations and Maintenance |  |  |  |  | 2.5 | -124.948 | 2065 | -2.1043 | -5.9645 | -0.032027 | -0.034463 | -0.037002 | -0.039645 | -0.042398 | -0.045263 | -0.048246 | -0.051349 | -0.054577 | -0.057934 | -0.061426 | -0.065055 | -0.068135 | -0.070618 | -0.073182 | -0.07583 | -0.078565 | -0.08139 | -0.084306 | -0.087318 | -0.090427 | -0.093638 | -0.041489 | 0.013326 | 0.012636 | 0.011904 | 0.011127 | 0.010304 | 0.0094327 | 0.0085115 | 0.0075383 | 0.0065112 | 0.005428 | 0.0042866 | 0.0030847 | 0.0038864 | 0.015488 | 0.028738 | -18.4364 | 0 | 0 | 0 | -27.7674
2022 | 8.8536 |  |  |  | b. | [5 empty] | 2.5 | 0 | 2066 | -1.9939 | -5.6518 | -0.030431 | -0.032828 | -0.035325 | -0.037927 | -0.040636 | -0.043458 | -0.046395 | -0.049452 | -0.052633 | -0.055941 | -0.059383 | -0.062961 | -0.066681 | -0.069838 | -0.071655 | -0.072027 | -0.070842 | -0.067986 | -0.063335 | -0.056762 | -0.048132 | -0.037304 | -0.024131 | 0.048392 | 0.18469 | 0.32968 | 0.48377 | 0.64736 | 0.82089 | 1.0048 | 1.1995 | 1.4056 | 1.6235 | 1.8538 | 2.0969 | 2.3535 | 2.6262 | 2.9268 | -18.8974 | 0 | 0 | 0 | -8.1337
2023 | 8.8536 |  |  |  | c. | [5 empty] | 2.5 | 0 | 2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 8.8536 |  |  |  | d. | [5 empty] | 2.5 | 0 | 2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 8.8536 | [10 empty] | -124.948 | 2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 8.8536 | [11 empty] | 2070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 8.8536 | [11 empty] | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 8.8536 | [7 empty] | Total NPV ($000) |  |  | -2092.924 | 45 | MaxCap
2029 | 8.8536 | [11 empty] | 0 | cap error
2030 | 8.8536 | [11 empty] | 0 | exp error
2031 | 8.8536 | [11 empty] | 0 | tot errors
2032 | 8.8536 | [9 empty] | Comments (press alt+enter to skip to new line)
2033 | 8.8536
2034 | 8.8536
2035 | 8.8536 | [11 empty] | 1 | -27.0226 | -76.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.376 | 0 | 0 | 0 | -109.9933
2036 | 8.8536 | [11 empty] | 2 | -26.6457 | -75.5263 | -0.39079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5354 | 0 | 0 | 0 | -109.0982
2037 | 8.8536 | [11 empty] | 3 | -26.2688 | -74.4579 | -0.38534 | -0.40056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6988 | 0 | 0 | 0 | -108.2114
2038 | 8.8536 | [11 empty] | 4 | -25.8918 | -73.3895 | -0.37989 | -0.39497 | -0.41057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8663 | 0 | 0 | 0 | -107.333
2039 | 8.8536 | [11 empty] | 5 | -25.5149 | -72.3211 | -0.37443 | -0.38938 | -0.40484 | -0.42084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.038 | 0 | 0 | 0 | -106.4634
2040 | 8.8536
2041 | 8.8536
2042 | 8.8536
2043 | 8.8536
2044 | 8.8536
2045 | 8.8536
2046 | 8.8536
2047 | 8.8536
2048 | 8.8536
2049 | 8.8536
2050 | 8.8536
2051 | 8.8536
2052 | 8.8536
2053 | 8.8536
2054 | 8.8536
2055 | 8.8536
2056 | 8.8536
2057 | 8.8536
2058 | 8.8536
2059 | 8.8536
2060 | 8.8536
2061 | 8.8536
2062 | 8.8536
2063 | 8.8536
2064 | 8.8536
2065 | 8.8536
2066
2067
2068
2069
2070
Note on BK6: Jonathan: Starting in 2018, bonus depreciation no longer available to public utilities
Note on A7: Enter year of operation for capital, or year of occurrence for expenses. Timing is assumed to be beginning-of-year. Amounts entered outside of study period are ignored.
Note on C7: Enter project expenditures required to implement this alternative. Amounts already spent on a proposed project should be included as part of the project cost in the alternative that completes the project. In competing alternatives where the project is abandoned (such as status quo), any amounts already spent should be shown as an expense in the year the project is written off.
Note on E7: Enter cost in financial dollars, including contingency and overheads. For multi-year construction projects, enter cost for each expenditure type as lump sum in year of operation.
Note on F7: Accept default escalation rate, enter a different rate, or enter zero if cost is already escalated to year of expenditure (as it would be in a job estimate).
Note on G7: Capital Type Life ¦ Capital Type Life Buildings bldg 50 ¦ Power Plants: Communication equip comm 15 ¦ Combined cycle cc 30 Computer hardware comp 5 ¦ Combustion turbine ct 25 Computer software soft 5 ¦ Micro turbine mt 10 Electric dist (<69kV) ed 45 ¦ Hydro hyd 50 Electric trans (69kV+) et 55 ¦ Hydro additions hyda 20 Electric smart meter em 20 ¦ Nuclear nuc 15 Gas distribution gasd 55 ¦ Nuclear additions nuca 7 Gas meters gm 30 ¦ Biomass bio 25 Gas trans & storage gast 55 ¦ Fuel cell fcl 8 Gas held for resale gasc 99 ¦ Geothermal geo 25 Land easement ease 99 ¦ Solar photovoltaic pv 20 Land purchase land 99 ¦ Solar thermal st 25 Motor vehicles mv 10 ¦ Tidal or wave tdl 10 Office furniture furn 20 ¦ Waste wst 25 Electricity Storage bat 15 ¦ Wind wnd 25 Expense exp ¦ Expense, after-tax atx This is a partial listing of expenditure types. See EASOP Help tab or Economic Guide for additional guidance in selecting expenditure types.
Note on H7: Enter the expected life for each capital asset, even if it extends beyond the study period. EASOP retires each asset at the end of its life or the end of the study period, whichever occurs first, at the salvage specified.
Note on I7: Accept zero as default salvage value, enter a different value, or delete entry to use value calculated by EASOP. For most analyses, use 100% for land and 0% for all other expenditures.
Note on BK8: =IF(OR(AND(A8>2011,RIGHT(G8,3)="sbd"),AND(A8>2012,RIGHT(G8,2)="bd")),1,0)
Note on BK9: =IF(OR(AND(A9>2011,RIGHT(G9,3)="sbd"),AND(A9>2012,RIGHT(G9,2)="bd")),1,0)
Note on BK10: =IF(OR(AND(A10>2011,RIGHT(G10,3)="sbd"),AND(A10>2012,RIGHT(G10,2)="bd")),1,0)
Note on BK11: =IF(OR(AND(A11>2011,RIGHT(G11,3)="sbd"),AND(A11>2012,RIGHT(G11,2)="bd")),1,0)
Note on BK12: =IF(OR(AND(A12>2011,RIGHT(G12,3)="sbd"),AND(A12>2012,RIGHT(G12,2)="bd")),1,0)
Note on BK13: =IF(OR(AND(A13>2011,RIGHT(G13,3)="sbd"),AND(A13>2012,RIGHT(G13,2)="bd")),1,0)
Note on BK14: =IF(OR(AND(A14>2011,RIGHT(G14,3)="sbd"),AND(A14>2012,RIGHT(G14,2)="bd")),1,0)
Note on BK15: =IF(OR(AND(A15>2011,RIGHT(G15,3)="sbd"),AND(A15>2012,RIGHT(G15,2)="bd")),1,0)
Note on BK16: =IF(OR(AND(A16>2011,RIGHT(G16,3)="sbd"),AND(A16>2012,RIGHT(G16,2)="bd")),1,0)
Note on BK17: =IF(OR(AND(A17>2011,RIGHT(G17,3)="sbd"),AND(A17>2012,RIGHT(G17,2)="bd")),1,0)
Note on BK18: =IF(OR(AND(A18>2011,RIGHT(G18,3)="sbd"),AND(A18>2012,RIGHT(G18,2)="bd")),1,0)
Note on BK19: =IF(OR(AND(A19>2011,RIGHT(G19,3)="sbd"),AND(A19>2012,RIGHT(G19,2)="bd")),1,0)
Note on BK20: =IF(OR(AND(A20>2011,RIGHT(G20,3)="sbd"),AND(A20>2012,RIGHT(G20,2)="bd")),1,0)
Note on BK21: =IF(OR(AND(A21>2011,RIGHT(G21,3)="sbd"),AND(A21>2012,RIGHT(G21,2)="bd")),1,0)
Note on BK22: =IF(OR(AND(A22>2011,RIGHT(G22,3)="sbd"),AND(A22>2012,RIGHT(G22,2)="bd")),1,0)
Note on BK23: =IF(OR(AND(A23>2011,RIGHT(G23,3)="sbd"),AND(A23>2012,RIGHT(G23,2)="bd")),1,0)
Note on BK24: =IF(OR(AND(A24>2011,RIGHT(G24,3)="sbd"),AND(A24>2012,RIGHT(G24,2)="bd")),1,0)
Note on BK25: =IF(OR(AND(A25>2011,RIGHT(G25,3)="sbd"),AND(A25>2012,RIGHT(G25,2)="bd")),1,0)
Note on BK26: =IF(OR(AND(A26>2011,RIGHT(G26,3)="sbd"),AND(A26>2012,RIGHT(G26,2)="bd")),1,0)
Note on BK27: =IF(OR(AND(A27>2011,RIGHT(G27,3)="sbd"),AND(A27>2012,RIGHT(G27,2)="bd")),1,0)
Note on BK28: =IF(OR(AND(A28>2011,RIGHT(G28,3)="sbd"),AND(A28>2012,RIGHT(G28,2)="bd")),1,0)
Note on BK29: =IF(OR(AND(A29>2011,RIGHT(G29,3)="sbd"),AND(A29>2012,RIGHT(G29,2)="bd")),1,0)
Note on BK30: =IF(OR(AND(A30>2011,RIGHT(G30,3)="sbd"),AND(A30>2012,RIGHT(G30,2)="bd")),1,0)
Note on BK31: =IF(OR(AND(A31>2011,RIGHT(G31,3)="sbd"),AND(A31>2012,RIGHT(G31,2)="bd")),1,0)
Note on BK32: =IF(OR(AND(A32>2011,RIGHT(G32,3)="sbd"),AND(A32>2012,RIGHT(G32,2)="bd")),1,0)
Note on BK33: =IF(OR(AND(A33>2011,RIGHT(G33,3)="sbd"),AND(A33>2012,RIGHT(G33,2)="bd")),1,0)
Note on BK34: =IF(OR(AND(A34>2011,RIGHT(G34,3)="sbd"),AND(A34>2012,RIGHT(G34,2)="bd")),1,0)
Note on BK35: =IF(OR(AND(A35>2011,RIGHT(G35,3)="sbd"),AND(A35>2012,RIGHT(G35,2)="bd")),1,0)
Note on BK36: =IF(OR(AND(A36>2011,RIGHT(G36,3)="sbd"),AND(A36>2012,RIGHT(G36,2)="bd")),1,0)
Note on BK37: =IF(OR(AND(A37>2011,RIGHT(G37,3)="sbd"),AND(A37>2012,RIGHT(G37,2)="bd")),1,0)
Note on BK38: =IF(OR(AND(A38>2011,RIGHT(G38,3)="sbd"),AND(A38>2012,RIGHT(G38,2)="bd")),1,0)
Note on BK39: =IF(OR(AND(A39>2011,RIGHT(G39,3)="sbd"),AND(A39>2012,RIGHT(G39,2)="bd")),1,0)
Note on BK40: =IF(OR(AND(A40>2011,RIGHT(G40,3)="sbd"),AND(A40>2012,RIGHT(G40,2)="bd")),1,0)
Note on BK41: =IF(OR(AND(A41>2011,RIGHT(G41,3)="sbd"),AND(A41>2012,RIGHT(G41,2)="bd")),1,0)
Note on BK42: =IF(OR(AND(A42>2011,RIGHT(G42,3)="sbd"),AND(A42>2012,RIGHT(G42,2)="bd")),1,0)
Note on BK43: =IF(OR(AND(A43>2011,RIGHT(G43,3)="sbd"),AND(A43>2012,RIGHT(G43,2)="bd")),1,0)
Note on BK44: =IF(OR(AND(A44>2011,RIGHT(G44,3)="sbd"),AND(A44>2012,RIGHT(G44,2)="bd")),1,0)
Note on BK45: =IF(OR(AND(A45>2011,RIGHT(G45,3)="sbd"),AND(A45>2012,RIGHT(G45,2)="bd")),1,0)
Note on BK46: =IF(OR(AND(A46>2011,RIGHT(G46,3)="sbd"),AND(A46>2012,RIGHT(G46,2)="bd")),1,0)
Note on BK47: =IF(OR(AND(A47>2011,RIGHT(G47,3)="sbd"),AND(A47>2012,RIGHT(G47,2)="bd")),1,0)
Note on A57: Timing of operating expenses and revenues is assumed to be end-of-year. Amounts entered beyond study period are ignored.
Note on H57: Enter recurring expenses and revenues (assuming no cost-of-service regulation) for this alternative. If a project will result in savings, enter them as a cost under status quo or as a savings under the proposed project, but not as both in the same evaluation.
Note on L57: Accept default escalation rate, enter a different rate, or enter zero if cost or revenue stream already includes escalation.

## 2 All OH AT
Underground vs. Overhead Analysis
Alternative 2 - All Overhead
Project Expenditures Over 45 Years (2021-2065) in $000 * | [7 empty] | Salvage% |  |  | Escalated | [47 empty] | life | salvage | ITC | BD
Year |  | Description |  | Cost | Esc% | Type | Life | Input | Calcd |  | Cost | NPV | boy | cap1 | cap2 | cap3 | cap4 | cap5 | cap6 | cap7 | cap8 | cap9 | cap10 | cap11 | cap12 | cap13 | cap14 | cap15 | cap16 | cap17 | cap18 | cap19 | cap20 | cap21 | cap22 | cap23 | cap24 | cap25 | cap26 | cap27 | cap28 | cap29 | cap30 | cap31 | cap32 | cap33 | cap34 | cap35 | cap36 | cap37 | cap38 | cap39 | cap40 | exp a | exp b | exp c | exp d | total acf | error | error | Check | Error
2021 | Overhead CapEx |  |  | 1174.869 | 2.5 | ed | 45 | 0 |  | 0 | 1146.2137 | -1158.1212 | 2021 | -1146.2137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1146.2137 | 0 | 0 | 0 | 0
2022 | Ongoing capital |  |  | 8.7895 | 0 | ed | 45 | 0 |  | 0 | 8.7895 | -8.3136 | 2022 | -17.5203 | -8.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.6531 | 0 | 0 | 0 | -36.9629 | 0 | 0 | 0 | 0
2023 | Ongoing capital |  |  | 9.0092 | 0 | ed | 45 | 0 |  | 0 | 9.0092 | -7.9769 | 2023 | -14.0312 | -0.13435 | -9.0092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.9194 | 0 | 0 | 0 | -34.0942 | 0 | 0 | 0 | 0
2024 | Ongoing capital |  |  | 9.2344 | 0 | ed | 45 | 0 |  | 0 | 9.2344 | -7.6536 | 2024 | 38.0184 | -0.1076 | -0.13771 | -9.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.1924 | 0 | 0 | 0 | 17.3462 | 0 | 0 | 0 | 0
2025 | Ongoing capital |  |  | 9.4653 | 0 | ed | 45 | 0 |  | 0 | 9.4653 | -7.3433 | 2025 | 3.879 | 0.29154 | -0.11029 | -0.14115 | -9.4653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.4722 | 0 | 0 | 0 | -17.0184 | 0 | 0 | 0 | 0
2026 | Ongoing capital |  |  | 9.7019 | 0 | ed | 45 | 0 |  | 0 | 9.7019 | -7.0452 | 2026 | 2.8582 | 0.029745 | 0.29882 | -0.11304 | -0.14468 | -9.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.759 | 0 | 0 | 0 | -18.5319 | 0 | 0 | 0 | 0
2027 | Ongoing capital |  |  | 9.9445 | 0 | ed | 45 | 0 |  | 0 | 9.9445 | -6.7589 | 2027 | 1.921 | 0.021918 | 0.030489 | 0.30629 | -0.11587 | -0.1483 | -9.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.053 | 0 | 0 | 0 | -19.9819 | 0 | 0 | 0 | 0
2028 | Ongoing capital |  |  | 10.1931 | 0 | ed | 45 | 0 |  | 0 | 10.1931 | -6.4841 | 2028 | 1.0612 | 0.014731 | 0.022466 | 0.031251 | 0.31395 | -0.11877 | -0.152 | -10.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.3544 | 0 | 0 | 0 | -21.3746 | 0 | 0 | 0 | 0
2029 | Ongoing capital |  |  | 10.4479 | 0 | ed | 45 | 0 |  | 0 | 10.4479 | -6.22 | 2029 | 0.27294 | 0.0081377 | 0.015099 | 0.023027 | 0.032033 | 0.3218 | -0.12173 | -0.1558 | -10.4479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.6632 | 0 | 0 | 0 | -22.7156 | 0 | 0 | 0 | 0
2030 | Ongoing capital |  |  | 10.7091 | 0 | ed | 45 | 0 |  | 0 | 10.7091 | -5.9665 | 2030 | 0.22205 | 0.002093 | 0.0083411 | 0.015477 | 0.023603 | 0.032833 | 0.32985 | -0.12478 | -0.1597 | -10.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.9798 | 0 | 0 | 0 | -23.3391 | 0 | 0 | 0 | 0
2031 | Ongoing capital |  |  | 10.9769 | 0 | ed | 45 | 0 |  | 0 | 10.9769 | -5.7229 | 2031 | 0.31629 | 0.0017028 | 0.0021453 | 0.0085496 | 0.015864 | 0.024193 | 0.033654 | 0.33809 | -0.1279 | -0.16369 | -10.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.3043 | 0 | 0 | 0 | -23.8322 | 0 | 0 | 0 | 0
2032 | Ongoing capital |  |  | 11.2513 | 0 | ed | 45 | 0 |  | 0 | 11.2513 | -5.4889 | 2032 | 0.41052 | 0.0024254 | 0.0017453 | 0.002199 | 0.0087634 | 0.01626 | 0.024798 | 0.034496 | 0.34654 | -0.13109 | -0.16778 | -11.2513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.6369 | 0 | 0 | 0 | -24.3393 | 0 | 0 | 0 | 0
2033 | Ongoing capital |  |  | 11.5326 | 0 | ed | 45 | 0 |  | 0 | 11.5326 | -5.2642 | 2033 | 0.50476 | 0.003148 | 0.002486 | 0.001789 | 0.0022539 | 0.0089825 | 0.016667 | 0.025418 | 0.035358 | 0.35521 | -0.13437 | -0.17198 | -11.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.9778 | 0 | 0 | 0 | -24.8607 | 0 | 0 | 0 | 0
2034 | Ongoing capital |  |  | 11.8209 | 0 | ed | 45 | 0 |  | 0 | 11.8209 | -5.0482 | 2034 | 0.59899 | 0.0038706 | 0.0032267 | 0.0025482 | 0.0018337 | 0.0023103 | 0.009207 | 0.017083 | 0.026053 | 0.036242 | 0.36409 | -0.13773 | -0.17628 | -11.8209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.3273 | 0 | 0 | 0 | -25.3967 | 0 | 0 | 0 | 0
2035 | Ongoing capital |  |  | 12.1164 | 0 | ed | 45 | 0 |  | 0 | 12.1164 | -4.8407 | 2035 | 0.69322 | 0.0045932 | 0.0039674 | 0.0033074 | 0.0026119 | 0.0018795 | 0.002368 | 0.0094372 | 0.017511 | 0.026704 | 0.037148 | 0.37319 | -0.14117 | -0.18069 | -12.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.6854 | 0 | 0 | 0 | -25.9478 | 0 | 0 | 0 | 0
2036 | Ongoing capital |  |  | 12.4193 | 0 | ed | 45 | 0 |  | 0 | 12.4193 | -4.6413 | 2036 | 0.78746 | 0.0053158 | 0.004708 | 0.0040665 | 0.00339 | 0.0026772 | 0.0019265 | 0.0024272 | 0.0096731 | 0.017948 | 0.027372 | 0.038077 | 0.38252 | -0.1447 | -0.1852 | -12.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -15.0526 | 0 | 0 | 0 | -26.5142 | 0 | 0 | 0 | 0
2037 | Ongoing capital |  |  | 12.7298 | 0 | ed | 45 | 0 |  | 0 | 12.7298 | -4.4497 | 2037 | 0.88169 | 0.0060384 | 0.0054487 | 0.0048257 | 0.0041682 | 0.0034748 | 0.0027441 | 0.0019747 | 0.0024879 | 0.009915 | 0.018397 | 0.028056 | 0.039029 | 0.39208 | -0.14832 | -0.18983 | -12.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -15.4289 | 0 | 0 | 0 | -27.0965 | 0 | 0 | 0 | 0
2038 | Ongoing capital |  |  | 13.048 | 0 | ed | 45 | 0 |  | 0 | 13.048 | -4.2655 | 2038 | 0.97592 | 0.006761 | 0.0061894 | 0.0055849 | 0.0049464 | 0.0042724 | 0.0035617 | 0.0028127 | 0.0020241 | 0.0025501 | 0.010163 | 0.018857 | 0.028758 | 0.040004 | 0.40188 | -0.15203 | -0.19458 | -13.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -15.8146 | 0 | 0 | 0 | -27.695 | 0 | 0 | 0 | 0
2039 | Ongoing capital |  |  | 13.3742 | 0 | ed | 45 | 0 |  | 0 | 13.3742 | -4.0885 | 2039 | 1.0702 | 0.0074837 | 0.0069301 | 0.0063441 | 0.0057246 | 0.00507 | 0.0043792 | 0.0036507 | 0.002883 | 0.0020747 | 0.0026139 | 0.010417 | 0.019328 | 0.029477 | 0.041004 | 0.41193 | -0.15583 | -0.19944 | -13.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.21 | 0 | 0 | 0 | -28.31 | 0 | 0 | 0 | 0
2040 | Ongoing capital |  |  | 13.7086 | 0 | ed | 45 | 0 |  | 0 | 13.7086 | -3.9182 | 2040 | 1.1644 | 0.0082063 | 0.0076707 | 0.0071033 | 0.0065027 | 0.0058677 | 0.0051968 | 0.0044887 | 0.003742 | 0.0029551 | 0.0021265 | 0.0026792 | 0.010677 | 0.019812 | 0.030214 | 0.04203 | 0.42223 | -0.15973 | -0.20443 | -13.7086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.6152 | 0 | 0 | 0 | -28.9421 | 0 | 0 | 0 | 0
2041 | Ongoing capital |  |  | 14.0513 | 0 | ed | 45 | 0 |  | 0 | 14.0513 | -3.7545 | 2041 | 1.2586 | 0.0089289 | 0.0084114 | 0.0078625 | 0.0072809 | 0.0066653 | 0.0060144 | 0.0053267 | 0.0046009 | 0.0038355 | 0.003029 | 0.0021797 | 0.0027462 | 0.010944 | 0.020307 | 0.030969 | 0.04308 | 0.43279 | -0.16372 | -0.20954 | -14.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17.0306 | 0 | 0 | 0 | -29.5916 | 0 | 0 | 0 | 0
2042 | Ongoing capital |  |  | 14.4026 | 0 | ed | 45 | 0 |  | 0 | 14.4026 | -3.597 | 2042 | -4.0167 | 0.0096515 | 0.0091521 | 0.0086217 | 0.0080591 | 0.0074629 | 0.0068319 | 0.0061647 | 0.0054599 | 0.004716 | 0.0039314 | 0.0031047 | 0.0022342 | 0.0028149 | 0.011218 | 0.020815 | 0.031743 | 0.044157 | 0.44361 | -0.16781 | -0.21478 | -14.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17.4564 | 0 | 0 | 0 | -35.6285 | 0 | 0 | 0 | 0
2043 | Ongoing capital |  |  | 14.7626 | 0 | ed | 45 | 0 |  | 0 | 14.7626 | -3.4454 | 2043 | -9.292 | -0.030801 | 0.0098928 | 0.0093809 | 0.0088372 | 0.0082606 | 0.0076495 | 0.0070027 | 0.0063188 | 0.0055964 | 0.0048338 | 0.0040297 | 0.0031823 | 0.00229 | 0.0028852 | 0.011498 | 0.021335 | 0.032537 | 0.045261 | 0.4547 | -0.17201 | -0.22015 | -14.7626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17.8928 | 0 | 0 | 0 | -41.7249 | 0 | 0 | 0 | 0
2044 | Ongoing capital |  |  | 15.1317 | 0 | ed | 45 | 0 |  | 0 | 15.1317 | -3.2996 | 2044 | -9.1978 | -0.071254 | -0.031571 | 0.01014 | 0.0096154 | 0.0090582 | 0.0084671 | 0.0078407 | 0.0071778 | 0.0064768 | 0.0057363 | 0.0049547 | 0.0041304 | 0.0032619 | 0.0023473 | 0.0029574 | 0.011786 | 0.021868 | 0.03335 | 0.046393 | 0.46606 | -0.17631 | -0.22565 | -15.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -18.3401 | 0 | 0 | 0 | -42.5127 | 0 | 0 | 0 | 0
2045 | Ongoing capital |  |  | 15.51 | 0 | ed | 45 | 0 |  | 0 | 15.51 | -3.1592 | 2045 | -9.1035 | -0.070531 | -0.073035 | -0.03236 | 0.010394 | 0.0098558 | 0.0092846 | 0.0086787 | 0.0080368 | 0.0073572 | 0.0066387 | 0.0058797 | 0.0050786 | 0.0042337 | 0.0033434 | 0.002406 | 0.0030313 | 0.01208 | 0.022415 | 0.034184 | 0.047553 | 0.47771 | -0.18072 | -0.23129 | -15.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -18.7986 | 0 | 0 | 0 | -43.3219 | 0 | 0 | 0 | 0
2046 | Ongoing capital |  |  | 15.8978 | 0 | ed | 45 | 0 |  | 0 | 15.8978 | -3.0237 | 2046 | -9.0093 | -0.069808 | -0.072294 | -0.074861 | -0.033169 | 0.010653 | 0.010102 | 0.0095167 | 0.0088957 | 0.0082377 | 0.0075412 | 0.0068047 | 0.0060267 | 0.0052055 | 0.0043395 | 0.003427 | 0.0024661 | 0.0031071 | 0.012382 | 0.022975 | 0.035039 | 0.048741 | 0.48966 | -0.18523 | -0.23708 | -15.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19.2686 | 0 | 0 | 0 | -44.1529 | 0 | 0 | 0 | 0
2047 | Ongoing capital |  |  | 16.2952 | 0 | ed | 45 | 0 |  | 0 | 16.2952 | -2.8927 | 2047 | -8.9151 | -0.069086 | -0.071554 | -0.074102 | -0.076732 | -0.033999 | 0.01092 | 0.010355 | 0.0097547 | 0.0091181 | 0.0084436 | 0.0077297 | 0.0069748 | 0.0061774 | 0.0053357 | 0.004448 | 0.0035127 | 0.0025278 | 0.0031847 | 0.012692 | 0.02355 | 0.035915 | 0.04996 | 0.5019 | -0.18986 | -0.243 | -16.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19.7503 | 0 | 0 | 0 | -45.0064 | 0 | 0 | 0 | 0
2048 | Ongoing capital |  |  | 16.7026 | 0 | ed | 45 | 0 |  | 0 | 16.7026 | -2.766 | 2048 | -8.8208 | -0.068363 | -0.070813 | -0.073342 | -0.075954 | -0.078651 | -0.034849 | 0.011193 | 0.010614 | 0.0099985 | 0.0093461 | 0.0086547 | 0.0079229 | 0.0071492 | 0.0063318 | 0.0054691 | 0.0045592 | 0.0036005 | 0.002591 | 0.0032644 | 0.013009 | 0.024139 | 0.036812 | 0.051209 | 0.51445 | -0.19461 | -0.24908 | -16.7026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -20.244 | 0 | 0 | 0 | -45.8828 | 0 | 0 | 0 | 0
2049 | Ongoing capital |  |  | 17.1201 | 0 | ed | 45 | 0 |  | 0 | 17.1201 | -2.6433 | 2049 | -8.7266 | -0.067641 | -0.070072 | -0.072583 | -0.075176 | -0.077853 | -0.080617 | -0.03572 | 0.011473 | 0.010879 | 0.010248 | 0.0095797 | 0.0088711 | 0.008121 | 0.0073279 | 0.0064901 | 0.0056058 | 0.0046732 | 0.0036905 | 0.0026557 | 0.003346 | 0.013335 | 0.024742 | 0.037733 | 0.052489 | 0.52731 | -0.19948 | -0.2553 | -17.1201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -20.7501 | 0 | 0 | 0 | -46.7828 | 0 | 0 | 0 | 0
2050 | Ongoing capital |  |  | 17.5481 | 0 | ed | 45 | 0 |  | 0 | 17.5481 | -2.5243 | 2050 | -8.6324 | -0.066918 | -0.069332 | -0.071824 | -0.074398 | -0.077055 | -0.079799 | -0.082632 | -0.036613 | 0.011759 | 0.011151 | 0.010505 | 0.0098192 | 0.0090928 | 0.008324 | 0.0075111 | 0.0066523 | 0.0057459 | 0.00479 | 0.0037828 | 0.0027221 | 0.0034296 | 0.013668 | 0.025361 | 0.038676 | 0.053801 | 0.54049 | -0.20446 | -0.26169 | -17.5481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -21.2689 | 0 | 0 | 0 | -47.7068 | 0 | 0 | 0 | 0
2051 | Ongoing capital |  |  | 17.9868 | 0 | ed | 45 | 0 |  | 0 | 17.9868 | -2.409 | 2051 | -8.5381 | -0.066195 | -0.068591 | -0.071065 | -0.07362 | -0.076258 | -0.078982 | -0.081794 | -0.084698 | -0.037528 | 0.012053 | 0.01143 | 0.010767 | 0.010065 | 0.0093202 | 0.0085321 | 0.0076989 | 0.0068186 | 0.0058896 | 0.0049098 | 0.0038773 | 0.0027902 | 0.0035154 | 0.01401 | 0.025995 | 0.039643 | 0.055146 | 0.554 | -0.20957 | -0.26823 | -17.9868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -21.8006 | 0 | 0 | 0 | -48.6557 | 0 | 0 | 0 | 0
2052 | Ongoing capital |  |  | 18.4365 | 0 | ed | 45 | 0 |  | 0 | 18.4365 | -2.297 | 2052 | -8.4439 | -0.065473 | -0.06785 | -0.070306 | -0.072841 | -0.07546 | -0.078164 | -0.080956 | -0.083839 | -0.086816 | -0.038466 | 0.012355 | 0.011715 | 0.011037 | 0.010316 | 0.0095532 | 0.0087454 | 0.0078914 | 0.0069891 | 0.0060368 | 0.0050325 | 0.0039743 | 0.0028599 | 0.0036032 | 0.01436 | 0.026644 | 0.040634 | 0.056525 | 0.56785 | -0.21481 | -0.27493 | -18.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -22.3456 | 0 | 0 | 0 | -49.6298 | 0 | 0 | 0 | 0
2053 | Ongoing capital |  |  | 18.8974 | 0 | ed | 45 | 0 |  | 0 | 18.8974 | -2.1882 | 2053 | -8.2638 | -0.06475 | -0.06711 | -0.069546 | -0.072063 | -0.074662 | -0.077347 | -0.080118 | -0.08298 | -0.085935 | -0.088986 | -0.039428 | 0.012664 | 0.012008 | 0.011312 | 0.010574 | 0.009792 | 0.0089641 | 0.0080887 | 0.0071638 | 0.0061877 | 0.0051583 | 0.0040736 | 0.0029314 | 0.0036933 | 0.014719 | 0.027311 | 0.04165 | 0.057938 | 0.58205 | -0.22018 | -0.28181 | -18.8974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -22.9043 | 0 | 0 | 0 | -50.5441 | 0 | 0 | 0 | 0
2054 | Ongoing capital |  |  | 19.3699 | 0 | ed | 45 | 0 |  | 0 | 19.3699 | -2.0824 | 2054 | -7.9978 | -0.063369 | -0.066369 | -0.068787 | -0.071285 | -0.073865 | -0.076529 | -0.07928 | -0.082121 | -0.085055 | -0.088084 | -0.091211 | -0.040414 | 0.01298 | 0.012309 | 0.011595 | 0.010839 | 0.010037 | 0.0091882 | 0.0082909 | 0.0073429 | 0.0063424 | 0.0052873 | 0.0041755 | 0.0030047 | 0.0037857 | 0.015087 | 0.027993 | 0.042691 | 0.059387 | 0.5966 | -0.22569 | -0.28885 | -19.3699 | 0 | 0 | 0 | 0 | 0 | 0 | -23.4769 | 0 | 0 | 0 | -51.3985 | 0 | 0 | 0 | 0
2055 | Ongoing capital |  |  | 19.8541 | 0 | ed | 45 | 0 |  | 0 | 19.8541 | -1.9793 | 2055 | -7.7318 | -0.061329 | -0.064953 | -0.068028 | -0.070507 | -0.073067 | -0.075711 | -0.078442 | -0.081262 | -0.084174 | -0.087181 | -0.090286 | -0.093491 | -0.041424 | 0.013305 | 0.012616 | 0.011885 | 0.01111 | 0.010288 | 0.0094179 | 0.0084981 | 0.0075265 | 0.006501 | 0.0054195 | 0.0042798 | 0.0030798 | 0.0038803 | 0.015464 | 0.028693 | 0.043758 | 0.060871 | 0.61151 | -0.23133 | -0.29607 | -19.8541 | 0 | 0 | 0 | 0 | 0 | -24.0638 | 0 | 0 | 0 | -52.2789 | 0 | 0 | 0 | 0
2056 | Ongoing capital |  |  | 20.3505 | 0 | ed | 45 | 0 |  | 0 | 20.3505 | -1.8789 | 2056 | -7.4658 | -0.05929 | -0.062863 | -0.066577 | -0.069729 | -0.07227 | -0.074894 | -0.077604 | -0.080403 | -0.083294 | -0.086279 | -0.089361 | -0.092543 | -0.095828 | -0.04246 | 0.013637 | 0.012932 | 0.012182 | 0.011387 | 0.010545 | 0.0096533 | 0.0087106 | 0.0077147 | 0.0066635 | 0.005555 | 0.0043868 | 0.0031568 | 0.0039773 | 0.015851 | 0.02941 | 0.044852 | 0.062393 | 0.6268 | -0.23711 | -0.30348 | -20.3505 | 0 | 0 | 0 | 0 | -24.6654 | 0 | 0 | 0 | -53.1859 | 0 | 0 | 0 | 0
2057 | Ongoing capital |  |  | 20.8592 | 0 | ed | 45 | 0 |  | 0 | 20.8592 | -1.7809 | 2057 | -7.1999 | -0.05725 | -0.060772 | -0.064434 | -0.068241 | -0.071472 | -0.074076 | -0.076766 | -0.079544 | -0.082413 | -0.085376 | -0.088436 | -0.091595 | -0.094856 | -0.098224 | -0.043521 | 0.013978 | 0.013255 | 0.012487 | 0.011672 | 0.010809 | 0.0098947 | 0.0089284 | 0.0079075 | 0.0068301 | 0.0056938 | 0.0044965 | 0.0032358 | 0.0040767 | 0.016247 | 0.030146 | 0.045974 | 0.063953 | 0.64247 | -0.24304 | -0.31106 | -20.8592 | 0 | 0 | 0 | -25.282 | 0 | 0 | 0 | -54.1202 | 0 | 0 | 0 | 0
2058 | Ongoing capital |  |  | 21.3807 | 0 | ed | 45 | 0 |  | 0 | 21.3807 | -1.6851 | 2058 | -6.9339 | -0.05521 | -0.058681 | -0.062291 | -0.066045 | -0.069947 | -0.073259 | -0.075928 | -0.078685 | -0.081533 | -0.084474 | -0.087511 | -0.090646 | -0.093884 | -0.097228 | -0.10068 | -0.044609 | 0.014328 | 0.013586 | 0.012799 | 0.011964 | 0.011079 | 0.010142 | 0.0091516 | 0.0081052 | 0.0070009 | 0.0058362 | 0.0046089 | 0.0033167 | 0.0041787 | 0.016653 | 0.030899 | 0.047123 | 0.065552 | 0.65853 | -0.24912 | -0.31884 | -21.3807 | 0 | 0 | -25.9141 | 0 | 0 | 0 | -55.0824 | 0 | 0 | 0 | 0
2059 | Ongoing capital |  |  | 21.9152 | 0 | ed | 45 | 0 |  | 0 | 21.9152 | -1.5914 | 2059 | -6.6679 | -0.053171 | -0.056591 | -0.060148 | -0.063849 | -0.067696 | -0.071696 | -0.07509 | -0.077826 | -0.080653 | -0.083571 | -0.086586 | -0.089698 | -0.092913 | -0.096232 | -0.099658 | -0.1032 | -0.045724 | 0.014686 | 0.013926 | 0.013119 | 0.012263 | 0.011356 | 0.010396 | 0.0093804 | 0.0083079 | 0.0071759 | 0.0059821 | 0.0047242 | 0.0033996 | 0.0042831 | 0.017069 | 0.031672 | 0.048301 | 0.067191 | 0.675 | -0.25535 | -0.32681 | -21.9152 | 0 | -26.5619 | 0 | 0 | 0 | -56.0733 | 0 | 0 | 0 | 0
2060 | Ongoing capital |  |  | 22.4631 | 0 | ed | 45 | 0 |  | 0 | 22.4631 | -1.4996 | 2060 | -6.4019 | -0.051131 | -0.0545 | -0.058006 | -0.061652 | -0.065445 | -0.069389 | -0.073489 | -0.076968 | -0.079772 | -0.082669 | -0.085661 | -0.08875 | -0.091941 | -0.095235 | -0.098637 | -0.10215 | -0.10578 | -0.046867 | 0.015053 | 0.014274 | 0.013447 | 0.012569 | 0.01164 | 0.010655 | 0.0096149 | 0.0085156 | 0.0073553 | 0.0061317 | 0.0048423 | 0.0034846 | 0.0043902 | 0.017496 | 0.032464 | 0.049509 | 0.06887 | 0.69187 | -0.26173 | -0.33498 | -22.4631 | -27.226 | 0 | 0 | 0 | -57.0936 | 0 | 0 | 0 | 0
2061 | Ongoing capital |  |  | 23.0247 | 0 | ed | 45 | 0 |  |  | 23.0247 | -1.4996
2062 | Ongoing capital |  |  | 23.6003 | 0 | ed | 45 | 0 |  |  | 23.6003 | -1.4996
2063 | Ongoing capital |  |  | 24.1903 | 0 | ed | 45 | 0 |  |  | 24.1903 | -1.4996
2064 | Ongoing capital |  |  | 24.7951 | 0 | ed | 45 | 0 |  |  | 24.7951 | -1.4996
2065 | Ongoing capital |  |  | 25.4149 | 0 | ed | 45 | 0 |  |  | 25.4149 | -1.4996
* Life and salvage fields ignored when expenditure is an expense (type exp or atx). | [10 empty] | 1715.6221 | -1320.1088 | 2061 | -6.1359 | -0.049092 | -0.05241 | -0.055863 | -0.059456 | -0.063193 | -0.067081 | -0.071123 | -0.075326 | -0.078892 | -0.081766 | -0.084736 | -0.087802 | -0.090969 | -0.094239 | -0.097616 | -0.1011 | -0.1047 | -0.10842 | -0.048039 | 0.015429 | 0.014631 | 0.013783 | 0.012884 | 0.011931 | 0.010922 | 0.0098552 | 0.0087284 | 0.0075392 | 0.0062849 | 0.0049633 | 0.0035717 | 0.0045 | 0.017933 | 0.033275 | 0.050746 | 0.070592 | 0.70917 | -0.26827 | -0.34336 | -27.9066 | 0 | 0 | 0 | -35.1193 | 0 | 0 | 0 | 0
[13 empty] | 2062 | -5.87 | -0.047052 | -0.050319 | -0.05372 | -0.057259 | -0.060942 | -0.064773 | -0.068758 | -0.072901 | -0.077209 | -0.080864 | -0.083811 | -0.086854 | -0.089997 | -0.093243 | -0.096595 | -0.10006 | -0.10363 | -0.10732 | -0.11113 | -0.04924 | 0.015815 | 0.014997 | 0.014128 | 0.013206 | 0.012229 | 0.011195 | 0.010102 | 0.0089467 | 0.0077276 | 0.0064421 | 0.0050874 | 0.003661 | 0.0046125 | 0.018382 | 0.034107 | 0.052015 | 0.072357 | 0.7269 | -0.27498 | -28.6043 | 0 | 0 | 0 | -35.273
Operating Expenses (+) and Revenues (-) Over 45 Years (2021-2065) in $000 | [12 empty] | 2063 | -5.604 | -0.045012 | -0.048228 | -0.051577 | -0.055063 | -0.058691 | -0.062466 | -0.066393 | -0.070477 | -0.074724 | -0.079139 | -0.082886 | -0.085906 | -0.089025 | -0.092247 | -0.095574 | -0.09901 | -0.10256 | -0.10622 | -0.11 | -0.11391 | -0.050471 | 0.01621 | 0.015372 | 0.014481 | 0.013536 | 0.012535 | 0.011475 | 0.010354 | 0.0091703 | 0.0079208 | 0.0066031 | 0.0052146 | 0.0037525 | 0.0047278 | 0.018841 | 0.03496 | 0.053315 | 0.074166 | 0.74507 | -29.3194 | 0 | 0 | 0 | -35.5053
Year | a | b | c | d |  |  | Description |  |  |  | Esc% | NPV | 2064 | -5.338 | -0.042973 | -0.046138 | -0.049434 | -0.052866 | -0.056439 | -0.060158 | -0.064027 | -0.068052 | -0.072239 | -0.076592 | -0.081118 | -0.084958 | -0.088054 | -0.091251 | -0.094553 | -0.097964 | -0.10149 | -0.10512 | -0.10888 | -0.11275 | -0.11676 | -0.051733 | 0.016616 | 0.015756 | 0.014843 | 0.013874 | 0.012848 | 0.011762 | 0.010613 | 0.0093996 | 0.0081188 | 0.0067682 | 0.0053449 | 0.0038463 | 0.004846 | 0.019312 | 0.035834 | 0.054648 | 0.07602 | -30.0524 | 0 | 0 | 0 | -36.7935
2021 | 14.7926 |  |  |  | a. | Annual Operations and Maintenance |  |  |  |  | 2.5 | -208.7639 | 2065 | -5.072 | -0.040933 | -0.044047 | -0.047291 | -0.05067 | -0.054188 | -0.05785 | -0.061662 | -0.065628 | -0.069754 | -0.074045 | -0.078507 | -0.083146 | -0.087082 | -0.090255 | -0.093532 | -0.096917 | -0.10041 | -0.10402 | -0.10775 | -0.1116 | -0.11557 | -0.11968 | -0.053026 | 0.017031 | 0.01615 | 0.015214 | 0.014221 | 0.013169 | 0.012056 | 0.010878 | 0.0096346 | 0.0083218 | 0.0069374 | 0.0054786 | 0.0039425 | 0.0049671 | 0.019795 | 0.03673 | 0.056014 | -30.8037 | 0 | 0 | 0 | -37.4327
2022 | 14.7926 |  |  |  | b. | [5 empty] | 2.5 | 0 | 2066 | -4.806 | -0.038893 | -0.041956 | -0.045148 | -0.048473 | -0.051937 | -0.055543 | -0.059297 | -0.063203 | -0.067269 | -0.071498 | -0.075896 | -0.080469 | -0.085224 | -0.089259 | -0.091581 | -0.092056 | -0.090542 | -0.086891 | -0.080947 | -0.072546 | -0.061516 | -0.047678 | -0.030841 | 0.061849 | 0.23605 | 0.42136 | 0.6183 | 0.82738 | 1.0492 | 1.2842 | 1.5331 | 1.7965 | 2.075 | 2.3693 | 2.68 | 3.0079 | 3.3565 | 3.7407 | 4.1642 | -31.5738 | 0 | 0 | 0 | -8.6871
2023 | 14.7926 |  |  |  | c. | [5 empty] | 2.5 | 0 | 2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 14.7926 |  |  |  | d. | [5 empty] | 2.5 | 0 | 2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 14.7926 | [10 empty] | -208.7639 | 2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 14.7926 | [11 empty] | 2070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 14.7926 | [11 empty] | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 14.7926 | [7 empty] | Total NPV ($000) |  |  | -1528.8727 | 45 | MaxCap
2029 | 14.7926 | [11 empty] | 0 | cap error
2030 | 14.7926 | [11 empty] | 0 | exp error
2031 | 14.7926 | [11 empty] | 0 | tot errors
2032 | 14.7926 | [9 empty] | Comments (press alt+enter to skip to new line)
2033 | 14.7926
2034 | 14.7926
2035 | 14.7926 | [11 empty] | 1 | -65.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.6531 | 0 | 0 | 0 | -75.7861
2036 | 14.7926 | [11 empty] | 2 | -64.2245 | -0.49946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.9194 | 0 | 0 | 0 | -75.6434
2037 | 14.7926 | [11 empty] | 3 | -63.3159 | -0.49249 | -0.51194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.1924 | 0 | 0 | 0 | -75.5128
2038 | 14.7926 | [11 empty] | 4 | -62.4074 | -0.48552 | -0.5048 | -0.52474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.4722 | 0 | 0 | 0 | -75.3947
2039 | 14.7926 | [11 empty] | 5 | -61.4989 | -0.47856 | -0.49766 | -0.51742 | -0.53786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.759 | 0 | 0 | 0 | -75.2894
2040 | 14.7926
2041 | 14.7926
2042 | 14.7926
2043 | 14.7926
2044 | 14.7926
2045 | 14.7926
2046 | 14.7926
2047 | 14.7926
2048 | 14.7926
2049 | 14.7926
2050 | 14.7926
2051 | 14.7926
2052 | 14.7926
2053 | 14.7926
2054 | 14.7926
2055 | 14.7926
2056 | 14.7926
2057 | 14.7926
2058 | 14.7926
2059 | 14.7926
2060 | 14.7926
2061 | 14.7926
2062 | 14.7926
2063 | 14.7926
2064 | 14.7926
2065 | 14.7926
2066
2067
2068
2069
2070
Note on BK6: Jonathan: Starting in 2018, bonus depreciation no longer available to public utilities
Note on A7: Enter year of operation for capital, or year of occurrence for expenses. Timing is assumed to be beginning-of-year. Amounts entered outside of study period are ignored.
Note on C7: Enter project expenditures required to implement this alternative. Amounts already spent on a proposed project should be included as part of the project cost in the alternative that completes the project. In competing alternatives where the project is abandoned (such as status quo), any amounts already spent should be shown as an expense in the year the project is written off.
Note on E7: Enter cost in financial dollars, including contingency and overheads. For multi-year construction projects, enter cost for each expenditure type as lump sum in year of operation.
Note on F7: Accept default escalation rate, enter a different rate, or enter zero if cost is already escalated to year of expenditure (as it would be in a job estimate).
Note on G7: Capital Type Life ¦ Capital Type Life Buildings bldg 50 ¦ Power Plants: Communication equip comm 15 ¦ Combined cycle cc 30 Computer hardware comp 5 ¦ Combustion turbine ct 25 Computer software soft 5 ¦ Micro turbine mt 10 Electric dist (<69kV) ed 45 ¦ Hydro hyd 50 Electric trans (69kV+) et 55 ¦ Hydro additions hyda 20 Electric smart meter em 20 ¦ Nuclear nuc 15 Gas distribution gasd 55 ¦ Nuclear additions nuca 7 Gas meters gm 30 ¦ Biomass bio 25 Gas trans & storage gast 55 ¦ Fuel cell fcl 8 Gas held for resale gasc 99 ¦ Geothermal geo 25 Land easement ease 99 ¦ Solar photovoltaic pv 20 Land purchase land 99 ¦ Solar thermal st 25 Motor vehicles mv 10 ¦ Tidal or wave tdl 10 Office furniture furn 20 ¦ Waste wst 25 Electricity Storage bat 15 ¦ Wind wnd 25 Expense exp ¦ Expense, after-tax atx This is a partial listing of expenditure types. See EASOP Help tab or Economic Guide for additional guidance in selecting expenditure types.
Note on H7: Enter the expected life for each capital asset, even if it extends beyond the study period. EASOP retires each asset at the end of its life or the end of the study period, whichever occurs first, at the salvage specified.
Note on I7: Accept zero as default salvage value, enter a different value, or delete entry to use value calculated by EASOP. For most analyses, use 100% for land and 0% for all other expenditures.
Note on BK8: =IF(OR(AND(A8>2011,RIGHT(G8,3)="sbd"),AND(A8>2012,RIGHT(G8,2)="bd")),1,0)
Note on BK9: =IF(OR(AND(A9>2011,RIGHT(G9,3)="sbd"),AND(A9>2012,RIGHT(G9,2)="bd")),1,0)
Note on BK10: =IF(OR(AND(A10>2011,RIGHT(G10,3)="sbd"),AND(A10>2012,RIGHT(G10,2)="bd")),1,0)
Note on BK11: =IF(OR(AND(A11>2011,RIGHT(G11,3)="sbd"),AND(A11>2012,RIGHT(G11,2)="bd")),1,0)
Note on BK12: =IF(OR(AND(A12>2011,RIGHT(G12,3)="sbd"),AND(A12>2012,RIGHT(G12,2)="bd")),1,0)
Note on BK13: =IF(OR(AND(A13>2011,RIGHT(G13,3)="sbd"),AND(A13>2012,RIGHT(G13,2)="bd")),1,0)
Note on BK14: =IF(OR(AND(A14>2011,RIGHT(G14,3)="sbd"),AND(A14>2012,RIGHT(G14,2)="bd")),1,0)
Note on BK15: =IF(OR(AND(A15>2011,RIGHT(G15,3)="sbd"),AND(A15>2012,RIGHT(G15,2)="bd")),1,0)
Note on BK16: =IF(OR(AND(A16>2011,RIGHT(G16,3)="sbd"),AND(A16>2012,RIGHT(G16,2)="bd")),1,0)
Note on BK17: =IF(OR(AND(A17>2011,RIGHT(G17,3)="sbd"),AND(A17>2012,RIGHT(G17,2)="bd")),1,0)
Note on BK18: =IF(OR(AND(A18>2011,RIGHT(G18,3)="sbd"),AND(A18>2012,RIGHT(G18,2)="bd")),1,0)
Note on BK19: =IF(OR(AND(A19>2011,RIGHT(G19,3)="sbd"),AND(A19>2012,RIGHT(G19,2)="bd")),1,0)
Note on BK20: =IF(OR(AND(A20>2011,RIGHT(G20,3)="sbd"),AND(A20>2012,RIGHT(G20,2)="bd")),1,0)
Note on BK21: =IF(OR(AND(A21>2011,RIGHT(G21,3)="sbd"),AND(A21>2012,RIGHT(G21,2)="bd")),1,0)
Note on BK22: =IF(OR(AND(A22>2011,RIGHT(G22,3)="sbd"),AND(A22>2012,RIGHT(G22,2)="bd")),1,0)
Note on BK23: =IF(OR(AND(A23>2011,RIGHT(G23,3)="sbd"),AND(A23>2012,RIGHT(G23,2)="bd")),1,0)
Note on BK24: =IF(OR(AND(A24>2011,RIGHT(G24,3)="sbd"),AND(A24>2012,RIGHT(G24,2)="bd")),1,0)
Note on BK25: =IF(OR(AND(A25>2011,RIGHT(G25,3)="sbd"),AND(A25>2012,RIGHT(G25,2)="bd")),1,0)
Note on BK26: =IF(OR(AND(A26>2011,RIGHT(G26,3)="sbd"),AND(A26>2012,RIGHT(G26,2)="bd")),1,0)
Note on BK27: =IF(OR(AND(A27>2011,RIGHT(G27,3)="sbd"),AND(A27>2012,RIGHT(G27,2)="bd")),1,0)
Note on BK28: =IF(OR(AND(A28>2011,RIGHT(G28,3)="sbd"),AND(A28>2012,RIGHT(G28,2)="bd")),1,0)
Note on BK29: =IF(OR(AND(A29>2011,RIGHT(G29,3)="sbd"),AND(A29>2012,RIGHT(G29,2)="bd")),1,0)
Note on BK30: =IF(OR(AND(A30>2011,RIGHT(G30,3)="sbd"),AND(A30>2012,RIGHT(G30,2)="bd")),1,0)
Note on BK31: =IF(OR(AND(A31>2011,RIGHT(G31,3)="sbd"),AND(A31>2012,RIGHT(G31,2)="bd")),1,0)
Note on BK32: =IF(OR(AND(A32>2011,RIGHT(G32,3)="sbd"),AND(A32>2012,RIGHT(G32,2)="bd")),1,0)
Note on BK33: =IF(OR(AND(A33>2011,RIGHT(G33,3)="sbd"),AND(A33>2012,RIGHT(G33,2)="bd")),1,0)
Note on BK34: =IF(OR(AND(A34>2011,RIGHT(G34,3)="sbd"),AND(A34>2012,RIGHT(G34,2)="bd")),1,0)
Note on BK35: =IF(OR(AND(A35>2011,RIGHT(G35,3)="sbd"),AND(A35>2012,RIGHT(G35,2)="bd")),1,0)
Note on BK36: =IF(OR(AND(A36>2011,RIGHT(G36,3)="sbd"),AND(A36>2012,RIGHT(G36,2)="bd")),1,0)
Note on BK37: =IF(OR(AND(A37>2011,RIGHT(G37,3)="sbd"),AND(A37>2012,RIGHT(G37,2)="bd")),1,0)
Note on BK38: =IF(OR(AND(A38>2011,RIGHT(G38,3)="sbd"),AND(A38>2012,RIGHT(G38,2)="bd")),1,0)
Note on BK39: =IF(OR(AND(A39>2011,RIGHT(G39,3)="sbd"),AND(A39>2012,RIGHT(G39,2)="bd")),1,0)
Note on BK40: =IF(OR(AND(A40>2011,RIGHT(G40,3)="sbd"),AND(A40>2012,RIGHT(G40,2)="bd")),1,0)
Note on BK41: =IF(OR(AND(A41>2011,RIGHT(G41,3)="sbd"),AND(A41>2012,RIGHT(G41,2)="bd")),1,0)
Note on BK42: =IF(OR(AND(A42>2011,RIGHT(G42,3)="sbd"),AND(A42>2012,RIGHT(G42,2)="bd")),1,0)
Note on BK43: =IF(OR(AND(A43>2011,RIGHT(G43,3)="sbd"),AND(A43>2012,RIGHT(G43,2)="bd")),1,0)
Note on BK44: =IF(OR(AND(A44>2011,RIGHT(G44,3)="sbd"),AND(A44>2012,RIGHT(G44,2)="bd")),1,0)
Note on BK45: =IF(OR(AND(A45>2011,RIGHT(G45,3)="sbd"),AND(A45>2012,RIGHT(G45,2)="bd")),1,0)
Note on BK46: =IF(OR(AND(A46>2011,RIGHT(G46,3)="sbd"),AND(A46>2012,RIGHT(G46,2)="bd")),1,0)
Note on BK47: =IF(OR(AND(A47>2011,RIGHT(G47,3)="sbd"),AND(A47>2012,RIGHT(G47,2)="bd")),1,0)
Note on A56: Timing of operating expenses and revenues is assumed to be end-of-year. Amounts entered beyond study period are ignored.
Note on H56: Enter recurring expenses and revenues (assuming no cost-of-service regulation) for this alternative. If a project will result in savings, enter them as a cost under status quo or as a savings under the proposed project, but not as both in the same evaluation.
Note on L56: Accept default escalation rate, enter a different rate, or enter zero if cost or revenue stream already includes escalation.

## 2 All OH
Underground vs. Overhead Analysis
Alternative 2 - All Overhead
Project Expenditures Over 45 Years (2021-2065) in $000 * | [7 empty] | Salvage% |  |  | Escalated | [47 empty] | life | salvage | ITC | BD
Year |  | Description |  | Cost | Esc% | Type | Life | Input | Calcd |  | Cost | NPV | boy | cap1 | cap2 | cap3 | cap4 | cap5 | cap6 | cap7 | cap8 | cap9 | cap10 | cap11 | cap12 | cap13 | cap14 | cap15 | cap16 | cap17 | cap18 | cap19 | cap20 | cap21 | cap22 | cap23 | cap24 | cap25 | cap26 | cap27 | cap28 | cap29 | cap30 | cap31 | cap32 | cap33 | cap34 | cap35 | cap36 | cap37 | cap38 | cap39 | cap40 | exp a | exp b | exp c | exp d | total acf | error | error | Check | Error
2021 | Overhead CapEx |  |  | 974.869 | 2.5 | ed | 45 | 0 |  | 0 | 951.0917 | -960.9722 | 2021 | -951.0917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -951.0917 | 0 | 0 | 0 | 0
2022 | Ongoing capital |  |  | 8.7895 | 0 | ed | 45 | 0 |  | 0 | 8.7895 | -8.3136 | 2022 | -14.5378 | -8.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.6531 | 0 | 0 | 0 | -33.9803 | 0 | 0 | 0 | 0
2023 | Ongoing capital |  |  | 9.0092 | 0 | ed | 45 | 0 |  | 0 | 9.0092 | -7.9769 | 2023 | -11.6427 | -0.13435 | -9.0092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.9194 | 0 | 0 | 0 | -31.7057 | 0 | 0 | 0 | 0
2024 | Ongoing capital |  |  | 9.2344 | 0 | ed | 45 | 0 |  | 0 | 9.2344 | -7.6536 | 2024 | 31.5464 | -0.1076 | -0.13771 | -9.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.1924 | 0 | 0 | 0 | 10.8743 | 0 | 0 | 0 | 0
2025 | Ongoing capital |  |  | 9.4653 | 0 | ed | 45 | 0 |  | 0 | 9.4653 | -7.3433 | 2025 | 3.2187 | 0.29154 | -0.11029 | -0.14115 | -9.4653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.4722 | 0 | 0 | 0 | -17.6788 | 0 | 0 | 0 | 0
2026 | Ongoing capital |  |  | 9.7019 | 0 | ed | 45 | 0 |  | 0 | 9.7019 | -7.0452 | 2026 | 2.3717 | 0.029745 | 0.29882 | -0.11304 | -0.14468 | -9.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.759 | 0 | 0 | 0 | -19.0185 | 0 | 0 | 0 | 0
2027 | Ongoing capital |  |  | 9.9445 | 0 | ed | 45 | 0 |  | 0 | 9.9445 | -6.7589 | 2027 | 1.594 | 0.021918 | 0.030489 | 0.30629 | -0.11587 | -0.1483 | -9.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.053 | 0 | 0 | 0 | -20.309 | 0 | 0 | 0 | 0
2028 | Ongoing capital |  |  | 10.1931 | 0 | ed | 45 | 0 |  | 0 | 10.1931 | -6.4841 | 2028 | 0.88056 | 0.014731 | 0.022466 | 0.031251 | 0.31395 | -0.11877 | -0.152 | -10.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.3544 | 0 | 0 | 0 | -21.5553 | 0 | 0 | 0 | 0
2029 | Ongoing capital |  |  | 10.4479 | 0 | ed | 45 | 0 |  | 0 | 10.4479 | -6.22 | 2029 | 0.22648 | 0.0081377 | 0.015099 | 0.023027 | 0.032033 | 0.3218 | -0.12173 | -0.1558 | -10.4479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.6632 | 0 | 0 | 0 | -22.7621 | 0 | 0 | 0 | 0
2030 | Ongoing capital |  |  | 10.7091 | 0 | ed | 45 | 0 |  | 0 | 10.7091 | -5.9665 | 2030 | 0.18425 | 0.002093 | 0.0083411 | 0.015477 | 0.023603 | 0.032833 | 0.32985 | -0.12478 | -0.1597 | -10.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.9798 | 0 | 0 | 0 | -23.3769 | 0 | 0 | 0 | 0
2031 | Ongoing capital |  |  | 10.9769 | 0 | ed | 45 | 0 |  | 0 | 10.9769 | -5.7229 | 2031 | 0.26245 | 0.0017028 | 0.0021453 | 0.0085496 | 0.015864 | 0.024193 | 0.033654 | 0.33809 | -0.1279 | -0.16369 | -10.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.3043 | 0 | 0 | 0 | -23.8861 | 0 | 0 | 0 | 0
2032 | Ongoing capital |  |  | 11.2513 | 0 | ed | 45 | 0 |  | 0 | 11.2513 | -5.4889 | 2032 | 0.34064 | 0.0024254 | 0.0017453 | 0.002199 | 0.0087634 | 0.01626 | 0.024798 | 0.034496 | 0.34654 | -0.13109 | -0.16778 | -11.2513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.6369 | 0 | 0 | 0 | -24.4092 | 0 | 0 | 0 | 0
2033 | Ongoing capital |  |  | 11.5326 | 0 | ed | 45 | 0 |  | 0 | 11.5326 | -5.2642 | 2033 | 0.41883 | 0.003148 | 0.002486 | 0.001789 | 0.0022539 | 0.0089825 | 0.016667 | 0.025418 | 0.035358 | 0.35521 | -0.13437 | -0.17198 | -11.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.9778 | 0 | 0 | 0 | -24.9466 | 0 | 0 | 0 | 0
2034 | Ongoing capital |  |  | 11.8209 | 0 | ed | 45 | 0 |  | 0 | 11.8209 | -5.0482 | 2034 | 0.49702 | 0.0038706 | 0.0032267 | 0.0025482 | 0.0018337 | 0.0023103 | 0.009207 | 0.017083 | 0.026053 | 0.036242 | 0.36409 | -0.13773 | -0.17628 | -11.8209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.3273 | 0 | 0 | 0 | -25.4987 | 0 | 0 | 0 | 0
2035 | Ongoing capital |  |  | 12.1164 | 0 | ed | 45 | 0 |  | 0 | 12.1164 | -4.8407 | 2035 | 0.57521 | 0.0045932 | 0.0039674 | 0.0033074 | 0.0026119 | 0.0018795 | 0.002368 | 0.0094372 | 0.017511 | 0.026704 | 0.037148 | 0.37319 | -0.14117 | -0.18069 | -12.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.6854 | 0 | 0 | 0 | -26.0658 | 0 | 0 | 0 | 0
2036 | Ongoing capital |  |  | 12.4193 | 0 | ed | 45 | 0 |  | 0 | 12.4193 | -4.6413 | 2036 | 0.65341 | 0.0053158 | 0.004708 | 0.0040665 | 0.00339 | 0.0026772 | 0.0019265 | 0.0024272 | 0.0096731 | 0.017948 | 0.027372 | 0.038077 | 0.38252 | -0.1447 | -0.1852 | -12.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -15.0526 | 0 | 0 | 0 | -26.6483 | 0 | 0 | 0 | 0
2037 | Ongoing capital |  |  | 12.7298 | 0 | ed | 45 | 0 |  | 0 | 12.7298 | -4.4497 | 2037 | 0.7316 | 0.0060384 | 0.0054487 | 0.0048257 | 0.0041682 | 0.0034748 | 0.0027441 | 0.0019747 | 0.0024879 | 0.009915 | 0.018397 | 0.028056 | 0.039029 | 0.39208 | -0.14832 | -0.18983 | -12.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -15.4289 | 0 | 0 | 0 | -27.2466 | 0 | 0 | 0 | 0
2038 | Ongoing capital |  |  | 13.048 | 0 | ed | 45 | 0 |  | 0 | 13.048 | -4.2655 | 2038 | 0.80979 | 0.006761 | 0.0061894 | 0.0055849 | 0.0049464 | 0.0042724 | 0.0035617 | 0.0028127 | 0.0020241 | 0.0025501 | 0.010163 | 0.018857 | 0.028758 | 0.040004 | 0.40188 | -0.15203 | -0.19458 | -13.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -15.8146 | 0 | 0 | 0 | -27.8611 | 0 | 0 | 0 | 0
2039 | Ongoing capital |  |  | 13.3742 | 0 | ed | 45 | 0 |  | 0 | 13.3742 | -4.0885 | 2039 | 0.88798 | 0.0074837 | 0.0069301 | 0.0063441 | 0.0057246 | 0.00507 | 0.0043792 | 0.0036507 | 0.002883 | 0.0020747 | 0.0026139 | 0.010417 | 0.019328 | 0.029477 | 0.041004 | 0.41193 | -0.15583 | -0.19944 | -13.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.21 | 0 | 0 | 0 | -28.4922 | 0 | 0 | 0 | 0
2040 | Ongoing capital |  |  | 13.7086 | 0 | ed | 45 | 0 |  | 0 | 13.7086 | -3.9182 | 2040 | 0.96618 | 0.0082063 | 0.0076707 | 0.0071033 | 0.0065027 | 0.0058677 | 0.0051968 | 0.0044887 | 0.003742 | 0.0029551 | 0.0021265 | 0.0026792 | 0.010677 | 0.019812 | 0.030214 | 0.04203 | 0.42223 | -0.15973 | -0.20443 | -13.7086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.6152 | 0 | 0 | 0 | -29.1403 | 0 | 0 | 0 | 0
2041 | Ongoing capital |  |  | 14.0513 | 0 | ed | 45 | 0 |  | 0 | 14.0513 | -3.7545 | 2041 | 1.0444 | 0.0089289 | 0.0084114 | 0.0078625 | 0.0072809 | 0.0066653 | 0.0060144 | 0.0053267 | 0.0046009 | 0.0038355 | 0.003029 | 0.0021797 | 0.0027462 | 0.010944 | 0.020307 | 0.030969 | 0.04308 | 0.43279 | -0.16372 | -0.20954 | -14.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17.0306 | 0 | 0 | 0 | -29.8058 | 0 | 0 | 0 | 0
2042 | Ongoing capital |  |  | 14.4026 | 0 | ed | 45 | 0 |  | 0 | 14.4026 | -3.597 | 2042 | -3.3329 | 0.0096515 | 0.0091521 | 0.0086217 | 0.0080591 | 0.0074629 | 0.0068319 | 0.0061647 | 0.0054599 | 0.004716 | 0.0039314 | 0.0031047 | 0.0022342 | 0.0028149 | 0.011218 | 0.020815 | 0.031743 | 0.044157 | 0.44361 | -0.16781 | -0.21478 | -14.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17.4564 | 0 | 0 | 0 | -34.9447 | 0 | 0 | 0 | 0
2043 | Ongoing capital |  |  | 14.7626 | 0 | ed | 45 | 0 |  | 0 | 14.7626 | -3.4454 | 2043 | -7.7102 | -0.030801 | 0.0098928 | 0.0093809 | 0.0088372 | 0.0082606 | 0.0076495 | 0.0070027 | 0.0063188 | 0.0055964 | 0.0048338 | 0.0040297 | 0.0031823 | 0.00229 | 0.0028852 | 0.011498 | 0.021335 | 0.032537 | 0.045261 | 0.4547 | -0.17201 | -0.22015 | -14.7626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17.8928 | 0 | 0 | 0 | -40.1431 | 0 | 0 | 0 | 0
2044 | Ongoing capital |  |  | 15.1317 | 0 | ed | 45 | 0 |  | 0 | 15.1317 | -3.2996 | 2044 | -7.632 | -0.071254 | -0.031571 | 0.01014 | 0.0096154 | 0.0090582 | 0.0084671 | 0.0078407 | 0.0071778 | 0.0064768 | 0.0057363 | 0.0049547 | 0.0041304 | 0.0032619 | 0.0023473 | 0.0029574 | 0.011786 | 0.021868 | 0.03335 | 0.046393 | 0.46606 | -0.17631 | -0.22565 | -15.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -18.3401 | 0 | 0 | 0 | -40.947 | 0 | 0 | 0 | 0
2045 | Ongoing capital |  |  | 15.51 | 0 | ed | 45 | 0 |  | 0 | 15.51 | -3.1592 | 2045 | -7.5538 | -0.070531 | -0.073035 | -0.03236 | 0.010394 | 0.0098558 | 0.0092846 | 0.0086787 | 0.0080368 | 0.0073572 | 0.0066387 | 0.0058797 | 0.0050786 | 0.0042337 | 0.0033434 | 0.002406 | 0.0030313 | 0.01208 | 0.022415 | 0.034184 | 0.047553 | 0.47771 | -0.18072 | -0.23129 | -15.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -18.7986 | 0 | 0 | 0 | -41.7722 | 0 | 0 | 0 | 0
2046 | Ongoing capital |  |  | 15.8978 | 0 | ed | 45 | 0 |  | 0 | 15.8978 | -3.0237 | 2046 | -7.4756 | -0.069808 | -0.072294 | -0.074861 | -0.033169 | 0.010653 | 0.010102 | 0.0095167 | 0.0088957 | 0.0082377 | 0.0075412 | 0.0068047 | 0.0060267 | 0.0052055 | 0.0043395 | 0.003427 | 0.0024661 | 0.0031071 | 0.012382 | 0.022975 | 0.035039 | 0.048741 | 0.48966 | -0.18523 | -0.23708 | -15.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19.2686 | 0 | 0 | 0 | -42.6193 | 0 | 0 | 0 | 0
2047 | Ongoing capital |  |  | 16.2952 | 0 | ed | 45 | 0 |  | 0 | 16.2952 | -2.8927 | 2047 | -7.3974 | -0.069086 | -0.071554 | -0.074102 | -0.076732 | -0.033999 | 0.01092 | 0.010355 | 0.0097547 | 0.0091181 | 0.0084436 | 0.0077297 | 0.0069748 | 0.0061774 | 0.0053357 | 0.004448 | 0.0035127 | 0.0025278 | 0.0031847 | 0.012692 | 0.02355 | 0.035915 | 0.04996 | 0.5019 | -0.18986 | -0.243 | -16.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19.7503 | 0 | 0 | 0 | -43.4888 | 0 | 0 | 0 | 0
2048 | Ongoing capital |  |  | 16.7026 | 0 | ed | 45 | 0 |  | 0 | 16.7026 | -2.766 | 2048 | -7.3192 | -0.068363 | -0.070813 | -0.073342 | -0.075954 | -0.078651 | -0.034849 | 0.011193 | 0.010614 | 0.0099985 | 0.0093461 | 0.0086547 | 0.0079229 | 0.0071492 | 0.0063318 | 0.0054691 | 0.0045592 | 0.0036005 | 0.002591 | 0.0032644 | 0.013009 | 0.024139 | 0.036812 | 0.051209 | 0.51445 | -0.19461 | -0.24908 | -16.7026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -20.244 | 0 | 0 | 0 | -44.3812 | 0 | 0 | 0 | 0
2049 | Ongoing capital |  |  | 17.1201 | 0 | ed | 45 | 0 |  | 0 | 17.1201 | -2.6433 | 2049 | -7.2411 | -0.067641 | -0.070072 | -0.072583 | -0.075176 | -0.077853 | -0.080617 | -0.03572 | 0.011473 | 0.010879 | 0.010248 | 0.0095797 | 0.0088711 | 0.008121 | 0.0073279 | 0.0064901 | 0.0056058 | 0.0046732 | 0.0036905 | 0.0026557 | 0.003346 | 0.013335 | 0.024742 | 0.037733 | 0.052489 | 0.52731 | -0.19948 | -0.2553 | -17.1201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -20.7501 | 0 | 0 | 0 | -45.2972 | 0 | 0 | 0 | 0
2050 | Ongoing capital |  |  | 17.5481 | 0 | ed | 45 | 0 |  | 0 | 17.5481 | -2.5243 | 2050 | -7.1629 | -0.066918 | -0.069332 | -0.071824 | -0.074398 | -0.077055 | -0.079799 | -0.082632 | -0.036613 | 0.011759 | 0.011151 | 0.010505 | 0.0098192 | 0.0090928 | 0.008324 | 0.0075111 | 0.0066523 | 0.0057459 | 0.00479 | 0.0037828 | 0.0027221 | 0.0034296 | 0.013668 | 0.025361 | 0.038676 | 0.053801 | 0.54049 | -0.20446 | -0.26169 | -17.5481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -21.2689 | 0 | 0 | 0 | -46.2373 | 0 | 0 | 0 | 0
2051 | Ongoing capital |  |  | 17.9868 | 0 | ed | 45 | 0 |  | 0 | 17.9868 | -2.409 | 2051 | -7.0847 | -0.066195 | -0.068591 | -0.071065 | -0.07362 | -0.076258 | -0.078982 | -0.081794 | -0.084698 | -0.037528 | 0.012053 | 0.01143 | 0.010767 | 0.010065 | 0.0093202 | 0.0085321 | 0.0076989 | 0.0068186 | 0.0058896 | 0.0049098 | 0.0038773 | 0.0027902 | 0.0035154 | 0.01401 | 0.025995 | 0.039643 | 0.055146 | 0.554 | -0.20957 | -0.26823 | -17.9868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -21.8006 | 0 | 0 | 0 | -47.2022 | 0 | 0 | 0 | 0
2052 | Ongoing capital |  |  | 18.4365 | 0 | ed | 45 | 0 |  | 0 | 18.4365 | -2.297 | 2052 | -7.0065 | -0.065473 | -0.06785 | -0.070306 | -0.072841 | -0.07546 | -0.078164 | -0.080956 | -0.083839 | -0.086816 | -0.038466 | 0.012355 | 0.011715 | 0.011037 | 0.010316 | 0.0095532 | 0.0087454 | 0.0078914 | 0.0069891 | 0.0060368 | 0.0050325 | 0.0039743 | 0.0028599 | 0.0036032 | 0.01436 | 0.026644 | 0.040634 | 0.056525 | 0.56785 | -0.21481 | -0.27493 | -18.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -22.3456 | 0 | 0 | 0 | -48.1924 | 0 | 0 | 0 | 0
2053 | Ongoing capital |  |  | 18.8974 | 0 | ed | 45 | 0 |  | 0 | 18.8974 | -2.1882 | 2053 | -6.857 | -0.06475 | -0.06711 | -0.069546 | -0.072063 | -0.074662 | -0.077347 | -0.080118 | -0.08298 | -0.085935 | -0.088986 | -0.039428 | 0.012664 | 0.012008 | 0.011312 | 0.010574 | 0.009792 | 0.0089641 | 0.0080887 | 0.0071638 | 0.0061877 | 0.0051583 | 0.0040736 | 0.0029314 | 0.0036933 | 0.014719 | 0.027311 | 0.04165 | 0.057938 | 0.58205 | -0.22018 | -0.28181 | -18.8974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -22.9043 | 0 | 0 | 0 | -49.1374 | 0 | 0 | 0 | 0
2054 | Ongoing capital |  |  | 19.3699 | 0 | ed | 45 | 0 |  | 0 | 19.3699 | -2.0824 | 2054 | -6.6363 | -0.063369 | -0.066369 | -0.068787 | -0.071285 | -0.073865 | -0.076529 | -0.07928 | -0.082121 | -0.085055 | -0.088084 | -0.091211 | -0.040414 | 0.01298 | 0.012309 | 0.011595 | 0.010839 | 0.010037 | 0.0091882 | 0.0082909 | 0.0073429 | 0.0063424 | 0.0052873 | 0.0041755 | 0.0030047 | 0.0037857 | 0.015087 | 0.027993 | 0.042691 | 0.059387 | 0.5966 | -0.22569 | -0.28885 | -19.3699 | 0 | 0 | 0 | 0 | 0 | 0 | -23.4769 | 0 | 0 | 0 | -50.0371 | 0 | 0 | 0 | 0
2055 | Ongoing capital |  |  | 19.8541 | 0 | ed | 45 | 0 |  | 0 | 19.8541 | -1.9793 | 2055 | -6.4156 | -0.061329 | -0.064953 | -0.068028 | -0.070507 | -0.073067 | -0.075711 | -0.078442 | -0.081262 | -0.084174 | -0.087181 | -0.090286 | -0.093491 | -0.041424 | 0.013305 | 0.012616 | 0.011885 | 0.01111 | 0.010288 | 0.0094179 | 0.0084981 | 0.0075265 | 0.006501 | 0.0054195 | 0.0042798 | 0.0030798 | 0.0038803 | 0.015464 | 0.028693 | 0.043758 | 0.060871 | 0.61151 | -0.23133 | -0.29607 | -19.8541 | 0 | 0 | 0 | 0 | 0 | -24.0638 | 0 | 0 | 0 | -50.9627 | 0 | 0 | 0 | 0
2056 | Ongoing capital |  |  | 20.3505 | 0 | ed | 45 | 0 |  | 0 | 20.3505 | -1.8789 | 2056 | -6.1949 | -0.05929 | -0.062863 | -0.066577 | -0.069729 | -0.07227 | -0.074894 | -0.077604 | -0.080403 | -0.083294 | -0.086279 | -0.089361 | -0.092543 | -0.095828 | -0.04246 | 0.013637 | 0.012932 | 0.012182 | 0.011387 | 0.010545 | 0.0096533 | 0.0087106 | 0.0077147 | 0.0066635 | 0.005555 | 0.0043868 | 0.0031568 | 0.0039773 | 0.015851 | 0.02941 | 0.044852 | 0.062393 | 0.6268 | -0.23711 | -0.30348 | -20.3505 | 0 | 0 | 0 | 0 | -24.6654 | 0 | 0 | 0 | -51.915 | 0 | 0 | 0 | 0
2057 | Ongoing capital |  |  | 20.8592 | 0 | ed | 45 | 0 |  | 0 | 20.8592 | -1.7809 | 2057 | -5.9742 | -0.05725 | -0.060772 | -0.064434 | -0.068241 | -0.071472 | -0.074076 | -0.076766 | -0.079544 | -0.082413 | -0.085376 | -0.088436 | -0.091595 | -0.094856 | -0.098224 | -0.043521 | 0.013978 | 0.013255 | 0.012487 | 0.011672 | 0.010809 | 0.0098947 | 0.0089284 | 0.0079075 | 0.0068301 | 0.0056938 | 0.0044965 | 0.0032358 | 0.0040767 | 0.016247 | 0.030146 | 0.045974 | 0.063953 | 0.64247 | -0.24304 | -0.31106 | -20.8592 | 0 | 0 | 0 | -25.282 | 0 | 0 | 0 | -52.8945 | 0 | 0 | 0 | 0
2058 | Ongoing capital |  |  | 21.3807 | 0 | ed | 45 | 0 |  | 0 | 21.3807 | -1.6851 | 2058 | -5.7535 | -0.05521 | -0.058681 | -0.062291 | -0.066045 | -0.069947 | -0.073259 | -0.075928 | -0.078685 | -0.081533 | -0.084474 | -0.087511 | -0.090646 | -0.093884 | -0.097228 | -0.10068 | -0.044609 | 0.014328 | 0.013586 | 0.012799 | 0.011964 | 0.011079 | 0.010142 | 0.0091516 | 0.0081052 | 0.0070009 | 0.0058362 | 0.0046089 | 0.0033167 | 0.0041787 | 0.016653 | 0.030899 | 0.047123 | 0.065552 | 0.65853 | -0.24912 | -0.31884 | -21.3807 | 0 | 0 | -25.9141 | 0 | 0 | 0 | -53.902 | 0 | 0 | 0 | 0
2059 | Ongoing capital |  |  | 21.9152 | 0 | ed | 45 | 0 |  | 0 | 21.9152 | -1.5914 | 2059 | -5.5328 | -0.053171 | -0.056591 | -0.060148 | -0.063849 | -0.067696 | -0.071696 | -0.07509 | -0.077826 | -0.080653 | -0.083571 | -0.086586 | -0.089698 | -0.092913 | -0.096232 | -0.099658 | -0.1032 | -0.045724 | 0.014686 | 0.013926 | 0.013119 | 0.012263 | 0.011356 | 0.010396 | 0.0093804 | 0.0083079 | 0.0071759 | 0.0059821 | 0.0047242 | 0.0033996 | 0.0042831 | 0.017069 | 0.031672 | 0.048301 | 0.067191 | 0.675 | -0.25535 | -0.32681 | -21.9152 | 0 | -26.5619 | 0 | 0 | 0 | -54.9382 | 0 | 0 | 0 | 0
2060 | Ongoing capital |  |  | 22.4631 | 0 | ed | 45 | 0 |  | 0 | 22.4631 | -1.4996 | 2060 | -5.3121 | -0.051131 | -0.0545 | -0.058006 | -0.061652 | -0.065445 | -0.069389 | -0.073489 | -0.076968 | -0.079772 | -0.082669 | -0.085661 | -0.08875 | -0.091941 | -0.095235 | -0.098637 | -0.10215 | -0.10578 | -0.046867 | 0.015053 | 0.014274 | 0.013447 | 0.012569 | 0.01164 | 0.010655 | 0.0096149 | 0.0085156 | 0.0073553 | 0.0061317 | 0.0048423 | 0.0034846 | 0.0043902 | 0.017496 | 0.032464 | 0.049509 | 0.06887 | 0.69187 | -0.26173 | -0.33498 | -22.4631 | -27.226 | 0 | 0 | 0 | -56.0038 | 0 | 0 | 0 | 0
2061 | Ongoing capital |  |  | 23.0247 | 0 | ed | 45 | 0 |  |  | 23.0247 | -1.4996
2062 | Ongoing capital |  |  | 23.6003 | 0 | ed | 45 | 0 |  |  | 23.6003 | -1.4996
2063 | Ongoing capital |  |  | 24.1903 | 0 | ed | 45 | 0 |  |  | 24.1903 | -1.4996
2064 | Ongoing capital |  |  | 24.7951 | 0 | ed | 45 | 0 |  |  | 24.7951 | -1.4996
2065 | Ongoing capital |  |  | 25.4149 | 0 | ed | 45 | 0 |  |  | 25.4149 | -1.4996
* Life and salvage fields ignored when expenditure is an expense (type exp or atx). | [10 empty] | 1520.5001 | -1122.9598 | 2061 | -5.0914 | -0.049092 | -0.05241 | -0.055863 | -0.059456 | -0.063193 | -0.067081 | -0.071123 | -0.075326 | -0.078892 | -0.081766 | -0.084736 | -0.087802 | -0.090969 | -0.094239 | -0.097616 | -0.1011 | -0.1047 | -0.10842 | -0.048039 | 0.015429 | 0.014631 | 0.013783 | 0.012884 | 0.011931 | 0.010922 | 0.0098552 | 0.0087284 | 0.0075392 | 0.0062849 | 0.0049633 | 0.0035717 | 0.0045 | 0.017933 | 0.033275 | 0.050746 | 0.070592 | 0.70917 | -0.26827 | -0.34336 | -27.9066 | 0 | 0 | 0 | -34.0748 | 0 | 0 | 0 | 0
[13 empty] | 2062 | -4.8707 | -0.047052 | -0.050319 | -0.05372 | -0.057259 | -0.060942 | -0.064773 | -0.068758 | -0.072901 | -0.077209 | -0.080864 | -0.083811 | -0.086854 | -0.089997 | -0.093243 | -0.096595 | -0.10006 | -0.10363 | -0.10732 | -0.11113 | -0.04924 | 0.015815 | 0.014997 | 0.014128 | 0.013206 | 0.012229 | 0.011195 | 0.010102 | 0.0089467 | 0.0077276 | 0.0064421 | 0.0050874 | 0.003661 | 0.0046125 | 0.018382 | 0.034107 | 0.052015 | 0.072357 | 0.7269 | -0.27498 | -28.6043 | 0 | 0 | 0 | -34.2738
Operating Expenses (+) and Revenues (-) Over 45 Years (2021-2065) in $000 | [12 empty] | 2063 | -4.65 | -0.045012 | -0.048228 | -0.051577 | -0.055063 | -0.058691 | -0.062466 | -0.066393 | -0.070477 | -0.074724 | -0.079139 | -0.082886 | -0.085906 | -0.089025 | -0.092247 | -0.095574 | -0.09901 | -0.10256 | -0.10622 | -0.11 | -0.11391 | -0.050471 | 0.01621 | 0.015372 | 0.014481 | 0.013536 | 0.012535 | 0.011475 | 0.010354 | 0.0091703 | 0.0079208 | 0.0066031 | 0.0052146 | 0.0037525 | 0.0047278 | 0.018841 | 0.03496 | 0.053315 | 0.074166 | 0.74507 | -29.3194 | 0 | 0 | 0 | -34.5513
Year | a | b | c | d |  |  | Description |  |  |  | Esc% | NPV | 2064 | -4.4293 | -0.042973 | -0.046138 | -0.049434 | -0.052866 | -0.056439 | -0.060158 | -0.064027 | -0.068052 | -0.072239 | -0.076592 | -0.081118 | -0.084958 | -0.088054 | -0.091251 | -0.094553 | -0.097964 | -0.10149 | -0.10512 | -0.10888 | -0.11275 | -0.11676 | -0.051733 | 0.016616 | 0.015756 | 0.014843 | 0.013874 | 0.012848 | 0.011762 | 0.010613 | 0.0093996 | 0.0081188 | 0.0067682 | 0.0053449 | 0.0038463 | 0.004846 | 0.019312 | 0.035834 | 0.054648 | 0.07602 | -30.0524 | 0 | 0 | 0 | -35.8848
2021 | 14.7926 |  |  |  | a. | Annual Operations and Maintenance |  |  |  |  | 2.5 | -208.7639 | 2065 | -4.2086 | -0.040933 | -0.044047 | -0.047291 | -0.05067 | -0.054188 | -0.05785 | -0.061662 | -0.065628 | -0.069754 | -0.074045 | -0.078507 | -0.083146 | -0.087082 | -0.090255 | -0.093532 | -0.096917 | -0.10041 | -0.10402 | -0.10775 | -0.1116 | -0.11557 | -0.11968 | -0.053026 | 0.017031 | 0.01615 | 0.015214 | 0.014221 | 0.013169 | 0.012056 | 0.010878 | 0.0096346 | 0.0083218 | 0.0069374 | 0.0054786 | 0.0039425 | 0.0049671 | 0.019795 | 0.03673 | 0.056014 | -30.8037 | 0 | 0 | 0 | -36.5693
2022 | 14.7926 |  |  |  | b. | [5 empty] | 2.5 | 0 | 2066 | -3.9879 | -0.038893 | -0.041956 | -0.045148 | -0.048473 | -0.051937 | -0.055543 | -0.059297 | -0.063203 | -0.067269 | -0.071498 | -0.075896 | -0.080469 | -0.085224 | -0.089259 | -0.091581 | -0.092056 | -0.090542 | -0.086891 | -0.080947 | -0.072546 | -0.061516 | -0.047678 | -0.030841 | 0.061849 | 0.23605 | 0.42136 | 0.6183 | 0.82738 | 1.0492 | 1.2842 | 1.5331 | 1.7965 | 2.075 | 2.3693 | 2.68 | 3.0079 | 3.3565 | 3.7407 | 4.1642 | -31.5738 | 0 | 0 | 0 | -7.8689
2023 | 14.7926 |  |  |  | c. | [5 empty] | 2.5 | 0 | 2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 14.7926 |  |  |  | d. | [5 empty] | 2.5 | 0 | 2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 14.7926 | [10 empty] | -208.7639 | 2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 14.7926 | [11 empty] | 2070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 14.7926 | [11 empty] | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 14.7926 | [7 empty] | Total NPV ($000) |  |  | -1331.7237 | 45 | MaxCap
2029 | 14.7926 | [11 empty] | 0 | cap error
2030 | 14.7926 | [11 empty] | 0 | exp error
2031 | 14.7926 | [11 empty] | 0 | tot errors
2032 | 14.7926 | [9 empty] | Comments (press alt+enter to skip to new line)
2033 | 14.7926
2034 | 14.7926
2035 | 14.7926 | [11 empty] | 1 | -54.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.6531 | 0 | 0 | 0 | -64.6984
2036 | 14.7926 | [11 empty] | 2 | -53.2914 | -0.49946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.9194 | 0 | 0 | 0 | -64.7103
2037 | 14.7926 | [11 empty] | 3 | -52.5375 | -0.49249 | -0.51194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.1924 | 0 | 0 | 0 | -64.7344
2038 | 14.7926 | [11 empty] | 4 | -51.7837 | -0.48552 | -0.5048 | -0.52474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.4722 | 0 | 0 | 0 | -64.771
2039 | 14.7926 | [11 empty] | 5 | -51.0298 | -0.47856 | -0.49766 | -0.51742 | -0.53786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.759 | 0 | 0 | 0 | -64.8204
2040 | 14.7926
2041 | 14.7926
2042 | 14.7926
2043 | 14.7926
2044 | 14.7926
2045 | 14.7926
2046 | 14.7926
2047 | 14.7926
2048 | 14.7926
2049 | 14.7926
2050 | 14.7926
2051 | 14.7926
2052 | 14.7926
2053 | 14.7926
2054 | 14.7926
2055 | 14.7926
2056 | 14.7926
2057 | 14.7926
2058 | 14.7926
2059 | 14.7926
2060 | 14.7926
2061 | 14.7926
2062 | 14.7926
2063 | 14.7926
2064 | 14.7926
2065 | 14.7926
2066
2067
2068
2069
2070
Note on BK6: Jonathan: Starting in 2018, bonus depreciation no longer available to public utilities
Note on A7: Enter year of operation for capital, or year of occurrence for expenses. Timing is assumed to be beginning-of-year. Amounts entered outside of study period are ignored.
Note on C7: Enter project expenditures required to implement this alternative. Amounts already spent on a proposed project should be included as part of the project cost in the alternative that completes the project. In competing alternatives where the project is abandoned (such as status quo), any amounts already spent should be shown as an expense in the year the project is written off.
Note on E7: Enter cost in financial dollars, including contingency and overheads. For multi-year construction projects, enter cost for each expenditure type as lump sum in year of operation.
Note on F7: Accept default escalation rate, enter a different rate, or enter zero if cost is already escalated to year of expenditure (as it would be in a job estimate).
Note on G7: Capital Type Life ¦ Capital Type Life Buildings bldg 50 ¦ Power Plants: Communication equip comm 15 ¦ Combined cycle cc 30 Computer hardware comp 5 ¦ Combustion turbine ct 25 Computer software soft 5 ¦ Micro turbine mt 10 Electric dist (<69kV) ed 45 ¦ Hydro hyd 50 Electric trans (69kV+) et 55 ¦ Hydro additions hyda 20 Electric smart meter em 20 ¦ Nuclear nuc 15 Gas distribution gasd 55 ¦ Nuclear additions nuca 7 Gas meters gm 30 ¦ Biomass bio 25 Gas trans & storage gast 55 ¦ Fuel cell fcl 8 Gas held for resale gasc 99 ¦ Geothermal geo 25 Land easement ease 99 ¦ Solar photovoltaic pv 20 Land purchase land 99 ¦ Solar thermal st 25 Motor vehicles mv 10 ¦ Tidal or wave tdl 10 Office furniture furn 20 ¦ Waste wst 25 Electricity Storage bat 15 ¦ Wind wnd 25 Expense exp ¦ Expense, after-tax atx This is a partial listing of expenditure types. See EASOP Help tab or Economic Guide for additional guidance in selecting expenditure types.
Note on H7: Enter the expected life for each capital asset, even if it extends beyond the study period. EASOP retires each asset at the end of its life or the end of the study period, whichever occurs first, at the salvage specified.
Note on I7: Accept zero as default salvage value, enter a different value, or delete entry to use value calculated by EASOP. For most analyses, use 100% for land and 0% for all other expenditures.
Note on BK8: =IF(OR(AND(A8>2011,RIGHT(G8,3)="sbd"),AND(A8>2012,RIGHT(G8,2)="bd")),1,0)
Note on BK9: =IF(OR(AND(A9>2011,RIGHT(G9,3)="sbd"),AND(A9>2012,RIGHT(G9,2)="bd")),1,0)
Note on BK10: =IF(OR(AND(A10>2011,RIGHT(G10,3)="sbd"),AND(A10>2012,RIGHT(G10,2)="bd")),1,0)
Note on BK11: =IF(OR(AND(A11>2011,RIGHT(G11,3)="sbd"),AND(A11>2012,RIGHT(G11,2)="bd")),1,0)
Note on BK12: =IF(OR(AND(A12>2011,RIGHT(G12,3)="sbd"),AND(A12>2012,RIGHT(G12,2)="bd")),1,0)
Note on BK13: =IF(OR(AND(A13>2011,RIGHT(G13,3)="sbd"),AND(A13>2012,RIGHT(G13,2)="bd")),1,0)
Note on BK14: =IF(OR(AND(A14>2011,RIGHT(G14,3)="sbd"),AND(A14>2012,RIGHT(G14,2)="bd")),1,0)
Note on BK15: =IF(OR(AND(A15>2011,RIGHT(G15,3)="sbd"),AND(A15>2012,RIGHT(G15,2)="bd")),1,0)
Note on BK16: =IF(OR(AND(A16>2011,RIGHT(G16,3)="sbd"),AND(A16>2012,RIGHT(G16,2)="bd")),1,0)
Note on BK17: =IF(OR(AND(A17>2011,RIGHT(G17,3)="sbd"),AND(A17>2012,RIGHT(G17,2)="bd")),1,0)
Note on BK18: =IF(OR(AND(A18>2011,RIGHT(G18,3)="sbd"),AND(A18>2012,RIGHT(G18,2)="bd")),1,0)
Note on BK19: =IF(OR(AND(A19>2011,RIGHT(G19,3)="sbd"),AND(A19>2012,RIGHT(G19,2)="bd")),1,0)
Note on BK20: =IF(OR(AND(A20>2011,RIGHT(G20,3)="sbd"),AND(A20>2012,RIGHT(G20,2)="bd")),1,0)
Note on BK21: =IF(OR(AND(A21>2011,RIGHT(G21,3)="sbd"),AND(A21>2012,RIGHT(G21,2)="bd")),1,0)
Note on BK22: =IF(OR(AND(A22>2011,RIGHT(G22,3)="sbd"),AND(A22>2012,RIGHT(G22,2)="bd")),1,0)
Note on BK23: =IF(OR(AND(A23>2011,RIGHT(G23,3)="sbd"),AND(A23>2012,RIGHT(G23,2)="bd")),1,0)
Note on BK24: =IF(OR(AND(A24>2011,RIGHT(G24,3)="sbd"),AND(A24>2012,RIGHT(G24,2)="bd")),1,0)
Note on BK25: =IF(OR(AND(A25>2011,RIGHT(G25,3)="sbd"),AND(A25>2012,RIGHT(G25,2)="bd")),1,0)
Note on BK26: =IF(OR(AND(A26>2011,RIGHT(G26,3)="sbd"),AND(A26>2012,RIGHT(G26,2)="bd")),1,0)
Note on BK27: =IF(OR(AND(A27>2011,RIGHT(G27,3)="sbd"),AND(A27>2012,RIGHT(G27,2)="bd")),1,0)
Note on BK28: =IF(OR(AND(A28>2011,RIGHT(G28,3)="sbd"),AND(A28>2012,RIGHT(G28,2)="bd")),1,0)
Note on BK29: =IF(OR(AND(A29>2011,RIGHT(G29,3)="sbd"),AND(A29>2012,RIGHT(G29,2)="bd")),1,0)
Note on BK30: =IF(OR(AND(A30>2011,RIGHT(G30,3)="sbd"),AND(A30>2012,RIGHT(G30,2)="bd")),1,0)
Note on BK31: =IF(OR(AND(A31>2011,RIGHT(G31,3)="sbd"),AND(A31>2012,RIGHT(G31,2)="bd")),1,0)
Note on BK32: =IF(OR(AND(A32>2011,RIGHT(G32,3)="sbd"),AND(A32>2012,RIGHT(G32,2)="bd")),1,0)
Note on BK33: =IF(OR(AND(A33>2011,RIGHT(G33,3)="sbd"),AND(A33>2012,RIGHT(G33,2)="bd")),1,0)
Note on BK34: =IF(OR(AND(A34>2011,RIGHT(G34,3)="sbd"),AND(A34>2012,RIGHT(G34,2)="bd")),1,0)
Note on BK35: =IF(OR(AND(A35>2011,RIGHT(G35,3)="sbd"),AND(A35>2012,RIGHT(G35,2)="bd")),1,0)
Note on BK36: =IF(OR(AND(A36>2011,RIGHT(G36,3)="sbd"),AND(A36>2012,RIGHT(G36,2)="bd")),1,0)
Note on BK37: =IF(OR(AND(A37>2011,RIGHT(G37,3)="sbd"),AND(A37>2012,RIGHT(G37,2)="bd")),1,0)
Note on BK38: =IF(OR(AND(A38>2011,RIGHT(G38,3)="sbd"),AND(A38>2012,RIGHT(G38,2)="bd")),1,0)
Note on BK39: =IF(OR(AND(A39>2011,RIGHT(G39,3)="sbd"),AND(A39>2012,RIGHT(G39,2)="bd")),1,0)
Note on BK40: =IF(OR(AND(A40>2011,RIGHT(G40,3)="sbd"),AND(A40>2012,RIGHT(G40,2)="bd")),1,0)
Note on BK41: =IF(OR(AND(A41>2011,RIGHT(G41,3)="sbd"),AND(A41>2012,RIGHT(G41,2)="bd")),1,0)
Note on BK42: =IF(OR(AND(A42>2011,RIGHT(G42,3)="sbd"),AND(A42>2012,RIGHT(G42,2)="bd")),1,0)
Note on BK43: =IF(OR(AND(A43>2011,RIGHT(G43,3)="sbd"),AND(A43>2012,RIGHT(G43,2)="bd")),1,0)
Note on BK44: =IF(OR(AND(A44>2011,RIGHT(G44,3)="sbd"),AND(A44>2012,RIGHT(G44,2)="bd")),1,0)
Note on BK45: =IF(OR(AND(A45>2011,RIGHT(G45,3)="sbd"),AND(A45>2012,RIGHT(G45,2)="bd")),1,0)
Note on BK46: =IF(OR(AND(A46>2011,RIGHT(G46,3)="sbd"),AND(A46>2012,RIGHT(G46,2)="bd")),1,0)
Note on BK47: =IF(OR(AND(A47>2011,RIGHT(G47,3)="sbd"),AND(A47>2012,RIGHT(G47,2)="bd")),1,0)
Note on A56: Timing of operating expenses and revenues is assumed to be end-of-year. Amounts entered beyond study period are ignored.
Note on H56: Enter recurring expenses and revenues (assuming no cost-of-service regulation) for this alternative. If a project will result in savings, enter them as a cost under status quo or as a savings under the proposed project, but not as both in the same evaluation.
Note on L56: Accept default escalation rate, enter a different rate, or enter zero if cost or revenue stream already includes escalation.

## 3 All UG
Underground vs. Overhead Analysis
Alternative 3 - All Underground
Project Expenditures Over 45 Years (2021-2065) in $000 * | [7 empty] | Salvage% |  |  | Escalated | [47 empty] | life | salvage | ITC | BD
Year |  | Description |  | Cost | Esc% | Type | Life | Input | Calcd |  | Cost | NPV | boy | cap1 | cap2 | cap3 | cap4 | cap5 | cap6 | cap7 | cap8 | cap9 | cap10 | cap11 | cap12 | cap13 | cap14 | cap15 | cap16 | cap17 | cap18 | cap19 | cap20 | cap21 | cap22 | cap23 | cap24 | cap25 | cap26 | cap27 | cap28 | cap29 | cap30 | cap31 | cap32 | cap33 | cap34 | cap35 | cap36 | cap37 | cap38 | cap39 | cap40 | exp a | exp b | exp c | exp d | total acf | error | error | Check | Error
2021 | Underground CapEx |  |  | 2763.2303 | 2.5 | ed | 47 | 0 |  | 0 | 2695.8345 | -2723.8403 | 2021 | -2695.8345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2695.8345 | 0 | 0 | 0 | 0
2022 | Ongoing capital |  |  | 4.9647 | 0 | ed | 47 | 0 |  | 0 | 4.9647 | -4.6959 | 2022 | -41.2067 | -4.9647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.099 | 0 | 0 | 0 | -48.2704 | 0 | 0 | 0 | 0
2023 | Ongoing capital |  |  | 5.0888 | 0 | ed | 47 | 0 |  | 0 | 5.0888 | -4.5057 | 2023 | -33.0007 | -0.075887 | -5.0888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1514 | 0 | 0 | 0 | -40.3169 | 0 | 0 | 0 | 0
2024 | Ongoing capital |  |  | 5.2161 | 0 | ed | 47 | 0 |  | 0 | 5.2161 | -4.3231 | 2024 | 89.4172 | -0.060775 | -0.077785 | -5.2161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2052 | 0 | 0 | 0 | 81.8574 | 0 | 0 | 0 | 0
2025 | Ongoing capital |  |  | 5.3465 | 0 | ed | 47 | 0 |  | 0 | 5.3465 | -4.1478 | 2025 | 9.1233 | 0.16467 | -0.062294 | -0.079729 | -5.3465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2603 | 0 | 0 | 0 | 1.5391 | 0 | 0 | 0 | 0
2026 | Ongoing capital |  |  | 5.4801 | 0 | ed | 47 | 0 |  | 0 | 5.4801 | -3.9795 | 2026 | 6.7224 | 0.016802 | 0.16879 | -0.063852 | -0.081722 | -5.4801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3169 | 0 | 0 | 0 | -1.0346 | 0 | 0 | 0 | 0
2027 | Ongoing capital |  |  | 5.6171 | 0 | ed | 47 | 0 |  | 0 | 5.6171 | -3.8178 | 2027 | 4.5182 | 0.01238 | 0.017222 | 0.17301 | -0.065448 | -0.083765 | -5.6171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3748 | 0 | 0 | 0 | -3.4203 | 0 | 0 | 0 | 0
2028 | Ongoing capital |  |  | 5.7575 | 0 | ed | 47 | 0 |  | 0 | 5.7575 | -3.6625 | 2028 | 2.4959 | 0.0083208 | 0.01269 | 0.017652 | 0.17733 | -0.067084 | -0.08586 | -5.7575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4341 | 0 | 0 | 0 | -5.6327 | 0 | 0 | 0 | 0
2029 | Ongoing capital |  |  | 5.9015 | 0 | ed | 47 | 0 |  | 0 | 5.9015 | -3.5134 | 2029 | 0.64195 | 0.0045965 | 0.0085288 | 0.013007 | 0.018094 | 0.18177 | -0.068761 | -0.088006 | -5.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.495 | 0 | 0 | 0 | -7.6853 | 0 | 0 | 0 | 0
2030 | Ongoing capital |  |  | 6.049 | 0 | ed | 47 | 0 |  | 0 | 6.049 | -3.3701 | 2030 | 0.52226 | 0.0011822 | 0.0047115 | 0.008742 | 0.013332 | 0.018546 | 0.18631 | -0.07048 | -0.090206 | -6.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5574 | 0 | 0 | 0 | -8.012 | 0 | 0 | 0 | 0
2031 | Ongoing capital |  |  | 6.2002 | 0 | ed | 47 | 0 |  | 0 | 6.2002 | -3.2326 | 2031 | 0.74389 | 0.0009618 | 0.0012118 | 0.0048292 | 0.0089606 | 0.013665 | 0.01901 | 0.19097 | -0.072242 | -0.092461 | -6.2002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6213 | 0 | 0 | 0 | -8.0028 | 0 | 0 | 0 | 0
2032 | Ongoing capital |  |  | 6.3553 | 0 | ed | 47 | 0 |  | 0 | 6.3553 | -3.1004 | 2032 | 0.96552 | 0.00137 | 0.00098585 | 0.0012421 | 0.00495 | 0.0091846 | 0.014007 | 0.019485 | 0.19574 | -0.074048 | -0.094773 | -6.3553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6868 | 0 | 0 | 0 | -7.9984 | 0 | 0 | 0 | 0
2033 | Ongoing capital |  |  | 6.5141 | 0 | ed | 47 | 0 |  | 0 | 6.5141 | -2.9735 | 2033 | 1.1872 | 0.0017781 | 0.0014042 | 0.0010105 | 0.0012731 | 0.0050737 | 0.0094142 | 0.014357 | 0.019972 | 0.20064 | -0.0759 | -0.097142 | -6.5141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.754 | 0 | 0 | 0 | -7.9991 | 0 | 0 | 0 | 0
2034 | Ongoing capital |  |  | 6.677 | 0 | ed | 47 | 0 |  | 0 | 6.677 | -2.8515 | 2034 | 1.4088 | 0.0021863 | 0.0018226 | 0.0014393 | 0.0010358 | 0.001305 | 0.0052006 | 0.0096496 | 0.014716 | 0.020471 | 0.20565 | -0.077797 | -0.099571 | -6.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8229 | 0 | 0 | 0 | -8.005 | 0 | 0 | 0 | 0
2035 | Ongoing capital |  |  | 6.8439 | 0 | ed | 47 | 0 |  | 0 | 6.8439 | -2.7343 | 2035 | 1.6304 | 0.0025945 | 0.002241 | 0.0018682 | 0.0014753 | 0.0010617 | 0.0013376 | 0.0053306 | 0.0098908 | 0.015084 | 0.020983 | 0.2108 | -0.079742 | -0.10206 | -6.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8934 | 0 | 0 | 0 | -8.0161 | 0 | 0 | 0 | 0
2036 | Ongoing capital |  |  | 7.015 | 0 | ed | 47 | 0 |  | 0 | 7.015 | -2.6217 | 2036 | 1.8521 | 0.0030026 | 0.0026593 | 0.002297 | 0.0019149 | 0.0015122 | 0.0010882 | 0.001371 | 0.0054638 | 0.010138 | 0.015461 | 0.021508 | 0.21607 | -0.081736 | -0.10461 | -7.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9658 | 0 | 0 | 0 | -8.0326 | 0 | 0 | 0 | 0
2037 | Ongoing capital |  |  | 7.1904 | 0 | ed | 47 | 0 |  | 0 | 7.1904 | -2.5134 | 2037 | 2.0737 | 0.0034108 | 0.0030777 | 0.0027258 | 0.0023544 | 0.0019627 | 0.00155 | 0.0011154 | 0.0014053 | 0.0056004 | 0.010392 | 0.015848 | 0.022045 | 0.22147 | -0.083779 | -0.10723 | -7.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0399 | 0 | 0 | 0 | -8.0547 | 0 | 0 | 0 | 0
2038 | Ongoing capital |  |  | 7.3701 | 0 | ed | 47 | 0 |  | 0 | 7.3701 | -2.4094 | 2038 | 2.2953 | 0.003819 | 0.0034961 | 0.0031546 | 0.002794 | 0.0024133 | 0.0020118 | 0.0015887 | 0.0011433 | 0.0014404 | 0.0057405 | 0.010651 | 0.016244 | 0.022596 | 0.227 | -0.085873 | -0.10991 | -7.3701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1159 | 0 | 0 | 0 | -8.0824 | 0 | 0 | 0 | 0
2039 | Ongoing capital |  |  | 7.5544 | 0 | ed | 47 | 0 |  | 0 | 7.5544 | -2.3094 | 2039 | 2.517 | 0.0042271 | 0.0039144 | 0.0035835 | 0.0032335 | 0.0028638 | 0.0024736 | 0.0020621 | 0.0016285 | 0.0011719 | 0.0014764 | 0.005884 | 0.010918 | 0.01665 | 0.023161 | 0.23268 | -0.08802 | -0.11266 | -7.5544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1938 | 0 | 0 | 0 | -8.116 | 0 | 0 | 0 | 0
2040 | Ongoing capital |  |  | 7.7433 | 0 | ed | 47 | 0 |  | 0 | 7.7433 | -2.2132 | 2040 | 2.7386 | 0.0046353 | 0.0043328 | 0.0040123 | 0.0036731 | 0.0033143 | 0.0029354 | 0.0025354 | 0.0021136 | 0.0016692 | 0.0012012 | 0.0015133 | 0.0060311 | 0.011191 | 0.017066 | 0.02374 | 0.2385 | -0.090221 | -0.11547 | -7.7433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2737 | 0 | 0 | 0 | -8.1556 | 0 | 0 | 0 | 0
2041 | Ongoing capital |  |  | 7.9368 | 0 | ed | 47 | 0 |  | 0 | 7.9368 | -2.1207 | 2041 | 2.9602 | 0.0050435 | 0.0047512 | 0.0044411 | 0.0041126 | 0.0037649 | 0.0033972 | 0.0030088 | 0.0025988 | 0.0021665 | 0.0017109 | 0.0012312 | 0.0015512 | 0.0061818 | 0.01147 | 0.017493 | 0.024334 | 0.24446 | -0.092476 | -0.11836 | -7.9368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3555 | 0 | 0 | 0 | -8.2012 | 0 | 0 | 0 | 0
2042 | Ongoing capital |  |  | 8.1353 | 0 | ed | 47 | 0 |  | 0 | 8.1353 | -2.0317 | 2042 | -9.447 | 0.0054516 | 0.0051695 | 0.00487 | 0.0045522 | 0.0042154 | 0.003859 | 0.0034821 | 0.003084 | 0.0026638 | 0.0022206 | 0.0017537 | 0.001262 | 0.00159 | 0.0063364 | 0.011757 | 0.01793 | 0.024942 | 0.25057 | -0.094788 | -0.12132 | -8.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4394 | 0 | 0 | 0 | -20.8821 | 0 | 0 | 0 | 0
2043 | Ongoing capital |  |  | 8.3386 | 0 | ed | 47 | 0 |  | 0 | 8.3386 | -1.9461 | 2043 | -21.8543 | -0.017398 | 0.0055879 | 0.0052988 | 0.0049917 | 0.004666 | 0.0043208 | 0.0039555 | 0.0035692 | 0.0031611 | 0.0027304 | 0.0022762 | 0.0017975 | 0.0012935 | 0.0016297 | 0.0064948 | 0.012051 | 0.018378 | 0.025566 | 0.25683 | -0.097158 | -0.12435 | -8.3386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5254 | 0 | 0 | 0 | -33.5926 | 0 | 0 | 0 | 0
2044 | Ongoing capital |  |  | 8.5471 | 0 | ed | 47 | 0 |  | 0 | 8.5471 | -1.8638 | 2044 | -21.6327 | -0.040247 | -0.017833 | 0.0057276 | 0.0054312 | 0.0051165 | 0.0047826 | 0.0044288 | 0.0040544 | 0.0036584 | 0.0032401 | 0.0027986 | 0.0023331 | 0.0018425 | 0.0013259 | 0.0016705 | 0.0066572 | 0.012352 | 0.018838 | 0.026205 | 0.26325 | -0.099587 | -0.12746 | -8.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6135 | 0 | 0 | 0 | -33.7047 | 0 | 0 | 0 | 0
2045 | Ongoing capital |  |  | 8.7608 | 0 | ed | 47 | 0 |  | 0 | 8.7608 | -1.7844 | 2045 | -21.411 | -0.039839 | -0.041254 | -0.018279 | 0.0058708 | 0.005567 | 0.0052444 | 0.0049022 | 0.0045395 | 0.0041557 | 0.0037499 | 0.0033211 | 0.0028686 | 0.0023914 | 0.0018885 | 0.001359 | 0.0017122 | 0.0068236 | 0.012661 | 0.019309 | 0.02686 | 0.26984 | -0.10208 | -0.13065 | -8.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7038 | 0 | 0 | 0 | -33.8247 | 0 | 0 | 0 | 0
2046 | Ongoing capital |  |  | 8.9798 | 0 | ed | 47 | 0 |  | 0 | 8.9798 | -1.7079 | 2046 | -21.1894 | -0.039431 | -0.040835 | -0.042285 | -0.018736 | 0.0060176 | 0.0057062 | 0.0053755 | 0.0050247 | 0.004653 | 0.0042596 | 0.0038436 | 0.0034042 | 0.0029403 | 0.0024512 | 0.0019357 | 0.001393 | 0.001755 | 0.0069942 | 0.012978 | 0.019791 | 0.027531 | 0.27658 | -0.10463 | -0.13391 | -8.9798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7964 | 0 | 0 | 0 | -33.9528 | 0 | 0 | 0 | 0
2047 | Ongoing capital |  |  | 9.2043 | 0 | ed | 47 | 0 |  | 0 | 9.2043 | -1.634 | 2047 | -20.9678 | -0.039023 | -0.040417 | -0.041856 | -0.043342 | -0.019204 | 0.006168 | 0.0058489 | 0.0055099 | 0.0051503 | 0.0047694 | 0.0043661 | 0.0039397 | 0.0034893 | 0.0030138 | 0.0025125 | 0.0019841 | 0.0014278 | 0.0017989 | 0.007169 | 0.013302 | 0.020286 | 0.02822 | 0.2835 | -0.10724 | -0.13726 | -9.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8913 | 0 | 0 | 0 | -34.0893 | 0 | 0 | 0 | 0
2048 | Ongoing capital |  |  | 9.4344 | 0 | ed | 47 | 0 |  | 0 | 9.4344 | -1.5624 | 2048 | -20.7461 | -0.038615 | -0.039999 | -0.041427 | -0.042903 | -0.044426 | -0.019684 | 0.0063222 | 0.0059951 | 0.0056477 | 0.0052791 | 0.0048886 | 0.0044753 | 0.0040382 | 0.0035765 | 0.0030892 | 0.0025753 | 0.0020337 | 0.0014635 | 0.0018439 | 0.0073483 | 0.013635 | 0.020793 | 0.028925 | 0.29058 | -0.10993 | -0.14069 | -9.4344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9886 | 0 | 0 | 0 | -34.2343 | 0 | 0 | 0 | 0
2049 | Ongoing capital |  |  | 9.6703 | 0 | ed | 47 | 0 |  | 0 | 9.6703 | -1.4931 | 2049 | -20.5245 | -0.038207 | -0.03958 | -0.040998 | -0.042463 | -0.043975 | -0.045536 | -0.020176 | 0.0064803 | 0.006145 | 0.0057888 | 0.0054111 | 0.0050108 | 0.0045871 | 0.0041392 | 0.0036659 | 0.0031664 | 0.0026397 | 0.0020846 | 0.0015001 | 0.00189 | 0.007532 | 0.013975 | 0.021313 | 0.029648 | 0.29785 | -0.11267 | -0.14421 | -9.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0883 | 0 | 0 | 0 | -34.3881 | 0 | 0 | 0 | 0
2050 | Ongoing capital |  |  | 9.912 | 0 | ed | 47 | 0 |  | 0 | 9.912 | -1.4259 | 2050 | -20.3029 | -0.037798 | -0.039162 | -0.04057 | -0.042023 | -0.043525 | -0.045074 | -0.046675 | -0.020681 | 0.0066423 | 0.0062986 | 0.0059336 | 0.0055464 | 0.0051361 | 0.0047018 | 0.0042426 | 0.0037576 | 0.0032456 | 0.0027056 | 0.0021367 | 0.0015376 | 0.0019372 | 0.0077203 | 0.014325 | 0.021846 | 0.03039 | 0.30529 | -0.11549 | -0.14781 | -9.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1906 | 0 | 0 | 0 | -34.5509 | 0 | 0 | 0 | 0
2051 | Ongoing capital |  |  | 10.1598 | 0 | ed | 47 | 0 |  | 0 | 10.1598 | -1.3607 | 2051 | -20.0812 | -0.03739 | -0.038743 | -0.040141 | -0.041584 | -0.043074 | -0.044613 | -0.046201 | -0.047842 | -0.021198 | 0.0068083 | 0.006456 | 0.0060819 | 0.005685 | 0.0052645 | 0.0048194 | 0.0043487 | 0.0038515 | 0.0033267 | 0.0027733 | 0.0021901 | 0.001576 | 0.0019856 | 0.0079133 | 0.014683 | 0.022392 | 0.031149 | 0.31293 | -0.11838 | -0.15151 | -10.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2953 | 0 | 0 | 0 | -34.7228 | 0 | 0 | 0 | 0
2052 | Ongoing capital |  |  | 10.4138 | 0 | ed | 47 | 0 |  | 0 | 10.4138 | -1.2975 | 2052 | -19.8596 | -0.036982 | -0.038325 | -0.039712 | -0.041144 | -0.042623 | -0.044151 | -0.045728 | -0.047356 | -0.049038 | -0.021728 | 0.0069785 | 0.0066174 | 0.0062339 | 0.0058271 | 0.0053961 | 0.0049398 | 0.0044574 | 0.0039478 | 0.0034099 | 0.0028426 | 0.0022449 | 0.0016154 | 0.0020353 | 0.0081111 | 0.01505 | 0.022952 | 0.031928 | 0.32075 | -0.12134 | -0.1553 | -10.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4027 | 0 | 0 | 0 | -34.9042 | 0 | 0 | 0 | 0
2053 | Ongoing capital |  |  | 10.6742 | 0 | ed | 47 | 0 |  | 0 | 10.6742 | -1.236 | 2053 | -19.436 | -0.036574 | -0.037907 | -0.039283 | -0.040705 | -0.042173 | -0.043689 | -0.045255 | -0.046871 | -0.04854 | -0.050264 | -0.022271 | 0.007153 | 0.0067829 | 0.0063898 | 0.0059728 | 0.005531 | 0.0050633 | 0.0045689 | 0.0040465 | 0.0034951 | 0.0029137 | 0.002301 | 0.0016558 | 0.0020862 | 0.0083139 | 0.015426 | 0.023526 | 0.032726 | 0.32877 | -0.12437 | -0.15918 | -10.6742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5128 | 0 | 0 | 0 | -34.8933 | 0 | 0 | 0 | 0
2054 | Ongoing capital |  |  | 10.941 | 0 | ed | 47 | 0 |  | 0 | 10.941 | -1.1762 | 2054 | -18.8104 | -0.035794 | -0.037488 | -0.038854 | -0.040265 | -0.041722 | -0.043227 | -0.044781 | -0.046386 | -0.048043 | -0.049754 | -0.05152 | -0.022828 | 0.0073318 | 0.0069525 | 0.0065495 | 0.0061221 | 0.0056693 | 0.0051899 | 0.0046831 | 0.0041476 | 0.0035825 | 0.0029865 | 0.0023585 | 0.0016972 | 0.0021383 | 0.0085217 | 0.015812 | 0.024114 | 0.033544 | 0.33699 | -0.12748 | -0.16316 | -10.941 | 0 | 0 | 0 | 0 | 0 | 0 | -4.6256 | 0 | 0 | 0 | -34.69 | 0 | 0 | 0 | 0
2055 | Ongoing capital |  |  | 11.2146 | 0 | ed | 47 | 0 |  | 0 | 11.2146 | -1.118 | 2055 | -18.1848 | -0.034642 | -0.036689 | -0.038426 | -0.039826 | -0.041272 | -0.042765 | -0.044308 | -0.045901 | -0.047546 | -0.049244 | -0.050998 | -0.052808 | -0.023398 | 0.0075151 | 0.0071263 | 0.0067133 | 0.0062752 | 0.005811 | 0.0053197 | 0.0048002 | 0.0042513 | 0.0036721 | 0.0030612 | 0.0024175 | 0.0017396 | 0.0021918 | 0.0087348 | 0.016207 | 0.024717 | 0.034383 | 0.34541 | -0.13067 | -0.16724 | -11.2146 | 0 | 0 | 0 | 0 | 0 | -4.7412 | 0 | 0 | 0 | -34.496 | 0 | 0 | 0 | 0
2056 | Ongoing capital |  |  | 11.4949 | 0 | ed | 47 | 0 |  | 0 | 11.4949 | -1.0613 | 2056 | -17.5593 | -0.03349 | -0.035508 | -0.037606 | -0.039386 | -0.040821 | -0.042304 | -0.043835 | -0.045416 | -0.047048 | -0.048734 | -0.050475 | -0.052273 | -0.054128 | -0.023983 | 0.007703 | 0.0073044 | 0.0068811 | 0.0064321 | 0.0059563 | 0.0054527 | 0.0049202 | 0.0043576 | 0.0037639 | 0.0031377 | 0.0024779 | 0.0017831 | 0.0022466 | 0.0089532 | 0.016612 | 0.025335 | 0.035243 | 0.35405 | -0.13393 | -0.17142 | -11.4949 | 0 | 0 | 0 | 0 | -4.8598 | 0 | 0 | 0 | -34.3117 | 0 | 0 | 0 | 0
2057 | Ongoing capital |  |  | 11.7823 | 0 | ed | 47 | 0 |  | 0 | 11.7823 | -1.0059 | 2057 | -16.9337 | -0.032338 | -0.034327 | -0.036395 | -0.038546 | -0.040371 | -0.041842 | -0.043361 | -0.04493 | -0.046551 | -0.048225 | -0.049953 | -0.051737 | -0.053579 | -0.055482 | -0.024583 | 0.0078956 | 0.007487 | 0.0070531 | 0.0065929 | 0.0061052 | 0.005589 | 0.0050432 | 0.0044666 | 0.003858 | 0.0032162 | 0.0025398 | 0.0018277 | 0.0023027 | 0.009177 | 0.017028 | 0.025968 | 0.036124 | 0.3629 | -0.13728 | -0.1757 | -11.7823 | 0 | 0 | 0 | -4.9813 | 0 | 0 | 0 | -34.1373 | 0 | 0 | 0 | 0
2058 | Ongoing capital |  |  | 12.0768 | 0 | ed | 47 | 0 |  | 0 | 12.0768 | -0.95183 | 2058 | -16.3081 | -0.031186 | -0.033146 | -0.035185 | -0.037305 | -0.03951 | -0.04138 | -0.042888 | -0.044445 | -0.046054 | -0.047715 | -0.04943 | -0.051201 | -0.05303 | -0.054919 | -0.056869 | -0.025197 | 0.008093 | 0.0076742 | 0.0072295 | 0.0067577 | 0.0062578 | 0.0057287 | 0.0051692 | 0.0045782 | 0.0039544 | 0.0032966 | 0.0026033 | 0.0018734 | 0.0023603 | 0.0094064 | 0.017453 | 0.026617 | 0.037027 | 0.37197 | -0.14071 | -0.1801 | -12.0768 | 0 | 0 | -5.1058 | 0 | 0 | 0 | -33.973 | 0 | 0 | 0 | 0
2059 | Ongoing capital |  |  | 12.3788 | 0 | ed | 47 | 0 |  | 0 | 12.3788 | -0.8989 | 2059 | -15.6825 | -0.030033 | -0.031965 | -0.033975 | -0.036065 | -0.038238 | -0.040497 | -0.042415 | -0.04396 | -0.045556 | -0.047205 | -0.048908 | -0.050666 | -0.052482 | -0.054356 | -0.056292 | -0.05829 | -0.025827 | 0.0082953 | 0.0078661 | 0.0074102 | 0.0069266 | 0.0064143 | 0.0058719 | 0.0052985 | 0.0046927 | 0.0040533 | 0.003379 | 0.0026684 | 0.0019202 | 0.0024193 | 0.0096416 | 0.01789 | 0.027283 | 0.037952 | 0.38127 | -0.14423 | -0.1846 | -12.3788 | 0 | -5.2334 | 0 | 0 | 0 | -33.8191 | 0 | 0 | 0 | 0
2060 | Ongoing capital |  |  | 12.6882 | 0 | ed | 47 | 0 |  | 0 | 12.6882 | -0.84702 | 2060 | -15.057 | -0.028881 | -0.030784 | -0.032764 | -0.034824 | -0.036966 | -0.039194 | -0.04151 | -0.043475 | -0.045059 | -0.046695 | -0.048385 | -0.05013 | -0.051933 | -0.053794 | -0.055715 | -0.057699 | -0.059748 | -0.026473 | 0.0085027 | 0.0080627 | 0.0075955 | 0.0070998 | 0.0065746 | 0.0060187 | 0.0054309 | 0.00481 | 0.0041546 | 0.0034635 | 0.0027351 | 0.0019682 | 0.0024798 | 0.0098826 | 0.018337 | 0.027965 | 0.038901 | 0.3908 | -0.14784 | -0.18921 | -12.6882 | -5.3643 | 0 | 0 | 0 | -33.6758 | 0 | 0 | 0 | 0
2061 | Ongoing capital |  |  | 13.0054 | 0 | ed | 47 | 0 |  |  | 13.0054 | -0.84702
2062 | Ongoing capital |  |  | 13.3306 | 0 | ed | 47 | 0 |  |  | 13.3306 | -0.84702
2063 | Ongoing capital |  |  | 13.6638 | 0 | ed | 47 | 0 |  |  | 13.6638 | -0.84702
2064 | Ongoing capital |  |  | 14.0054 | 0 | ed | 47 | 0 |  |  | 14.0054 | -0.84702
2065 | Ongoing capital |  |  | 14.3556 | 0 | ed | 47 | 0 |  |  | 14.3556 | -0.84702
* Life and salvage fields ignored when expenditure is an expense (type exp or atx). |  |  |  | 14.7145 | [6 empty] | 3017.4636 | -2815.3387 | 2061 | -14.4314 | -0.027729 | -0.029603 | -0.031554 | -0.033583 | -0.035695 | -0.03789 | -0.040174 | -0.042548 | -0.044562 | -0.046186 | -0.047863 | -0.049595 | -0.051384 | -0.053231 | -0.055138 | -0.057108 | -0.059142 | -0.061241 | -0.027135 | 0.0087152 | 0.0082643 | 0.0077853 | 0.0072773 | 0.006739 | 0.0061692 | 0.0055667 | 0.0049302 | 0.0042585 | 0.00355 | 0.0028035 | 0.0020175 | 0.0025418 | 0.01013 | 0.018795 | 0.028664 | 0.039874 | 0.40057 | -0.15153 | -0.19394 | -5.4984 | 0 | 0 | 0 | -20.5379 | 0 | 0 | 0 | 0
[13 empty] | 2062 | -13.8058 | -0.026577 | -0.028423 | -0.030343 | -0.032343 | -0.034423 | -0.036587 | -0.038838 | -0.041178 | -0.043611 | -0.045676 | -0.04734 | -0.049059 | -0.050835 | -0.052668 | -0.054562 | -0.056517 | -0.058536 | -0.06062 | -0.062772 | -0.027813 | 0.0089331 | 0.0084709 | 0.00798 | 0.0074592 | 0.0069075 | 0.0063234 | 0.0057059 | 0.0050535 | 0.0043649 | 0.0036388 | 0.0028736 | 0.0020679 | 0.0026053 | 0.010383 | 0.019265 | 0.029381 | 0.040871 | 0.41059 | -0.15532 | -5.6358 | 0 | 0 | 0 | -19.8928
Operating Expenses (+) and Revenues (-) Over 45 Years (2021-2065) in $000 | [12 empty] | 2063 | -13.1802 | -0.025425 | -0.027242 | -0.029133 | -0.031102 | -0.033151 | -0.035284 | -0.037502 | -0.039809 | -0.042208 | -0.044702 | -0.046818 | -0.048524 | -0.050286 | -0.052106 | -0.053985 | -0.055926 | -0.05793 | -0.059999 | -0.062136 | -0.064342 | -0.028508 | 0.0091564 | 0.0086827 | 0.0081795 | 0.0076457 | 0.0070801 | 0.0064815 | 0.0058485 | 0.0051798 | 0.0044741 | 0.0037298 | 0.0029454 | 0.0021196 | 0.0026705 | 0.010642 | 0.019747 | 0.030115 | 0.041892 | 0.42085 | -5.7767 | 0 | 0 | 0 | -19.2856
Year | a | b | c | d |  |  | Description |  |  |  | Esc% | NPV | 2064 | -12.5547 | -0.024273 | -0.026061 | -0.027923 | -0.029861 | -0.03188 | -0.03398 | -0.036166 | -0.038439 | -0.040804 | -0.043263 | -0.045819 | -0.047988 | -0.049737 | -0.051543 | -0.053408 | -0.055335 | -0.057324 | -0.059378 | -0.061499 | -0.063689 | -0.06595 | -0.029221 | 0.0093854 | 0.0088997 | 0.008384 | 0.0078369 | 0.0072571 | 0.0066435 | 0.0059947 | 0.0053093 | 0.0045859 | 0.003823 | 0.0030191 | 0.0021726 | 0.0027372 | 0.010909 | 0.020241 | 0.030868 | 0.04294 | -5.9211 | 0 | 0 | 0 | -19.2683
2021 | 2.9146 |  |  |  | a. | Operations and Maintenance |  |  |  |  | 2.5 | -41.1322 | 2065 | -11.9291 | -0.023121 | -0.02488 | -0.026712 | -0.028621 | -0.030608 | -0.032677 | -0.03483 | -0.03707 | -0.0394 | -0.041824 | -0.044344 | -0.046965 | -0.049188 | -0.05098 | -0.052831 | -0.054743 | -0.056718 | -0.058757 | -0.060862 | -0.063037 | -0.065281 | -0.067599 | -0.029952 | 0.00962 | 0.0091222 | 0.0085936 | 0.0080328 | 0.0074386 | 0.0068096 | 0.0061446 | 0.0054421 | 0.0047006 | 0.0039186 | 0.0030946 | 0.0022269 | 0.0028057 | 0.011181 | 0.020747 | 0.03164 | -6.0692 | 0 | 0 | 0 | -18.8777
2022 | 2.9146 |  |  |  | b. | [5 empty] | 2.5 | 0 | 2066 | -11.3035 | -0.021969 | -0.023699 | -0.025502 | -0.02738 | -0.029336 | -0.031373 | -0.033494 | -0.0357 | -0.037997 | -0.040385 | -0.04287 | -0.045453 | -0.048139 | -0.050418 | -0.051729 | -0.051997 | -0.051142 | -0.04908 | -0.045723 | -0.040977 | -0.034747 | -0.026931 | -0.017421 | 0.034935 | 0.13333 | 0.23801 | 0.34924 | 0.46734 | 0.59262 | 0.72538 | 0.86598 | 1.0147 | 1.1721 | 1.3383 | 1.5138 | 1.699 | 1.8959 | 2.1129 | 2.3521 | -6.2209 | 0 | 0 | 0 | -1.8822
2023 | 2.9146 |  |  |  | c. | [5 empty] | 2.5 | 0 | 2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 2.9146 |  |  |  | d. | [5 empty] | 2.5 | 0 | 2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 2.9146 | [10 empty] | -41.1322 | 2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 2.9146 | [11 empty] | 2070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 2.9146 | [11 empty] | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 2.9146 | [10 empty] | -2856.4709 | 45 | MaxCap
2029 | 2.9146 | [11 empty] | 0 | cap error
2030 | 2.9146 | [11 empty] | 0 | exp error
2031 | 2.9146 | [11 empty] | 0 | tot errors
2032 | 2.9146 | [9 empty] | Comments (press alt+enter to skip to new line)
2033 | 2.9146
2034 | 2.9146
2035 | 2.9146 | [11 empty] | 1 | -153.1893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.099 | 0 | 0 | 0 | -155.2883
2036 | 2.9146 | [11 empty] | 2 | -151.0525 | -0.28212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1514 | 0 | 0 | 0 | -153.4861
2037 | 2.9146 | [11 empty] | 3 | -148.9157 | -0.27818 | -0.28917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2052 | 0 | 0 | 0 | -151.6883
2038 | 2.9146 | [11 empty] | 4 | -146.779 | -0.27425 | -0.28514 | -0.2964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2603 | 0 | 0 | 0 | -149.8951
2039 | 2.9146 | [11 empty] | 5 | -144.6422 | -0.27031 | -0.2811 | -0.29227 | -0.30381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3169 | 0 | 0 | 0 | -148.1065
2040 | 2.9146
2041 | 2.9146
2042 | 2.9146
2043 | 2.9146
2044 | 2.9146
2045 | 2.9146
2046 | 2.9146
2047 | 2.9146
2048 | 2.9146
2049 | 2.9146
2050 | 2.9146
2051 | 2.9146
2052 | 2.9146
2053 | 2.9146
2054 | 2.9146
2055 | 2.9146
2056 | 2.9146
2057 | 2.9146
2058 | 2.9146
2059 | 2.9146
2060 | 2.9146
2061 | 2.9146
2062 | 2.9146
2063 | 2.9146
2064 | 2.9146
2065 | 2.9146
2066
2067
2068
2069
2070
Note on BK6: Jonathan: Starting in 2018, bonus depreciation no longer available to public utilities
Note on A7: Enter year of operation for capital, or year of occurrence for expenses. Timing is assumed to be beginning-of-year. Amounts entered outside of study period are ignored.
Note on C7: Enter project expenditures required to implement this alternative. Amounts already spent on a proposed project should be included as part of the project cost in the alternative that completes the project. In competing alternatives where the project is abandoned (such as status quo), any amounts already spent should be shown as an expense in the year the project is written off.
Note on E7: Enter cost in financial dollars, including contingency and overheads. For multi-year construction projects, enter cost for each expenditure type as lump sum in year of operation.
Note on F7: Accept default escalation rate, enter a different rate, or enter zero if cost is already escalated to year of expenditure (as it would be in a job estimate).
Note on G7: Capital Type Life ¦ Capital Type Life Buildings bldg 50 ¦ Power Plants: Communication equip comm 15 ¦ Combined cycle cc 30 Computer hardware comp 5 ¦ Combustion turbine ct 25 Computer software soft 5 ¦ Micro turbine mt 10 Electric dist (<69kV) ed 45 ¦ Hydro hyd 50 Electric trans (69kV+) et 55 ¦ Hydro additions hyda 20 Electric smart meter em 20 ¦ Nuclear nuc 15 Gas distribution gasd 55 ¦ Nuclear additions nuca 7 Gas meters gm 30 ¦ Biomass bio 25 Gas trans & storage gast 55 ¦ Fuel cell fcl 8 Gas held for resale gasc 99 ¦ Geothermal geo 25 Land easement ease 99 ¦ Solar photovoltaic pv 20 Land purchase land 99 ¦ Solar thermal st 25 Motor vehicles mv 10 ¦ Tidal or wave tdl 10 Office furniture furn 20 ¦ Waste wst 25 Electricity Storage bat 15 ¦ Wind wnd 25 Expense exp ¦ Expense, after-tax atx This is a partial listing of expenditure types. See EASOP Help tab or Economic Guide for additional guidance in selecting expenditure types.
Note on H7: Enter the expected life for each capital asset, even if it extends beyond the study period. EASOP retires each asset at the end of its life or the end of the study period, whichever occurs first, at the salvage specified.
Note on I7: Accept zero as default salvage value, enter a different value, or delete entry to use value calculated by EASOP. For most analyses, use 100% for land and 0% for all other expenditures.
Note on BK8: =IF(OR(AND(A8>2011,RIGHT(G8,3)="sbd"),AND(A8>2012,RIGHT(G8,2)="bd")),1,0)
Note on BK9: =IF(OR(AND(A9>2011,RIGHT(G9,3)="sbd"),AND(A9>2012,RIGHT(G9,2)="bd")),1,0)
Note on BK10: =IF(OR(AND(A10>2011,RIGHT(G10,3)="sbd"),AND(A10>2012,RIGHT(G10,2)="bd")),1,0)
Note on BK11: =IF(OR(AND(A11>2011,RIGHT(G11,3)="sbd"),AND(A11>2012,RIGHT(G11,2)="bd")),1,0)
Note on BK12: =IF(OR(AND(A12>2011,RIGHT(G12,3)="sbd"),AND(A12>2012,RIGHT(G12,2)="bd")),1,0)
Note on BK13: =IF(OR(AND(A13>2011,RIGHT(G13,3)="sbd"),AND(A13>2012,RIGHT(G13,2)="bd")),1,0)
Note on BK14: =IF(OR(AND(A14>2011,RIGHT(G14,3)="sbd"),AND(A14>2012,RIGHT(G14,2)="bd")),1,0)
Note on BK15: =IF(OR(AND(A15>2011,RIGHT(G15,3)="sbd"),AND(A15>2012,RIGHT(G15,2)="bd")),1,0)
Note on BK16: =IF(OR(AND(A16>2011,RIGHT(G16,3)="sbd"),AND(A16>2012,RIGHT(G16,2)="bd")),1,0)
Note on BK17: =IF(OR(AND(A17>2011,RIGHT(G17,3)="sbd"),AND(A17>2012,RIGHT(G17,2)="bd")),1,0)
Note on BK18: =IF(OR(AND(A18>2011,RIGHT(G18,3)="sbd"),AND(A18>2012,RIGHT(G18,2)="bd")),1,0)
Note on BK19: =IF(OR(AND(A19>2011,RIGHT(G19,3)="sbd"),AND(A19>2012,RIGHT(G19,2)="bd")),1,0)
Note on BK20: =IF(OR(AND(A20>2011,RIGHT(G20,3)="sbd"),AND(A20>2012,RIGHT(G20,2)="bd")),1,0)
Note on BK21: =IF(OR(AND(A21>2011,RIGHT(G21,3)="sbd"),AND(A21>2012,RIGHT(G21,2)="bd")),1,0)
Note on BK22: =IF(OR(AND(A22>2011,RIGHT(G22,3)="sbd"),AND(A22>2012,RIGHT(G22,2)="bd")),1,0)
Note on BK23: =IF(OR(AND(A23>2011,RIGHT(G23,3)="sbd"),AND(A23>2012,RIGHT(G23,2)="bd")),1,0)
Note on BK24: =IF(OR(AND(A24>2011,RIGHT(G24,3)="sbd"),AND(A24>2012,RIGHT(G24,2)="bd")),1,0)
Note on BK25: =IF(OR(AND(A25>2011,RIGHT(G25,3)="sbd"),AND(A25>2012,RIGHT(G25,2)="bd")),1,0)
Note on BK26: =IF(OR(AND(A26>2011,RIGHT(G26,3)="sbd"),AND(A26>2012,RIGHT(G26,2)="bd")),1,0)
Note on BK27: =IF(OR(AND(A27>2011,RIGHT(G27,3)="sbd"),AND(A27>2012,RIGHT(G27,2)="bd")),1,0)
Note on BK28: =IF(OR(AND(A28>2011,RIGHT(G28,3)="sbd"),AND(A28>2012,RIGHT(G28,2)="bd")),1,0)
Note on BK29: =IF(OR(AND(A29>2011,RIGHT(G29,3)="sbd"),AND(A29>2012,RIGHT(G29,2)="bd")),1,0)
Note on BK30: =IF(OR(AND(A30>2011,RIGHT(G30,3)="sbd"),AND(A30>2012,RIGHT(G30,2)="bd")),1,0)
Note on BK31: =IF(OR(AND(A31>2011,RIGHT(G31,3)="sbd"),AND(A31>2012,RIGHT(G31,2)="bd")),1,0)
Note on BK32: =IF(OR(AND(A32>2011,RIGHT(G32,3)="sbd"),AND(A32>2012,RIGHT(G32,2)="bd")),1,0)
Note on BK33: =IF(OR(AND(A33>2011,RIGHT(G33,3)="sbd"),AND(A33>2012,RIGHT(G33,2)="bd")),1,0)
Note on BK34: =IF(OR(AND(A34>2011,RIGHT(G34,3)="sbd"),AND(A34>2012,RIGHT(G34,2)="bd")),1,0)
Note on BK35: =IF(OR(AND(A35>2011,RIGHT(G35,3)="sbd"),AND(A35>2012,RIGHT(G35,2)="bd")),1,0)
Note on BK36: =IF(OR(AND(A36>2011,RIGHT(G36,3)="sbd"),AND(A36>2012,RIGHT(G36,2)="bd")),1,0)
Note on BK37: =IF(OR(AND(A37>2011,RIGHT(G37,3)="sbd"),AND(A37>2012,RIGHT(G37,2)="bd")),1,0)
Note on BK38: =IF(OR(AND(A38>2011,RIGHT(G38,3)="sbd"),AND(A38>2012,RIGHT(G38,2)="bd")),1,0)
Note on BK39: =IF(OR(AND(A39>2011,RIGHT(G39,3)="sbd"),AND(A39>2012,RIGHT(G39,2)="bd")),1,0)
Note on BK40: =IF(OR(AND(A40>2011,RIGHT(G40,3)="sbd"),AND(A40>2012,RIGHT(G40,2)="bd")),1,0)
Note on BK41: =IF(OR(AND(A41>2011,RIGHT(G41,3)="sbd"),AND(A41>2012,RIGHT(G41,2)="bd")),1,0)
Note on BK42: =IF(OR(AND(A42>2011,RIGHT(G42,3)="sbd"),AND(A42>2012,RIGHT(G42,2)="bd")),1,0)
Note on BK43: =IF(OR(AND(A43>2011,RIGHT(G43,3)="sbd"),AND(A43>2012,RIGHT(G43,2)="bd")),1,0)
Note on BK44: =IF(OR(AND(A44>2011,RIGHT(G44,3)="sbd"),AND(A44>2012,RIGHT(G44,2)="bd")),1,0)
Note on BK45: =IF(OR(AND(A45>2011,RIGHT(G45,3)="sbd"),AND(A45>2012,RIGHT(G45,2)="bd")),1,0)
Note on BK46: =IF(OR(AND(A46>2011,RIGHT(G46,3)="sbd"),AND(A46>2012,RIGHT(G46,2)="bd")),1,0)
Note on BK47: =IF(OR(AND(A47>2011,RIGHT(G47,3)="sbd"),AND(A47>2012,RIGHT(G47,2)="bd")),1,0)
Note on A56: Timing of operating expenses and revenues is assumed to be end-of-year. Amounts entered beyond study period are ignored.
Note on H56: Enter recurring expenses and revenues (assuming no cost-of-service regulation) for this alternative. If a project will result in savings, enter them as a cost under status quo or as a savings under the proposed project, but not as both in the same evaluation.
Note on L56: Accept default escalation rate, enter a different rate, or enter zero if cost or revenue stream already includes escalation.

## Notes
Enter backup data/info on this tab.
6.8%

## Help
EASOP 2018 Help
EASOP 2018 is an Excel application that performs an economic evaluation of proposed projects or business
decisions. It is designed to evaluate up to 5 alternatives and compare them to status quo. If you need to
evaluate a larger number of alternatives, simply perform a second EASOP analysis that includes the
additional alternatives, making sure that status quo is defined the same way in both analyses.
EASOP provides three "Edition" options that are identical except for the number of project expenditures allowed for
each alternative: the Standard Edition accepts 6, ExtraCap accepts 20, and the MaxCap Edition accepts 40.
Click cell J6 of the Summary tab:
Because the Standard Edition is easiest to review on-screen, it should be used whenever possible. EASOP 2018
can be downloaded from the Economics Network website: |  |  |  |  | http://pgeweb/finance/utilityfinance/epa/econnet
EASOP includes a "Big Project" feature that allows for the evaluation of a project with a large
number of expenditures. This feature can also be used to evaluate a project that consists of multiple phases,
and you wish to evaluate the economics of each phase as well as the total project in one analysis. To use
this feature, enter data in Alternatives A through E as if they were components or phases of the large project.
To see the financial results, in the Excel 2010 menu bar select: Home > Format > Visibility > Unhide Sheet and
choose "Big Project". This will unhide the summary of financial results for the project and its components or phases.
Entering Data
Enter data in the yellow input fields, with all dollar amounts in thousands. Data may be entered as values
or formulas, or linked to data in other spreadsheets. Supporting data may be entered in the "Notes"
tab where linked data may be updated via Excel’s “Change Source.”
Delete data by selecting the data cell(s) and using the Delete key or by choosing Editing > Clear Contents. Do not
use Clear All, as it will also remove cell formats. (If this happens, see "Copying and Pasting Data" below.)
Click on the Summary tab to enter analysis data, such as title and subtitle of the evaluation, study period,
discount rate, first year of study period, cost estimate year, your name, the EASOP “Edition” option you wish
to use, and titles of the alternatives. A title for an alternative must be entered on the Summary page for financial
results to be displayed. Note that EASOP requires that status quo be included in the evaluation.
Click on the tabs titled S.Q., Alt A, etc. to enter expenditure data for the alternatives. Place the cursor
over the Type column heading to view the project expenditure symbols accepted by EASOP. If you wish
to enter the same data into the same cells on multiple alternatives, simply select the tabs for the
alternatives (by holding down the Control key while clicking on the tabs) and then enter the data.
Be sure to deselect the tabs when done.
Copying and Pasting Data
Data may be copied from another alternative or workbook and pasted into the input fields for an alternative.
However, do not cut data from an alternative to paste elsewhere, as it will result in errors. When copying
data from one EASOP alternative into another, use Home > Clipboard > Copy and then Clipboard > Paste.
However, when copying data from some source other than another EASOP alternative, it is recommended that
you paste the data using Paste Special > Formulas (or Values) to avoid altering cell formats in EASOP.
If you inadvertently change the format of a data input cell, you can change the format back to its original form.
Simply copy a similar cell that still has the original format, then select the offending cell and choose
Home > Clipboard > Paste > Paste Special > Formats.
Study Period, Service Life, and Salvage Value
If the service life of an investment extends beyond the end of the study period, EASOP will retire the asset
at the end of the study period at the specified salvage value. Any expenses or revenues that extend beyond
the study period will be ignored and a Warning note will be visible.
If you perform an analysis and then shorten the study period, EASOP will not automatically delete
expenditures that occur beyond the study period, but will ignore the data when calculating financial results.
The service life entered for each capital expenditure should be the expected service life of the asset, even if it
extends beyond the study period. If you want EASOP to calculate salvage values that reflect the economic
value of any service remaining for an asset beyond the study period, delete the value shown in the salvage
input column.
Financial Results
EASOP computes the financial measures described below. The calculation of these measures requires that
you ignore any revenues from cost-of-service ratemaking when entering data into EASOP.
NPV - Net present value of cash flow represents the value created by a project, and is the primary financial
measure used to make investment decisions. A project is attractive if its NPV is positive or greater than
that of all other project alternatives.
ROE - Return on equity represents the incremental rate of return earned on a project relative to status quo.
A project is attractive if the ROE exceeds the cost of equity, in which case the project would have a positive
NPV relative to status quo. EASOP may indicate that ROE is "n/a" if either (1) there are little or no revenues
or expense savings, (2) the project has a negative NPV relative to status quo, (3) the project represents a net
borrowing rather than an investment, or (4) multiple sign changes in the annual cash flows make it impossible
to calculate a unique ROE.
Payback - Payback represents the number of years required for the cost of the project to be recovered. The
shorter the payback the better, although an attractive payback is usually defined as 1/3 of the project life.
EASOP will indicate that payback is "never" if the project does not pay back within the study period, in which
case the project would have a negative NPV relative to status quo. EASOP will indicate that payback is "0"
if the project pays back immediately.
B/C Ratio - Benefit-cost ratio is defined as the present value of net benefits divided by the present value of
project costs. A project is attractive if its B/C ratio exceeds one. EASOP will indicate that the B/C ratio is
"n/a" if there are no benefits or project costs (compared to status quo).
PVRR - Present value of revenue requirements represents the amount of revenue that must be collected from
customers to earn a fair and reasonable rate of return on a project. A project is attractive if its PVRR is
negative or less than that of all other project alternatives.
Saving and Retrieving Analyses
You may save an analysis at any time by choosing File > Save As. It is preferable to save an analysis
before printing so the filename will be printed on the output. Analyses that have been saved can later be
opened using Excel and revised.
EASOP files are quite large: about 1 MB for the Excel 2010 version. You can reduce the file size by deleting
unneeded alternatives. However, that precludes changing the "Edition" option and deleted alternatives cannot be
added back. Delete alternatives (other than S.Q.) by right clicking on the tab for the alternative and choosing Delete.
Printing
You may print results by choosing File > Print. It is recommended that you select and print only the
alternatives used in the analysis. For example, if the evaluation consists of only status quo and two
alternatives, first click on the Summary tab and then click on the Alt B tab while holding down the Shift key.
This will select the worksheets. Then choose File > Print. Be sure to deselect the tabs when done.
You can easily add headers or revise footers on the printed output. Simply select the pages you wish to
modify and then choose File, Page Setup and make the desired changes.
Limitations
The study period cannot exceed 50 years. Do not use Clear All or Cut when editing.
Reference Information
Guidelines for evaluating proposed projects and documentation for EASOP are available on the
Analysis Guidelines Page. |  | Sample evaluations can be found on the |  |  |  | EASOP Software Page.
Financial data for year 2018 is summarized below:
|  |  | Discount |  |  |  | Escalation
| Description |  | Rate% |  | Cost Category |  | Rate%
| Target |  | 7 |  | Construction Costs |  | 2.5
| Range |  | 6.0 - 8.0 |  | M&O Expenses |  | 2.5
Project Expenditure Types Available in EASOP
| Capital Investments |  |  | Symbol | Capital lnvestments |  | Symbol
| Buildings |  |  | bldg | Power plants:
| Communication equipment |  |  | comm | Combined cycle |  | cc
| Computer hardware |  |  | comp | Combustion turbine |  | ct
| Computer software |  |  | soft | Micro turbine |  | mt
| Electric distribution (<69kV) |  |  | ed | Hydro |  | hyd
| Electric transmission (69kV+) |  |  | et | Hydro additions |  | hyda
| Electric smart meter |  |  | em | Nuclear |  | nuc
| Gas distribution |  |  | gasd | Nuclear additions |  | nuca
| Gas meters |  |  | gm | Biomass |  | bio
| Gas transmission & storage |  |  | gast | Fuel cell |  | fcl
| Gas held for resale |  |  | gasc | Geothermal |  | geo
| Land easement |  |  | ease | Solar photovoltaic2 |  | pv
| Land purchase |  |  | land | Solar thermal 2 |  | st
| Motor vehicles |  |  | mv | Tidal or wave |  | tdl
| Office furniture |  |  | furn | Waste |  | wst
| Electric Storage Battery 1 |  |  | bat | Wind 2 |  | wnd
| Expense |  |  | exp | Expense, after-tax |  | atx
1 Electric Storage Battery where by and large the value for this project is coming from the forecasted market participation revenues. For batteries primarily intended to support electric T or D, use expenditure type "et" or "ed" respectively. Contact Economic and Project Analysis for additional guidance in these cases.
2 The listing of expenditure types above is only a partial listing. Renewable projects eligible for ITC should include the year they commenced construction as a suffix - e.g. "pv19" for a solar photovoltaic plant that began construction before 2020. "wnd18" and "wnd19" are also valid types.
Technical Support
Technical support is available from Economic and Project Analysis

## Unit Capital inputs
For this year's update (2021), the OH base system hardening data was obtained from Business Finance. To estimate the UG base system hardening costs, the comparison between fire rebuild and base syatem hardening was used. The Fire Rebuild UG projects are a better comparison to base UG System hardening projects than MAT 56A and MAT 20A because fire rebuild is an expedited version of base UG system hardening. As more UG system hardening projects are completed on a planned basis there will be more UG system hardening costs data available in future will not be a need to extrapolate costs from similar projects.
|  | Unit costs | Unit costs
| OH | OH (removing risks) | UG
FRRB (Fire Rebuild) | 790312 |  | 2154851
Admin & General | 271306 |  | 313536
Construction | 495757 |  | 1794746
Land & Regulatory | 4921 |  | 20410
Planning & prep | 18328 |  | 26159
Base System Hardening | 1124869 | 974869
Admin & General | 316817 | 316817
Construction | 728010 | 578010 |  | 0
Land & Regulatory | 35771 | 35771
Planning & prep | 44271 | 44271
| Ratio OH base/OH FRRB | UG unit costs | UG unit costs (Removing risk)
|  | 3213230.3419 | 2763230.3419 |  | Step 1 | Calculate ratios of OH base syst hardening/OH FRRB for each category
Admin & General | 1.1677 | 366130.992 | 366130.992 |  | Step 2 | For each category, UG base cost = above ratio * UG FRRB cost
Construction | 1.4685 | 2635551.3598 | 2185551.3598 |  | Step 3 | Remove $450K from UG Construction costs because additional construction risk costs will be added as part of the EASOP
Land & Regulatory | 7.2691 | 148361.331 | 148361.331 |  | Step 4 | Remove $150K from OH Construction costs because additional construction risk costs will be added as part of the EASOP
Planning & prep | 2.4155 | 63186.6592 | 63186.6592 |  | Step 5 | Add individual category costs to calculate the total UG base syst hardening cost

## Unit O&M Inputs
Operating Expenses (Op Ex or O&M) ($000/mile)
Purpose: | This worksheet captures O&M. It levelizes as a single annual cost, the present value of the unlevel stream of costs.
See O&M data tab for sources.
Type | Cost Description | Source/Notes | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
Patrols, inspections, testing |  | $000/mile (see OH O&M data tab for details)
| Patrols and inspections | Tier 1 | 1: 3.1322; 6: 3.1322; 11: 3.1322; 16: 3.1322; 21: 3.1322; 26: 3.1322; 31: 3.1322; 36: 3.1322; 41: 3.1322; 46: 3.1322
|  | Tier 2 | 1: 3.1322; 4: 3.1322; 7: 3.1322; 10: 3.1322; 13: 3.1322; 16: 3.1322; 19: 3.1322; 22: 3.1322; 25: 3.1322; 28: 3.1322; 31: 3.1322; 34: 3.1322; 37: 3.1322; 40: 3.1322; 43: 3.1322; 46: 3.1322; 49: 3.1322
|  | Tier 3 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322 | 3.1322
| NPV (@discount rate, less inflation rate) | 63.9663
| Annualized Cost over Study Period | 3.2374
$000/mile (see OH O&M data tab for details)
| Poles Testing (starts at yr 15 and applies every 10 yrs thereafter) |  | 15: 2.4348; 25: 2.4348; 35: 2.4348; 45: 2.4348
| NPV (@discount rate, less inflation rate) | 8.7758
| Annualized Cost over Study Period | 0.44415
OH outage & emergency |  | $000/mile (see OH O&M data tab for details)
| Outage and emergency |  | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308 | 7.5308
Ongoing capital
| NPV (@discount rate, less inflation rate) | 153.7968
| Annualized Cost over Study Period | 7.7838
OH Maintenance & repair |  | $000/mile (see OH O&M data tab for details)
| Maintenance and repair |  | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694 | 0.75694
| NPV (@discount rate, less inflation rate) | 15.4585
| Annualized Cost over Study Period | 0.78238
OH Supervision & engg |  | $000/mile (see OH O&M data tab for details)
| Supervision & engg |  | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299
| NPV (@discount rate, less inflation rate) | 9.8637
| Annualized Cost over Study Period | 0.49921
OH Veg mgmt |  | $000/mile (see OH O&M data tab for details)
| Veg mgmt ($/tree) |  | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967 | 0.15967
| Veg mgmt($/mile) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NPV (@discount rate, less inflation rate) | 0
| Annualized Cost over Study Period | 0
PSPS |  | $000/mile (see OH O&M data tab for details)
| PSPS |  | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791 | 1.9791
| NPV (@discount rate, less inflation rate) | 40.4186
| Annualized Cost over Study Period | 2.0456
$000/mile (see OH O&M data tab for details)
| OH Ongoing capital as part of O&M (Outage & emergency + maint & repair) | $/mile | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895
|  | $ Total | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895 | 8.7895
|  | $ escalated | 8.7895 | 9.0092 | 9.2344 | 9.4653 | 9.7019 | 9.9445 | 10.1931 | 10.4479 | 10.7091 | 10.9769 | 11.2513 | 11.5326 | 11.8209 | 12.1164 | 12.4193 | 12.7298 | 13.048 | 13.3742 | 13.7086 | 14.0513 | 14.4026 | 14.7626 | 15.1317 | 15.51 | 15.8978 | 16.2952 | 16.7026 | 17.1201 | 17.5481 | 17.9868 | 18.4365 | 18.8974 | 19.3699 | 19.8541 | 20.3505 | 20.8592 | 21.3807 | 21.9152 | 22.4631 | 23.0247 | 23.6003 | 24.1903 | 24.7951 | 25.4149 | 26.0503 | 26.7016 | 27.3691 | 28.0533 | 28.7547 | 29.4735
UG petrols& inspection |  | $000/mile (see UG O&M data tab for details)
| Petrols and inspections |  | 1: 1.17; 4: 1.17; 7: 1.17; 10: 1.17; 13: 1.17; 16: 1.17; 19: 1.17; 22: 1.17; 25: 1.17; 28: 1.17; 31: 1.17; 34: 1.17; 37: 1.17; 40: 1.17; 43: 1.17; 46: 1.17; 49: 1.17
| NPV (@discount rate, less inflation rate) | 13.9085
| Annualized Cost over Study Period | 0.70393
UG outage & emergency |  | $000/mile (see UG O&M data tab for details)
| Outage and emergency |  | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 1.0785
| NPV (@discount rate, less inflation rate) | 22.0258
| Annualized Cost over Study Period | 1.1148
UG Maintenance & repair |  | $000/mile (see UG O&M data tab for details)
| Maintenance and repair |  | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726 | 0.57726
| NPV (@discount rate, less inflation rate) | 11.7891
| Annualized Cost over Study Period | 0.59666
UG Supervision & engg |  | $000/mile (see UG O&M data tab for details)
| Supervision & engg |  | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299 | 0.48299
| NPV (@discount rate, less inflation rate) | 9.8637
| Annualized Cost over Study Period | 0.49921
$000/mile (see UG O&M data tab for details)
| UG Ongoing capital as part of O&M | $/mile | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647
|  | $ Total | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647 | 4.9647
|  | $ escalated | 4.9647 | 5.0888 | 5.2161 | 5.3465 | 5.4801 | 5.6171 | 5.7575 | 5.9015 | 6.049 | 6.2002 | 6.3553 | 6.5141 | 6.677 | 6.8439 | 7.015 | 7.1904 | 7.3701 | 7.5544 | 7.7433 | 7.9368 | 8.1353 | 8.3386 | 8.5471 | 8.7608 | 8.9798 | 9.2043 | 9.4344 | 9.6703 | 9.912 | 10.1598 | 10.4138 | 10.6742 | 10.941 | 11.2146 | 11.4949 | 11.7823 | 12.0768 | 12.3788 | 12.6882 | 13.0054 | 13.3306 | 13.6638 | 14.0054 | 14.3556 | 14.7145 | 15.0823 | 15.4594 | 15.8459 | 16.242 | 16.6481
| Hybrid Ongoing capital as part of O&M | $ Total | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771 | 6.8771
|  | $ escalated | 6.8771 | 7.049 | 7.2252 | 7.4059 | 7.591 | 7.7808 | 7.9753 | 8.1747 | 8.3791 | 8.5886 | 8.8033 | 9.0233 | 9.2489 | 9.4802 | 9.7172 | 9.9601 | 10.2091 | 10.4643 | 10.7259 | 10.9941 | 11.2689 | 11.5506 | 11.8394 | 12.1354 | 12.4388 | 12.7498 | 13.0685 | 13.3952 | 13.7301 | 14.0733 | 14.4252 | 14.7858 | 15.1554 | 15.5343 | 15.9227 | 16.3208 | 16.7288 | 17.147 | 17.5757 | 18.0151 | 18.4654 | 18.9271 | 19.4003 | 19.8853 | 20.3824 | 20.892 | 21.4143 | 21.9496 | 22.4983 | 23.0608

## OH O&M data
OH O&M costs
| OH circuit miles |  | 80390
| Tier III+II miles |  | 26262
| UG circuit miles |  | 26980
Poles (Patrols, inspections, testing, maintenance)
|  |  | 2017 | 2018 | 2019 | 2020 | 2021
MAT code | Description | Source | Total cost ($)
BFA | Poles Patrol | Business Finance | 2692903.99 | 4549742.89 | 6151577.08 | 7737250.18 | 6079237.24
BFB | Poles inspected | Business Finance | 8546092.75 | 10787075.51 | 143845260.36 | 93970366.27 | 95920603
GAA | Pole testing and treatment | Business Finance | 11218034.78 | 8842355.3 | 17848706.57 | 17446665.22 | 17628532.11
MAT code | Description | Source | Units (No. of poles)
BFA | Poles Patrol | Business Finance | 1143750 | 1601777 | 1601338 | 1651152 | 1327910
BFB | Poles inspected | Business Finance | 454005 | 456071 | 486749 | 681145 | 960862
GAA | Pole testing and treatment | Business Finance | 244479 | 138730 | 224419 | 238253 | 217211
MAT code | Description | Source | Unit cost ($/pole)
BFA | Poles Patrol | Calculated | 2.3545 | 2.8404 | 3.8415 | 4.686 | 4.578
BFB | Poles inspected | Calculated | 18.8238 | 23.6522 | 295.5225 | 137.9594 | 99.8277
GAA | Pole testing and treatment | Calculated | 45.8855 | 63.7379 | 79.533 | 73.2275 | 81.1586
| No. of poles per mile | Assumption (see note) |  |  |  |  | 30
| Poles patrols and inspections ($/mile) | [5 empty] | 3132.1712
| Poles testing and treatment ($/mile) | [5 empty] | 2434.7568
Outage & Emergency
|  |  | 2017 | 2018 | 2019 | 2020 | 2021
MAT code | Description | Source | Total cost ($)
17B | Routine emergency | Business Finance | 92351333.05 | 98840964.07 | 113766058.34 | 144221789.42 | 155821002.4
17D |  | Business Finance | 30143602.63 | 26396745.06 | 37349910.02 | 42559452.52 | 41321878.32
17P |  | Business Finance | 19139277.9 | 13794871.74 | 15982114.82 | 14979723.57 | 19570134.11
95A | Major emergency | Business Finance | 253785216.61 | 259198525.86 | 205415101.87 | 220351383.11 | 266709660.7
BHB | Routine emergency | Business Finance | 16961861.33 | 15628513.32 | 22482513.91 | 19187037.38 | 23469499.12
BHE |  | Business Finance | 18051265.59 | 18169264.63 | 19271111.59 | 21585690.85 | 36858708.08
IFA | Major emergency | Business Finance | 277909732.61 | 312816029.36 | 469247589.72 | 331232300.42 | 377055606.92
MAT code | Description | Source | Units (FDA - Facility Damage Action) |  |  |  |  | FDA/mile
17B | FDA for replacing the damaged Asset/Equipment during Emergency Response | Business Finance | 10854 | 10335 | 11390 | 12068 | 12946 | 0.14328
17D |  | Business Finance | 2654 | 2862 | 2633 | 2975 | 3215 | 0.035674 | To calculate the unit costs in $/mile, the FDA/mile was calculated by dividing the average FDAs for each MAT code by total OH circuit miles. The FDA/mile is then multiplied by units costs in $/FDA for each MAT code to calculate $/mile (FDA/mile * $/FDA). The $/mile costs for the capital MAT codes are then added together to calculate the capital part of unit costs, and the $/mile costs for the O&M MAT codes are added together to calculate the O&M part of unit costs.
17P |  | Business Finance | 97 | 73 | 78 | 79 | 87 | 0.00103
95A |  | Business Finance | 12695 | 10785 | 9484 | 15010 | 11772 | 0.14864
BHB | FDA for repairing the damaged Asset/Equipment during Emergency Response | Business Finance | 6806 | 5965 | 6739 | 5529 | 6050 | 0.077345
BHE |  | Business Finance | 109350 | 90617 | 105754 | 89561 | 96472 | 1.2234
IFA |  | Business Finance | 7187 | 1117 | 6225 | 2267 | 6832 | 0.058783
MAT code | Description | Source | $/FDA |  |  |  |  | $/mile (FDA/mile * $/FDA)
17B |  | Calculated | 8508.5068 | 9563.7121 | 9988.2404 | 11950.7615 | 12036.2276 | 1491.5132 | Capital
17D |  | Calculated | 11357.8005 | 9223.1814 | 14185.3057 | 14305.6983 | 12852.8393 | 441.8162
17P |  | Calculated | 197312.1433 | 188970.8458 | 204898.9079 | 189616.7541 | 224944.0702 | 207.1787
95A |  | Calculated | 19990.9584 | 24033.243 | 21659.1208 | 14680.3053 | 22656.2743 | 3062.5834
BHB |  | Calculated | 2492.1924 | 2620.0358 | 3336.1795 | 3470.2545 | 3879.2561 | 244.3794 | O&M
BHE |  | Calculated | 165.0779 | 200.5061 | 182.2258 | 241.0166 | 382.0664 | 286.4989
IFA |  | Calculated | 38668.3919 | 280050.1606 | 75381.1389 | 146110.4104 | 55189.638 | 6999.9279
|  | No. of FDA/mile |  |  |  |  | 30 | 80390 | Total OH circuit miles
|  | Unit capital cost ($/mile) | [5 empty] | 5203.0916
|  | Unit O&M cost ($/mile) | [5 empty] | 7530.8062
Maint & repair
|  |  | 2017 | 2018 | 2019 | 2020 | 2021
MAT code | Description | Source |  |  | Cost ($)
2AA | General OH installations/replacements | Business Finance | 56617699.7 | 96499748.26 | 228227833.22 | 179951104.44 | 232990043
2AE |  | Business Finance | 25291948.83 | 36564281.45 | 34474896.18 | 44166493.28 | 54680464
2AS |  | Business Finance | 601030.85 | 680695.74 | 600134.9 | 221252.84 | 638927
KAA | General OH maintenance | Business Finance | 16282178.14 | 21275963.39 | 87190386.66 | 94866573.98 | 49612461
KAF |  | Business Finance | 5143293.33 | 4742564.26 | 5377224.26 | 6259342.76 | 6227715
KAQ |  | Business Finance | 6895.68 | 0 | 0 | 19834.43 | 984
KAS |  | Business Finance | 1405443.66 | 1523944.6 | 1561842.22 | 1681320.17 | 1551385
GAD | Poles maintenece | Business Finance | 4855700.47 | 2838632.38 | 3764324.2 | 4783468.07 | 3458006
MAT code | Description | Source | Units (No. of maintenance tags) |  |  |  |  | No. of tags/mile
2AA | # of Notifications Completed | Business Finance | 11466 | 14687 | 20959 | 13716 | 24641 | 0.30652
2AE | # of Tags Completed | Business Finance | 1219 | 1463 | 1207 | 1102 | 1686 | 0.020973
2AS | # of Notifications Completed | Business Finance | 2091 | 2129 | 2171 | 1271 | 2130.03 | 0.026496
KAA | # of Notifications Completed | Business Finance | 26867 | 29501 | 49232 | 40176 | 21438 | 0.26667
KAF | # of Notifications Completed | Business Finance | 1213 | 1302 | 1233 | 1203 | 1380 | 0.017166
KAQ | # of Notifications Completed | Business Finance | - | 2 | 3 | 9 | 2 | 2.4879e-05
KAS | # of Notifications Completed | Business Finance | 10706 | 9964 | 10670 | 9207 | 10453.33 | 0.13003
GAD | Poles maintenance | Business Finance | 5277 | 3440 | 5459 | 4402 | 4199.98 | 0.052245
MAT code | Description | Source | $/no. of tags completed |  |  |  |  | $/mile (no. of tags/mile * $/ no. of tags)
2AA |  | Calculated | 4937.8772 | 6570.4193 | 10889.252 | 13119.7947 | 9455.381 | 2898.2466
2AE |  | Calculated | 20748.1122 | 24992.6736 | 28562.4658 | 40078.4875 | 32432.0664 | 680.1899 | Capital
2AS |  | Calculated | 287.437 | 319.7256 | 276.4325 | 174.0778 | 299.9615 | 7.9478
KAA |  | Calculated | 606.0289 | 721.1947 | 1771.0105 | 2361.2747 | 2314.2299 | 617.1472
KAF |  | Calculated | 4240.1429 | 3642.5225 | 4361.0902 | 5203.1112 | 4512.837 | 77.4688
KAQ |  | Calculated | #VALUE! | 0 | 0 | 2203.8256 | 492 | 0.01224 | O&M
KAS |  | Calculated | 131.2763 | 152.9451 | 146.377 | 182.6132 | 148.4106 | 19.2982
GAD |  | Calculated | 920.1631 | 825.1838 | 689.563 | 1086.6579 | 823.3387 | 43.0154
|  | No. of tags/mile |  |  |  |  | 30 | 80390 | Total OH circuit miles
|  | Unit capital cost($/mile) | [5 empty] | 3586.3843
|  | Unit O&M cost ($/mile) | [5 empty] | 756.9418
Supervision & engg |  |  | Cost ($) |  |  |  |  | Updated
MAT code |  |  | 2017 | 2018 | 2019 | 2020 | 2021
FZ | Planing & ops engineering | Business Finance | 12822684.21 | 12107035.92 | 11106152.93 | 16644752.77 | 18406372.56
BA | General System Operation | Business Finance | 15675852.03 | 17449653.15 | 22595845.41 | 30016615.45 | 33451762.93
Total system circuit miles |  |  | 107370 | 107370 | 107370 | 107370 | 107370
$/mile
MAT code |  |  | 2017 | 2018 | 2019 | 2020 | 2021
FZ |  |  | 119.4252 | 112.76 | 103.4381 | 155.0224 | 171.4294
BA |  |  | 145.9984 | 162.5189 | 210.4484 | 279.5624 | 311.556
|  | Total unit cost ($/mile) | 265.4236 | 275.2788 | 313.8865 | 434.5848 | 482.9853
PSPS 2021 data | Column Labels
Row Labels | Dist Field Support | Helicopter | Grand Total | Dx Cicuit Miles | Cost per mile ($)
PSPS Event 01.18.21 | 1509.9902 | 383.5543 | 1893.5445 | 424 | 4465.9069
PSPS Event 08.17.21 | 6964.5212 | 50.8517 | 7015.3729 | 3683 | 1904.7985
PSPS Event 9.20.21 (WMBA) | 1152.9991 | 15.4085 | 1168.4076 | 300.43 | 3889.1176
PSPS Event 10.11.21 (WMBA) | 2442.2269 | 601.0983 | 3043.3252 | 2434 | 1250.339
PSPS Event 10.14.21 - 2021 (WMBA) | 533.6104 | 4.5976 | 538.208 | 60 | 8970.1327
Grand Total | 12603.3479 | 1055.5103 | 13658.8582 | 6901.43 | 1979.1345
Total by Avg event size |  |  | 2731.7716 | 1380.286 | 1979.1345
Veg Management
2020 routine veg mgmt actuals ($/tree) |  | 479
159.6667
The vegetation management costs are in $/tree, which gets multiplied by user-defined trees/mile input to calculate the total $/mile of vegetation management costs. A same tree is not cut every year. It is assumed thata same tree is cut every 3 years. Hence 1/3rd of veg mgmt cost is applied every year. Data received from: Enterprise Veg management
Engineering as well as general system operations serve the entire distribution system. Hence the unite costs are based on the total system miles
2021 PSPS data obtained from the PSPS operations group. The average cost per mile is calculated based on the total $ spent on each event and circuit miles impacted.
To calculate the unit costs in $/mile, the tags/mile was calculated by dividing the tags for each MAT code by total OH circuit miles. The tags/mile is then multiplied by units costs in $/tags for each MAT code to calculate $/mile tags/mile * $/tags). The $/mile costs for the capital MAT codes are then added together to calculate the capital part of unit costs, and the $/mile costs for the O&M MAT codes are added together to calculate the O&M part of unit costs.
The O&M input costs were obtained from Business Finance Electric Ops T&D Maintenance. For overhead costs, year 2021 costs were used in most cases. For underground costs, data from 2017-2021 was averaged to eliminate any year-to year- variability and also to remain consistent with the same data years utilized for capital costs estimation.
The totals in each category was divided by total miles (or poles, as applicable) for OH and UG to obtain the unit costs. The mileage data was obtained from Electric Distribution Asset data on “PG&E Electric: by the numbers” sharepoint site. The totals for each category was divided by mileage to obtain $/miles.
The data were sorted based on MAT codes. The list of MAT codes to be used was obtained from EO investment planning group. The MAT codes were categorized in the original data for each year as capital (ongoing capital which is part of O&M activities) and expense (expense part of the O&M). In this analysis, the capital part of the O&M is treated as capital to be added in EASOP as ongoing capital costs. The rest of the O&M which was categorized as expense, was treated as operating expense.
The vegetation management costs were obtained from EO Vegetation Management Business project manager. The vegetation management costs are in $/tree, which gets multiplied by user-defined trees/mile input to calculate the total $/mile of vegetation management costs. . PSPS costs were obtained from PSPS program management.
Average span between poles is 250 ft. That would be 5280 ft per mile/250 = 21 poles per mile. However, for a hardened system, this is too low. Due to the additional weight and forces due to wind on the higher cross-sectional area conductor, 250’ spans would not be a good approximation. Electric ops is installing/replacing closer to 30 poles per mile. Hencce, 30 poles per mile is assumed. (Source: communication with Grid Engineering).
MAT codes 2AB, 2AC, KAC and KAD for Bird safety program are excluded since these costs are not applicable to system hardening projects.

## UG O&M data
OH circuit miles |  | 80390
The O&M input costs were obtained from Business Finance Electric Ops T&D Maintenance. For overhead costs, year 2021 costs were used in most cases. For underground costs, data from 2017-2021 was averaged to eliminate any year-to year- variability and also to remain consistent with the same data years utilized for capital costs estimation. The totals in each category was divided by total miles (or poles, as applicable) for OH and UG to obtain the unit costs. The mileage data was obtained from Electric Distribution Asset data on “PG&E Electric: by the numbers” sharepoint site. The totals for each category was divided by mileage to obtain $/miles. The data were sorted based on MAT codes. The list of MAT codes to be used was obtained from EO investment planning group. The MAT codes were categorized in the original data for each year as capital (ongoing capital which is part of O&M activities) and expense (expense part of the O&M). In this analysis, the capital part of the O&M is treated as capital to be added in EASOP as ongoing capital costs. The rest of the O&M which was categorized as expense, was treated as operating expense.
UG circuit miles |  | 26980
Patrols & inspections
MAT code | 2017 ($) | 2018 ($) | 2019 ($) | 2020 ($) | 2021 ($)
BFD | 1285386.5 | 1086134.39 | 1178489.5 | 2166470.72 | 2447307.27 | UG patrol
BFE | 8005556.07 | 4754532.21 | 4889578.89 | 11357680.43 | 12968745.68 | UG inpection
BFF | 477139.2 | 367440.9 | 458105.73 | 611572.85 | 557745.55 | UG manhole insp
Total | 9768081.77 | 6208107.5 | 6526174.12 | 14135724 | 15973798.5
$/mile | 362.049 | 230.1004 | 241.8893 | 523.9334 | 592.0607 |  | 390.0066
Outage & emergency
MAT code | 2017 ($) | 2018 ($) | 2019 ($) | 2020 ($) | 2021 ($)
17C | 40256690.44 | 44063582.77 | 39893073.05 | 49295255.9 | 54023348.4 | Routine emerg capital
95B | 24957363.71 | 49439393.82 | 23187078.61 | 15692805.48 | 16926761.47 | Major emerg capital
IFB | 13190980.75 | 1390120.59 | 11200152.6 | 4278204.97 | 7608486.64 | Major emerg expense
BHC | 16531081.89 | 19957599.83 | 23260867.27 | 21571025.94 | 26503103.67 | Routine emerg expense
Total | 65214054.15 | 93502976.59 | 63080151.66 | 64988061.38 | 70950109.87
Total | 29722062.64 | 21347720.42 | 34461019.87 | 25849230.91 | 34111590.31
$/mile | 2417.1258 | 3465.6403 | 2338.0338 | 2408.7495 | 2629.7298 |  | 2651.8558
$/mile | 1101.6332 | 791.2424 | 1277.2802 | 958.0886 | 1264.3288 |  | 1078.5146
Maintenance & repair
MAT code | 2017 ($) | 2018 ($) | 2019 ($) | 2020 ($) | 2021 ($)
2BA | 41289789.87 | 62719985.59 | 57177506.4 | 38039019.9 | 72974757.55 | Install/replacement
2BB | 980999.49 | 1034569.73 | 528258.04 | 409850.65 | 813178.26
2BD | 4640515.27 | 6036808.71 | 6813613.89 | 7595877.28 | 9440958.46
2BF | 359221.79 | 409350.82 | 469523.75 | 175803.77 | 95245.4
KBA | 11857410.6 | 15497896.78 | 15233741.55 | 11881331.42 | 18813866.45 | Maintenance
KBC | 635141.99 | 653909.54 | 1016718.32 | 929323.2 | 1353503.72
Total | 47270526.42 | 70200714.85 | 64988902.08 | 46220551.6 | 83324139.67
Total | 12492552.59 | 16151806.32 | 16250459.87 | 12810654.62 | 20167370.17
$/mile | 1752.0581 | 2601.9538 | 2408.7807 | 1713.1413 | 3088.3669 |  | 2312.8602
$/mile | 463.0301 | 598.6585 | 602.315 | 474.8204 | 747.4933 |  | 577.2635
Supervision & engg
MAT code | 2017 ($) | 2018 ($) | 2019 ($) | 2020 ($) | 2021 ($)
FZ | 12822684.21 | 12107035.92 | 11106152.93 | 16644752.77 | 18406372.56 | Planing & ops engr |  | Engineering as well as general system operations serve the entire distribution system. Hence the unite costs are based on the total distribution miles
BA | 15675852.03 | 17449653.15 | 22595845.41 | 30016615.45 | 33451762.93 | General System Operat
Total | 28498536.24 | 29556689.07 | 33701998.34 | 46661368.22 | 51858135.49
$/mile | 265.4236 | 275.2788 | 313.8865 | 434.5848 | 482.9853 |  | 354.4318

## Lists
Detailed Cost Input
Historical Low Avg. CapEx
Historical High Avg. CapEx
1
2
3

## Data
EASOP Data | [6 empty] | Income Tax Rate = | 27.98% |  | Bond Interest = |  | 4.17%
[10 empty] | Debt Ratio = |  | 48%
| bldg |  | comm |  | comp |  | soft |  | ed |  | et |  | em |  | gasd |  | gm |  | gast |  | gasc |  | ease |  | land |  | mv |  | furn |  | cc |  | ct |  | mt |  | hyd |  | hyda |  | nuc |  | nuca |  | bio |  | fcl |  | geo |  | pv |  | pv19 |  | pv20 |  | pv21 |  | st |  | st19 |  | st20 |  | st21 |  | tdl |  | wst |  | wnd |  | wnd18 |  | wnd19 |  | bat
Year | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last | Cash | Last
0 | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -100 |  | -90 |  | -70 |  | -74 |  | -78 |  | -90 |  | -70 |  | -74 |  | -78 |  | -100 |  | -100 |  | -100 |  | -82 |  | -88 |  | -100
1 | -1.6759 | 7.0168 | -1.3579 | 7.0168 | -0.34987 | 7.0168 | 1.1235 | 7.0168 | -1.5285 | 7.0168 | -1.5285 | 7.0168 | -0.34987 | 7.0168 | -1.5706 | 7.0168 | -1.5706 | 7.0168 | -1.4214 | 7.0168 | -1.8232 | 7.0168 | -1.7271 | 7.0168 | -1.8232 | 7.0168 | -0.0552 | 7.0168 | -0.9392 | 7.0168 | -1.5075 | 7.0168 | -1.3812 | 7.0168 | -1.3812 | 7.0168 | -1.6464 | 7.0168 | -1.6464 | 7.0168 | -1.3812 | 7.0168 | -1.3812 | 7.0168 | -1.0865 | 7.0168 | -1.0865 | 7.0168 | -1.5075 | 7.0168 | -1.0865 | 7.0168 | -1.0865 | 7.0168 | -1.0865 | 7.0168 | -1.0865 | 7.0168 | -1.5075 | 7.0168 | -1.5075 | 7.0168 | -1.5075 | 7.0168 | -1.5075 | 7.0168 | -1.0865 | 7.0168 | -1.5075 | 7.0168 | -1.0865 | 7.0168 | -1.0865 | 7.0168 | -1.0865 | 7.0168 | -1.0865 | 7.0168
2 | -1.507 | 6.8959 | -0.85353 | 6.6397 | 0.89672 | 5.8078 | 1.3878 | 4.3345 | -1.2241 | 6.7515 | -1.2295 | 6.7462 | 0.69845 | 5.6096 | -1.3085 | 6.7883 | -1.2884 | 6.8083 | -1.0321 | 6.639 | -1.8232 | 7.0168 | -1.631 | 6.9207 | -1.8232 | 7.0168 | 1.1378 | 5.381 | -0.16591 | 6.1989 | -1.1703 | 6.7451 | -0.93053 | 6.6277 | -0.85122 | 6.707 | -1.4502 | 6.8664 | -1.4106 | 6.9061 | -0.89528 | 6.6629 | -0.79457 | 6.7636 | -0.41977 | 6.333 | -0.30742 | 6.4454 | -1.1614 | 6.754 | -0.40655 | 6.3462 | -0.40655 | 6.3462 | -0.40655 | 6.3462 | -0.40655 | 6.3462 | -1.1614 | 6.754 | -1.1614 | 6.754 | -1.1614 | 6.754 | -1.1614 | 6.754 | -0.34046 | 6.4123 | -1.1614 | 6.754 | -0.41977 | 6.333 | -0.41977 | 6.333 | -0.41977 | 6.333 | -0.38452 | 6.3683
3 | 0.83728 | 26.9081 | 7.4347 | 26.0829 | 15.2112 | 23.7423 | 21.7779 | 21.7779 | 3.3169 | 26.4849 | 4.4444 | 26.4776 | 12.2411 | 23.4707 | 3.2787 | 26.5987 | 3.3061 | 26.6261 | 4.5168 | 26.173 | -0.67458 | 27.309 | 0.558 | 27.0208 | -0.67458 | 27.309 | 14.9597 | 22.8933 | 11.7678 | 24.9244 | 3.3519 | 26.4448 | 4.5812 | 26.0997 | 14.8013 | 26.2083 | 3.2228 | 26.8219 | 3.2772 | 26.8762 | 4.6294 | 26.1479 | 4.7674 | 26.2859 | 11.7017 | 25.2942 | 14.9913 | 25.4482 | 14.6103 | 26.4569 | 14.1079 | 24.2623 | 12.6127 | 22.1623 | 12.9117 | 22.5823 | 13.2108 | 23.0023 | 13.8627 | 25.4069 | 12.3675 | 23.3069 | 12.6665 | 23.7269 | 12.9656 | 24.1469 | 11.8104 | 25.4029 | 9.0831 | 26.4569 | 14.8374 | 25.2942 | 13.4917 | 23.4042 | 13.9403 | 24.0342 | 11.75 | 25.3425
4 | -0.62531 | 24.6932 | 1.5995 | 17.4167 | 2.6918 | 7.7173 | -0.81379 | -0.81379 | 0.33842 | 21.7973 | 0.64464 | 20.6498 | 3.3012 | 9.9459 | 0.27336 | 21.9366 | 0.32083 | 21.9841 | 0.76851 | 20.2729 | -1.4403 | 26.5433 | -0.83199 | 25.0224 | -1.4403 | 26.5433 | 2.3397 | 6.8065 | 2.2714 | 11.8729 | 0.39863 | 21.757 | 0.87983 | 20.2035 | 1.871 | 10.2799 | 0.17936 | 22.2214 | 0.27334 | 22.3154 | 0.96337 | 20.287 | 1.2021 | 20.5257 | 2.1466 | 12.2775 | 2.2081 | 9.4081 | 1.5416 | 10.5315 | 1.8522 | 8.8707 | 1.6103 | 8.2659 | 1.6587 | 8.3869 | 1.7071 | 8.5079 | 1.4207 | 10.2291 | 1.1788 | 9.6243 | 1.2271 | 9.7453 | 1.2755 | 9.8663 | 2.3345 | 12.4655 | 1.6947 | 16.0588 | 1.9419 | 9.1418 | 1.7241 | 8.5975 | 1.7967 | 8.7789 | 2.2301 | 12.361
5 | -0.61156 | 23.9617 | 1.2612 | 14.6554 | 2.5902 | 4.4206 | -0.60494 | -0.60494 | 0.24936 | 20.1114 | 0.48705 | 18.6408 | 3.0431 | 5.4131 | 0.184 | 20.2989 | 0.24729 | 20.3622 | 0.59842 | 18.14 | -1.4403 | 26.5433 | -0.83199 | 24.4141 | -1.4403 | 26.5433 | 1.5362 | 3.4442 | 1.4497 | 8.37 | 0.31901 | 20.0572 | 0.72693 | 18.0504 | 1.9424 | 7.3863 | 0.097493 | 20.6852 | 0.2228 | 20.8105 | 0.83831 | 18.1618 | 1.1566 | 18.48 | 1.3505 | 8.8577 | 2.2505 | 6.2817 | 1.5663 | 7.7166 | 1.8163 | 5.787 | 1.5743 | 5.4242 | 1.6227 | 5.4967 | 1.6711 | 5.5693 | 1.4453 | 7.5352 | 1.2034 | 7.1723 | 1.2518 | 7.2449 | 1.3001 | 7.3175 | 1.6011 | 9.1083 | 1.7193 | 13.0908 | 1.8955 | 5.9267 | 1.6777 | 5.6001 | 1.7503 | 5.709 | 1.4619 | 8.9691
6 | -0.59756 | 23.2374 | 0.98482 | 12.302 | 1.2791 | 1.4343 | -0.39609 | -0.39609 | 0.1676 | 18.5377 | 0.34561 | 16.8084 | 1.0356 | 1.1908 | 0.10194 | 18.7695 | 0.18105 | 18.8486 | 0.44449 | 16.1962 | -1.4403 | 26.5433 | -0.83199 | 23.8057 | -1.4403 | 26.5433 | 0.29139 | 0.98975 | 1.3778 | 5.741 | 0.24667 | 18.4719 | 0.59018 | 16.092 | 0.80413 | 4.5257 | 0.02292 | 19.2518 | 0.17956 | 19.4085 | 0.72941 | 16.2312 | 1.1272 | 16.629 | 1.3041 | 6.2757 | 1.0832 | 3.2436 | 0.38127 | 4.9189 | 0.63118 | 2.7915 | 0.51022 | 2.6705 | 0.53441 | 2.6947 | 0.5586 | 2.7189 | 0.32079 | 4.8584 | 0.19983 | 4.7375 | 0.22403 | 4.7616 | 0.24822 | 4.7858 | 1.6173 | 6.589 | 1.744 | 10.14 | 0.63945 | 2.7998 | 0.53058 | 2.6909 | 0.56687 | 2.7272 | 1.4433 | 6.415
7 | -0.58334 | 22.5199 | 0.76003 | 10.2945 | -0.2409 | -0.2409 | -0.39609 | -0.39609 | 0.092584 | 17.069 | 0.28073 | 15.1364 | -0.97187 | -0.97187 | 0.026622 | 17.3411 | 0.12155 | 17.4361 | 0.3671 | 14.4253 | -1.4403 | 26.5433 | -0.83199 | 23.1974 | -1.4403 | 26.5433 | -0.81379 | -0.11543 | 1.3059 | 3.2362 | 0.18109 | 16.9938 | 0.52998 | 14.3121 | -0.33412 | 2.9077 | -0.044904 | 17.9139 | 0.14306 | 18.1019 | 0.69706 | 14.4792 | 1.1744 | 14.9565 | 1.2577 | 3.7819 | -0.084001 | 1.5032 | -0.80371 | 3.3479 | -0.55391 | 1.0333 | -0.55391 | 1.0333 | -0.55391 | 1.0333 | -0.55391 | 1.0333 | -0.80371 | 3.3479 | -0.80371 | 3.3479 | -0.80371 | 3.3479 | -0.80371 | 3.3479 | 1.6336 | 4.1579 | 1.7686 | 7.2063 | -0.61656 | 0.97062 | -0.61656 | 0.97062 | -0.61656 | 0.97062 | 1.4247 | 3.949
8 | -0.5689 | 21.8091 | 0.67589 | 8.5815 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.023813 | 15.6986 | 0.28473 | 13.5482 | -1.0748 | -1.0748 | -0.042451 | 16.0071 | 0.068302 | 16.1178 | 0.3586 | 12.7507 | -1.4403 | 26.5433 | -0.83199 | 22.5891 | -1.4403 | 26.5433 | -0.70936 | -0.011002 | 0.2968 | 0.85549 | 0.12175 | 15.616 | 0.53867 | 12.6342 | -0.26278 | 2.5325 | -0.10648 | 16.6647 | 0.11281 | 16.884 | 0.73359 | 12.8291 | 1.2905 | 13.386 | 0.27414 | 1.3763 | -0.041648 | 1.0606 | -0.7791 | 3.0037 | -0.58987 | 0.51234 | -0.58987 | 0.51234 | -0.58987 | 0.51234 | -0.58987 | 0.51234 | -0.7791 | 3.0037 | -0.7791 | 3.0037 | -0.7791 | 3.0037 | -0.7791 | 3.0037 | 0.71272 | 1.8149 | 0.50704 | 4.2898 | -0.66297 | 0.43924 | -0.66297 | 0.43924 | -0.66297 | 0.43924 | 0.46906 | 1.5713
9 | -0.55424 | 21.1048 | 0.70896 | 7.0222 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.019373 | 14.4201 | 0.28873 | 11.975 | -1.0226 | -1.0226 | -0.047192 | 14.7611 | 0.079382 | 14.8877 | 0.3501 | 11.1037 | -1.4403 | 26.5433 | -0.83199 | 21.9807 | -1.4403 | 26.5433 | -0.60494 | 0.093422 | -0.71225 | -0.46394 | 0.12674 | 14.3324 | 0.54736 | 10.9893 | -0.19144 | 2.1903 | -0.10373 | 15.4979 | 0.14688 | 15.7485 | 0.77013 | 11.2121 | 1.2574 | 11.6994 | -0.70938 | -0.0039623 | 0.00070525 | 0.70612 | -0.75448 | 2.6766 | -0.62584 | 0.079577 | -0.62584 | 0.079577 | -0.62584 | 0.079577 | -0.62584 | 0.079577 | -0.75448 | 2.6766 | -0.75448 | 2.6766 | -0.75448 | 2.6766 | -0.75448 | 2.6766 | -0.20814 | 0.49727 | -0.75448 | 2.6766 | -0.70938 | -0.0039623 | -0.70938 | -0.0039623 | -0.70938 | -0.0039623 | -0.48661 | 0.21881
10 | -0.53937 | 20.4066 | 0.74204 | 5.4994 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.027594 | 13.1692 | 0.29273 | 10.4169 | -0.97042 | -0.97042 | -0.039273 | 13.5388 | 0.10312 | 13.6812 | 0.34161 | 9.4841 | -1.4403 | 26.5433 | -0.83199 | 21.3724 | -1.4403 | 26.5433 | -0.50051 | 0.19785 | -0.78419 | -0.72212 | 0.14439 | 13.0786 | 0.55605 | 9.3776 | -0.12009 | 1.8813 | -0.088322 | 14.3493 | 0.19362 | 14.6312 | 0.80667 | 9.6282 | 1.2244 | 10.0459 | -0.75578 | -0.35899 | -0.087472 | 0.30932 | -0.72987 | 2.3667 | -0.6618 | -0.26501 | -0.6618 | -0.26501 | -0.6618 | -0.26501 | -0.6618 | -0.26501 | -0.72987 | 2.3667 | -0.72987 | 2.3667 | -0.72987 | 2.3667 | -0.72987 | 2.3667 | -0.1919 | 0.2049 | -0.72987 | 2.3667 | -0.75578 | -0.35899 | -0.75578 | -0.35899 | -0.75578 | -0.35899 | -0.50517 | -0.10837
11 | -0.52431 | 19.7145 | 0.77511 | 4.0132 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.035815 | 11.9333 | 0.29673 | 8.8737 | -0.91821 | -0.91821 | -0.031353 | 12.3276 | 0.12686 | 12.4859 | 0.33311 | 7.8921 | -1.4403 | 26.5433 | -0.83199 | 20.7641 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.85613 | -0.85613 | 0.16205 | 11.842 | 0.56474 | 7.7989 | -0.048748 | 1.6053 | -0.07291 | 13.2061 | 0.24036 | 13.5194 | 0.8432 | 8.0773 | 1.1913 | 8.4254 | -0.80219 | -0.62584 | -0.17565 | 0.00070525 | -0.70526 | 2.0739 | -0.69777 | -0.52141 | -0.69777 | -0.52141 | -0.69777 | -0.52141 | -0.69777 | -0.52141 | -0.70526 | 2.0739 | -0.70526 | 2.0739 | -0.70526 | 2.0739 | -0.70526 | 2.0739 | -0.17565 | 0.00070525 | -0.70526 | 2.0739 | -0.80219 | -0.62584 | -0.80219 | -0.62584 | -0.80219 | -0.62584 | -0.52373 | -0.34737
12 | -0.50904 | 19.0282 | 0.80819 | 2.5636 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.044037 | 10.7125 | 0.30074 | 7.3454 | -0.866 | -0.866 | -0.023433 | 11.1275 | 0.15061 | 11.3016 | 0.32461 | 6.3275 | -1.4403 | 26.5433 | -0.83199 | 20.1557 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.866 | -0.866 | 0.1797 | 10.6225 | 0.57343 | 6.2533 | -0.081828 | 1.2579 | -0.057498 | 12.0684 | 0.2871 | 12.413 | 0.87974 | 6.5596 | 1.1582 | 6.8381 | -0.8486 | -0.80451 | -0.26383 | -0.21974 | -0.68064 | 1.7983 | -0.73373 | -0.68964 | -0.73373 | -0.68964 | -0.73373 | -0.68964 | -0.73373 | -0.68964 | -0.68064 | 1.7983 | -0.68064 | 1.7983 | -0.68064 | 1.7983 | -0.68064 | 1.7983 | -0.26383 | -0.21974 | -0.68064 | 1.7983 | -0.8486 | -0.80451 | -0.8486 | -0.80451 | -0.8486 | -0.80451 | -0.54229 | -0.4982
13 | -0.4936 | 18.3476 | 0.25519 | 1.1504 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.052258 | 9.5066 | 0.30474 | 5.8322 | -0.81379 | -0.81379 | -0.015514 | 9.9385 | 0.17435 | 10.1283 | 0.31611 | 4.7904 | -1.4403 | 26.5433 | -0.83199 | 19.5474 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.81379 | -0.81379 | 0.19735 | 9.4201 | 0.58212 | 4.7408 | -0.11491 | 0.94366 | -0.042087 | 10.9362 | 0.33384 | 11.3121 | 0.91627 | 5.0749 | 1.1251 | 5.2838 | -0.89501 | -0.89501 | -0.352 | -0.352 | -0.65603 | 1.5399 | -0.7697 | -0.7697 | -0.7697 | -0.7697 | -0.7697 | -0.7697 | -0.7697 | -0.7697 | -0.65603 | 1.5399 | -0.65603 | 1.5399 | -0.65603 | 1.5399 | -0.65603 | 1.5399 | -0.352 | -0.352 | -0.65603 | 1.5399 | -0.89501 | -0.89501 | -0.89501 | -0.89501 | -0.89501 | -0.89501 | -0.56085 | -0.56085
14 | -0.47797 | 17.6724 | -0.29781 | 0.35993 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.060479 | 8.3156 | 0.30874 | 4.334 | -0.76157 | -0.76157 | -0.0075938 | 8.7605 | 0.19809 | 8.9661 | 0.30762 | 3.2807 | -1.4403 | 26.5433 | -0.83199 | 18.939 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.76157 | -0.76157 | 0.215 | 8.235 | 0.59081 | 3.2613 | -0.14799 | 0.66248 | -0.026675 | 9.8095 | 0.38058 | 10.2167 | 0.95281 | 3.6233 | 1.092 | 3.7625 | -0.89732 | -0.89732 | -0.39609 | -0.39609 | -0.63141 | 1.2986 | -0.76157 | -0.76157 | -0.76157 | -0.76157 | -0.76157 | -0.76157 | -0.76157 | -0.76157 | -0.63141 | 1.2986 | -0.63141 | 1.2986 | -0.63141 | 1.2986 | -0.63141 | 1.2986 | -0.39609 | -0.39609 | -0.63141 | 1.2986 | -0.89732 | -0.89732 | -0.89732 | -0.89732 | -0.89732 | -0.89732 | -0.53532 | -0.53532
15 | -0.46216 | 17.0024 | -0.26473 | 0.19203 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.068701 | 7.1397 | 0.31274 | 2.8507 | -0.70936 | -0.70936 | 0.00032586 | 7.5935 | 0.22183 | 7.815 | 0.29912 | 1.7986 | -1.4403 | 26.5433 | -0.83199 | 18.3307 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.70936 | -0.70936 | 0.23266 | 7.0669 | 0.5995 | 1.815 | -0.18107 | 0.41437 | -0.011263 | 8.6882 | 0.42732 | 9.1268 | 0.98934 | 2.2048 | 1.059 | 2.2744 | -0.85555 | -0.85555 | -0.39609 | -0.39609 | -0.6068 | 1.0744 | -0.70936 | -0.70936 | -0.70936 | -0.70936 | -0.70936 | -0.70936 | -0.70936 | -0.70936 | -0.6068 | 1.0744 | -0.6068 | 1.0744 | -0.6068 | 1.0744 | -0.6068 | 1.0744 | -0.39609 | -0.39609 | -0.6068 | 1.0744 | -0.85555 | -0.85555 | -0.85555 | -0.85555 | -0.85555 | -0.85555 | -0.46571 | -0.46571
16 | -0.44619 | 16.3375 | -0.23166 | 0.06067 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.076922 | 5.9788 | -0.30327 | 1.3824 | -0.65715 | -0.65715 | 0.0082456 | 6.4377 | 0.24557 | 6.675 | -0.32939 | 0.34396 | -1.4403 | 26.5433 | -0.83199 | 17.7224 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.65715 | -0.65715 | 0.25031 | 5.9161 | -0.01183 | 0.40167 | -0.21415 | 0.19935 | 0.0041492 | 7.5724 | 0.47406 | 8.0423 | 0.40587 | 0.81937 | 0.40587 | 0.81937 | -0.81379 | -0.81379 | -0.39609 | -0.39609 | -0.58219 | 0.86745 | -0.65715 | -0.65715 | -0.65715 | -0.65715 | -0.65715 | -0.65715 | -0.65715 | -0.65715 | -0.58219 | 0.86745 | -0.58219 | 0.86745 | -0.58219 | 0.86745 | -0.58219 | 0.86745 | -0.39609 | -0.39609 | -0.58219 | 0.86745 | -0.81379 | -0.81379 | -0.81379 | -0.81379 | -0.81379 | -0.81379 | -0.39609 | -0.39609
17 | -0.42772 | 15.6775 | -0.2682 | -0.10376 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.085143 | 4.8328 | -0.91928 | 0.54915 | -0.60494 | -0.60494 | 0.016165 | 5.2929 | 0.26931 | 5.546 | -0.95791 | -0.4632 | -1.4403 | 26.5433 | -0.83199 | 17.114 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.60494 | -0.60494 | 0.26796 | 4.7824 | -0.62315 | -0.35851 | -0.24723 | 0.017412 | 0.019561 | 6.4621 | 0.5208 | 6.9633 | -0.24723 | 0.017412 | -0.24723 | 0.017412 | -0.77202 | -0.77202 | -0.39609 | -0.39609 | -0.55757 | 0.67762 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.55757 | 0.67762 | -0.55757 | 0.67762 | -0.55757 | 0.67762 | -0.55757 | 0.67762 | -0.39609 | -0.39609 | -0.55757 | 0.67762 | -0.77202 | -0.77202 | -0.77202 | -0.77202 | -0.77202 | -0.77202 | -0.39609 | -0.39609
18 | -0.40683 | 15.0199 | -0.30474 | -0.23166 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.093365 | 3.7018 | -0.91528 | 0.35087 | -0.55273 | -0.55273 | 0.024085 | 4.1591 | 0.29306 | 4.4281 | -0.9664 | -0.62286 | -1.4403 | 26.5433 | -0.83199 | 16.5057 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.55273 | -0.55273 | 0.28561 | 3.6658 | -0.61447 | -0.4656 | -0.28031 | -0.13145 | 0.034973 | 5.3572 | 0.56753 | 5.8898 | -0.28031 | -0.13145 | -0.28031 | -0.13145 | -0.73025 | -0.73025 | -0.39609 | -0.39609 | -0.53296 | 0.50495 | -0.55273 | -0.55273 | -0.55273 | -0.55273 | -0.55273 | -0.55273 | -0.55273 | -0.55273 | -0.53296 | 0.50495 | -0.53296 | 0.50495 | -0.53296 | 0.50495 | -0.53296 | 0.50495 | -0.39609 | -0.39609 | -0.53296 | 0.50495 | -0.73025 | -0.73025 | -0.73025 | -0.73025 | -0.73025 | -0.73025 | -0.39609 | -0.39609
19 | -0.38595 | 14.3624 | -0.34128 | -0.32301 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.10159 | 2.5858 | -0.91128 | 0.16757 | -0.50051 | -0.50051 | 0.032005 | 3.0365 | 0.3168 | 3.3213 | -0.9749 | -0.75503 | -1.4403 | 26.5433 | -0.83199 | 15.8973 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.50051 | -0.50051 | 0.30327 | 2.5664 | -0.60578 | -0.53962 | -0.31339 | -0.24723 | 0.050385 | 4.2579 | 0.61427 | 4.8218 | -0.31339 | -0.24723 | -0.31339 | -0.24723 | -0.68848 | -0.68848 | -0.39609 | -0.39609 | -0.50834 | 0.34943 | -0.50051 | -0.50051 | -0.50051 | -0.50051 | -0.50051 | -0.50051 | -0.50051 | -0.50051 | -0.50834 | 0.34943 | -0.50834 | 0.34943 | -0.50834 | 0.34943 | -0.50834 | 0.34943 | -0.39609 | -0.39609 | -0.50834 | 0.34943 | -0.68848 | -0.68848 | -0.68848 | -0.68848 | -0.68848 | -0.68848 | -0.39609 | -0.39609
20 | -0.36506 | 13.7048 | -0.37782 | -0.37782 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | 0.10981 | 1.4848 | -0.90728 | -0.00074551 | -0.4483 | -0.4483 | 0.039924 | 1.9249 | 0.34054 | 2.2255 | -0.9834 | -0.85972 | -1.4403 | 26.5433 | -0.83199 | 15.289 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.4483 | -0.4483 | 0.32092 | 1.4842 | -0.59709 | -0.58055 | -0.34647 | -0.32993 | 0.065797 | 3.164 | 0.66101 | 3.7592 | -0.34647 | -0.32993 | -0.34647 | -0.32993 | -0.64671 | -0.64671 | -0.39609 | -0.39609 | -0.48373 | 0.21107 | -0.4483 | -0.4483 | -0.4483 | -0.4483 | -0.4483 | -0.4483 | -0.4483 | -0.4483 | -0.48373 | 0.21107 | -0.48373 | 0.21107 | -0.48373 | 0.21107 | -0.48373 | 0.21107 | -0.39609 | -0.39609 | -0.48373 | 0.21107 | -0.64671 | -0.64671 | -0.64671 | -0.64671 | -0.64671 | -0.64671 | -0.39609 | -0.39609
21 | -0.34418 | 13.0472 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.35043 | 0.39877 | -0.90327 | -0.15408 | -0.39609 | -0.39609 | -0.42062 | 0.82436 | -0.10418 | 1.1408 | -0.9919 | -0.93693 | -1.4403 | 26.5433 | -0.83199 | 14.6807 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.12989 | 0.41909 | -0.5884 | -0.5884 | -0.37955 | -0.37955 | -0.38725 | 2.0755 | 0.23929 | 2.7021 | -0.37955 | -0.37955 | -0.37955 | -0.37955 | -0.60494 | -0.60494 | -0.39609 | -0.39609 | -0.45912 | 0.089859 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.45912 | 0.089859 | -0.45912 | 0.089859 | -0.45912 | 0.089859 | -0.45912 | 0.089859 | -0.39609 | -0.39609 | -0.45912 | 0.089859 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.60494 | -0.39609 | -0.39609
22 | -0.32329 | 12.3896 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.81067 | -0.20382 | -0.89927 | -0.29242 | -0.39609 | -0.39609 | -0.88116 | 0.20336 | -0.5489 | 0.53561 | -1.0004 | -0.98665 | -1.4403 | 26.5433 | -0.83199 | 14.0723 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.5807 | -0.16039 | -0.56317 | -0.56317 | -0.39609 | -0.39609 | -0.8403 | 1.461 | -0.23464 | 2.0667 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.56317 | -0.56317 | -0.39609 | -0.39609 | -0.4345 | -0.014193 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.4345 | -0.014193 | -0.4345 | -0.014193 | -0.4345 | -0.014193 | -0.4345 | -0.014193 | -0.39609 | -0.39609 | -0.4345 | -0.014193 | -0.56317 | -0.56317 | -0.56317 | -0.56317 | -0.56317 | -0.56317 | -0.39609 | -0.39609
23 | -0.30241 | 11.7321 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.80245 | -0.32296 | -0.89527 | -0.41578 | -0.39609 | -0.39609 | -0.87324 | 0.061879 | -0.52516 | 0.40996 | -1.0089 | -1.0089 | -1.4403 | 26.5433 | -0.83199 | 13.464 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.56304 | -0.25424 | -0.5214 | -0.5214 | -0.39609 | -0.39609 | -0.82489 | 1.3205 | -0.24011 | 1.9052 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.5214 | -0.5214 | -0.39609 | -0.39609 | -0.40989 | -0.10109 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.40989 | -0.10109 | -0.40989 | -0.10109 | -0.40989 | -0.10109 | -0.40989 | -0.10109 | -0.39609 | -0.39609 | -0.40989 | -0.10109 | -0.5214 | -0.5214 | -0.5214 | -0.5214 | -0.5214 | -0.5214 | -0.39609 | -0.39609
24 | -0.28152 | 11.0745 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.79423 | -0.42712 | -0.89127 | -0.52416 | -0.39609 | -0.39609 | -0.86532 | -0.068532 | -0.50142 | 0.29537 | -1.0036 | -1.0036 | -1.4403 | 26.5433 | -0.83199 | 12.8556 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.54539 | -0.33095 | -0.47963 | -0.47963 | -0.39609 | -0.39609 | -0.80947 | 1.1854 | -0.24559 | 1.7493 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.47963 | -0.47963 | -0.39609 | -0.39609 | -0.38527 | -0.17083 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.38527 | -0.17083 | -0.38527 | -0.17083 | -0.38527 | -0.17083 | -0.38527 | -0.17083 | -0.39609 | -0.39609 | -0.38527 | -0.17083 | -0.47963 | -0.47963 | -0.47963 | -0.47963 | -0.47963 | -0.47963 | -0.39609 | -0.39609
25 | -0.26064 | 10.4169 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.78601 | -0.51629 | -0.88726 | -0.61755 | -0.39609 | -0.39609 | -0.8574 | -0.18788 | -0.47767 | 0.19185 | -0.98466 | -0.98466 | -1.4403 | 26.5433 | -0.83199 | 12.2473 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.52774 | -0.39049 | -0.43786 | -0.43786 | -0.39609 | -0.39609 | -0.79406 | 1.0558 | -0.25106 | 1.5988 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.43786 | -0.43786 | -0.39609 | -0.39609 | -0.36066 | -0.22342 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.36066 | -0.22342 | -0.36066 | -0.22342 | -0.36066 | -0.22342 | -0.36066 | -0.22342 | -0.39609 | -0.39609 | -0.36066 | -0.22342 | -0.43786 | -0.43786 | -0.43786 | -0.43786 | -0.43786 | -0.43786 | -0.39609 | -0.39609
26 | -0.23975 | 9.7594 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.77778 | -0.59048 | -0.88326 | -0.69596 | -0.39609 | -0.39609 | -0.84948 | -0.29615 | -0.45393 | 0.09939 | -0.96567 | -0.96567 | -1.4403 | 26.5433 | -0.83199 | 11.639 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.51009 | -0.43289 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.77865 | 0.93162 | -0.25653 | 1.4537 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.33605 | -0.25885 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.33605 | -0.25885 | -0.33605 | -0.25885 | -0.33605 | -0.25885 | -0.33605 | -0.25885 | -0.39609 | -0.39609 | -0.33605 | -0.25885 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
27 | -0.21887 | 9.1018 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.76956 | -0.64969 | -0.87926 | -0.75939 | -0.39609 | -0.39609 | -0.84156 | -0.39337 | -0.43019 | 0.018001 | -0.94669 | -0.94669 | -1.4403 | 26.5433 | -0.83199 | 11.0306 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.49243 | -0.45812 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.76324 | 0.81295 | -0.26201 | 1.3142 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.3532 | -0.31889 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.3532 | -0.31889 | -0.3532 | -0.31889 | -0.3532 | -0.31889 | -0.3532 | -0.31889 | -0.39609 | -0.39609 | -0.3532 | -0.31889 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
28 | -0.19798 | 8.4442 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.76134 | -0.69391 | -0.87526 | -0.80783 | -0.39609 | -0.39609 | -0.83364 | -0.47951 | -0.40645 | -0.052323 | -0.9277 | -0.9277 | -1.4403 | 26.5433 | -0.83199 | 10.4223 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.47478 | -0.4662 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.74783 | 0.69974 | -0.26748 | 1.1801 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.37036 | -0.36178 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.37036 | -0.36178 | -0.37036 | -0.36178 | -0.37036 | -0.36178 | -0.37036 | -0.36178 | -0.39609 | -0.39609 | -0.37036 | -0.36178 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
29 | -0.1771 | 7.7866 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.75312 | -0.72315 | -0.87126 | -0.84129 | -0.39609 | -0.39609 | -0.82572 | -0.55459 | -0.38271 | -0.11158 | -0.90872 | -0.90872 | -1.4403 | 26.5433 | -0.83199 | 9.8139 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.45713 | -0.45713 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.73242 | 0.59202 | -0.27295 | 1.0515 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.38751 | -0.38751 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.38751 | -0.38751 | -0.38751 | -0.38751 | -0.38751 | -0.38751 | -0.38751 | -0.38751 | -0.39609 | -0.39609 | -0.38751 | -0.38751 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
30 | -0.15621 | 7.1291 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.7449 | -0.73741 | -0.86725 | -0.85976 | -0.39609 | -0.39609 | -0.8178 | -0.6186 | -0.35897 | -0.15977 | -0.88973 | -0.88973 | -1.4403 | 26.5433 | -0.83199 | 9.2056 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.4309 | -0.4309 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.717 | 0.48976 | -0.27842 | 0.92834 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
31 | -0.13533 | 6.4715 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.73668 | -0.73668 | -0.86325 | -0.86325 | -0.39609 | -0.39609 | -0.80988 | -0.67155 | -0.33522 | -0.19689 | -0.87074 | -0.87074 | -1.4403 | 26.5433 | -0.83199 | 8.5973 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.70159 | 0.39298 | -0.2839 | 0.81068 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
32 | -0.11445 | 5.8139 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.72096 | -0.72096 | -0.85176 | -0.85176 | -0.39609 | -0.39609 | -0.80196 | -0.71343 | -0.34629 | -0.25776 | -0.85176 | -0.85176 | -1.4403 | 26.5433 | -0.83199 | 7.9889 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.68618 | 0.30167 | -0.28937 | 0.69848 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
33 | -0.09356 | 5.1564 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.69776 | -0.69776 | -0.83277 | -0.83277 | -0.39609 | -0.39609 | -0.79404 | -0.74424 | -0.35736 | -0.30756 | -0.83277 | -0.83277 | -1.4403 | 26.5433 | -0.83199 | 7.3806 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.67077 | 0.21584 | -0.29484 | 0.59176 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
34 | -0.072676 | 4.4988 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.67455 | -0.67455 | -0.81379 | -0.81379 | -0.39609 | -0.39609 | -0.78612 | -0.76399 | -0.36842 | -0.34629 | -0.81379 | -0.81379 | -1.4403 | 26.5433 | -0.83199 | 6.7723 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.65536 | 0.13547 | -0.30032 | 0.49051 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
35 | -0.051791 | 3.8412 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.65135 | -0.65135 | -0.7948 | -0.7948 | -0.39609 | -0.39609 | -0.7782 | -0.77267 | -0.37949 | -0.37396 | -0.7948 | -0.7948 | -1.4403 | 26.5433 | -0.83199 | 6.1639 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.63994 | 0.060582 | -0.30579 | 0.39474 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
36 | -0.030906 | 3.1837 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.62814 | -0.62814 | -0.77581 | -0.77581 | -0.39609 | -0.39609 | -0.77028 | -0.77028 | -0.39056 | -0.39056 | -0.77581 | -0.77581 | -1.4403 | 26.5433 | -0.83199 | 5.5556 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.62453 | -0.0088352 | -0.31126 | 0.30444 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
37 | -0.010021 | 2.5261 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.60494 | -0.60494 | -0.75683 | -0.75683 | -0.39609 | -0.39609 | -0.75683 | -0.75683 | -0.39609 | -0.39609 | -0.75683 | -0.75683 | -1.4403 | 26.5433 | -0.83199 | 4.9472 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.60912 | -0.07278 | -0.31673 | 0.21961 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
38 | 0.010863 | 1.8685 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.58173 | -0.58173 | -0.73784 | -0.73784 | -0.39609 | -0.39609 | -0.73784 | -0.73784 | -0.39609 | -0.39609 | -0.73784 | -0.73784 | -1.4403 | 26.5433 | -0.83199 | 4.3389 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.59371 | -0.13125 | -0.32221 | 0.14025 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
39 | 0.031748 | 1.2109 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.55853 | -0.55853 | -0.71885 | -0.71885 | -0.39609 | -0.39609 | -0.71885 | -0.71885 | -0.39609 | -0.39609 | -0.71885 | -0.71885 | -1.4403 | 26.5433 | -0.83199 | 3.7306 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.5783 | -0.18425 | -0.32768 | 0.066367 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
40 | -0.2166 | 0.55337 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.53532 | -0.53532 | -0.69987 | -0.69987 | -0.39609 | -0.39609 | -0.69987 | -0.69987 | -0.39609 | -0.39609 | -0.69987 | -0.69987 | -1.4403 | 26.5433 | -0.83199 | 3.1222 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.56288 | -0.23178 | -0.33315 | -0.0020441 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
41 | -0.46494 | 0.16503 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.51212 | -0.51212 | -0.68088 | -0.68088 | -0.39609 | -0.39609 | -0.68088 | -0.68088 | -0.39609 | -0.39609 | -0.68088 | -0.68088 | -1.4403 | 26.5433 | -0.83199 | 2.5139 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.54747 | -0.27383 | -0.33863 | -0.064982 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
42 | -0.44406 | 0.04592 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.48891 | -0.48891 | -0.6619 | -0.6619 | -0.39609 | -0.39609 | -0.6619 | -0.6619 | -0.39609 | -0.39609 | -0.6619 | -0.6619 | -1.4403 | 26.5433 | -0.83199 | 1.9055 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.53206 | -0.31041 | -0.3441 | -0.12245 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
43 | -0.42317 | -0.073189 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.46571 | -0.46571 | -0.64291 | -0.64291 | -0.39609 | -0.39609 | -0.64291 | -0.64291 | -0.39609 | -0.39609 | -0.64291 | -0.64291 | -1.4403 | 26.5433 | -0.83199 | 1.2972 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.51665 | -0.34152 | -0.34957 | -0.17444 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
44 | -0.40229 | -0.1923 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.4425 | -0.4425 | -0.62392 | -0.62392 | -0.39609 | -0.39609 | -0.62392 | -0.62392 | -0.39609 | -0.39609 | -0.62392 | -0.62392 | -1.4403 | 26.5433 | -0.83199 | 0.68886 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.50124 | -0.36715 | -0.35504 | -0.22096 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
45 | -0.3814 | -0.31141 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.4193 | -0.4193 | -0.60494 | -0.60494 | -0.39609 | -0.39609 | -0.60494 | -0.60494 | -0.39609 | -0.39609 | -0.60494 | -0.60494 | -1.4403 | 26.5433 | -0.83199 | 0.08052 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.48583 | -0.38731 | -0.36052 | -0.26201 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
46 | -0.43052 | -0.43052 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.58595 | -0.58595 | -0.39609 | -0.39609 | -0.58595 | -0.58595 | -0.39609 | -0.39609 | -0.58595 | -0.58595 | -1.4403 | 26.5433 | -0.83199 | -0.52782 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.47041 | -0.402 | -0.36599 | -0.29758 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
47 | -0.47963 | -0.47963 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.56697 | -0.56697 | -0.39609 | -0.39609 | -0.56697 | -0.56697 | -0.39609 | -0.39609 | -0.56697 | -0.56697 | -1.4403 | 26.5433 | -1.1362 | -1.1362 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.455 | -0.41122 | -0.37146 | -0.32768 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
48 | -0.45874 | -0.45874 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.54798 | -0.54798 | -0.39609 | -0.39609 | -0.54798 | -0.54798 | -0.39609 | -0.39609 | -0.54798 | -0.54798 | -1.4403 | 26.5433 | -1.4403 | -1.4403 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.43959 | -0.41496 | -0.37694 | -0.35231 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
49 | -0.43786 | -0.43786 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.52899 | -0.52899 | -0.39609 | -0.39609 | -0.52899 | -0.52899 | -0.39609 | -0.39609 | -0.52899 | -0.52899 | -1.4403 | 26.5433 | -1.4403 | -1.4403 | -1.4403 | 26.5433 | -0.39609 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.42418 | -0.41323 | -0.38241 | -0.37146 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
50 | -0.41697 | -0.41697 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.51001 | -0.51001 | -0.39609 | -0.39609 | -0.51001 | -0.51001 | -0.39609 | -0.39609 | -0.51001 | -0.51001 | 26.5433 | 26.5433 | -1.4403 | -1.4403 | 26.5433 | 26.5433 | 0.30227 | 0.30227 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.40603 | -0.40603 | -0.38514 | -0.38514 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609 | -0.39609
| Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book | Earnings | Book
1 | -4.4662 | 97.8 | -7.6829 | 93.3333 | -17.2851 | 80 | -17.2851 | 80 | -5.6824 | 96.1111 | -4.715 | 97.4545 | -7.0228 | 94.25 | -5.3042 | 96.6364 | -6.7227 | 94.6667 | -4.5185 | 97.7273 | -2.8818 | 100 | -2.8818 | 100 | -2.8818 | 100 | -9.3633 | 91 | -6.4826 | 95 | -5.2824 | 96.6667 | -5.7625 | 96 | -10.0834 | 90 | -4.4662 | 97.8 | -6.8427 | 94.5 | -7.6829 | 93.3333 | -13.1699 | 85.7143 | -5.7625 | 96 | -11.8839 | 87.5 | -5.7625 | 96 | -6.4826 | 95 | -6.4826 | 95 | -6.4826 | 95 | -6.4826 | 95 | -5.7625 | 96 | -5.7625 | 96 | -5.7625 | 96 | -5.7625 | 96 | -10.0834 | 90 | -5.7625 | 96 | -5.7625 | 96 | -5.7625 | 96 | -5.7625 | 96 | -7.6829 | 93.3333
2 | -4.4136 | 95.6 | -7.5172 | 86.6667 | -16.7879 | 60 | -16.7879 | 60 | -5.6032 | 92.2222 | -4.6593 | 94.9091 | -6.8877 | 88.5 | -5.2367 | 93.2727 | -6.611 | 89.3333 | -4.4668 | 95.4545 | -2.8818 | 100 | -2.8818 | 100 | -2.8818 | 100 | -9.1291 | 82 | -6.3583 | 90 | -5.1995 | 93.3333 | -5.663 | 92 | -9.8349 | 80 | -4.4136 | 95.6 | -6.7112 | 89 | -7.5172 | 86.6667 | -12.8148 | 71.4286 | -5.663 | 92 | -11.5731 | 75 | -5.663 | 92 | -6.3583 | 90 | -6.3583 | 90 | -6.3583 | 90 | -6.3583 | 90 | -5.663 | 92 | -5.663 | 92 | -5.663 | 92 | -5.663 | 92 | -9.8349 | 80 | -5.663 | 92 | -5.663 | 92 | -5.663 | 92 | -5.663 | 92 | -7.5172 | 86.6667
3 | -4.361 | 93.4 | -7.3515 | 80 | -16.2908 | 40 | -16.2908 | 40 | -5.5239 | 88.3333 | -4.6036 | 92.3636 | -6.7526 | 82.75 | -5.1692 | 89.9091 | -6.4993 | 84 | -4.4151 | 93.1818 | -2.8818 | 100 | -2.8818 | 100 | -2.8818 | 100 | -8.895 | 73 | -6.2341 | 85 | -5.1166 | 90 | -5.5636 | 88 | -9.5863 | 70 | -4.361 | 93.4 | -6.5797 | 83.5 | -7.3515 | 80 | -12.4597 | 57.1429 | -5.5636 | 88 | -11.2624 | 62.5 | -5.5636 | 88 | -6.2341 | 85 | -6.2341 | 85 | -6.2341 | 85 | -6.2341 | 85 | -5.5636 | 88 | -5.5636 | 88 | -5.5636 | 88 | -5.5636 | 88 | -9.5863 | 70 | -5.5636 | 88 | -5.5636 | 88 | -5.5636 | 88 | -5.5636 | 88 | -7.3515 | 80
4 | -4.3084 | 91.2 | -7.1858 | 73.3333 | -15.7937 | 20 | -15.7937 | 20 | -5.4447 | 84.4444 | -4.5479 | 89.8182 | -6.6175 | 77 | -5.1018 | 86.5455 | -6.3876 | 78.6667 | -4.3633 | 90.9091 | -2.8818 | 100 | -2.8818 | 100 | -2.8818 | 100 | -8.6608 | 64 | -6.1098 | 80 | -5.0338 | 86.6667 | -5.4642 | 84 | -9.3377 | 60 | -4.3084 | 91.2 | -6.4482 | 78 | -7.1858 | 73.3333 | -12.1046 | 42.8571 | -5.4642 | 84 | -10.9517 | 50 | -5.4642 | 84 | -6.1098 | 80 | -6.1098 | 80 | -6.1098 | 80 | -6.1098 | 80 | -5.4642 | 84 | -5.4642 | 84 | -5.4642 | 84 | -5.4642 | 84 | -9.3377 | 60 | -5.4642 | 84 | -5.4642 | 84 | -5.4642 | 84 | -5.4642 | 84 | -7.1858 | 73.3333
5 | -4.2558 | 89 | -7.02 | 66.6667 | -15.2965 | 0 | -15.2965 | 0 | -5.3654 | 80.5556 | -4.4922 | 87.2727 | -6.4824 | 71.25 | -5.0343 | 83.1818 | -6.2759 | 73.3333 | -4.3116 | 88.6364 | -2.8818 | 100 | -2.8818 | 100 | -2.8818 | 100 | -8.4267 | 55 | -5.9855 | 75 | -4.9509 | 83.3333 | -5.3647 | 80 | -9.0892 | 50 | -4.2558 | 89 | -6.3167 | 72.5 | -7.02 | 66.6667 | -11.7495 | 28.5714 | -5.3647 | 80 | -10.641 | 37.5 | -5.3647 | 80 | -5.9855 | 75 | -5.9855 | 75 | -5.9855 | 75 | -5.9855 | 75 | -5.3647 | 80 | -5.3647 | 80 | -5.3647 | 80 | -5.3647 | 80 | -9.0892 | 50 | -5.3647 | 80 | -5.3647 | 80 | -5.3647 | 80 | -5.3647 | 80 | -7.02 | 66.6667