## 2023 Outage Log
Outage Date | Circuit | Substation | Location (Street Address) | Area | Response Time | Number of Customers Out | AFN Customers Out | Outage Duration | Customer Minutes Out | Event SAIDI | Daily SAIDI | Outage Cause Category | Wire Down | Protective Device Actuated | Description of Cause
2023-01-09 | Erwin Lake | Maltby Substation | 416 San Martin | Sugarloaf | <5 Minutes | 5 | 0 | 96 | 480 | 0.019653 | 0.019653 | Vegetation contact | Yes | ELF Blown | A tree fell and broke the #2 str. H.T. that feeds the area.
2023-01-10 | Boulder | Village Substation | 39771 Forest | Big Bear Lake | <5 Minutes | 8 | 0 | 120 | 960 | 0.039306 | 3.277 | Vegetation contact | Yes | No | High winds blew a tree down leading to contact with the lines.
2023-01-10 | North Shore | Fawnskin Substation | 40006 North Shore | Fawnskin | <5 Minutes | 1523 | 46 | 49 | 74627 | 3.0555 |  | Vegetation contact | No | AR/Switch Actuated | High Winds lead to vegetation contact with the lines.
2023-01-10 | Boulder | Village Substation | 749 Cienega | Big Bear Lake | <5 Minutes | 50 | 1 | 89 | 4450 | 0.1822 |  | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | The TripSaver opened. The cause of the opening is unknown
2023-01-19 | Erwin Lake | Maltby Substation | 357 Greenspot | Big Bear City | <5 Minutes | 11 | 0 | 247 | 2717 | 0.11124 | 0.11124 | Equipment / facility failure or damage- Conductor | No | No | There was a bad primary connection at cut-out of transformer.
2023-01-21 | Sunrise | Maple Substation | 190 Victoria Ln | Sugarloaf | <5 Minutes | 8 | 0 | 150 | 1200 | 0.049132 | 0.049132 | Equipment / facility failure or damage- Cutout | No | ELF Blown | Elf fuse opened for unknown reasons.
2023-01-22 | North Shore | Fawnskin Substation | BB track lease #311 | Fawnskin | <5 Minutes | 3 | 0 | 347 | 1041 | 0.042622 | 0.042622 | Equipment / facility failure or damage- Transformer | No | TripSaver Actuated | There was a bad 5kVA transformer, which lead to a fuse opening
2023-02-14 | Pioneer | Palomino Substation | 454040 3rd | Big Bear City | <5 Minutes | 3 | 0 | 113 | 339 | 0.01388 | 0.01388 | Equipment / facility failure or damage- Connection Device | No | No | Due to high winds a Neutral broke off transformer.
2023-02-21 | Sunset | Maple Substation | 600 block of Orange s/o Barton | Sugarloaf | <5 Minutes | 1629 | 61 | 180 | 293220 | 12.0054 | 18.9315 | Wire-to-wire contact | No | AR/Switch Actuated | High winds lead to line to line contact (slap) of the primary phases
2023-02-21 | North Shore | Fawnskin Substation | Rim of the World 1/4 mile beyond pavement | Fawnskin | <5 Minutes | 1353 | 27 | 120 | 162360 | 6.6476 |  | Vegetation contact | Yes | AR/Switch Actuated | Wind event caused down tree which broke the primary line
2023-02-21 | North Shore | Fawnskin Substation | Rim of the World 1/4 mile beyond pavement | Fawnskin |  | 12 |  | 567 | 6804 | 0.27858 |  | Vegetation contact |  |  | Same outage as above
2023-02-22 | Paradise | Maltby Substation | 437 Sugarloaf | Big Bear City | 5-10 Minutes | 4 | 0 | 118 | 472 | 0.019325 | 0.019325 | Vegetation contact | Yes | No | A tree fell due to snow and wind taking down service and secondary lines
2023-04-18 | Erwin Lake | Maltby Substation | Woodland x 7th | Erwin Lake | <5 Minutes | 2015 | 61 | 60 | 120900 | 4.95 | 4.8957 | All Other | No | AR/Switch Actuated | Line crews contaced phases during work, which created an outage.
2023-05-05 | Erwin Lake | Maltby Substation | 2129 1st Ln | Erwin Lake | <5 Minutes | 14 | 0 | 92 | 1288 | 0.052735 | 0.052156 | Equipment / facility failure or damage- Fuse | No | ELF Blown | Elf fuse opened for unknown reasons.
2023-06-19 | Baldwin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City | <5 Minutes | 6802 | 683 | 108 | 734616 | 30.0776 | 126.9049 | All Other | No | AR/Switch Actuated | Southern California Edison had a fault at the Substation that feeds BVES. This caused the supply of energy to drop.
2023-06-19 | Baldwin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City |  | 4907 |  | 2 | 9814 | 0.40182 |  | All Other |  |  | Same outage as above
2023-06-19 | Baldwin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City |  | 4 |  | 10 | 40 | 0.0016377 |  | All Other |  |  | Same outage as above
2023-06-19 | Shay | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake |  | 7644 |  | 184 | 1406496 | 57.5866 |  | All Other |  |  | Same outage as above
2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake |  | 1056 |  | 111 | 117216 | 4.7992 |  | All Other |  |  | Same outage as above
2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake |  | 1040 |  | 17 | 17680 | 0.72388 |  | All Other |  |  | Same outage as above
2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Shay IR3440 | Big Bear Lake |  | 1020 |  | 44 | 44880 | 1.8375 |  | All Other |  |  | Same outage as above
2023-06-19 | Garstin | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 1056 |  | 9 | 9504 | 0.38913 |  | All Other |  |  | Same outage as above
2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 880 |  | 120 | 105600 | 4.3236 |  | All Other |  |  | Same outage as above
2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 850 |  | 4 | 3400 | 0.13921 |  | All Other |  |  | Same outage as above
2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 840 |  | 8 | 6720 | 0.27514 |  | All Other |  |  | Same outage as above
2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 810 |  | 18 | 14580 | 0.59695 |  | All Other |  |  | Same outage as above
2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 800 |  | 22 | 17600 | 0.7206 |  | All Other |  |  | Same outage as above
2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 880 |  | 9 | 7920 | 0.32427 |  | All Other |  |  | Same outage as above
2023-06-19 | Interlaken | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 100 |  | 145 | 14500 | 0.59368 |  | All Other |  |  | Same outage as above
2023-06-19 | Fox Farm | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear Lake |  | 35 |  | 182 | 6370 | 0.26081 |  | All Other |  |  | Same outage as above
2023-06-19 | Erwin Lake | SCE Goldhill Substation | 34kV Baldwin IR3430 | Big Bear City |  | 2533 |  | 230 | 582590 | 23.8532 |  | All Other |  |  | Same outage as above
2023-07-01 | Eagle | Pineknot Substation | s/e corner Finch x Swallow | Big Bear Lake | <5 Minutes | 50 | 1 | 53 | 2650 | 0.1085 | 0.1085 | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | Tripsaver fuse opened and needed to be replaced.
2023-07-09 | Shay | Moonridge Substation | 896 Clubview Dr | Big Bear Lake | <5 Minutes | 15000 | 378 | 61 | 915000 | 37.4632 | 98.6079 | Object contact- Land Vehicle Contact | No | AR/Switch Actuated | A car hit the guy wire and cracked the pole. The vehicle incident also broke a 34kV cross arm two spans away.
2023-07-09 | Shay | Moonridge Substation | 896 Clubview Dr | Big Bear Lake |  | 3800 |  | 393 | 1493400 | 61.1448 |  | Object contact- Land Vehicle Contact |  |  | Same outage as above
2023-07-12 | Erwin Lake | Maltby Substation | C ln x Juniper | Erwin Lake | <5 Minutes | 18 | 0 | 120 | 2160 | 0.088438 | 0.1474 | All Other | No | Other | Outsource had a planned outage and the crew didn't hook up one transformer on primary lead.
2023-07-12 | Erwin Lake | Maltby Substation | Oak x D ln | Erwin Lake |  | 16 |  | 90 | 1440 | 0.058958 |  | All Other |  |  | Same outage as above
2023-07-22 | Shay |  | PS3436IR Shay w/o Barranca | Service Area Wide | <5 Minutes | 16599 | 683 | 89 | 1477311 | 60.486 | 60.486 | Equipment / facility failure or damage- Other | No | AR/Switch Actuated | Switch opened because of an imbalence. Sensing equipment was found to be bad and needed replacement.
2023-08-13 | Garstin | Meadow Substation | 562 Ponderosa x Brownie | Big Bear Lake | <5 Minutes | 8 | 0 | 83 | 664 | 0.027186 | 0.068785 | Lightning | No | ELF Blown | 25kVA transformer ELF blew because of lightning.
2023-08-13 | Castle Glen | Division Substation | 1209 Juniper | Big Bear City | <5 Minutes | 11 | 0 | 74 | 814 | 0.033328 |  | Lightning | No | ELF Blown | 15kVA transformer ELF blew because of lightning.
2023-08-13 | Castle Glen | Division Substation | 626 McAlister | Big Bear City | <5 Minutes | 2 | 0 | 101 | 202 | 0.0082706 |  | Lightning | No | ELF Blown | 15kVA transformer ELF blew because of lightning.
2023-08-30 | Interlaken | Meadow Substation | Club View Dr | Big Bear Lake | <5 Minutes | 3014 | 95 | 61 | 183854 | 7.5276 | 7.6504 | All Other | No | AR/Switch Actuated | Outsource crew contacted phase Interlaken servicing Goldmine and portion of Club View circuits
2023-08-30 | Interlaken | Meadow Substation | Club View Dr | Big Bear Lake |  | 150 |  | 20 | 3000 | 0.12283 |  | All Other |  |  | Same outage as above
2023-09-12 | North Shore | Fawnskin Substation | 1023 Fawnskin Dr | Fawnskin | <5 Minutes | 8 | 0 | 90 | 720 | 0.029479 | 0.029479 | Unknown | No | ELF Blown | Uknown reason for outage.
2023-09-16 | Baldwin | Fawnskin Substation | Fawnskin Substation | Big Bear City | <5 Minutes | 8700 | 207 | 58 | 504600 | 20.66 | 22.3925 | Object contact- Animal contact | No | AR/Switch Actuated | A hawk contacted the Baldwin 34kV line at Fawnskin Sub. No damage was reported.
2023-09-16 | Baldwin | Fawnskin Substation | Fawnskin Substation | Big Bear City |  | 2015 |  | 21 | 42315 | 1.7325 |  | Object contact- Animal contact |  |  | Same outage as above
2023-09-21 | Castle Glen | Division Substation | 1161 Sugarpine Dr | Big Bear City | 5-10 Minutes | 14 | 0 | 51 | 714 | 0.029234 | 0.029234 | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | Tripsaver fuse opened and needed to be replaced.
2023-11-12 | Erwin Lake | Maltby Substation | Malabar/Zaca | Big Bear City | <5 Minutes | 25 | 1 | 63 | 1575 | 0.064486 | 0.063778 | Unknown | No | TripSaver Actuated | The TripSaver opened on 0 amps (fault) and had 13 amps when it reclosed
2023-11-16 | Goldmine | Moonridge Substation | Wolf x Villa Grove | Big Bear Lake | <5 Minutes | 2660 | 61 | 25 | 66500 | 2.7227 | 4.5496 | Object contact- Other | No | AR/Switch Actuated | Line crews contaced phases during work, which created an outage.
2023-11-16 | Goldmine | Moonridge Substation | Wolf x Villa Grove | Big Bear Lake |  | 2000 |  | 13 | 26000 | 1.0645 |  | Object contact- Other |  |  | Same outage as above
2023-11-16 | Goldmine | Moonridge Substation | Wolf x Villa Grove | Big Bear Lake |  | 2660 |  | 7 | 18620 | 0.76236 |  | Object contact- Other |  |  | Same outage as above
2023-11-17 | Goldmine | Moonridge Substation | 828 Tehama | Big Bear Lake | <5 Minutes | 30 | 0 | 137 | 4110 | 0.16828 | 0.16643 | Unknown | No | TripSaver Actuated | Tripsaver fuse opened for unknown reasons.
2023-11-19 | Baldwin |  | 2 spans e/o Bear Loop | Big Bear Lake | <5 Minutes | 11621 | 318 | 72 | 836712 | 34.2578 | 37.7584 | Object contact- Land Vehicle Contact | Yes | AR/Switch Actuated | A car made cntact with a pole. The associated report is listed below. CHP report # 9865
2023-11-19 | Baldwin |  | 2 spans e/o Bear Loop | Big Bear Lake |  | 75 |  | 1140 | 85500 | 3.5007 |  | Object contact- Land Vehicle Contact |  |  | Same outage as above
2023-12-20 | SCE Goldhill Ute Lines | SCE Goldhill Substation | SCE Goldhill Substation | Service Area Wide | <5 Minutes | 21203 | 683 | 4 | 84812 | 3.4725 | 3.4725 | All Other | No | No | Southern California Edison had a fault at the Substation that feeds BVES. This caused the supply of energy to drop.
2023-12-21 | Clubview | Moonridge Substation | 42736 Sonoma | Big Bear Lake | <5 Minutes | 50 | 1 | 78 | 3900 | 0.15968 | 0.15968 | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | A TripSaver opened but the cause of the opening is unknown
2023-12-22 | Goldmine | Moonridge Substation | Primrose x Primrose Ct. Pole 3566BV | Big Bear Lake | <5 Minutes | 30 | 1 | 140 | 4200 | 0.17196 | 7.2081 | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | Tripsaver fuse opened and needed to be replaced.
2023-12-22 |  | Village Substation | Village Substation: 4kV Bouder, Harnish & Lagunita circuits | Big Bear Lake | <5 Minutes | 3437 | 232 | 50 | 171850 | 7.0361 |  | Equipment / facility failure or damage- Other | No | AR/Switch Actuated | 34kV Radford IR3470 opened but the reason is unknown. The switch over to Shay Line did not occur on it's own.
2023-12-23 |  | Village Substation | Village Substation: 4kV Bouder, Harnish & Lagunita circuits | Big Bear Lake |  | 2046 |  | 31 | 63426 | 2.5969 | 2.6629 | Equipment / facility failure or damage- Other |  |  | Same outage as above
2023-12-23 | Clubview | Moonridge Substation | 42935 Dogwood | Big Bear Lake | <5 Minutes | 13 | 0 | 124 | 1612 | 0.066001 |  | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | Tripsaver fuse opened and needed to be replaced.
2023-12-25 | Erwin Lake | Maltby Substation | 1208 Big Bear Bl. | Big Bear City | <5 Minutes | 1000 | 121 | 121 | 121000 | 4.9541 | 4.9541 | Equipment / facility failure or damage- Connection Device | No | AR/Switch Actuated | Possible bad connector on transformer on 13739BV Big Bear Blvd / Barranca
2023-12-27 | North Shore | Fawnskin Substation | 42402 Golden Oak | Big Bear Lake | <5 Minutes | 100 | 2 | 59 | 5900 | 0.24157 | 0.41783 | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | Tripsaver fuse opened and needed to be replaced.
2023-12-27 | Interlaken | Meadow Substation | 200 N Teakwood | Big Bear Lake |  | 50 |  | 75 | 3750 | 0.15354 |  | Equipment / facility failure or damage- Fuse |  |  | Same outage as above
2023-12-27 | Sunrise | Maple Substation | 240 Los Angeles | Sugarloaf | <5 Minutes | 15 | 0 | 37 | 555 | 0.022724 |  | Equipment / facility failure or damage- Other | No | ELF Blown | There was a blown 6 amp ELF fuse. The 10kVA transformer and 6 amp ELF fuse were replaced with a 12 amp ELF fuse
2023-12-29 | Castle Glen | Division Substation | corner of Grove x Division | Big Bear Lake | <5 Minutes | 25 | 0 | 90 | 2250 | 0.092123 | 0.092123 | Equipment / facility failure or damage- Fuse | No | TripSaver Actuated | Tripsaver fuse opened for unknown reasons.