## Sheet 1
ACI-23-10 - Transmission Conductor Splice Assessment 2022 Findings
# | a) ID Number |  | b) Date of X-ray | c) Date of most recent detailed inspection prior to X-ray |  | d) Date of most recent infared inspection | e) Circuit |  | f) Issue Category | g) (why the P1, P2, or P3 notification was generated) | h) Root Cause | i) Potential Systematic Causes
| FLOC | Detail | Inspection Date | Date of Ground Inspection | Date of Aerial Inspection | Inspection Date | Circuit Name | Circuit ET | Findings (P1, P2, None)
1 | OH-7017134 | T4-1 to T4-2 Top phase right sub conductor | 2022-03-25 | 5/18/2021 | 2021-04-01 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | None | N/A | N/A | N/A
2 | OH-7017134 | T4-1 to T4-2 Top phase left sub conductor | 2022-03-25 | 5/18/2021 | 2021-04-01 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | P3 | Foreign object, lack of grease | N/A | N/A
3 | OH-7005604 | 100/4-101/1 Left Phase Left Sub | 2022-03-29 | 6/6/2021 | 2021-06-09 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | P3 | steel sleeve off centered and bad crimps, steel core gap, lack of grease | N/A | N/A
4 | OH-7005604 | 100/4-101/1 Left Phase Right Sub | 2022-03-29 | 6/6/2021 | 2021-06-09 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | P3 | Steel sleeve bad crimps | N/A | N/A
5 | OH-7005604 | 100/4-101/1 Middle Phase Left Sub | 2022-03-29 | 6/6/2021 | 2021-06-09 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | P3 | steel sleeve off centered, steel core gap | N/A | N/A
6 | OH-7005604 | 100/4-101/1 Middle Phase Right Sub | 2022-03-29 | 6/6/2021 | 2021-06-09 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | None | N/A | N/A | N/A
7 | OH-7005604 | 100/4-101/1 Right Phase Left Sub | 2022-03-29 | 6/6/2021 | 2021-06-09 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | P3 | steel sleeve off centered, steel core gap | N/A | N/A
8 | OH-7005604 | 100/4-101/1 Right Phase Right Sub | 2022-03-29 | 6/6/2021 | 2021-06-09 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | P2 | steel sleeve off center and bowed, aluminum strands touching steel sleeve | N/A | N/A
9 | OH-7005617 | 103/3-103/4 Left Phase Left Sub | 2022-03-29 | 6/22/2021 | 2021-06-07 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | P3 | steel sleeve off centered | N/A | N/A
10 | OH-7005617 | 103/3-103/4 Left Phase Right Sub | 2022-03-29 | 6/22/2021 | 2021-06-07 | 2021-10-13 | MIDWAY-VINCENT NO. 1 | ET-00126 | P2 | steel sleeve off centered | N/A | N/A
11 | OH-7005720 | 101/4-102/1 Left Phase Left Sub | 2022-03-31 | 6/6/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | P3 | steel sleeve off centered, steel core gap | N/A | N/A
12 | OH-7005720 | 101/4-102/1 Left Phase Right Sub | 2022-03-31 | 6/6/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | None | N/A | N/A | N/A
13 | OH-7005720 | 101/4-102/1 Middle Phase Left Sub | 2022-03-31 | 6/6/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | P3 | steel sleeve off centered steel core gap, Aluminum sleeve touching steel sleeve | N/A | N/A
14 | OH-7005720 | 101/4-102/1 Middle Phase Right Sub | 2022-03-31 | 6/6/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | P3 | steel sleeve off centered steel core gap, Aluminum sleeve touching steel sleeve | N/A | N/A
15 | OH-7005720 | 101/4-102/1 Right Phase Left Sub | 2022-03-31 | 6/6/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | None | N/A | N/A | N/A
16 | OH-7005720 | 101/4-102/1 Right Phase Right Sub | 2022-03-31 | 6/6/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | P2 | steel core gap and insufficient grease | N/A | N/A
17 | OH-7005746 | 103/3-103/4 Left Phase Left Sub | 2022-03-31 | 6/22/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | P2 | Steel sleeve off-centered, steel core gap, aluminum strands touching steel sleeve, lack of grease | N/A | N/A
18 | OH-7005746 | 103/3-103/4 Left Phase Right Sub | 2022-03-31 | 6/22/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | P2 | Steel sleeve off-centered and bad crimps, steel core gap, aluminum strands touching steel sleeve, lack of grease | N/A | N/A
19 | OH-7005746 | 103/3-103/4 Middle Phase Left Sub | 2022-03-31 | 6/22/2021 | 2021-06-07 | 2021-11-16 | MIDWAY-VINCENT NO. 2 | ET-00127 | P2 | Steel sleeve off centered, steel core gap, aluminum strands touching steel core | N/A | N/A
20 | OH-7009486 | T5-2 to T5-3 Top Phase Left Sub | 2022-04-05 | 3/6/2021 | 2021-08-19 | 2019-02-22 | PADUA-RANCHO VISTA NO.2 | ET-01900 | P1 | Steel sleeve off centered and bad crimps, steel core gap | N/A | N/A
21 | OH-7009488 | T5-4 to T6-1 Top Phase Left Sub | 2022-04-05 | 2/22/2022 | 2022-02-22 | 2019-02-22 | PADUA-RANCHO VISTA NO.2 | ET-01900 | P3 | Steel sleeve bad compressions, Steel core gap, | N/A | N/A
22 | OH-7009494 | T6-4 to T6-5 Top Phase Right Sub | 2022-04-05 | 4/23/2021 | 2022-02-25 | 2019-02-22 | PADUA-RANCHO VISTA NO.2 | ET-01900 | P3 | Steel sleeve off centered, lack of grease | N/A | N/A
23 | OH-7010956 | T36-3 to T37-1 Top Phase Left Sub | 2022-04-08 | 9/14/2020 | 2020-10-22 | 2020-11-02 | CHINO-SERRANO | ET-00470 | P3 | Steel core gap, need more images, lack of grease | N/A | N/A
24 | OH-7010956 | T36-3 to T37-1 Top Phase Right Sub | 2022-04-08 | 9/14/2020 | 2020-10-22 | 2020-11-02 | CHINO-SERRANO | ET-00470 | P3 | Steel core gap, lack of grease | N/A | N/A
25 | OH-7010956 | T36-3 to T37-1 Top Phase Left Sub | 2022-04-08 | 9/14/2020 | 2020-10-22 | 2020-11-02 | CHINO-VIEJO | ET-00880 | P3 | Steel sleeve bad compressions, Steel core gap, lack of grease | N/A | N/A
26 | OH-7010956 | T36-3 to T37-1 Top Phase Right Sub | 2022-04-08 | 9/14/2020 | 2020-10-22 | 2020-11-02 | CHINO-VIEJO | ET-00880 | P3 | Steel core gap, lack of grease | N/A | N/A
27 | OH-7016941 | T4-1 to T4-2 Top Phase Left Sub | 2022-05-24 | 5/11/2022 | 2022-03-30 | 2022-04-20 | MOORPARK-PARDEE NO.1 | ET-00845 | P2 | Steel core gap and bad compressions, aluminum strands touching steel sleeve, lack of grease | N/A | N/A
28 | OH-7016941 | T4-1 to T4-2 Top Phase Right Sub | 2022-05-24 | 5/11/2022 | 2022-03-30 | 2022-04-20 | MOORPARK-PARDEE NO.1 | ET-00845 | P2 | Steel sleeve off-centered, lack of grease, Aluminum strands not fully compressed | N/A | N/A
29 | OH-7016941 | T4-1 to T4-2 Middle Phase Left Sub | 2022-05-24 | 5/11/2022 | 2022-03-30 | 2022-04-20 | MOORPARK-PARDEE NO.1 | ET-00845 | P3 | Steel core gap, lack of grease | N/A | N/A
30 | OH-7016941 | T4-1 to T4-2 Middle Phase Right Sub | 2022-05-24 | 5/11/2022 | 2022-03-30 | 2022-04-20 | MOORPARK-PARDEE NO.1 | ET-00845 | P3 | Steel core gap, lack of grease | N/A | N/A
31 | OH-7016946 | T5-3 to T5-4 Top Phase Right Sub | 2022-05-24 | 5/12/2022 | 2022-03-30 | 2022-04-20 | MOORPARK-PARDEE NO.1 | ET-00845 | P2 | steel sleeve off centered, aluminum strands not fully compressed, lack of grease | N/A | N/A
32 | OH-7017134 | T4-1 to T4-2 Top Phase Left Sub | 2022-05-25 | 5/18/2021 | 2021-04-01 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | None | N/A | N/A | N/A
33 | OH-7017134 | T4-1 to T4-2 Top Phase Right Sub | 2022-05-25 | 5/18/2021 | 2021-04-01 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | None | N/A | N/A | N/A
34 | OH-7017134 | T4-1 to T4-2 Middle Phase Left Sub | 2022-05-25 | 5/18/2021 | 2021-04-01 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | P3 | Steel core gap, | N/A | N/A
35 | OH-7017134 | T4-1 to T4-2 Middle Phase Right Sub | 2022-05-25 | 5/18/2021 | 2021-04-01 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | P3 | steel core gap, | N/A | N/A
36 | OH-7017241 | T6-3 to T6-4 Top Phase Left Sub | 2022-05-25 | 5/12/2022 | 2021-08-10 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | P3 | Steel core gap, aluminum strands close to steel sleeve, lack of grease | N/A | N/A
37 | OH-7017241 | T6-3 to T6-4 Top Phase Right Sub | 2022-05-25 | 5/12/2022 | 2021-08-10 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | P3 | Steel core off centered, steel core gap, lack of grease | N/A | N/A
38 | OH-7017241 | T6-3 to T6-4 Middle Phase Left Sub | 2022-05-25 | 5/12/2022 | 2021-08-10 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | P3 | Lack of grease | N/A | N/A
39 | OH-7017241 | T6-3 to T6-4 Middle Phase Right Sub | 2022-05-25 | 5/12/2022 | 2021-08-10 | 2022-04-20 | MOORPARK-PARDEE NO.2 | ET-00729 | P2 | Steel core gap, aluminum strands touching steel core, lack of grease | N/A | N/A
40 | OH-7017134 | T4-1 to T4-2 Middle Phase Left Sub | 2022-05-26 | 5/18/2021 | 2021-04-01 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | None | N/A | N/A | N/A
41 | OH-7017134 | T4-1 to T4-2 Middle Phase Right Sub | 2022-05-26 | 5/18/2021 | 2021-04-01 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | P3 | Foreign Object with in splice. | N/A | N/A
42 | OH-7017241 | T6-3 to T6-4 Top Phase Left Sub | 2022-05-26 | 5/12/2022 | 2021-08-10 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | P2 | Steel core gap, aluminum strands touching steel core, lack of grease | N/A | N/A
43 | OH-7017241 | T6-3 to T6-4 Top Phase Right Sub | 2022-05-26 | 5/12/2022 | 2021-08-10 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | P2 | Aluminum strands touching steel core, lack of grease | N/A | N/A
44 | OH-7017241 | T6-3 to T6-4 Middle Phase Left Sub | 2022-05-26 | 5/12/2022 | 2021-08-10 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | P3 | Aluminum strands close to steel sleeve, lack of grease | N/A | N/A
45 | OH-7017241 | T6-3 to T6-4 Middle Phase Right Sub | 2022-05-26 | 5/12/2022 | 2021-08-10 | 2019-05-06 | MOORPARK-PARDEE NO.3 | ET-00731 | P2 | Aluminum strands touching steel core, lack of grease | N/A | N/A
46 | OH-7018521 | T10-3 to T10-4 Left Phase Left Sub | 2022-06-28 | 5/9/2022 | 2021-09-07 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve off centered, aluminum strands touching steel core, lack of grease | N/A | N/A
47 | OH-7018521 | T10-3 to T10-4 Left Phase Right Sub | 2022-06-28 | 5/9/2022 | 2021-09-07 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P1 | Steel sleeve off centered, steel core gap, aluminum strands touching steel core | N/A | N/A
48 | OH-7018521 | T10-3 to T10-4 Middle Phase Left Sub | 2022-06-28 | 5/9/2022 | 2021-09-07 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve off centered, steel core gap, aluminum strands not fully compressed, lack of grease | N/A | N/A
49 | OH-7018521 | T10-3 to T10-4 Middle Phase Right Sub | 2022-06-28 | 5/9/2022 | 2021-09-07 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve off centered, aluminum strands not fully compressed, lack of grease | N/A | N/A
50 | OH-7018521 | T10-3 to T10-4 Right Phase Left Sub | 2022-06-28 | 5/9/2022 | 2021-09-07 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P3 | Steel core gap, lack of grease | N/A | N/A
51 | OH-7018521 | T10-3 to T10-4 Right Phase Right Sub | 2022-06-28 | 5/9/2022 | 2021-09-07 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve off centered, aluminum strands not fully compressed, aluminum stands touching steel core, lack of grease | N/A | N/A
52 | OH-7018533 | T13-2 to T13-3 Left Phase Left Sub | 2022-06-28 | 5/10/2022 | 2022-05-12 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve off centered, steel core gap, aluminum strands not fully compressed, lack of grease | N/A | N/A
53 | OH-7018533 | T13-2 to T13-3 Left Phase Right Sub | 2022-06-28 | 5/10/2022 | 2022-05-12 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve off centered, aluminum strands not fully compressed, lack of grease | N/A | N/A
54 | OH-7018533 | T13-2 to T13-3 Middle Phase Left Sub | 2022-06-28 | 5/10/2022 | 2022-05-12 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve bad crimps, steel core gap, aluminum strands touching steel sleeve, grease missing | N/A | N/A
55 | OH-7018533 | T13-2 to T13-3 Middle Phase Right Sub | 2022-06-28 | 5/10/2022 | 2022-05-12 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | steel sleeve off centered, steel core gap, aluminum strands not fully compressed, lack of grease | N/A | N/A
56 | OH-7018533 | T13-2 to T13-3 Right Phase Left Sub | 2022-06-28 | 5/10/2022 | 2022-05-12 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P1 | Steel sleeve off centered and bad crimps, steel core gap, aluminum strands touching steel core, grease missing | N/A | N/A
57 | OH-7018533 | T13-2 to T13-3 Right Phase Right Sub | 2022-06-28 | 5/10/2022 | 2022-05-12 | 2021-11-03 | SANTA CLARA-VINCENT | ET-00770 | P2 | Steel sleeve off centered, steel core gap, aluminum strands touching steel core, grease missing | N/A | N/A
58 | OH-7009491 | T6-3 to T6-4 Middle Phase Right Sub | 2022-08-25 | 3/6/2021 | 2021-07-06 | 2019-02-22 | PADUA-RANCHO VISTA NO.1 | ET-01899 | P2 | steel sleeve bad crimps and bowed, steel core gap, lack of grease | N/A | N/A
59 | OH-7009494 | T6-4 to T6-5 Bottom Phase Left Sub | 2022-08-25 | 4/23/2021 | 2022-02-25 | 2019-02-22 | PADUA-RANCHO VISTA NO.1 | ET-01899 | P2 | Steel core gap, aluminum strands touching steel core, lack of grease | N/A | N/A
60 | OH-7009494 | T6-4 to T6-5 Middle Phase Left Sub | 2022-08-25 | 4/23/2021 | 2022-02-25 | 2019-02-22 | PADUA-RANCHO VISTA NO.1 | ET-01899 | P2 | Steel core gap, aluminum strands touching steel core, lack of grease | N/A | N/A
61 | OH-7009497 | T7-1 to T7-2 Top Phase Left Sub | 2022-08-25 | 2/22/2022 | 2022-02-25 | 2019-02-22 | PADUA-RANCHO VISTA NO.1 | ET-01899 | P2 | steel sleeve bad crimps and bowed, lack of grease | N/A | N/A
62 | OH-7009499 | T7-3 to T7-4 Middle Phase Right Sub | 2022-08-25 | 2/22/2022 | 2022-03-02 | 2019-02-22 | PADUA-RANCHO VISTA NO.1 | ET-01899 | P3 | Steel core gap | N/A | N/A
63 | OH-7009499 | T7-3 to T7-4 Top Phase Left Sub | 2022-08-25 | 2/22/2022 | 2022-03-02 | 2019-02-22 | PADUA-RANCHO VISTA NO.1 | ET-01899 | P3 | steel sleeve off centered, steel core gap, lack of grease | N/A | N/A