## Cover Sheet Tables 1-12
| Yes | No | <-- for dropdowns
Energy Safety Data Guidelines Appendix D, Section 1.2
Wildifire Mitigation Data Tables Template: Tables 1 - 15
Update the below table to establish which reporting period this submission this represents.
Utility Name |  | PG&E
First year of 3-year WMP cycle |  | 2023
Reporting Period year |  | 2023
Reporting Period quarter |  | Q2
Date Modified |  | 2025-03-12

## Table 1
UtilityID | SubmissionDate | InitiativeClassification | ProjectStartDate | ProjectEndDate | UtilityInitiativeName | InitiativeDescription | InitiativeObjective | WMPInitiativeCategory | WMPInitiativeCategory# | WMPInitiativeActivity | ActivityNameifOther | WMPInitiativeActivity# | UtilityInitiativeTrackingID | WMPInitiativeCode | WMPPageNumber | RiskTargetReduction | MidYearTarget (Yes/No) | QuantTargetUnits | AnnualQuantTarget | ProjectedQuantProgressQ1 | ProjectedQuantProgressQ1-2 | ProjectedQuantProgressQ1-3 | ProjectedQuantProgressQ1-4 | QuantActualProgressQ1 | QuantActualProgressQ1-2 | QuantActualProgressQ1-3 | QuantActualProgressQ1-4 | AnnualQualTarget | QualActualProgressQ1 | QualActualProgressQ1-2 | QualActualProgressQ1-3 | QualActualProgressQ1-4 | Status | CorrectiveActionsIfDelayed | REFERENCE: Compliance Branch Requirements --> | Audit | Audit File Documentation Requested | FolderLink | PersonInChargeName | PersonInChargeEmail
PGE | 2023-05-01 | Program |  |  | System Hardening - Distribution | Complete 420 circuit miles of system hardening work which includes overhead system hardening, undergrounding, and removal of overhead lines in HFTD, HFRA, or buffer zone areas except for any mileage being undergrounded and tracked separately as part of our Butte County Rebuild and other Community Rebuild efforts | This initiative will harden distribution circuit miles through overhead system hardening, undergrounding, and the removal of overhead lines to reduce the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Covered conductor installation |  | 8.1.2.1 | GH-01 | UtilityID_Grid Design, Operations and Maintenance_Covered conductor installation _GH-01_2023 | 324 to 333 | Equipment ignition likelihood | No | # of circuit miles | 420 | 15 | 127 | 283 | 420 | 13.6 | 90.16 | [7 empty] | Delayed | We fell behind the Q2 YTD target of completing 127 miles with 90.16 miles completed by the end of June. The multiple storm/snow events in Q1 delayed work and prevented access to overhead and underground construction sites where work was otherwise ready to execute. Additionally, some underground projects have encountered land acquisition and county permitting delays. Corrective Actions: There are 221.8 miles in active construction and another 106.5 miles ready for construction. The catch back is in place, and we plan to be back on track to the original plan by 9/30. Project Management team is partnering with construction teams to accelerate the completion of remaining OH miles and acceleration of UG civil construction.
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Evaluate Covered Conductor Effectiveness | Update the covered conductor recorded effectiveness calculation using 2023 and 2024 outage data on the lines that have Covered Conductors for consideration in future system hardening workplans. | This initiative will update the covered conductor recorded effectiveness calculation to assist with calculating the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Covered conductor installation |  | 8.1.2.1 | GH-02 | PGE_Grid Design, Operations and Maintenance_Covered conductor installation _GH-02_2023 | 318 to 323 | Equipment ignition likelihood | No | [10 empty] | Update the covered conductor recorded effectiveness calculation using 2023 and 2024 outage data on the lines that have Covered Conductors for consideration in future system hardening workplans. | Since this objective is to update the covered conductor recorded effectiveness calculation using 2023 and 2024 outage data, there is no applicable update for Q1. | Since this objective is to update the covered conductor recorded effectiveness calculation using 2023 and 2024 outage data, there is no applicable update for Q2. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Evaluate and Implement Covered Conductor Effectiveness Impact on Inspections and Maintenance Standards | Evaluate the output of the Phase 1 and Phase 2 covered conductor effectiveness study to: (1) determine the impacts of the study on the maintenance and inspections standards for deployed covered conductor assets; and (2) update TD-2305M-JA02 (overhead inspections job aid), as needed. | This initiative will evaluate the output of the Phase 1 and Phase 2 covered conductor effectiveness study to assist with reducing the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Covered conductor installation |  | 8.1.2.1 | GH-03 | PGE_Grid Design, Operations and Maintenance_Covered conductor installation _GH-03_2023 | 318 to 323 | Equipment ignition likelihood | No | [10 empty] | Evaluate the output of the Phase 1 and Phase 2 covered conductor effectiveness study to: (1) determine the impacts of the study on the maintenance and inspections standards for deployed covered conductor assets; and (2) update TD-2305M-JA02 (overhead inspections job aid), as needed. | We have met all the interim Q1 milestones by providing the ATS report to the Wildfire Risk Governance Steering Committee (WRGSC) outlining the impacts of the study methodology. The team is currently working on Q2 milestones by evaluating the impacts of the study on the maintenance and inspection standards for deployed covered conductor assets and identifying potential guidance documents that may need updates. | Based on the results from the Covered Conductor Testing, we have identified the recommended changes to maintenance and inspection practices. These changes have been drafted as part of the upcoming update to EDPM (Electric Distribution Preventive Maintenance) document. Additional documents that have been identified to be updated include: inspection checklist, Overhead Inspections Job Aid TD-2305M-JA02, and inspection training material. These updates will be made by Q4 2023 to ensure that the changes take into effect for our 2024 inspection and maintenance process. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | 10K Undergrounding | Complete 350 circuit miles of undergrounding work. The 350-circuit mile target includes: (1) undergrounding taking place as part of System Hardening, (2) undergrounding taking place as part of the Butte County Rebuild program (including a small volume of previously hardened overhead lines that are being placed underground) or other Community Rebuild programs, and (3) any other undergrounding work performed in HFTD, HFRA, Buffer Zone, or fire rebuild areas. | This initiative will underground electrical facilities to reduce the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Undergrounding of electric lines and/or equipment |  | 8.1.2.2 | GH-04 | PGE_Grid Design, Operations and Maintenance_Undergrounding of electric lines and/or equipment_GH-04_2023 | 324 to 333 | Equipment ignition likelihood | No | # of circuit miles | 350 | 7 | 63 | 195 | 350 | 3.1 | 26.89 | [7 empty] | Delayed | We fell behind the Q2 YTD target of completing 63 circuit miles with 26.93 circuit miles completed by the end of June. The multiple storm/snow events in Q1 delayed work and prevented access to underground construction sites where work was otherwise ready to execute. Additionally, some underground projects have encountered land acquisition and county permitting delays. Corrective Actions: There are 209.9 miles in active construction between System Hardening (156.8), Butte Rebuild (52.4) and Community Rebuild (0.7), and another 101.0 miles ready for construction between System Hardening (94.1), Butte Rebuild (4.6) and Community Rebuild (2.3). The project Management team is partnering with construction teams to accelerate UG civil construction. Based on current construction schedules the program anticipates returning to plan by 9/30.
PGE | 2023-05-01 | Program |  |  | System Hardening - Transmission | Remove or replace 43 circuit miles of transmission conductor on lines. | This initiative will harden transmission circuit miles through removing or replacing conductor to reduce the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Traditional overhead hardening - Transmission |  | 8.1.2.5.1 | GH-05 | PGE_Grid Design, Operations and Maintenance_Traditional overhead hardening - Transmission_GH-05_2023 | 324 to 333 | Equipment ignition likelihood | No | # of circuit miles | 43 | 12 | 33 | 41 | 43 | 8.6 | 26.5 | [7 empty] | Delayed | We fell behind the Q2 YTD target of completing 33 circuit miles with 26.5 circuit miles completed by the end of June. Drum-Rio Oso 115kV Rebuild (phase 3) project Forecasted In-Service Date changed due to delays caused by the earlier this year, causing sites to be inaccessible due to snow and road conditions. Corrective Actions: A catch back plan is in place that includes clearances being rescheduled for Q3-Q4 timeframe.
PGE | 2023-05-01 | Program |  |  | System Hardening - Transmission Shunt Splices | Install shunt splice(s) on 20 transmission lines. | This initiative will install shunt splice(s) on transmission lines to reduce the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Traditional overhead hardening - Transmission |  | 8.1.2.5.1 | GH-06 | PGE_Grid Design, Operations and Maintenance_Traditional overhead hardening - Transmission_GH-06_2023 | 324 to 333 | Equipment ignition likelihood | No | # of Transmission Lines | 20 | 0 | 9 | 17 | 20 | 0 | 12 | [7 empty] | On Track
PGE | 2023-05-01 | Program |  |  | Distribution Protective Devices | Install and SCADA commission 75 new SCADA protective devices (Line Recloser, Fuse Saver, or Interrupter). | This initiative will install and SCADA commission protective devices to reduce the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Installation of System Automation Equipment – Distribution EPSS Protective Devices |  | 8.1.2.8.1 | GH-07 | PGE_Grid Design, Operations and Maintenance_Installation of System Automation Equipment – Distribution EPSS Protective Devices_GH-07_2023 | 324 to 333 | PSPS exposure potential | No | # of distribution sectionalizing devices | 75 | 3 | 43 | 75 | 75 | 0 | 7 | [7 empty] | Delayed | We fell behind the Q2 YTD target of 43 installations with 7 installations completed by the end of June. The delay was due to winter storms that occurred in Q1 which impacted working conditions and caused resource constraints as crews were diverted to storm response work. The program was re-baselined during Q2 to adjust to the interim completion targets. Corrective Actions: A catch back plan is in place to work through all job stages: pre-commissioning, construction, and commissioning by December 31.
PGE | 2023-05-01 | Program |  |  | Surge Arrestor - Removals | Remove 663 non-exempt surge arrestors (based on the known population as of 01/12/2023) where known grounding issues exist. If no non-exempt surge arrestor is identified at a location during pre-field work, the unit will be resolved, and the notification will be canceled. Canceled notifications will count towards this target. | This initiative will remove non-exempt equipment with exempt equipment that has a lower propensity to cause a fire ignition. | Grid Design, Operations and Maintenance | 8.1 | Surge Arrestors |  | 8.1.2.10.4 | GH-08 | PGE_Grid Design, Operations and Maintenance_Surge Arrestors_GH-08_2023 | 324 to 333 | Equipment ignition likelihood | No | # of surge arrestors | 663 | 135 | 340 | 555 | 663 | 98 | 438 | [7 empty] | On Track
PGE | 2023-05-01 | Program |  |  | Distribution Line Motor Switch Operator (MSO) - Replacements | Replace or remove 20 Motor Switch Operators (from the 47 identified as of January 26, 2023) | This initiative is to replace Motorized Switch Operators, which have a potential to arc flash during operations, with other devices. | Grid Design, Operations and Maintenance | 8.1 | Motor Switch Operator (MSO) Switch Replacement |  | 8.1.2.10.3 | GH-09 | PGE_Grid Design, Operations and Maintenance_Motor Switch Operator (MSO) Switch Replacement_GH-09_2023 | 324 to 333 | Equipment ignition likelihood | No | # of MSOs replacements | 20 | 1 | 6 | 14 | 20 | 4 | 11 | [7 empty] | On Track
PGE | 2023-05-01 | Program |  |  | Non-Exempt Expulsion Fuse - Removal | Remove non-exempt expulsion fuses/ cutouts from 3,000 fuse locations identified on distribution poles. | This initiative will remove non-exempt equipment that may generate electrical arcs, sparks, or hot material during its normal operation. | Grid Design, Operations and Maintenance | 8.1 | Non-Exempt Expulsion Fuses |  | 8.1.2.10.5 | GH-10 | PGE_Grid Design, Operations and Maintenance_Non-Exempt Expulsion Fuses_GH-10_2023 | 324 to 333 | Equipment ignition likelihood | No | # of fuses | 3000 | 90 | 940 | 2390 | 3000 | 79 | 1910 | [7 empty] | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Retainment of Inspectors and Internal Workforce Development | 1) Develop a plan to increase retention over time for trained and qualified inspectors. 2) Develop a plan to focus on increasing and sustaining a consistent, year-over-year internal workforce that builds on existing experience and mentors new employees for asset inspections. | This initiative will develop a plan to increase retention of internal inspectors to assist with reducing the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Asset Inspections |  | 8.1.9.1 | AI-01 | PGE_Grid Design, Operations and Maintenance_Asset Inspections_AI-01_2023 | 318 to 323 | Equipment ignition likelihood | No | [10 empty] | 1) Develop a plan to increase retention over time for trained and qualified inspectors. 2) Develop a plan to focus on increasing and sustaining a consistent, year-over-year internal workforce that builds on existing experience and mentors new employees for asset inspections. | PG&E has begun benchmarking with other IOUs to evaluate classifications who perform inspections and patrols (San Diego Gas & Electric and Southern California Edison) as part of developing the plan to increase retention for trained and qualified inspections. | PG&E continues to make progress on the plan to improve our workforce. We have reviewed the current staffing and identified the number of Supervisors, Inspectors and Inspection Review Specialist that have been approved for hiring. PG&E is working on getting these roles posted and filled. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | Detailed Inspection Transmission – Ground | Complete detailed ground inspections on 27,000 transmission structures in PG&E's asset registry as of January 1, 2023. | This initiative includes detailed inspections (ground) of transmission poles which can reduce the potential for equipment failure which could cause a potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Ground Detailed Inspections |  | 8.1.3.1.1 | AI-02 | PGE_Grid Design, Operations and Maintenance_Ground Detailed Inspections_AI-02_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of structures | 27000 | 6000 | 18000 | 27000 | 27000 | 4014 | 26887 | [7 empty] | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Develop Distribution Aerial Inspections program | Evaluate the continued use of aerial inspections for distribution overhead equipment. | This initiative will evaluate the use of aerial inspections for distribution overhead equipment to assist with reducing the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Pilot Inspections |  | 8.1.3.2.7 | AI-03 | PGE_Grid Design, Operations and Maintenance_Pilot Inspections_AI-03_2023 | 318 to 323 | Equipment ignition likelihood | No | [10 empty] | Evaluate the continued use of aerial inspections for distribution overhead equipment. | The program has met all interim milestones, including the identification of the Pilot scope, establishing linked data repository and conducted desktop inspector onboarding and training. | The program continues to meet all interim milestones including staging notifications and conducting on-boarding. The program is on track and in progress on capturing images, completing assigned inspections, and completing issuance of notifications. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | Detailed Inspection Transmission – Aerial | Complete detailed aerial inspections on 24,000 transmission structures in PG&E's asset registry as of January 1, 2023. | This initiative includes detailed inspections (aerial) of transmission poles which can reduce the potential for equipment failure which could cause a potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Aerial Detailed Inspections |  | 8.1.3.1.2 | AI-04 | PGE_Grid Design, Operations and Maintenance_Aerial Detailed Inspections_AI-04_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of structures | 24000 | 5000 | 17000 | 24000 | 24000 | 6915 | 24343 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Detailed Inspection Transmission – Climbing | Complete detailed climbing inspections of 1,700 transmission structures in PG&E's asset registry as of January 1, 2023. | This initiative includes detailed inspections (climbing) of transmission poles which can reduce the potential for equipment failure which could case a potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Climbing Detailed Inspections |  | 8.1.3.1.3 | AI-05 | PGE_Grid Design, Operations and Maintenance_Climbing Detailed Inspections_AI-05_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of structures | 1700 | 500 | 1200 | 1700 | 1700 | 557 | 1773 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Perform transmission infrared inspections | Infrared patrols will be performed on 4,000 circuit miles of energized transmission line. | This initiative includes transmission infrared inspections which can reduce the potential for equipment failure which could cause a potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Infrared Inspections |  | 8.1.3.1.4 | AI-06 | PGE_Grid Design, Operations and Maintenance_Infrared Inspections_AI-06_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of miles | 4000 | 1000 | 1500 | 3000 | 4000 | 1352.09 | 2964.55 | [7 empty] | On Track
PGE | 2023-05-01 | Program |  |  | Detailed Ground Inspections - Distribution | Complete detailed ground inspections on 234,648 distribution poles, which were identified in PG&E's asset registry as of December 27, 2022. As part of the target number above, detailed ground inspections will be completed on a 42,470-pole subset of distribution poles in Severe, Extreme, or High plat maps by July 31, 2023, which were identified in PG&E's asset registry as of December 27, 2022. Similarly, detailed ground inspections will be completed on a 30,062-pole subset of distribution poles in Medium plat maps by September 30, 2023, which were identified in PG&E's asset registry as of December 27, 2022. Lastly, detailed ground inspections will be completed on a 162,116-pole subset of distribution poles in Low plat maps by December 31, 2023, which were identified in PG&E's asset registry as of December 27, 2022. | This initiative includes detailed inspections of distribution poles which can reduce the potential for equipment failure which could cause a potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Detailed Ground Inspections |  | 8.1.3.2.1 | AI-07 | PGE_Grid Design, Operations and Maintenance_Detailed Ground Inspections_AI-07_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of poles | 234648 | 5000 | 30000 | 72532 | 234648 | 59 | 79295 | [7 empty] | On Track
PGE | 2023-05-01 | Program |  |  | Supplemental Inspections - Substation Distribution | Complete supplemental inspections on 52 distribution substations. Co-located Hydroelectric substations and Transmission & Distribution substations are counted separately as two distinct units. | This initiative provides for supplemental substation inspections to identify equipment issues and damages that may impact reliability and/or pose wildfire ignition risk. | Grid Design, Operations and Maintenance | 8.1 | Asset Inspection Program - Substation |  | 8.1.3.3.1 | AI-08 | PGE_Grid Design, Operations and Maintenance_Asset Inspection Program - Substation_AI-08_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of Distribution Substations | 52 | 14 | 46 | 52 | 52 | 6 | 52 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Supplemental Inspections - Substation Transmission | Complete supplemental inspections on 34 transmission substations. Co-located Hydroelectric substations and Transmission & Distribution substations are counted separately as two distinct units. | This initiative provides for supplemental substation inspections to identify equipment issues and damages that may impact reliability and/or pose wildfire ignition risk. | Grid Design, Operations and Maintenance | 8.1 | Asset Inspection Program - Substation |  | 8.1.3.3.1 | AI-09 | PGE_Grid Design, Operations and Maintenance_Asset Inspection Program - Substation_AI-09_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of Transmission Substations | 34 | 15 | 31 | 34 | 34 | 3 | 34 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Supplemental Inspections - Hydroelectric Substations and Powerhouses | Complete supplemental inspections on 41 Hydroelectric Generation Substations and Powerhouses. Co-located Hydroelectric substations and Transmission & Distribution substations are counted separately as two distinct units. | This initiative provides for supplemental substation inspections to identify equipment issues and damages that may impact reliability and/or pose wildfire ignition risk. | Grid Design, Operations and Maintenance | 8.1 | Asset Inspection Program - Substation |  | 8.1.3.3.1 | AI-10 | PGE_Grid Design, Operations and Maintenance_Asset Inspection Program - Substation_AI-10_2023 | 324 to 333 | Equipment ignition likelihood | Yes | # of Hydroelectric Substations and Powerhouses | 41 | 14 | 41 | 41 | 41 | 1 | 40 | [7 empty] | Completed
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Filling Asset Inventory Data Gaps | Populate missing age data in the Asset Registry (using “Installation Date” data element as a proxy) to 90% weighted average across risk prioritized distribution and transmission equipment. | This initiative will populate missing age data in the Asset Registry (distribution and transmission equipment), to identify equipment issues and damages that may impact reliability and/or pose wildfire ignition risk. | Grid Design, Operations and Maintenance | 8.1 | Asset Management and Inspection Enterprise System(s) |  | 8.1.5 | AI-11 | PGE_Grid Design, Operations and Maintenance_Asset Management and Inspection Enterprise System(s)_AI-11_2023 | 318 to 323 | Equipment ignition likelihood | No | [10 empty] | Populate missing age data in the Asset Registry (using “Installation Date” data element as a proxy) to 90% weighted average across risk prioritized distribution and transmission equipment. | We fell behind on key milestones due to delays in obtaining the project charter which describes in detail work to be approved. The charter is needed prior to setting up detailed project plans and moving forward with a proof of concept. | Due to the successful corrective actions, this program is now back on track as the project charter was approved in May, and the draft of the project plan was completed and is scheduled for review in early July. We have selected the features that we will be checking in our Field Proof of Concept and have identified mappers to work on the records review proof of concept. We are also starting on the Estimated Dates algorithm. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Asset Inspections - Quality Assurance | Perform annually, year-round Transmission and Distribution system inspection quality assurance audits of “QC complete” locations in HFTD areas. Statistically valid methodology parameters, such as a confidence level of 95% and 5% margin of error, will be utilized. | This initiative audits the quality of transmission and distribution system inspections, which can help identify gaps and implement improvements for inspections. | Grid Design, Operations and Maintenance | 8.1 | Quality Assurance (QA) |  | 8.1.6.1 | GM-01 | PGE_Grid Design, Operations and Maintenance_Quality Assurance (QA)_GM-01_2023 | 318 to 323 | Equipment ignition likelihood | No | % Confidence Level | [9 empty] | Perform annually, year-round Transmission and Distribution system inspection quality assurance audits of “QC complete” locations in HFTD areas. Statistically valid methodology parameters, such as a confidence level of 95% and 5% margin of error, will be utilized. | The results of the 2023 Q1 transmission audits are as follows: Number of poles inspected: 28. Number of poles passed: 27. Number of poles failed: 1. Percentage pass rate: 96.43%. Please note that the distribution audits have not yet begun. | We surpassed the YTD Target of 97.25% Pass Rate with 100.00% Actual YTD Pass Rate for Transmission and surpassed the YTD Target of 79.77% Pass Rate with 95.25% Actual YTD Pass Rate for Distribution QA System Inspection Transmission Pass Rate: Total # of Tower Passed / Total # of Towers Audited Year to Date (01/01/23 – 07/02/23): Pass Rate -> 99.80% Total # of Towers Audited -> 489 Total # of Towers Passed -> 488 Total # of Towers Failed -> 1 Quarter 2 (04/03/23 – 07/02/23): Pass Rate -> 100.00% Total # of Towers Audited -> 461 Total # of Towers Passed -> 461 Total # of Towers Failed -> 0 QA System Inspection Distribution Pass Rate: Total # of Poles Passed / Total # of Poles Audited Year to Date (01/01/23 – 07/02/23): Pass Rate -> 95.25% Total # of Towers Audited -> 1516 Total # of Towers Passed -> 1444 Total # of Towers Failed -> 72 Quarter 2 (04/03/23 – 07/02/23): Pass Rate -> 95.25% Total # of Towers Audited -> 1516 Total # of Towers Passed -> 1444 Total # of Towers Failed -> 72 |  |  | On Track
PGE | 2023-05-01 | Program |  |  | HFTD-HFRA Open Tag Reduction - Transmission | PG&E will eliminate the known 16,831 HFTD and HFRA transmission Ignition Risk tags (tags found prior to January 1, 2023, with required end dates in 2023 or earlier). | This initiative is focused on closing out open maintenance tags for transmission facilities in HFTD and HFRA areas. | Grid Design, Operations and Maintenance | 8.1 | Open Work Orders - Transmission |  | 8.1.7.1 | GM-02 | PGE_Grid Design, Operations and Maintenance_Open Work Orders - Transmission_GM-02_2023 | 324 to 333 | Equipment ignition likelihood | No | # of Transmission LC Tags | 16831 | 1800 | 8300 | 13800 | 16831 | 3262 | 9259 | [7 empty] | On Track
PGE | 2023-05-01 | Program |  |  | HFTD-HFRA Open Tag Reduction – Distribution Backlog | Reduce 48% of the wildfire risk associated with backlog* ignition risk tags from 151.1 (risk units as of January 1, 2023) by 72.5 (48%) risk units. *Backlog is defined as the open ignition EC notifications known as of January 5, 2023, and found prior to Jan 1, 2023, in HFTD/HFRA locations. | This initiative is focused on closing out open E maintenance tags for distribution facilities in HFTD and HFRA areas. | Grid Design, Operations and Maintenance | 8.1 | Open Work Orders - Distribution |  | 8.1.7.2 | GM-03 | PGE_Grid Design, Operations and Maintenance_Open Work Orders - Distribution_GM-03_2023 | 324 to 333 | Equipment ignition likelihood | No | # of Distribution EC Tags | 48% | 9.47% | 25.71% | 40.32% | 48% | 6.386% | 20.5% | [7 empty] | Delayed | We fell behind the Q2 YTD target of 38.8 (25.7%) risk points with 30.9 (20.5%) risk points reduction as of the end of June. This delay was due to the unprecedented winter storms which caused resource constrains to execute the planned maintenance work. Corrective Actions: A catch back plan was implemented to schedule 40 (26.5%) risk points by July 31. The target is anticipated to be met by end of Q3.
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | HFTD-HFRA Open Tag Reduction - Backlog Elimination - 3 Year Plan | Eliminate the backlog* of distribution open non-pole ignition risk tags. *Backlog is defined as the open ignition EC notifications known as of January 5, 2023, and found prior to Jan 1, 2023, in HFTD/HFRA locations. | This initiative is focused on closing out open E maintenance tags for distribution facilities in HFTD and HFRA areas. | Grid Design, Operations and Maintenance | 8.1 | Open Work Orders - Distribution |  | 8.1.7.2 | GM-04 | PGE_Grid Design, Operations and Maintenance_Open Work Orders - Distribution_GM-04_2023 | 318 to 323 | Equipment ignition likelihood | No | [10 empty] | Eliminate the backlog* of distribution open non-pole ignition risk tags. *Backlog is defined as the open ignition EC notifications known as of January 5, 2023, and found prior to Jan 1, 2023, in HFTD/HFRA locations. | PG&E is planning the approach to eliminate the backlog of open distribution non pole ignition risk tags by 2025. | We continue to refine our plan to eliminate the backlog of open distribution non-pole ignition risk tags by 2025. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | EPSS - Down Conductor Detection (DCD) | Make capable for Down Conductor Detection (DCD) 500 protective device controllers or relays. This count includes protection devices that due to repair status cannot receive the DCD settings, and circuit reconfiguration resulting in descoping of device. | This initiative will make capable for Down Conductor Detection (DCD) 500 protective device controllers or relays to reduce the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Downed Conductor Detection (DCD) Devices |  | 8.1.2.10.1 | GM-06 | PGE_Grid Design, Operations and Maintenance_Downed Conductor Detection (DCD) Devices_GM-06_2023 | 324 to 333 | Equipment ignition likelihood | No | # of Protective Device Controllers or Relays that are DCD capable | 500 | 142 | 309 | 474 | 500 | 60 | 336 | [7 empty] | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Updates on EPSS Reliability Study | Provide annually an updated EPSS reliability impact study per ACI 22-32. | This initiative will provide an updated EPSS reliability impact study to assist with reducing the risk of potential wildfire ignition. | Grid Design, Operations and Maintenance | 8.1 | Protective Equipment and Device Settings |  | 8.1.8.1.1 | GM-07 | PGE_Grid Design, Operations and Maintenance_Protective Equipment and Device Settings_GM-07_2023 | 318 to 323 | Equipment ignition likelihood | No | [10 empty] | Provide annually an updated EPSS reliability impact study per ACI 22-32. | This study is developed at the end of the calendar year to provide data associated with the full year of EPSS enablement. Therefore, there will not be any progress to report on this program until Q1 of 2024. | This study is developed at the end of the calendar year to provide data associated with the full year of EPSS enablement. Therefore, there will not be any progress to report on this program until Q1 of 2024. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | LiDAR Data Collection - Transmission | Collect LiDAR data of the Transmission System (17,500 circuit miles). The Transmission System circuit miles include both HFTD / HFRA and non-HFTD Transmission circuit miles | This initiative includes the collection of LiDAR data for the Transmission System which can reduce the potential for asset-caused ignitions and wildfires. | Vegetation Management and Inspection | 8.2 | Routine Transmission NERC and Non-NERC |  | 8.2.2.1.1 | VM-01 | PGE_Vegetation Management and Inspection_Routine Transmission NERC and Non-NERC_VM-01_2023 | 499 to 506 | Contact from vegetation ignition likelihood | Yes | # of circuit miles | 17500 | 17500 | 17500 | 17500 | 17500 | 17808.29 | 17808.29 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Pole Clearing Program | Inspect, clear, and maintain, where clearing is necessary 77,503 poles per Vegetation Control Standard TD-7112S. | This initiative performs pole clearing inspections and work (where needed) for poles in HFTD and HFRA areas where clearance is not required by PRC Section 4292. Pole clearing can reduce the potential for a wildfire ignition. | Vegetation Management and Inspection | 8.2 | Pole Clearing |  | 8.2.3.1 | VM-02 | PGE_Vegetation Management and Inspection_Pole Clearing_VM-02_2023 | 499 to 506 | Contact from vegetation ignition likelihood | Yes | # of distribution poles | 77503 | 64632 | 77503 | 77503 | 77503 | 68536 | 79037 |  |  |  |  | The Target is marked as “On Track” rather than “complete” despite exceeding the annual target of 77,503 because our asset database is dynamic and poles may be added or removed during the annual work cycle from October 1st to September 30th. We anticipate that the target is planned to be marked as “complete” at the end of Q3. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Focused Tree Inspection Program | 1) Identify the Areas of Concern (AOC) by developing a collaborative, cross-functional team to evaluate the service territory with electric overhead assets and create system wide map that includes Vegetation Management AOCs. 2) Initiate a pilot program in at least one Areas of Concern (AOC). 3) Fully implement AOC cross-functional team to implement guidelines across all AOCs. Determine value of a multi-year historical tree data set. | This initiative will identify the Areas of Concern (AOC) and implement guidelines to reduce the risk associated with vegetation contact that could cause a potential ignition. | Vegetation Management and Inspection | 8.2 | Focused Tree Inspections |  | 8.2.2.2.5 | VM-03 | PGE_Vegetation Management and Inspection_Focused Tree Inspections_VM-03_2023 | 493 to 498 | Contact from vegetation ignition likelihood | No | [10 empty] | 1) Identify the Areas of Concern (AOC) by developing a collaborative, cross-functional team to evaluate the service territory with electric overhead assets and create system wide map that includes Vegetation Management AOCs. 2) Initiate a pilot program in at least one Areas of Concern (AOC). 3) Fully implement AOC cross-functional team to implement guidelines across all AOCs. Determine value of a multi-year historical tree data set. | The program is on track and has met all interim milestones for Q1. Initial drafts for AOCs were completed on January 31, 2023. Two AOCs (approx. 30 mi) were added by approval of the WRGSC on March 16, 2023, based on reviews and feedback. | The program is on track by meeting key milestone in Q2 of standing up this Pilot program. The evaluation of how the mid-cycle inspections sequence can adjust with AOC has begun. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | Tree Removal | Removal of 15,000 trees identified from the legacy EVM program. | This initiative will remove 15,000 trees identified from the legacy EVM program to reduce the risk associated with vegetation contact causing a potential ignition. | Vegetation Management and Inspection | 8.2 | Fall-in Mitigation |  | 8.2.3.4 | VM-04 | PGE_Vegetation Management and Inspection_Fall-in Mitigation_VM-04_2023 | 499 to 506 | Contact from vegetation ignition likelihood | No | # of trees Removed | 15000 | 0 | 2274 | 9281 | 15000 | 11 | 933 | [7 empty] | Delayed | We fell behind the Q2 YTD target of 2,274 trees with 933 trees removed by the end of June. This was the result of delays in beginning this work due to the required changes to existing technology field guides that had to be completed prior to releasing work to the tree crews. Corrective Actions: We developed revised guidance and implemented change communication prior to work beginning in the field. VM is successfully implementing a catch back plan that will have a removal rate of over 400 trees per week starting in July and is forecasting to be back on target by the end of August.
PGE | 2023-05-01 | Program |  |  | Defensible Space Inspections - Distribution Substation | Complete defensible space inspections in alignment with the guidelines set forth in LAND 4001P-01 at 131 distribution substations. Co-located Hydroelectric substations and Transmission & Distribution substations are counted separately as two distinct units. | This initiative clears defensible space areas around distribution substations to minimize the potential for ignition spread outside of facilities and to provide improved structure defense capability for firefighting purposes. | Vegetation Management and Inspection | 8.2 | Substation Defensible Space |  | 8.2.2.3.1 | VM-05 | PGE_Vegetation Management and Inspection_Substation Defensible Space_VM-05_2023 | 499 to 506 | Wildfire exposure potential | Yes | # of Distribution Substations | 131 | 125 | 130 | 131 | 131 | 116 | 131 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Defensible Space Inspections - Transmission Substation | Complete defensible space inspections in alignment with the guidelines set forth in LAND 4001P-01 at 55 transmission substations. Co-located Hydroelectric substations and Transmission & Distribution substations are counted separately as two distinct units. | This initiative clears defensible space areas around transmission substations to minimize the potential for ignition spread outside of facilities and to provide improved structure defense capability for firefighting purposes. | Vegetation Management and Inspection | 8.2 | Substation Defensible Space |  | 8.2.2.3.1 | VM-06 | PGE_Vegetation Management and Inspection_Substation Defensible Space_VM-06_2023 | 499 to 506 | Wildfire exposure potential | Yes | # of Transmission Substations | 55 | 37 | 55 | 55 | 55 | 40 | 55 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Defensible Space Inspections - Hydroelectric Substations and Powerhouses | Complete defensible space inspections in alignment with the guidelines set forth in LAND 5201P-01 at 61 Hydroelectric Generation Substations and Powerhouses. Co-located Hydroelectric substations and Transmission & Distribution substations are counted separately as two distinct units. | This initiative clears defensible space areas around hydroelectric substations to minimize the potential for ignition spread outside of facilities and to provide improved structure defense capability for firefighting purposes. | Vegetation Management and Inspection | 8.2 | Substation Defensible Space |  | 8.2.2.3.1 | VM-07 | PGE_Vegetation Management and Inspection_Substation Defensible Space_VM-07_2023 | 499 to 506 | Wildfire exposure potential | Yes | # of Hydroelectric Substations and Powerhouses | 61 | 24 | 61 | 61 | 61 | 28 | 61 | [7 empty] | Completed
PGE | 2023-05-01 | Program |  |  | Vegetation Management – Quality Verification | Each of the 3 programs (Routine Distribution, Routine Transmission and Pole Clearing) must achieve an 95% quality verification audit results pass rate. The number of quality verification audit locations for the 3 programs (Routine Distribution, Routine Transmission and Pole Clearing) are based on quality control completed work in HFTD areas. Quality verification audit locations will be identified using a statistically valid approach with a 95% confidence level (CL) and 5% margin of error. The pass rate and associated number of quality verification audit locations are based on the actual work completed in the calendar year. | This initiative performs Quality Assurance and Quality Verification audits and reviews of various aspects of our Vegetation Management program to identify gaps and areas of improvement. | Vegetation Management and Inspection | 8.2 | Quality Assurance and Quality Control |  | 8.2.5 | VM-08 | PGE_Vegetation Management and Inspection_Quality Assurance and Quality Control_VM-08_2023 | 499 to 506 | Contact from vegetation ignition likelihood | No | # of Audit Locations % Pass Rate | 95% | 95% | 95% | 95% | 95% | 99% | 99.36% | [7 empty] | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Constraint Resolution Procedural Guideline | Develop a process of centralizing constraints resolution. As part of the build out of the centralized constraints team, three major categories will be addressed: customer constraints, environmental constraints (including internal PG&E procedures required to perform work) and permitting constraints (including both Land and Environmental permits). For each major constraint category build a process for addressing each constraint type, implement the new process, and create metrics to track each constraint type. Reporting will track total constraints by type and the time it takes to resolve a constraint after it has been identified. PG&E will consider creating a “right tree-right place” program, as part of the centralize Constraints Resolution process. | This initiative will develop a process of centralizing customer, environmental, and permitting constraints to reduce the risk associated with vegetation contact causing a potential ignition. | Vegetation Management and Inspection | 8.2 | Open Work Orders |  | 8.2.6 | VM-09 | PGE_Vegetation Management and Inspection_Open Work Orders_VM-09_2023 | 493 to 498 | Contact from vegetation ignition likelihood | No | [10 empty] | Develop a process of centralizing constraints resolution. As part of the build out of the centralized constraints team, three major categories will be addressed: customer constraints, environmental constraints (including internal PG&E procedures required to perform work) and permitting constraints (including both Land and Environmental permits). For each major constraint category build a process for addressing each constraint type, implement the new process, and create metrics to track each constraint type. Reporting will track total constraints by type and the time it takes to resolve a constraint after it has been identified. PG&E will consider creating a “right tree-right place” program, as part of the centralize Constraints Resolution process. | This objective is on track. The team completed draft updates, and subject matter expert review of the Distribution Routine Refusal Procedure (TD-7102P-04). Changes included in this draft procedure are being piloted with regional operations, and the updated version of the of the procedure will roll out to the wider VM department mid-year. In addition to the Refusal procedure, the team is reviewing our existing procedures for Riparian, and Nesting Bird Reviews to see if these require updates. There are no identified risks at this time. | This objective is on track. The team completed and published the updated Distribution Interference Procedure (TD-7102P-04). The team is now working on communications associated with the updated procedure and training. The team is starting to draft updated procedures for Riparian, and Nesting Bird Reviews as it has been determined these are necessary. Lastly, the team has initiated a weekly operating review with all regional operations teams where we are starting to evaluate active constraints and measure timely resolutions. There are no identified risks at this time. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | AI in Wildfire Cameras | Enable AI processing of Wildfire Camera Data to provide automated wildfire notifications in the internal PG&E monitoring tool (Wildfire Incident Viewer – WIV). | This initiative will further PG&E's situational awareness by provide automated wildfire notifications. | Situational Awareness and Forecasting | 8.3 | Planned Improvements |  | 8.3.2.3 | SA-01 | PGE_Situational Awareness and Forecasting_Planned Improvements_SA-01_2023 | 565 to 568 | Wildfire hazard | No | [10 empty] | Enable AI processing of Wildfire Camera Data to provide automated wildfire notifications in the internal PG&E monitoring tool (Wildfire Incident Viewer – WIV). | We fell behind on this work due to an unexpected delay resulting from a contract change order with the Regents of the University of California (on behalf of the University of California, San Diego). | In June 2023, we met our objectives with completion this work. Through our vendor partnership, we developed, tested, and implemented an AI system that can detect and alert the analysts in our Hazard Awareness Warning Center of potential wildfires before they spread. The technology was pushed into live production and fully deployed on June 1, 2023. |  |  | Completed
PGE | 2023-05-01 | Program |  |  | Line Sensor - Installations | Install Line Sensor devices on 40 circuits. | This initiative will help PG&E continuously measure current in real time and report events as they occur. | Situational Awareness and Forecasting | 8.3 | Grid Monitoring Systems, Existing Systems, Technologies, and Procedures |  | 8.3.3.1 | SA-02 | PGE_Situational Awareness and Forecasting_Grid Monitoring Systems, Existing Systems, Technologies, and Procedures_SA-02_2023 | 499 to 506 | Equipment ignition likelihood | No | # of circuits | 40 | 0 | 0 | 30 | 40 | 0 | 0 | [7 empty] | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | EFD and DFA Reporting | Develop scalable processes to: (a) analyze alarms and alerts from Early Fault Detection (EFD) and Distribution Fault Anticipation (DFA) sensors; (b) conduct field investigation and reporting; (c) track identified mitigations to completion; and (d) track effectiveness of issue identification and remediation using EFD/DFA technologies. | This initiative will help PG&E identify and address latent or incipient issues in their early stages and assist with removing conditions that cause wildfires. | Situational Awareness and Forecasting | 8.3 | Grid Monitoring Systems, Planned Improvements |  | 8.3.3.3 | SA-03 | PGE_Situational Awareness and Forecasting_Grid Monitoring Systems, Planned Improvements _SA-03_2023 | 565 to 568 | Equipment ignition likelihood | No | [10 empty] | Develop scalable processes to: (a) analyze alarms and alerts from Early Fault Detection (EFD) and Distribution Fault Anticipation (DFA) sensors; (b) conduct field investigation and reporting; (c) track identified mitigations to completion; and (d) track effectiveness of issue identification and remediation using EFD/DFA technologies. | The program has met all interim milestones. The team is in process of identifying analytics use cases for DFA/EFD. On-track to meet goals in 2023. | This program remains on track to meet its 2023 target, with the analytics use case specifications for EFD and DFA being completed as of May 31, 2023. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | FPI and IPW Modeling - Revision Evaluation | Evaluate enhancements to the FPI (Fire Potential Index) model and the IPW (Ignition Probability Weather) model. This involves testing new features and types of model configurations that could improve model skill. At present we do not know if model skills can be improved but we will attempt to do so. | This initiative will help further develop PG&E's risk modeling capabilities and weather-related situational awareness. | Situational Awareness and Forecasting | 8.3 | Planned Improvements |  | 8.3.6.3 | SA-04 | PGE_Situational Awareness and Forecasting_Planned Improvements_SA-04_2023 | 565 to 568 | PSPS likelihood | No | [10 empty] | Evaluate enhancements to the FPI (Fire Potential Index) model and the IPW (Ignition Probability Weather) model. This involves testing new features and types of model configurations that could improve model skill. At present we do not know if model skills can be improved but we will attempt to do so. | The program has met all interim milestones. The meteorology team is currently evaluating improvements to the FPI/OPW and is on track to complete evaluation and any potential development on time. Q1 work was almost exclusively research and will transition to development in Q2. | The program continues to meet all interim milestones. In Q2, the meteorology team completed its evaluation of improvements to the FPI/OPW and began data preparation for model training. FPI and IPW model |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Evaluate FPI and IPW Modeling enhancements in 2023 - 2025 | Evaluate enhancements to the FPI (Fire Potential Index) model and the IPW (Ignition Probability Weather). | This initiative will help further develop PG&E's risk modeling capabilities and weather-related situational awareness. | Situational Awareness and Forecasting | 8.3 | Planned Improvements |  | 8.3.6.3 | SA-05 | PGE_Situational Awareness and Forecasting_Planned Improvements_SA-05_2023 | 565 to 568 | PSPS likelihood | No | [10 empty] | Evaluate enhancements to the FPI (Fire Potential Index) model and the IPW (Ignition Probability Weather). | The program has met all interim milestones. The meteorology team is currently evaluating improvements to the FPI/OPW and is on track to complete evaluation and any potential development on time. Q1 work was almost exclusively research and will transition to development in Q2. | The program continues to meet all interim milestones. In Q2, the meteorology team completed its evaluation of improvements to the FPI/OPW and began data preparation for model training. FPI and IPW model training, test model configurations and features are underway, and work on these items will continue through Q3. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Complete PSPS and Wildfire Tabletop and Functional Exercises | Complete PSPS and Wildfire Tabletop and Functional Exercise annually in compliance with the guiding principles of the Homeland Security Exercise Evaluation Program (HSEEP) | This initiative will complete the PSPS and Wildfire Tabletop and Functional Exercise to assist with our response to emergency activations, including wildfires. | Emergency Preparedness Plan | 8.4 | Drills, Simulations, and Tabletop Exercises |  | 8.4.2.3.1 | EP-01 | PGE_Emergency Preparedness Plan_Drills, Simulations, and Tabletop Exercises_EP-01_2023 | 623 to 628 | PSPS likelihood | No | [10 empty] | Complete PSPS and Wildfire Tabletop and Functional Exercise annually in compliance with the guiding principles of the Homeland Security Exercise Evaluation Program (HSEEP) | We fell behind on key milestones for this program due to the functional exercise being rescheduled from the week of March 27 to the week of May 8th as a result of the unprecedented winter storms. | As a result of our corrective actions, we have now met all interim milestones and this work is on track to meet our annual target, despite the delays resulting from the winter storms. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Maintain all hazards planning and preparedness program in 2023 - 2025 | Maintain the all hazards planning and preparedness program to provide emergency response and safely and expeditiously restore service. | This initiative will Maintain the all hazards planning and preparedness program to provide emergency response and safely and expeditiously restore service, including during wildfires. | Emergency Preparedness Plan | 8.4 | Emergency Planning |  | 8.4.3.1 | EP-02 | PGE_Emergency Preparedness Plan_Emergency Planning_EP-02_2023 | 623 to 628 | PSPS likelihood | No | [10 empty] | Maintain the all hazards planning and preparedness program to provide emergency response and safely and expeditiously restore service. | The program met all interim milestones by conducting a PSPS Seminar and a PSPS Functional Exercise. | This program met the annual commitment with the submittal of the GO-166 report and presentation to the State. This work has been marked as complete as of May 31, 2023. |  |  | Completed
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Expand all hazards planning to include additional threats and scenarios in 2023 - 2025 | Expand the all hazards planning program to include additional threats and scenarios. | This initiative will expand the all hazards planning program to include additional threats and scenarios to provide emergency response and safely and expeditiously restore service, including during wildfires. | Emergency Preparedness Plan | 8.4 | Emergency Planning |  | 8.4.3.1 | EP-04 | PGE_Emergency Preparedness Plan_Emergency Planning_EP-04_2023 | 623 to 628 | PSPS likelihood | No | [10 empty] | Expand the all hazards planning program to include additional threats and scenarios. | The program met all interim milestones, including scheduling initial meetings with the project workgroup, obtaining buy-in for a draft table of contents, confirming the subject matter expert (SME) list, and gathering intel to populate the draft annex. | This program remains on target with one hazard annex published and one on track to be reviewed in August of 2023. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | Review, and revise the CERP and 2 Wildfire Related Annexes on a yearly basis | Review, and revise the CERP and 2 Wildfire Related Annexes on a yearly basis. | This initiative will review, and revise the CERP and 2 Wildfire Related Annexes to provide emergency response and safely and expeditiously restore service, including during wildfires. | Emergency Preparedness Plan | 8.4 | Emergency Planning |  | 8.4.3.1 | EP-06 | PGE_Emergency Preparedness Plan_Emergency Planning_EP-06_2023 | 629 to 631 | PSPS likelihood | No | Company Emergency Response Plan (CERP) and the two wildfire related annexes | 3 | 0 | 0 | 2 | 3 | 0 | 2 | [7 empty] | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Evaluate enhancements for the PSPS Transmission guidance | Evaluate enhancements for the PSPS Transmission guidance to enhance focus of PSPS events. | This initiative will evaluate enhancements for the PSPS Transmission guidance to enhance focus of PSPS events and help prevent ignitions that could cause wildfires. | Public Safety Power Shutoff | 9.2 | Risk Thresholds (e.g., WS, FPI, etc.) and Decision Making Process That Determine the Need for a PSPS |  | 9.2.1 | PS-01 | PGE_Public Safety Power Shutoff_Risk Thresholds (e.g., WS, FPI, etc.) and Decision Making Process That Determine the Need for a PSPS_PS-01_2023 | 756 to 759 | PSPS likelihood | No | [10 empty] | Evaluate enhancements for the PSPS Transmission guidance to enhance focus of PSPS events. | The program met all interim milestones, which was to have a kickoff and planning meeting with the project teams by the end of Q1. This program remains on track. | The program met all interim milestones and remains on track. We are targeting approval of the 2023 Transmission Guidance in Q3. |  |  | On Track
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Evaluate incorporation of approved IPW enhancements into the PSPS Distribution guidance | Evaluate incorporation of approved IPW enhancements into the PSPS Distribution guidance to enhance focus of PSPS events. | This initiative will evaluate the incorporation of approved IPW enhancements into the PSPS Distribution guidance to enhance focus of PSPS events and help prevent ignitions that could cause wildfires. | Public Safety Power Shutoff | 9.2 | Risk Thresholds (e.g., WS, FPI, etc.) and Decision Making Process That Determine the Need for a PSPS |  | 9.2.1 | PS-02 | PGE_Public Safety Power Shutoff_Risk Thresholds (e.g., WS, FPI, etc.) and Decision Making Process That Determine the Need for a PSPS_PS-02_2023 | 756 to 759 | PSPS likelihood | No | [10 empty] | Evaluate incorporation of approved IPW enhancements into the PSPS Distribution guidance to enhance focus of PSPS events. | The program met all interim milestones, which was to have a kickoff and planning meeting with project teams by Q1. This program remains on track. | The program met all interim milestones, which were to evaluate potential improvements to the FPI/OPW and begin data preparation for model training. FPI and IPW model training, test model configurations and features are underway, and work on these items will continue through Q3. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | Provide 12,000 new or replacement portable batteries to PG&E customers at risk of PSPS or EPSS | Provide 4,000 cumulative new or replacement portable batteries to PG&E customers | This initiative will provide 4,000 cumulative new or replacement portable batteries to PG&E customers to assist them during emergency events, including wildfires. | Public Safety Power Shutoff | 8.5 | Customer Support in Wildfire and PSPS Emergencies |  | 8.5.3 | PS-06 | PGE_Public Safety Power Shutoff_Customer Support in Wildfire and PSPS Emergencies_PS-06_2023 | 760 to 762 | PSPS likelihood | No | # of batteries | 4000 | 63 | 213 | 2926 | 4000 | 448 | 631 | [7 empty] | On Track
PGE | 2023-05-01 | Program |  |  | PSPS Customer Impact Reduction | 15,000 customer events based on Wildfire mitigation projects including but not limited to MSO replacements and Undergrounded miles planned for 2023 | This initiative will focus on the reduction of 15,000 customer events based on Wildfire mitigation projects and help improve PG&E's response to wildfires. | Public Safety Power Shutoff | 9.1 | Performance Metrics Identified by the Electrical Corporation |  | 9.1.5 | PS-07 | PGE_Public Safety Power Shutoff_Performance Metrics Identified by the Electrical Corporation_PS-07_2023 | 763 to 765 | PSPS likelihood | No | # of Customer events | 15000 | 265 | 2388 | 8421 | 15000 | 341.31 | 1674.04 | [7 empty] | Delayed | We fell behind the Q2 YTD target of reducing the impact to 2,388 with a reduction of 1,675 customers impacted by PSPS events, as of the end of June. This work is tied to the miles of undergrounding completed and the number of MSO devices replaced/removed. The multiple storm/snow events in Q1 delayed work and prevented access to underground construction sites where work was otherwise ready to execute. Corrective Actions: The Undergrounding Program is accelerating work readiness activities for 2024 and beyond work with estimating having recently completed 400 miles of system hardening work for 2023 & 2024 that will allow the program to build in some buffer against future delays. The catch back plan is in place and forecast being on track with original target by September 30.
PGE | 2023-05-01 | Project | 2023-01-01 | 2023-12-31 | Community Engagement - Meetings | Hold community engagement meetings within the five PG&E regions of service that will include, but are not limited to, a mix of webinars, open houses, town halls, and/or answer centers. | This initiative concerns customer and community events to further awareness of WMP activities. | Community Outreach and Engagement | 8.5 | Public Outreach and Education Awareness Program |  | 8.5.2 | CO-01 | PGE_Community Outreach and Engagement_Public Outreach and Education Awareness Program_CO-01_2023 | 718 to 721 | Wildfire vulnerability | No | [10 empty] | Hold community engagement meetings within the five PG&E regions of service that will include, but are not limited to, a mix of webinars, open houses, town halls, and/or answer centers. | This program met all interim milestones by conducting community engagement meetings within five PG&E service regions as defined in the annual qualitative target. We exceeded the Q1 2023 target by conducting a sixth outreach through a Wildfire Safety Webinar. | This program continues to meet the interim milestone of conducting community engagement meetings within five PG&E service regions on a quarterly basis, as defined in the annual qualitative target. We exceeded the Q2 2023 target by conducting outreach within five service regions and other targeted counties through six Regional Halls, six Wildfire Safety Webinars, and two in-person events. |  |  | On Track
PGE | 2023-05-01 | Program |  |  | Community Engagement - Surveys | PG&E will complete two PSPS education and outreach surveys. | This initiative concerns customer and community events to further awareness of WMP activities. | Community Outreach and Engagement | 8.5 | Public Outreach and Education Awareness Program |  | 8.5.2 | CO-02 | PGE_Community Outreach and Engagement_Public Outreach and Education Awareness Program_CO-02_2023 | 722 to 726 | Wildfire vulnerability | Yes | # of surveys | 2 | 1 | 1 | 1 | 2 | 0 | 2 | [7 empty] | On Track
Notes:
1. For Column Q (RiskTargetReduction), PG&E has attempted to chose the risk components targeted listed in the Data Guidelines that most closely matches the Initiative Target.
2. For some quantitative initiative targets, numbers may change as data is validated, SAP transaction processing, and/or clerical work is performed to input data.
3. For Column G (InitiativeDescription), some initiatives may have more than 500 characters. We have included in this Table 1 all of the language from the 2023 WMP describing each Initiative Description and therefore may exceed the 500 character limit.
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
____2023
Note on C2: Author: Select cells for dropdown list.

## Table 2
| Utility | PG&E | Notes:
| Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2025-03-12 | HWW = High wind warning
RFW = Red flag warning
[10 empty] | Actuals | [15 empty] | Note: These columns are placeholders for future QR submissions. | [7 empty] | Projected
| Table 2: Performance Metrics | [8 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Metric type | # | Metric name | Wind Warning Status | Program Name | HFTD Tier | Line Type | Inspection Type | Inspection Method | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 8; Actuals 3: 229; Actuals 4: 76; Actuals 1: 4; Actuals 2: 31; Actuals 3: 9; Actuals 4: 29; Actuals 1: 0; Actuals 2: 18; Actuals 3: 3; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 122.8 | 122.8 | 122.8 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 320; Actuals 2: 0; Actuals 3: 135; Actuals 4: 8; Actuals 1: 7; Actuals 2: 0; Actuals 3: 0; Actuals 4: 5; Actuals 1: 424; Actuals 2: 0 | 181.2 | 181.2 | 181.2 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 0; Actuals 3: 59; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 13.2 | 13.2 | 13.2 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 1560; Actuals 2: 1288; Actuals 3: 1205; Actuals 4: 1114; Actuals 1: 2344; Actuals 2: 1498; Actuals 3: 1488; Actuals 4: 1644; Actuals 1: 953; Actuals 2: 1195; Actuals 3: 1107; Actuals 4: 1100; Actuals 1: 2538; Actuals 2: 1091 | 5780.6 | 5780.6 | 5780.6 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 3; Actuals 3: 369; Actuals 4: 49; Actuals 1: 1; Actuals 2: 19; Actuals 3: 3; Actuals 4: 16; Actuals 1: 0; Actuals 2: 8; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 180.6 | 180.6 | 180.6 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 381; Actuals 2: 0; Actuals 3: 44; Actuals 4: 1; Actuals 1: 17; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 200; Actuals 2: 0 | 143.8 | 143.8 | 143.8 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 36; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 7.4 | 7.4 | 7.4 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 1480; Actuals 2: 716; Actuals 3: 980; Actuals 4: 667; Actuals 1: 1590; Actuals 2: 696; Actuals 3: 651; Actuals 4: 1011; Actuals 1: 567; Actuals 2: 581; Actuals 3: 512; Actuals 4: 587; Actuals 1: 1303; Actuals 2: 530 | 3604.8 | 3604.8 | 3604.8 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 56; Actuals 3: 980; Actuals 4: 449; Actuals 1: 14; Actuals 2: 221; Actuals 3: 14; Actuals 4: 646; Actuals 1: 0; Actuals 2: 232; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 744.2 | 744.2 | 744.2 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 31; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1108; Actuals 2: 3; Actuals 3: 681; Actuals 4: 55; Actuals 1: 13; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2580; Actuals 2: 0 | 556.2 | 556.2 | 556.2 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 196; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 105.4 | 105.4 | 105.4 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 6094; Actuals 2: 6687; Actuals 3: 7162; Actuals 4: 6804; Actuals 1: 9596; Actuals 2: 8001; Actuals 3: 6885; Actuals 4: 13017; Actuals 1: 7376; Actuals 2: 8964; Actuals 3: 8770; Actuals 4: 8034; Actuals 1: 21335; Actuals 2: 8060 | 30172.4 | 30172.4 | 30172.4 | Number of events | 5 year average used for this risk event and projections
| 1. Risk Events | 1.b. | Number of wires down | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 24; Actuals 4: 7; Actuals 1: 2; Actuals 2: 1; Actuals 3: 0; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 12.4 | 12.4 | 12.4 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 99; Actuals 2: 0; Actuals 3: 11; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 158; Actuals 2: 0 | 52.4 | 52.4 | 52.4 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 4; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0.8 | 0.8 | 0.8 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 256; Actuals 2: 135; Actuals 3: 85; Actuals 4: 76; Actuals 1: 365; Actuals 2: 105; Actuals 3: 108; Actuals 4: 174; Actuals 1: 63; Actuals 2: 84; Actuals 3: 45; Actuals 4: 104; Actuals 1: 471; Actuals 2: 54 | 704.6 | 704.6 | 704.6 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 49; Actuals 4: 8; Actuals 1: 1; Actuals 2: 3; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 17.6 | 17.6 | 17.6 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 207; Actuals 2: 0; Actuals 3: 4; Actuals 4: 0; Actuals 1: 4; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 64; Actuals 2: 0 | 63.4 | 63.4 | 63.4 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0.4 | 0.4 | 0.4 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 385; Actuals 2: 94; Actuals 3: 95; Actuals 4: 70; Actuals 1: 342; Actuals 2: 59; Actuals 3: 58; Actuals 4: 149; Actuals 1: 51; Actuals 2: 52; Actuals 3: 29; Actuals 4: 94; Actuals 1: 267; Actuals 2: 23 | 584.2 | 584.2 | 584.2 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 3; Actuals 3: 61; Actuals 4: 33; Actuals 1: 2; Actuals 2: 12; Actuals 3: 0; Actuals 4: 66; Actuals 1: 0; Actuals 2: 22; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 62.2 | 62.2 | 62.2 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 4; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 174; Actuals 2: 1; Actuals 3: 31; Actuals 4: 5; Actuals 1: 6; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 702; Actuals 2: 0 | 85.8 | 85.8 | 85.8 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 9; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 10.4 | 10.4 | 10.4 | Number of events | 5 year average used for this risk event and projections
|  |  | Number of wires down | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 576; Actuals 2: 492; Actuals 3: 525; Actuals 4: 486; Actuals 1: 861; Actuals 2: 506; Actuals 3: 489; Actuals 4: 2252; Actuals 1: 562; Actuals 2: 644; Actuals 3: 545; Actuals 4: 990; Actuals 1: 3778; Actuals 2: 454 | 2759.4 | 2759.4 | 2759.4 | Number of events | 5 year average used for this risk event and projections
| 1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 7; Actuals 3: 196; Actuals 4: 63; Actuals 1: 2; Actuals 2: 30; Actuals 3: 9; Actuals 4: 23; Actuals 1: 0; Actuals 2: 15; Actuals 3: 3; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 3 | 3 | 3 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 197; Actuals 2: 0; Actuals 3: 119; Actuals 4: 6; Actuals 1: 5; Actuals 2: 0; Actuals 3: 0; Actuals 4: 4; Actuals 1: 206; Actuals 2: 1 | 2 | 2 | 2 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 0; Actuals 3: 49; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 1167; Actuals 2: 1096; Actuals 3: 1053; Actuals 4: 999; Actuals 1: 1778; Actuals 2: 1322; Actuals 3: 1318; Actuals 4: 1255; Actuals 1: 818; Actuals 2: 1033; Actuals 3: 990; Actuals 4: 901; Actuals 1: 1816; Actuals 2: 984 | 3742 | 3742 | 3742 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 288; Actuals 4: 37; Actuals 1: 0; Actuals 2: 16; Actuals 3: 3; Actuals 4: 13; Actuals 1: 0; Actuals 2: 7; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 1 | 1 | 1 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 170; Actuals 2: 0; Actuals 3: 38; Actuals 4: 1; Actuals 1: 13; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 110; Actuals 2: 0 | 8 | 8 | 8 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 30; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 714; Actuals 2: 505; Actuals 3: 834; Actuals 4: 508; Actuals 1: 957; Actuals 2: 565; Actuals 3: 546; Actuals 4: 646; Actuals 1: 406; Actuals 2: 420; Actuals 3: 413; Actuals 4: 358; Actuals 1: 860; Actuals 2: 426 | 1597 | 1597 | 1597 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 48; Actuals 3: 896; Actuals 4: 386; Actuals 1: 10; Actuals 2: 203; Actuals 3: 14; Actuals 4: 519; Actuals 1: 0; Actuals 2: 197; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 35 | 35 | 35 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 28; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 883; Actuals 2: 3; Actuals 3: 648; Actuals 4: 46; Actuals 1: 6; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1554; Actuals 2: 0 | 7 | 7 | 7 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 182; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 5594; Actuals 2: 6282; Actuals 3: 6800; Actuals 4: 6494; Actuals 1: 8711; Actuals 2: 7652; Actuals 3: 6567; Actuals 4: 10348; Actuals 1: 6909; Actuals 2: 8396; Actuals 3: 8322; Actuals 4: 7193; Actuals 1: 15775; Actuals 2: 7783 | 30820 | 30820 | 30820 | Number of events
| 1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1; Actuals 3: 33; Actuals 4: 13; Actuals 1: 2; Actuals 2: 1; Actuals 3: 0; Actuals 4: 6; Actuals 1: 0; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 3 | 3 | 3 | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 123; Actuals 2: 0; Actuals 3: 16; Actuals 4: 2; Actuals 1: 2; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 218; Actuals 2: 0 | 2 | 2 | 2 | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 10; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 393; Actuals 2: 192; Actuals 3: 152; Actuals 4: 115; Actuals 1: 566; Actuals 2: 176; Actuals 3: 170; Actuals 4: 389; Actuals 1: 135; Actuals 2: 162; Actuals 3: 117; Actuals 4: 199; Actuals 1: 722; Actuals 2: 91 | 613 | 613 | 613 | Number of events
|  |  | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 2; Actuals 3: 81; Actuals 4: 12; Actuals 1: 1; Actuals 2: 3; Actuals 3: 0; Actuals 4: 3; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 1 | 1 | 1 | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 211; Actuals 2: 0; Actuals 3: 6; Actuals 4: 0; Actuals 1: 4; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 90; Actuals 2: 0 | 5 | 5 | 5 | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 6; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 766; Actuals 2: 211; Actuals 3: 146; Actuals 4: 159; Actuals 1: 633; Actuals 2: 131; Actuals 3: 105; Actuals 4: 365; Actuals 1: 161; Actuals 2: 161; Actuals 3: 99; Actuals 4: 229; Actuals 1: 443; Actuals 2: 80 | 650 | 650 | 650 | Number of events
|  |  | Number of outage events caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 8; Actuals 3: 84; Actuals 4: 63; Actuals 1: 4; Actuals 2: 18; Actuals 3: 0; Actuals 4: 127; Actuals 1: 0; Actuals 2: 35; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 35 | 35 | 35 | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 3; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 225; Actuals 2: 0; Actuals 3: 33; Actuals 4: 9; Actuals 1: 7; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1026; Actuals 2: 0 | 7 | 7 | 7 | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 14; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 500; Actuals 2: 405; Actuals 3: 362; Actuals 4: 310; Actuals 1: 885; Actuals 2: 349; Actuals 3: 318; Actuals 4: 2669; Actuals 1: 467; Actuals 2: 568; Actuals 3: 448; Actuals 4: 841; Actuals 1: 5560; Actuals 2: 316 | - | - | - | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
| 1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 11; Actuals 3: 6; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0 | 17.8105 | 17.4316 | 17.0526 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 167; Actuals 3: 443; Actuals 4: 216; Actuals 1: 2; Actuals 2: 110 | 817.3053 | 799.9158 | 782.5263 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 2.9684 | 2.9053 | 2.8421 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 71; Actuals 3: 153; Actuals 4: 50; Actuals 1: 0; Actuals 2: 36 | 271.1158 | 265.3474 | 259.5789 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 17; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 16.8211 | 16.4632 | 16.1053 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 4; Actuals 2: 306; Actuals 3: 726; Actuals 4: 201; Actuals 1: 5; Actuals 2: 82 | 1223.9789 | 1197.9368 | 1171.8947 | Number of events | This program started in 2022. Unable to provide actuals from 2020 - 2021.
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.2.a. | Median time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 3013; Actuals 2: 1477; Actuals 3: 1408; Actuals 4: 1331; Actuals 1: 902; Actuals 2: 927; Actuals 3: 1064; Actuals 4: 1258; Actuals 1: 2029; Actuals 2: 1548.5; Actuals 3: 1451; Actuals 4: 1788; Actuals 1: 3038; Actuals 2: 1980 | 1700 | 1600 | 1500 | hours
|  | 2.d.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 4887; Actuals 2: 4869.8; Actuals 3: 3544; Actuals 4: 4045; Actuals 1: 2869.9; Actuals 2: 2913; Actuals 3: 3300; Actuals 4: 5221; Actuals 1: 5336; Actuals 2: 5004; Actuals 3: 5291; Actuals 4: 7332.9; Actuals 1: 8197; Actuals 2: 8029 | 4750 | 4650 | 4550 | hours
|  | 2.d.3.a. | Median time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 2919; Actuals 2: 1330; Actuals 3: 1622; Actuals 4: 1451; Actuals 1: 996; Actuals 2: 857; Actuals 3: 876; Actuals 4: 1359; Actuals 1: 2102; Actuals 2: 1499; Actuals 3: 1477; Actuals 4: 1786; Actuals 1: 3206; Actuals 2: 2003 | 1700 | 1600 | 1500 | hours
|  | 2.d.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 5965; Actuals 2: 6517; Actuals 3: 4167; Actuals 4: 4838; Actuals 1: 5463; Actuals 2: 4574; Actuals 3: 3491; Actuals 4: 4379; Actuals 1: 4742; Actuals 2: 5892; Actuals 3: 4695.85; Actuals 4: 6228; Actuals 1: 7691; Actuals 2: 9160 | 4750 | 4650 | 4550 | hours
|  | 2.d.4.a. | Median time | N/A |  | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 2313; Actuals 2: 1381; Actuals 3: 1235; Actuals 4: 1068; Actuals 1: 1114; Actuals 2: 928; Actuals 3: 830; Actuals 4: 1047; Actuals 1: 1765; Actuals 2: 1359; Actuals 3: 1165; Actuals 4: 1334; Actuals 1: 3037; Actuals 2: 2053 | 1700 | 1600 | 1500 | hours
|  | 2.d.4.b. | 95 percentile time | N/A |  | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 4981; Actuals 2: 7762; Actuals 3: 4646; Actuals 4: 3639.3; Actuals 1: 3999; Actuals 2: 3493; Actuals 3: 2823; Actuals 4: 3135; Actuals 1: 4359; Actuals 2: 5463.65; Actuals 3: 5318; Actuals 4: 5842; Actuals 1: 5411; Actuals 2: 6683 | 4750 | 4650 | 4550 | hours
|  | 2.t.2.a. | Median time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 3251; Actuals 2: 1622; Actuals 3: 1525; Actuals 4: 1741; Actuals 1: 2678; Actuals 2: 1334; Actuals 3: 1978; Actuals 4: 3133; Actuals 1: 3994; Actuals 2: 1546; Actuals 3: 1957; Actuals 4: 3206; Actuals 1: 1885; Actuals 2: 1668 | 2700 | 2600 | 2500 | hours
|  | 2.t.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 5939; Actuals 2: 6877; Actuals 3: 5384; Actuals 4: 6061; Actuals 1: 8267.3; Actuals 2: 7500; Actuals 3: 7641; Actuals 4: 8792; Actuals 1: 8432; Actuals 2: 9207.55; Actuals 3: 5174; Actuals 4: 5797; Actuals 1: 9830; Actuals 2: 6923 | 7800 | 7700 | 7600 | hours
|  | 2.t.3.a. | Median time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 3755; Actuals 2: 1886; Actuals 3: 1453; Actuals 4: 2537; Actuals 1: 853; Actuals 2: 995; Actuals 3: 2149; Actuals 4: 3516.5; Actuals 1: 3298; Actuals 2: 2103; Actuals 3: 2820; Actuals 4: 3662; Actuals 1: 2821.5; Actuals 2: 1571 | 2700 | 2600 | 2500 | hours
|  | 2.t.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 7310; Actuals 2: 8896; Actuals 3: 9828; Actuals 4: 8292.6; Actuals 1: 11439; Actuals 2: 6827.3; Actuals 3: 9086; Actuals 4: 5557; Actuals 1: 7533; Actuals 2: 4548; Actuals 3: 7217; Actuals 4: 7716; Actuals 1: 10956; Actuals 2: 12303 | 7800 | 7700 | 7600 | hours
|  | 2.t.4.a. | Median time | N/A |  | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 2416; Actuals 2: 1524; Actuals 3: 1693; Actuals 4: 2126; Actuals 1: 1165; Actuals 2: 952; Actuals 3: 1695; Actuals 4: 1620; Actuals 1: 1934; Actuals 2: 1523; Actuals 3: 1884; Actuals 4: 3180; Actuals 1: 1861; Actuals 2: 1506 | 2700 | 2600 | 2500 | hours
|  | 2.t.4.b. | 95 percentile time | N/A |  | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 7018; Actuals 2: 9012; Actuals 3: 9030; Actuals 4: 9005; Actuals 1: 9731; Actuals 2: 7525; Actuals 3: 9212.8; Actuals 4: 8127; Actuals 1: 7810; Actuals 2: 8886; Actuals 3: 9079; Actuals 4: 10357.6; Actuals 1: 9085; Actuals 2: 9922 | 7800 | 7700 | 7600 | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | days
|  | 3.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 4; Actuals 2: 2; Actuals 3: 2; Actuals 4: 3; Actuals 1: 1; Actuals 2: 1; Actuals 3: 2; Actuals 4: 1; Actuals 1: 4; Actuals 2: 1; Actuals 3: 1; Actuals 4: 2; Actuals 1: 3; Actuals 2: 3 | 2 | 2 | 2 | days
|  | 3.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | days
|  | 3.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 2; Actuals 2: 2; Actuals 3: 2; Actuals 4: 2; Actuals 1: 1; Actuals 2: 2; Actuals 3: 2; Actuals 4: 1; Actuals 1: 2; Actuals 2: 1; Actuals 3: 1; Actuals 4: 2; Actuals 1: 4; Actuals 2: 3 | 2 | 2 | 2 | days
|  | 3.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | days
|  | 3.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 13; Actuals 2: 5; Actuals 3: 5; Actuals 4: 7; Actuals 1: 7; Actuals 2: 3; Actuals 3: 3; Actuals 4: 7; Actuals 1: 10; Actuals 2: 4; Actuals 3: 3; Actuals 4: 5; Actuals 1: 4; Actuals 2: 4 | 6 | 6 | 6 | days
|  | 3.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 1; Actuals 2: 1; Actuals 3: 6; Actuals 4: 4; Actuals 1: 1; Actuals 2: 1; Actuals 3: 1; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1; Actuals 3: 1; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1 | 1 | 1 | 1 | days | These forecasts are based on the 2022 average data.
|  | 3.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 26; Actuals 2: 25; Actuals 3: 27; Actuals 4: 10; Actuals 1: 4; Actuals 2: 4; Actuals 3: 3; Actuals 4: 5; Actuals 1: 13; Actuals 2: 19; Actuals 3: 11; Actuals 4: 1; Actuals 1: 16; Actuals 2: 25 | 10 | 10 | 10 | days | These forecasts are based on the 2022 average data.
|  | 3.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 1; Actuals 2: 22; Actuals 3: 17; Actuals 4: 3; Actuals 1: 3; Actuals 2: 1; Actuals 3: 2; Actuals 4: 1; Actuals 1: 8; Actuals 2: 0; Actuals 3: 8; Actuals 4: 3; Actuals 1: 2; Actuals 2: 1 | 5 | 5 | 5 | days | These forecasts are based on the 2022 average data.
|  | 3.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 85; Actuals 2: 88; Actuals 3: 28; Actuals 4: 25; Actuals 1: 4; Actuals 2: 76; Actuals 3: 12; Actuals 4: 3; Actuals 1: 14; Actuals 2: 7; Actuals 3: 14; Actuals 4: 120; Actuals 1: 13; Actuals 2: 11 | 12 | 12 | 12 | days | These forecasts are based on the 2022 average data, excluding Q4.
|  | 3.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 1; Actuals 2: 2; Actuals 3: 2; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 1 | 1 | 1 | 1 | days
|  | 3.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 98; Actuals 2: 46; Actuals 3: 20; Actuals 4: 13; Actuals 1: 6; Actuals 2: 4; Actuals 3: 4; Actuals 4: 15; Actuals 1: 7; Actuals 2: 3; Actuals 3: 16; Actuals 4: 19; Actuals 1: 26; Actuals 2: 38 | 13 | 13 | 13 | days | These forecasts are based on the 2022 average data.
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 311; Actuals 2: 393; Actuals 3: 473; Actuals 4: 567; Actuals 1: 668; Actuals 2: 712; Actuals 3: 645; Actuals 4: 561; Actuals 1: 568; Actuals 2: 415; Actuals 3: 441; Actuals 4: 556; Actuals 1: 903; Actuals 2: 760 | 528 | 502 | 380 | days
|  | 4.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 370; Actuals 2: 461; Actuals 3: 543; Actuals 4: 628; Actuals 1: 730; Actuals 2: 807; Actuals 3: 880; Actuals 4: 990; Actuals 1: 1082; Actuals 2: 1149; Actuals 3: 1233; Actuals 4: 1340; Actuals 1: 1421; Actuals 2: 1524 | 1273 | 1209 | 420 | days
|  | 4.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 283; Actuals 2: 343; Actuals 3: 397; Actuals 4: 509; Actuals 1: 603; Actuals 2: 349; Actuals 3: 415; Actuals 4: 496; Actuals 1: 558; Actuals 2: 399; Actuals 3: 443; Actuals 4: 579; Actuals 1: 895.5; Actuals 2: 744 | 550 | 180 | 180 | days
|  | 4.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 344; Actuals 2: 441; Actuals 3: 561; Actuals 4: 1639; Actuals 1: 716; Actuals 2: 785; Actuals 3: 860; Actuals 4: 962; Actuals 1: 1046; Actuals 2: 1120; Actuals 3: 1166; Actuals 4: 1317; Actuals 1: 1426; Actuals 2: 1515 | 1251 | 220 | 200 | days
|  | 4.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 44; Actuals 2: 81; Actuals 3: 67; Actuals 4: 61; Actuals 1: 187; Actuals 2: 113; Actuals 3: 46; Actuals 4: 54; Actuals 1: 89; Actuals 2: 67; Actuals 3: 44; Actuals 4: 48; Actuals 1: 195.5; Actuals 2: 262 | 46 | 44 | 42 | days | These forecasts are based on the 2022 Q4 data.
|  | 4.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 383; Actuals 2: 445; Actuals 3: 536; Actuals 4: 599; Actuals 1: 713; Actuals 2: 790; Actuals 3: 859; Actuals 4: 925; Actuals 1: 1008; Actuals 2: 1078; Actuals 3: 1065; Actuals 4: 915; Actuals 1: 1338; Actuals 2: 1455 | 869 | 826 | 785 | days | These forecasts are based on the 2022 Q4 data.
|  | 4.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 340; Actuals 2: 409; Actuals 3: 469; Actuals 4: 542; Actuals 1: 635; Actuals 2: 330; Actuals 3: 237; Actuals 4: 222; Actuals 1: 299; Actuals 2: 355; Actuals 3: 409; Actuals 4: 414; Actuals 1: 283; Actuals 2: 354 | 331 | 331 | 331 | days | These forecasts are based on the 2022 average data.
|  | 4.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 429; Actuals 2: 519; Actuals 3: 593; Actuals 4: 691; Actuals 1: 787; Actuals 2: 860; Actuals 3: 888; Actuals 4: 987; Actuals 1: 1172; Actuals 2: 1115; Actuals 3: 804; Actuals 4: 1174; Actuals 1: 586; Actuals 2: 643 | 1003.5 | 365 | 365 | days | 2024-2025: set allowable duration as max; 2023 from 2022
|  | 4.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 306; Actuals 2: 364; Actuals 3: 306; Actuals 4: 227; Actuals 1: 251; Actuals 2: 279; Actuals 3: 141; Actuals 4: 224; Actuals 1: 294; Actuals 2: 364; Actuals 3: 420; Actuals 4: 234; Actuals 1: 281.5; Actuals 2: 346 | 321.75 | 163.2329 | 163.2329 | days | 2023 forecast is based on the 2022 average data. Projections for 2024-2025 has same ratio of median to 95% as T2
|  | 4.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 441; Actuals 2: 515; Actuals 3: 599; Actuals 4: 675; Actuals 1: 737; Actuals 2: 778; Actuals 3: 791; Actuals 4: 923; Actuals 1: 1168; Actuals 2: 808; Actuals 3: 653; Actuals 4: 825; Actuals 1: 620; Actuals 2: 458 | 855.5 | 180 | 180 | days | 2024-2025: set allowable duration as max; 2023 from 2022
|  | 4.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 286; Actuals 2: 300; Actuals 3: 86; Actuals 4: 75; Actuals 1: 167; Actuals 2: 247; Actuals 3: 83; Actuals 4: 75; Actuals 1: 320; Actuals 2: 358; Actuals 3: 412; Actuals 4: 519; Actuals 1: 516; Actuals 2: 529 | 348 | 348 | 348 | days | These forecasts are based on the 2022 average data.
|  | 4.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 427; Actuals 2: 484; Actuals 3: 508; Actuals 4: 617; Actuals 1: 731; Actuals 2: 823; Actuals 3: 808; Actuals 4: 845; Actuals 1: 1047; Actuals 2: 1144; Actuals 3: 1159; Actuals 4: 1268; Actuals 1: 944; Actuals 2: 1094 | 1105.6667 | 1105.6667 | 1105.6667 | days | These forecasts are based on the 2022 average data.
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 1386; Actuals 2: 1271; Actuals 3: 540; Actuals 4: 592; Actuals 1: 682; Actuals 2: 795; Actuals 3: 1548; Actuals 4: 1528; Actuals 1: 1941; Actuals 2: 1653; Actuals 3: 1276; Actuals 4: 1328; Actuals 1: 1121; Actuals 2: 822 | 1603 | 1664 | 1724 | days | These forecasts are based on the 2020 - 2022 data.
|  | 5.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | Actuals 1: 1953; Actuals 2: 2053; Actuals 3: 1941; Actuals 4: 1982; Actuals 1: 2152; Actuals 2: 2235; Actuals 3: 2311; Actuals 4: 2451; Actuals 1: 2549; Actuals 2: 2606; Actuals 3: 2689; Actuals 4: 2676; Actuals 1: 2576; Actuals 2: 2653 | 2803 | 2880 | 2958 | days | These forecasts are based on the 2020 - 2022 data.
|  | 5.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 994; Actuals 2: 1144; Actuals 3: 856; Actuals 4: 708; Actuals 1: 692; Actuals 2: 795; Actuals 3: 1853; Actuals 4: 1227; Actuals 1: 1456; Actuals 2: 1130; Actuals 3: 1174; Actuals 4: 1290; Actuals 1: 915; Actuals 2: 773 | 1379 | 1421 | 1462 | days | These forecasts are based on the 2020 - 2022 data.
|  | 5.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | Actuals 1: 1936; Actuals 2: 1921; Actuals 3: 1961; Actuals 4: 2027; Actuals 1: 2164; Actuals 2: 2220; Actuals 3: 2264; Actuals 4: 2290; Actuals 1: 2507; Actuals 2: 2545; Actuals 3: 2614; Actuals 4: 2636; Actuals 1: 2412; Actuals 2: 2602 | 2731 | 2804 | 2877 | days | These forecasts are based on the 2020 - 2022 data.
|  | 5.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 1687; Actuals 2: 1576; Actuals 3: 1647; Actuals 4: 1303; Actuals 1: 1916; Actuals 2: 1887; Actuals 3: 1741; Actuals 4: 1856; Actuals 1: 1696; Actuals 2: 1558; Actuals 3: 738; Actuals 4: 769; Actuals 1: 1952; Actuals 2: 1818 | 1153 | 1095 | 1037 | days | These forecasts are based on the 2020 - 2022 data.
|  | 5.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | Actuals 1: 1956; Actuals 2: 1925; Actuals 3: 1994; Actuals 4: 2092; Actuals 1: 2205; Actuals 2: 2258; Actuals 3: 2301; Actuals 4: 2476; Actuals 1: 2665; Actuals 2: 2652; Actuals 3: 2366; Actuals 4: 2723; Actuals 1: 2689; Actuals 2: 2837 | 2772 | 2845 | 2917 | days | These forecasts are based on the 2020 - 2022 data.
|  | 5.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 251; Actuals 2: 315; Actuals 3: 302; Actuals 4: 308; Actuals 1: 227; Actuals 2: 329; Actuals 3: 363; Actuals 4: 250; Actuals 1: 311; Actuals 2: 409; Actuals 3: 407; Actuals 4: 221; Actuals 1: 580; Actuals 2: 381 | 1095 | 1095 | 1095 | days | Assumes 3 years
|  | 5.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | Actuals 1: 414; Actuals 2: 454; Actuals 3: 601; Actuals 4: 562; Actuals 1: 678; Actuals 2: 839; Actuals 3: 834; Actuals 4: 946; Actuals 1: 1076; Actuals 2: 1084; Actuals 3: 1174; Actuals 4: 1245; Actuals 1: 975; Actuals 2: 1471 | 1825 | 1825 | 1825 | days | Assumes 5 years
|  | 5.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 224; Actuals 2: 302; Actuals 3: 55; Actuals 4: 177; Actuals 1: 229; Actuals 2: 272; Actuals 3: 217; Actuals 4: 195; Actuals 1: 310; Actuals 2: 370; Actuals 3: 435; Actuals 4: 545; Actuals 1: 611; Actuals 2: 371 | 1095 | 1095 | 1095 | days | Assumes 3 years
|  | 5.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | Actuals 1: 312; Actuals 2: 358; Actuals 3: 544; Actuals 4: 526; Actuals 1: 605; Actuals 2: 746; Actuals 3: 717; Actuals 4: 912; Actuals 1: 1007; Actuals 2: 1021; Actuals 3: 807; Actuals 4: 899; Actuals 1: 1007; Actuals 2: 1095 | 1825 | 1825 | 1825 | days | Assumes 5 years
|  | 5.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 157; Actuals 2: 306; Actuals 3: 121; Actuals 4: 136; Actuals 1: 185; Actuals 2: 325; Actuals 3: 282; Actuals 4: 341; Actuals 1: 471; Actuals 2: 568; Actuals 3: 687; Actuals 4: 743; Actuals 1: 556; Actuals 2: 548 | 1095 | 1095 | 1095 | days | Assumes 3 years
|  | 5.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | Actuals 1: 729; Actuals 2: 795; Actuals 3: 777; Actuals 4: 760; Actuals 1: 1020; Actuals 2: 1010; Actuals 3: 770; Actuals 4: 902; Actuals 1: 1038; Actuals 2: 1057; Actuals 3: 1312; Actuals 4: 1352; Actuals 1: 961; Actuals 2: 1141 | 1825 | 1825 | 1825 | days | Assumes 5 years
| 6. Vegetation management work orders | 6.a. | Number of vegetation management open work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 34; Actuals 1: 54; Actuals 2: 821; Actuals 3: 358; Actuals 4: 1670; Actuals 1: 9243; Actuals 2: 27906; Actuals 3: 119416; Actuals 4: 153017; Actuals 1: 268665; Actuals 2: 54151 | <275,000 | <275,000 | <275,000 | Number of orders | Data is in total number of trees.​
|  | 6.b. | Number of vegetation management past due work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 34; Actuals 2: 51; Actuals 3: 7; Actuals 4: 112; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 11; Actuals 1: 24; Actuals 2: 0; Actuals 3: 57; Actuals 4: 33; Actuals 1: 384; Actuals 2: 962 | 110 | 105 | 100 | Number of orders | Data is in total number of trees and is based off P1/P2 and Second Patrol numbers. These numbers do not include constrained trees.
| 7. Asset management work orders | 7.a. | Number of asset management open work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 35596; Actuals 2: 65421; Actuals 3: 141912; Actuals 4: 176656; Actuals 1: 179580; Actuals 2: 251275; Actuals 3: 316300; Actuals 4: 358354; Actuals 1: 365025; Actuals 2: 479543; Actuals 3: 588721; Actuals 4: 621313; Actuals 1: 758367; Actuals 2: 793253 | 644618 | 623091 | 610239 | Number of nofications
|  | 7.b. | Number of asset management past due work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 15319; Actuals 2: 35918; Actuals 3: 76651; Actuals 4: 94485; Actuals 1: 99047; Actuals 2: 141343; Actuals 3: 187678; Actuals 4: 221670; Actuals 1: 223100; Actuals 2: 242582; Actuals 3: 262561; Actuals 4: 267605; Actuals 1: 393665; Actuals 2: 442156 | 282584 | 259680 | 255572 | Number of nofications
| 8. Response Time | 8.a. | Response time to locked open circuit breaker | N/A | N/A | N/A | N/A | N/A | N/A | [27 empty] | Hours | For metric 8a, data for crew response time to a locked circuit breaker incident is only readily available for instances involving hazard conditions such as 911 or wire down calls. PG&E will continue to review the available information in its outage systems to provide this information in a future filing, although we anticipate creating a system to capture this data could take many months. Currently, any quarterly data would reflect only 911 and wire down events and is not a good representation of our overall response time. | bar: Actuals 1 to Actuals 3
| 9. Fatalities and injuries due to utility-related ignitions | 9.a. | Fatalities due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 4; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of fatalities | Number of fatalities per year
|  | 9.b. | Injuries due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 5; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of injuries | Number of OSHA-reportable injuries per year
| 10. Value of assets destroyed by utility-related ignitions, listed by asset type | 10.a. | Value of assets destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 381.3M; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 491.4M; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | 1000
| 11. Structures damaged or destroyed by utility-related ignitions | 11.a. | Number of structures destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 206; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1334; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 78; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of structures
|  | 11.b. | Critical infrastructure damaged/destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 16; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of structures
| 12. Acreage burned by utility-ignited wildfires | 12.a. | Acreage burned by utility-ignited wildfires | N/A | N/A | N/A | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 1547; Actuals 3: 57738; Actuals 4: 10; Actuals 1: 742; Actuals 2: 446; Actuals 3: 967619; Actuals 4: 517; Actuals 1: 0; Actuals 2: 300; Actuals 3: 76848; Actuals 4: 42; Actuals 1: 0; Actuals 2: 318 | 0 | 0 | 0 | Acres
| 13. Number of utility-related ignitions | 13.a. | Number of ignitions | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 3; Actuals 3: 5; Actuals 4: 0; Actuals 1: 1; Actuals 2: 2; Actuals 3: 2; Actuals 4: 0; Actuals 1: 0; Actuals 2: 3; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
|  |  | Number of ignitions | None | N/A | Non- HFTD | N/A | N/A | N/A | Actuals 1: 0; Actuals 2: 12; Actuals 3: 7; Actuals 4: 1; Actuals 1: 1; Actuals 2: 2; Actuals 3: 0; Actuals 4: 2; Actuals 1: 0; Actuals 2: 5; Actuals 3: 1; Actuals 4: 1; Actuals 1: 0; Actuals 2: 4 | 0 | 0 | 0 | Number of ignitions | CPUC Reportable, fire size >10 acre
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections. | bar: Actuals 1 to Note: These columns are placeholders for future QR submissions. 4
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections. | bar: Actuals 1 to Note: These columns are placeholders for future QR submissions. 4
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections. | bar: Actuals 1 to Note: These columns are placeholders for future QR submissions. 4
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 248708; Actuals 2: 71890; Actuals 3: 31515; Actuals 4: 86; Actuals 1: 97044; Actuals 2: 193114; Actuals 3: 51978; Actuals 4: 0; Actuals 1: 464; Actuals 2: 226994 | 224111 | 307781 | 313910 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on the delta change from 2021 to 2022 for 2023 projection. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 10616; Actuals 2: 179858; Actuals 3: 55763; Actuals 4: 3107; Actuals 1: 5449; Actuals 2: 118700; Actuals 3: 65654; Actuals 4: 367; Actuals 1: 54; Actuals 2: 69812 | 219494 | 135824 | 129695 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 9611.47; Actuals 2: 2778.23; Actuals 3: 1217.92; Actuals 4: 3.32; Actuals 1: 3750.32; Actuals 2: 7463.01; Actuals 3: 2008.72; Actuals 4: 0; Actuals 1: 17.93; Actuals 2: 8772.32 | 8660.905 | 11894.3828 | 12131.2417 | # of circuit miles inspected by the utility | Projected data is based on the delta change from 2021 to 2022 for 2023 projection. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 410.26; Actuals 2: 6950.72; Actuals 3: 2154.99; Actuals 4: 120.07; Actuals 1: 210.58; Actuals 2: 4587.23; Actuals 3: 2537.24; Actuals 4: 14.18; Actuals 1: 2.09; Actuals 2: 2697.93 | 8482.4783 | 5249.0006 | 5012.1417 | # of circuit miles inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 4; Actuals 2: 15; Actuals 3: 12; Actuals 4: 1; Actuals 1: 20; Actuals 2: 7; Actuals 3: 4; Actuals 4: 4; Actuals 1: 8; Actuals 2: 8; Actuals 3: 6; Actuals 4: 0; Actuals 1: 0; Actuals 2: 27 |  |  |  | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 9; Actuals 2: 90; Actuals 3: 52; Actuals 4: 10; Actuals 1: 12; Actuals 2: 207; Actuals 3: 85; Actuals 4: 9; Actuals 1: 31; Actuals 2: 230; Actuals 3: 166; Actuals 4: 14; Actuals 1: 0; Actuals 2: 369 | 1576.6357 | 975.6301 | 931.6052 | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 538; Actuals 2: 812; Actuals 3: 650; Actuals 4: 598; Actuals 1: 592; Actuals 2: 780; Actuals 3: 853; Actuals 4: 591; Actuals 1: 618; Actuals 2: 794; Actuals 3: 742; Actuals 4: 527; Actuals 1: 448; Actuals 2: 854 | 2038.6667 | 2038.6667 | 2038.6667 | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 43; Actuals 2: 78; Actuals 3: 45; Actuals 4: 5; Actuals 1: 48; Actuals 2: 25; Actuals 3: 8; Actuals 4: 1; Actuals 1: 9; Actuals 2: 8; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 48 |  |  |  | # of findings from these asset inspections |  | PG&E does not project Patrol Inspection findings.
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 170 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 212; Actuals 2: 11823; Actuals 3: 9583; Actuals 4: 100; Actuals 1: 476; Actuals 2: 8600; Actuals 3: 2352; Actuals 4: 112; Actuals 1: 113; Actuals 2: 1483; Actuals 3: 902; Actuals 4: 20; Actuals 1: 11; Actuals 2: 17729 | 54920.2451 | 33984.9261 | 32451.3708 | # of findings from these asset inspections; projections based on WMP and execution of 10% in non-HFTD
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 779; Actuals 2: 2507; Actuals 3: 1859; Actuals 4: 640; Actuals 1: 690; Actuals 2: 5176; Actuals 3: 906; Actuals 4: 1040; Actuals 1: 987; Actuals 2: 476; Actuals 3: 366; Actuals 4: 157; Actuals 1: 741; Actuals 2: 2433 | 6306 | 6306 | 6306 | # of findings from these asset inspections |  | Blank: Projection data at this granularity is unavailable at this time of submission. PG&E is refining it's back end system for future quarters.
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 7; Actuals 3: 3; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 4 |  |  |  | # of findings from these asset inspections |  | PG&E does not project Patrol Inspection findings.
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 10 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 53; Actuals 2: 3309; Actuals 3: 2272; Actuals 4: 30; Actuals 1: 25; Actuals 2: 311; Actuals 3: 130; Actuals 4: 9; Actuals 1: 10; Actuals 2: 33; Actuals 3: 17; Actuals 4: 3; Actuals 1: 6; Actuals 2: 3117 | 9501.3651 | 5879.4929 | 5614.1833 | # of findings from these asset inspections; projections based on WMP and execution of 10% in non-HFTD
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 55; Actuals 2: 172; Actuals 3: 166; Actuals 4: 37; Actuals 1: 43; Actuals 2: 133; Actuals 3: 46; Actuals 4: 17; Actuals 1: 19; Actuals 2: 20; Actuals 3: 11; Actuals 4: 2; Actuals 1: 57; Actuals 2: 495 | 520.6667 | 521 | 521 | # of findings from these asset inspections |  | Blank: Projection data at this granularity is unavailable at this time of submission. PG&E is refining it's back end system for future quarters.
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1325; Actuals 2: 24757 | 192913 | 110077 | 91032 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Prior to 2023, PG&E did not have to patrol inspections as it was covered by Detailed Inspections. Starting 2023, PG&E has started inspections based on wildfire risk consequence. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 10972; Actuals 2: 161321; Actuals 3: 28300; Actuals 4: 710; Actuals 1: 740; Actuals 2: 122872; Actuals 3: 81486; Actuals 4: 135; Actuals 1: 4; Actuals 2: 7204 | 9578 | 92414 | 111459 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 51.21; Actuals 2: 956.75 | 7455.2395 | 4253.9922 | 3517.9867 | # of circuit miles inspected by the utility | Projected data is based on the delta change from 2021 to 2022 for 2023 projection. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 424.02; Actuals 2: 6234.35; Actuals 3: 1093.67; Actuals 4: 27.44; Actuals 1: 28.6; Actuals 2: 4748.46; Actuals 3: 3149.08; Actuals 4: 5.22; Actuals 1: 0.15; Actuals 2: 278.4 | 370.1476 | 3571.3949 | 4307.4004 | # of circuit miles inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 1; Actuals 3: 8; Actuals 4: 1; Actuals 1: 2; Actuals 2: 6; Actuals 3: 4; Actuals 4: 3; Actuals 1: 1; Actuals 2: 3; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 23 |  |  |  | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors.
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 5; Actuals 2: 105; Actuals 3: 71; Actuals 4: 6; Actuals 1: 11; Actuals 2: 187; Actuals 3: 51; Actuals 4: 15; Actuals 1: 6; Actuals 2: 205; Actuals 3: 143; Actuals 4: 3; Actuals 1: 0; Actuals 2: 32 | 40.882 | 394.4525 | 475.7426 | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 295; Actuals 2: 411; Actuals 3: 405; Actuals 4: 392; Actuals 1: 362; Actuals 2: 399; Actuals 3: 445; Actuals 4: 402; Actuals 1: 376; Actuals 2: 507; Actuals 3: 417; Actuals 4: 309; Actuals 1: 373; Actuals 2: 558 | 1254.6667 | 1254.6667 | 1254.6667 | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 1; Actuals 2: 10; Actuals 3: 18; Actuals 4: 0; Actuals 1: 4; Actuals 2: 16; Actuals 3: 1; Actuals 4: 1; Actuals 1: 1; Actuals 2: 2; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 10 |  |  |  | # of findings from these asset inspections |  | PG&E does not project Patrol Inspection findings.
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 182 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 775; Actuals 2: 14221; Actuals 3: 11507; Actuals 4: 88; Actuals 1: 590; Actuals 2: 7825; Actuals 3: 1091; Actuals 4: 147; Actuals 1: 48; Actuals 2: 1041; Actuals 3: 933; Actuals 4: 2; Actuals 1: 4; Actuals 2: 1133 | 1448.6962 | 13977.8466 | 16858.45 | # of findings from these asset inspections; projections based on WMP and execution of 10% in non-HFTD
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 491; Actuals 2: 1938; Actuals 3: 1476; Actuals 4: 441; Actuals 1: 340; Actuals 2: 3188; Actuals 3: 506; Actuals 4: 349; Actuals 1: 563; Actuals 2: 196; Actuals 3: 271; Actuals 4: 15; Actuals 1: 479; Actuals 2: 855 | 3344 | 3344 | 3344 | # of findings from these asset inspections |  | Blank: Projection data at this granularity is unavailable at this time of submission. PG&E is refining it's back end system for future quarters.
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 4; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 0 |  |  |  | # of findings from these asset inspections |  | PG&E does not project Patrol Inspection findings.
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 7 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 120; Actuals 2: 4149; Actuals 3: 3061; Actuals 4: 30; Actuals 1: 30; Actuals 2: 276; Actuals 3: 38; Actuals 4: 4; Actuals 1: 9; Actuals 2: 22; Actuals 3: 11; Actuals 4: 2; Actuals 1: 2; Actuals 2: 230 | 281.7402 | 2718.3899 | 3278.6052 | # of findings from these asset inspections; projections based on WMP and execution of 10% in non-HFTD
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 38; Actuals 2: 180; Actuals 3: 136; Actuals 4: 82; Actuals 1: 35; Actuals 2: 58; Actuals 3: 40; Actuals 4: 9; Actuals 1: 7; Actuals 2: 4; Actuals 3: 5; Actuals 4: 2; Actuals 1: 31; Actuals 2: 140 | 330 | 330 | 330 | # of findings from these asset inspections |  | Blank: Projection data at this granularity is unavailable at this time of submission. PG&E is refining it's back end system for future quarters.
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 137222; Actuals 2: 185915; Actuals 3: 275676; Actuals 4: 375500; Actuals 1: 137039; Actuals 2: 154168; Actuals 3: 276387; Actuals 4: 367926; Actuals 1: 9366; Actuals 2: 268874 | 950000 | 950000 | 950000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on the average of 2021 and 2022 patrols. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 5851; Actuals 2: 84262; Actuals 3: 193727; Actuals 4: 139870; Actuals 1: 16469; Actuals 2: 135659; Actuals 3: 184726; Actuals 4: 67766; Actuals 1: 692; Actuals 2: 105565 | 314929 | 319691 | 320167 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 4493.59; Actuals 2: 6088.13; Actuals 3: 9027.52; Actuals 4: 12296.44; Actuals 1: 4487.59; Actuals 2: 5048.51; Actuals 3: 9050.8; Actuals 4: 12048.41; Actuals 1: 306.71; Actuals 2: 8804.77 | 36713.3241 | 36713.3241 | 36713.3241 | # of circuit miles inspected by the utility | Projected data is based on the delta change from 2021 to 2022 for 2023 projection. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 191.6; Actuals 2: 2759.31; Actuals 3: 6343.95; Actuals 4: 4580.3; Actuals 1: 539.31; Actuals 2: 4442.4; Actuals 3: 6049.19; Actuals 4: 2219.12; Actuals 1: 22.66; Actuals 2: 3457 | 12170.6215 | 12354.6519 | 12373.0472 | # of circuit miles inspected by the utility | Projected data is based on the delta change from 2021 to 2022 for 2023 projection. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 40; Actuals 2: 30; Actuals 3: 56; Actuals 4: 143; Actuals 1: 34; Actuals 2: 41; Actuals 3: 58; Actuals 4: 68; Actuals 1: 30; Actuals 2: 42; Actuals 3: 85; Actuals 4: 58; Actuals 1: 4; Actuals 2: 99 |  |  |  | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors.
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 1 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 23; Actuals 2: 83; Actuals 3: 285; Actuals 4: 192; Actuals 1: 44; Actuals 2: 227; Actuals 3: 583; Actuals 4: 474; Actuals 1: 96; Actuals 2: 890; Actuals 3: 1175; Actuals 4: 676; Actuals 1: 5; Actuals 2: 1792 | 4343.0968 | 4408.7682 | 4415.3326 | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 2879; Actuals 2: 3851; Actuals 3: 3444; Actuals 4: 3127; Actuals 1: 3075; Actuals 2: 3636; Actuals 3: 3436; Actuals 4: 3287; Actuals 1: 3229; Actuals 2: 3981; Actuals 3: 3704; Actuals 4: 3125; Actuals 1: 2510; Actuals 2: 3975 | 11954.6667 | 11954.6667 | 11954.6667 | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 337; Actuals 2: 215; Actuals 3: 300; Actuals 4: 242; Actuals 1: 62; Actuals 2: 74; Actuals 3: 63; Actuals 4: 78; Actuals 1: 42; Actuals 2: 47; Actuals 3: 59; Actuals 4: 17; Actuals 1: 21; Actuals 2: 111 |  |  |  | # of findings from these asset inspections |  | PG&E does not project Patrol Inspection findings.
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 10 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 2996; Actuals 2: 10385; Actuals 3: 34005; Actuals 4: 9080; Actuals 1: 1999; Actuals 2: 5176; Actuals 3: 5161; Actuals 4: 3380; Actuals 1: 2692; Actuals 2: 3817; Actuals 3: 3681; Actuals 4: 1743; Actuals 1: 221; Actuals 2: 35578 | 101880.6445 | 103421.1683 | 103575.156 | # of findings from these asset inspections; projections based on WMP and execution of 10% in non-HFTD
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 3646; Actuals 2: 2780; Actuals 3: 5541; Actuals 4: 3463; Actuals 1: 1681; Actuals 2: 2460; Actuals 3: 2345; Actuals 4: 2239; Actuals 1: 1308; Actuals 2: 1446; Actuals 3: 1370; Actuals 4: 407; Actuals 1: 5154; Actuals 2: 3335 | 12615.6667 | 12616 | 12616 | # of findings from these asset inspections |  | Blank: Projection data at this granularity is unavailable at this time of submission. PG&E is refining it's back end system for future quarters.
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 1; Actuals 2: 14; Actuals 3: 18; Actuals 4: 5; Actuals 1: 2; Actuals 2: 0; Actuals 3: 2; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 11 |  |  |  | # of findings from these asset inspections |  | PG&E does not project Patrol Inspection findings.
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 724; Actuals 2: 3413; Actuals 3: 14093; Actuals 4: 3510; Actuals 1: 208; Actuals 2: 327; Actuals 3: 706; Actuals 4: 263; Actuals 1: 239; Actuals 2: 281; Actuals 3: 248; Actuals 4: 224; Actuals 1: 45; Actuals 2: 6530 | 19363.3623 | 19656.1532 | 19685.42 | # of findings from these asset inspections; projections based on WMP and execution of 10% in non-HFTD
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Distribution Inspections.
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 263; Actuals 2: 204; Actuals 3: 567; Actuals 4: 138; Actuals 1: 35; Actuals 2: 46; Actuals 3: 51; Actuals 4: 44; Actuals 1: 44; Actuals 2: 26; Actuals 3: 15; Actuals 4: 7; Actuals 1: 561; Actuals 2: 357 | 1338.3333 | 1338 | 1338 | # of findings from these asset inspections |  | Blank: Projection data at this granularity is unavailable at this time of submission. PG&E is refining it's back end system for future quarters.
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 16892; Actuals 2: 19602; Actuals 3: 108; Actuals 4: 0; Actuals 1: 5150; Actuals 2: 22694; Actuals 3: 0; Actuals 4: 0; Actuals 1: 4093; Actuals 2: 22333 | 26000 | 26000 | 26000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on expected 2023 patrols. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 260; Actuals 2: 10820; Actuals 3: 3368; Actuals 4: 57; Actuals 1: 6398; Actuals 2: 19057; Actuals 3: 1512; Actuals 4: 42; Actuals 1: 5642; Actuals 2: 13676 | 20000 | 13000 | 15000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 2115; Actuals 2: 11869; Actuals 3: 117; Actuals 4: 44; Actuals 1: 1457; Actuals 2: 25023; Actuals 3: 307; Actuals 4: 36; Actuals 1: 3104; Actuals 2: 15436 | 19000 | 16000 | 18000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 135636.07; Actuals 2: 157396.3; Actuals 3: 867.2; Actuals 4: 0; Actuals 1: 41352.46; Actuals 2: 182223.83; Actuals 3: 0; Actuals 4: 0; Actuals 1: 32865.17; Actuals 2: 179325 | 1004.7857 | 1004.7857 | 1004.7857 | # of circuit miles inspected by the utility | Projected data is based on expected 2023 patrols. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 2087.7; Actuals 2: 86880.32; Actuals 3: 27043.71; Actuals 4: 457.69; Actuals 1: 51373.41; Actuals 2: 153020.16; Actuals 3: 12140.76; Actuals 4: 337.24; Actuals 1: 45303.03; Actuals 2: 109813 | 772.9121 | 502.3929 | 579.6841 | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 16982.61; Actuals 2: 95303.37; Actuals 3: 939.46; Actuals 4: 353.3; Actuals 1: 11699.13; Actuals 2: 200924.78; Actuals 3: 2465.09; Actuals 4: 289.07; Actuals 1: 24923.89; Actuals 2: 123945 | 734.2665 | 618.3297 | 695.6209 | # of circuit miles inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 1; Actuals 3: 21; Actuals 4: 1; Actuals 1: 28; Actuals 2: 1; Actuals 3: 2; Actuals 4: 7; Actuals 1: 2; Actuals 2: 2; Actuals 3: 5; Actuals 4: 1; Actuals 1: 7; Actuals 2: 1 | 26 | 29 | 27 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 10; Actuals 2: 11; Actuals 3: 24; Actuals 4: 21; Actuals 1: 17; Actuals 2: 5; Actuals 3: 14; Actuals 4: 30; Actuals 1: 4; Actuals 2: 15; Actuals 3: 11; Actuals 4: 5; Actuals 1: 73; Actuals 2: 18 | 54 | 60 | 57 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 8; Actuals 3: 10; Actuals 4: 0; Actuals 1: 13; Actuals 2: 19; Actuals 3: 1; Actuals 4: 0; Actuals 1: 23; Actuals 2: 30 | 25 | 28 | 27 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 3; Actuals 3: 4; Actuals 4: 1; Actuals 1: 0; Actuals 2: 6; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 5; Actuals 3: 2; Actuals 4: 0; Actuals 1: 1; Actuals 2: 10 | 7 | 8 | 7 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 2; Actuals 2: 8; Actuals 3: 20; Actuals 4: 7; Actuals 1: 8; Actuals 2: 19; Actuals 3: 4; Actuals 4: 4; Actuals 1: 3; Actuals 2: 5; Actuals 3: 17; Actuals 4: 4; Actuals 1: 13; Actuals 2: 8 | 33 | 37 | 35 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | Actuals 1: 18; Actuals 2: 38; Actuals 3: 11; Actuals 4: 17; Actuals 1: 45; Actuals 2: 28; Actuals 3: 5; Actuals 4: 86; Actuals 1: 40; Actuals 2: 35; Actuals 3: 0; Actuals 4: 5; Actuals 1: 2; Actuals 2: 16 | 97 | 74 | 78 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 17; Actuals 2: 22; Actuals 3: 38; Actuals 4: 18; Actuals 1: 13; Actuals 2: 69; Actuals 3: 266; Actuals 4: 8; Actuals 1: 21; Actuals 2: 15; Actuals 3: 10; Actuals 4: 17; Actuals 1: 12; Actuals 2: 11 | 157 | 119 | 126 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 1; Actuals 2: 14; Actuals 3: 25; Actuals 4: 16; Actuals 1: 209; Actuals 2: 3469; Actuals 3: 1149; Actuals 4: 44; Actuals 1: 2375; Actuals 2: 6802; Actuals 3: 525; Actuals 4: 27; Actuals 1: 1330; Actuals 2: 3402 | 5802 | 4405 | 4675 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 17; Actuals 2: 290; Actuals 3: 1249; Actuals 4: 119; Actuals 1: 250; Actuals 2: 1905; Actuals 3: 37; Actuals 4: 11; Actuals 1: 369; Actuals 2: 2865; Actuals 3: 64; Actuals 4: 16; Actuals 1: 400; Actuals 2: 2219 | 2266 | 1721 | 1826 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 312; Actuals 2: 1572; Actuals 3: 1585; Actuals 4: 421; Actuals 1: 114; Actuals 2: 308; Actuals 3: 272; Actuals 4: 70; Actuals 1: 113; Actuals 2: 134; Actuals 3: 144; Actuals 4: 107; Actuals 1: 147; Actuals 2: 306 | 496 | 377 | 400 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 2; Actuals 3: 4; Actuals 4: 1; Actuals 1: 3; Actuals 2: 3; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 5 | 4 | 4 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 1; Actuals 2: 4; Actuals 3: 0; Actuals 4: 3; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 3; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 5; Actuals 2: 1 | 4 | 3 | 3 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 15; Actuals 3: 25; Actuals 4: 13; Actuals 1: 94; Actuals 2: 1862; Actuals 3: 539; Actuals 4: 5; Actuals 1: 756; Actuals 2: 2451; Actuals 3: 207; Actuals 4: 5; Actuals 1: 925; Actuals 2: 2294 | 2340 | 1729 | 1854 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 3; Actuals 2: 178; Actuals 3: 681; Actuals 4: 34; Actuals 1: 137; Actuals 2: 612; Actuals 3: 12; Actuals 4: 22; Actuals 1: 87; Actuals 2: 884; Actuals 3: 13; Actuals 4: 3; Actuals 1: 196; Actuals 2: 1180 | 718 | 531 | 569 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 19; Actuals 2: 818; Actuals 3: 1200; Actuals 4: 271; Actuals 1: 14; Actuals 2: 41; Actuals 3: 17; Actuals 4: 6; Actuals 1: 13; Actuals 2: 13; Actuals 3: 10; Actuals 4: 82; Actuals 1: 42; Actuals 2: 122 | 89 | 65 | 70 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 11657; Actuals 2: 12465; Actuals 3: 2816; Actuals 4: 2136; Actuals 1: 3087; Actuals 2: 17578; Actuals 3: 248; Actuals 4: 1457; Actuals 1: 1228; Actuals 2: 12124 | 16000 | 16000 | 16000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on expected 2023 patrols. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 206; Actuals 2: 9538; Actuals 3: 1794; Actuals 4: 29; Actuals 1: 1705; Actuals 2: 9275; Actuals 3: 479; Actuals 4: 6; Actuals 1: 1080; Actuals 2: 3011 | 4000 | 7000 | 4000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 3149; Actuals 2: 8300; Actuals 3: 140; Actuals 4: 0; Actuals 1: 1128; Actuals 2: 10163; Actuals 3: 71; Actuals 4: 2; Actuals 1: 891; Actuals 2: 6184 | 7000 | 4000 | 4000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 93601.09; Actuals 2: 100089.01; Actuals 3: 22611.37; Actuals 4: 17151.23; Actuals 1: 24787.39; Actuals 2: 141144.38; Actuals 3: 1991.34; Actuals 4: 11699.13; Actuals 1: 9860.35; Actuals 2: 97351 | 618.3297 | 618.3297 | 618.3297 | # of circuit miles inspected by the utility | Projected data is based on expected 2023 patrols. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 1654.1; Actuals 2: 76586.36; Actuals 3: 14405.11; Actuals 4: 232.86; Actuals 1: 13690.47; Actuals 2: 74474.58; Actuals 3: 3846.18; Actuals 4: 48.18; Actuals 1: 8671.97; Actuals 2: 24177 | 154.5824 | 270.5192 | 154.5824 | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 25285.22; Actuals 2: 66645.71; Actuals 3: 1124.14; Actuals 4: 0; Actuals 1: 9057.39; Actuals 2: 81604.87; Actuals 3: 570.1; Actuals 4: 16.06; Actuals 1: 7154.38; Actuals 2: 49655 | 270.5192 | 154.5824 | 154.5824 | # of circuit miles inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 132; Actuals 4: 9; Actuals 1: 8; Actuals 2: 1; Actuals 3: 0; Actuals 4: 3; Actuals 1: 3; Actuals 2: 0; Actuals 3: 2; Actuals 4: 0; Actuals 1: 10; Actuals 2: 2 | 4 | 4 | 4 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 17; Actuals 2: 1; Actuals 3: 33; Actuals 4: 11; Actuals 1: 14; Actuals 2: 5; Actuals 3: 14; Actuals 4: 41; Actuals 1: 3; Actuals 2: 2; Actuals 3: 5; Actuals 4: 3; Actuals 1: 43; Actuals 2: 0 | 18 | 18 | 20 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 6; Actuals 3: 7; Actuals 4: 0; Actuals 1: 3; Actuals 2: 8; Actuals 3: 0; Actuals 4: 0; Actuals 1: 5; Actuals 2: 6 | 5 | 5 | 5 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 1; Actuals 3: 3; Actuals 4: 1; Actuals 1: 4; Actuals 2: 4; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 5; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 1 | 3 | 3 | 3 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 5; Actuals 2: 8; Actuals 3: 44; Actuals 4: 1; Actuals 1: 3; Actuals 2: 26; Actuals 3: 4; Actuals 4: 4; Actuals 1: 20; Actuals 2: 1; Actuals 3: 6; Actuals 4: 2; Actuals 1: 5; Actuals 2: 3 | 13 | 13 | 15 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 6; Actuals 3: 15; Actuals 4: 4; Actuals 1: 2; Actuals 2: 5; Actuals 3: 0; Actuals 4: 0; Actuals 1: 6; Actuals 2: 6; Actuals 3: 10; Actuals 4: 0; Actuals 1: 2; Actuals 2: 13 | 6 | 7 | 4 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 3; Actuals 2: 4; Actuals 3: 43; Actuals 4: 7; Actuals 1: 2; Actuals 2: 13; Actuals 3: 4; Actuals 4: 9; Actuals 1: 7; Actuals 2: 4; Actuals 3: 52; Actuals 4: 30; Actuals 1: 5; Actuals 2: 5 | 25 | 28 | 19 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 20; Actuals 3: 13; Actuals 4: 1; Actuals 1: 71; Actuals 2: 2321; Actuals 3: 582; Actuals 4: 20; Actuals 1: 311; Actuals 2: 2191; Actuals 3: 141; Actuals 4: 2; Actuals 1: 151; Actuals 2: 665 | 1195 | 1335 | 897 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 37; Actuals 2: 321; Actuals 3: 657; Actuals 4: 85; Actuals 1: 264; Actuals 2: 922; Actuals 3: 32; Actuals 4: 7; Actuals 1: 171; Actuals 2: 703; Actuals 3: 17; Actuals 4: 7; Actuals 1: 83; Actuals 2: 588 | 470 | 525 | 353 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 73; Actuals 2: 1443; Actuals 3: 864; Actuals 4: 213; Actuals 1: 67; Actuals 2: 148; Actuals 3: 183; Actuals 4: 43; Actuals 1: 40; Actuals 2: 48; Actuals 3: 122; Actuals 4: 71; Actuals 1: 74; Actuals 2: 87 | 149 | 167 | 112 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 2; Actuals 3: 2; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 3 | 0 | 0 | 0 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 1 | 1 | 1 | 1 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 14; Actuals 3: 25; Actuals 4: 4; Actuals 1: 65; Actuals 2: 1288; Actuals 3: 252; Actuals 4: 11; Actuals 1: 121; Actuals 2: 758; Actuals 3: 58; Actuals 4: 3; Actuals 1: 151; Actuals 2: 597 | 426 | 479 | 308 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 13; Actuals 2: 175; Actuals 3: 315; Actuals 4: 31; Actuals 1: 162; Actuals 2: 401; Actuals 3: 16; Actuals 4: 1; Actuals 1: 14; Actuals 2: 234; Actuals 3: 1; Actuals 4: 2; Actuals 1: 56; Actuals 2: 381 | 142 | 160 | 103 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 8; Actuals 2: 932; Actuals 3: 740; Actuals 4: 173; Actuals 1: 4; Actuals 2: 27; Actuals 3: 19; Actuals 4: 6; Actuals 1: 7; Actuals 2: 5; Actuals 3: 16; Actuals 4: 14; Actuals 1: 11; Actuals 2: 57 | 18 | 20 | 13 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 2926; Actuals 2: 19670; Actuals 3: 27029; Actuals 4: 15376; Actuals 1: 21; Actuals 2: 11840; Actuals 3: 20066; Actuals 4: 29065; Actuals 1: 1097; Actuals 2: 26066 | 63000 | 63000 | 63000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on expected 2023 patrols. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 285; Actuals 2: 7411; Actuals 3: 21311; Actuals 4: 11566; Actuals 1: 1633; Actuals 2: 4245; Actuals 3: 11612; Actuals 4: 3058; Actuals 1: 6359; Actuals 2: 2512 | 25000 | 25000 | 22000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | PG&E interprets "Other Inspection Method" as Detailed Ground Inspections. Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 3075; Actuals 2: 25007; Actuals 3: 6720; Actuals 4: 4373; Actuals 1: 1024; Actuals 2: 7307; Actuals 3: 9076; Actuals 4: 3073; Actuals 1: 2046; Actuals 2: 2321 | 20000 | 25000 | 18000 | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 24121.34; Actuals 2: 162155.39; Actuals 3: 222821.46; Actuals 4: 126756.55; Actuals 1: 173.12; Actuals 2: 97606.5; Actuals 3: 165419.93; Actuals 4: 239605.82; Actuals 1: 9043.44; Actuals 2: 214883 | 2434.6731 | 2434.6731 | 2434.6731 | # of circuit miles inspected by the utility | Projected data is based on expected 2023 patrols. 2024 and 2025 projected data stays flat until further data is obtained to update the projected data. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 2349.48; Actuals 2: 61094.74; Actuals 3: 175683.45; Actuals 4: 95347.7; Actuals 1: 13462.11; Actuals 2: 34994.9; Actuals 3: 95726.91; Actuals 4: 25209.52; Actuals 1: 52422.27; Actuals 2: 20708 | 966.1401 | 966.1401 | 850.2033 | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 25349.66; Actuals 2: 206152.51; Actuals 3: 55398.28; Actuals 4: 36050.1; Actuals 1: 8441.64; Actuals 2: 60237.39; Actuals 3: 74820.66; Actuals 4: 25333.17; Actuals 1: 16866.8; Actuals 2: 19134 | 772.9121 | 966.1401 | 695.6209 | # of circuit miles inspected by the utility | Projected data is based on expected inspection cycles. Values are approximate and may change in future. | PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. PG&E is unable to provide historical data prior to 2021 with this level of granularity.
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | [27 empty] | # of circuit miles inspected by the utility |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | Actuals 1: 1; Actuals 2: 3; Actuals 3: 7; Actuals 4: 3; Actuals 1: 20; Actuals 2: 6; Actuals 3: 15; Actuals 4: 7; Actuals 1: 2; Actuals 2: 12; Actuals 3: 2; Actuals 4: 5; Actuals 1: 16; Actuals 2: 6 | 39 | 39 | 36 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 35; Actuals 2: 33; Actuals 3: 56; Actuals 4: 34; Actuals 1: 52; Actuals 2: 62; Actuals 3: 31; Actuals 4: 37; Actuals 1: 33; Actuals 2: 42; Actuals 3: 45; Actuals 4: 22; Actuals 1: 206; Actuals 2: 38 | 186 | 186 | 169 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 2; Actuals 3: 55; Actuals 4: 15; Actuals 1: 4; Actuals 2: 2; Actuals 3: 33; Actuals 4: 5; Actuals 1: 12; Actuals 2: 7 | 70 | 70 | 63 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 1; Actuals 3: 13; Actuals 4: 16; Actuals 1: 2; Actuals 2: 13; Actuals 3: 8; Actuals 4: 1; Actuals 1: 4; Actuals 2: 10; Actuals 3: 14; Actuals 4: 4; Actuals 1: 10; Actuals 2: 8 | 34 | 34 | 31 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 30; Actuals 2: 83; Actuals 3: 73; Actuals 4: 116; Actuals 1: 79; Actuals 2: 68; Actuals 3: 44; Actuals 4: 31; Actuals 1: 16; Actuals 2: 49; Actuals 3: 33; Actuals 4: 31; Actuals 1: 70; Actuals 2: 24 | 203 | 203 | 184 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | Actuals 1: 62; Actuals 2: 178; Actuals 3: 126; Actuals 4: 113; Actuals 1: 53; Actuals 2: 154; Actuals 3: 145; Actuals 4: 63; Actuals 1: 83; Actuals 2: 83; Actuals 3: 45; Actuals 4: 32; Actuals 1: 9; Actuals 2: 34 | 274 | 273 | 230 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 74; Actuals 2: 102; Actuals 3: 98; Actuals 4: 40; Actuals 1: 72; Actuals 2: 69; Actuals 3: 117; Actuals 4: 38; Actuals 1: 49; Actuals 2: 57; Actuals 3: 58; Actuals 4: 49; Actuals 1: 26; Actuals 2: 31 | 221 | 221 | 186 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 4; Actuals 2: 403; Actuals 3: 425; Actuals 4: 1155; Actuals 1: 430; Actuals 2: 2353; Actuals 3: 7275; Actuals 4: 4717; Actuals 1: 868; Actuals 2: 1665; Actuals 3: 5006; Actuals 4: 1553; Actuals 1: 1085; Actuals 2: 466 | 10111 | 10085 | 8488 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 87; Actuals 2: 196; Actuals 3: 4481; Actuals 4: 558; Actuals 1: 529; Actuals 2: 4523; Actuals 3: 1427; Actuals 4: 691; Actuals 1: 614; Actuals 2: 1660; Actuals 3: 1241; Actuals 4: 439; Actuals 1: 383; Actuals 2: 603 | 4853 | 4841 | 4074 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 273; Actuals 2: 3153; Actuals 3: 3129; Actuals 4: 5116; Actuals 1: 343; Actuals 2: 443; Actuals 3: 256; Actuals 4: 294; Actuals 1: 427; Actuals 2: 361; Actuals 3: 460; Actuals 4: 277; Actuals 1: 177; Actuals 2: 261 | 1223 | 1220 | 1027 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | Actuals 1: 4; Actuals 2: 5; Actuals 3: 22; Actuals 4: 19; Actuals 1: 8; Actuals 2: 28; Actuals 3: 12; Actuals 4: 0; Actuals 1: 2; Actuals 2: 3; Actuals 3: 0; Actuals 4: 5; Actuals 1: 15; Actuals 2: 13 | 27 | 27 | 23 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 2; Actuals 2: 5; Actuals 3: 4; Actuals 4: 4; Actuals 1: 0; Actuals 2: 2; Actuals 3: 0; Actuals 4: 156; Actuals 1: 49; Actuals 2: 0; Actuals 3: 0; Actuals 4: 30; Actuals 1: 15; Actuals 2: 1 | 88 | 88 | 75 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 3; Actuals 2: 53; Actuals 3: 58; Actuals 4: 104; Actuals 1: 230; Actuals 2: 1441; Actuals 3: 3552; Actuals 4: 1887; Actuals 1: 306; Actuals 2: 512; Actuals 3: 1437; Actuals 4: 687; Actuals 1: 899; Actuals 2: 284 | 4145 | 4133 | 3516 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 48; Actuals 2: 159; Actuals 3: 2896; Actuals 4: 343; Actuals 1: 254; Actuals 2: 2314; Actuals 3: 600; Actuals 4: 439; Actuals 1: 102; Actuals 2: 462; Actuals 3: 352; Actuals 4: 139; Actuals 1: 178; Actuals 2: 374 | 1929 | 1924 | 1637 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | These metrics are not applicable for the Transmission Inspections.
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 110; Actuals 2: 2030; Actuals 3: 2399; Actuals 4: 3326; Actuals 1: 18; Actuals 2: 67; Actuals 3: 122; Actuals 4: 23; Actuals 1: 33; Actuals 2: 31; Actuals 3: 106; Actuals 4: 71; Actuals 1: 222; Actuals 2: 53 | 211 | 211 | 179 | # of findings from these asset inspections | Projections are approximate and actual finds will be dependent on future find rates that may differ from forecasted rates, the order that different inspection methods occur, the final number of inspections performed, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include findings that were gatekept by CIRT at the time of the data pull at the end of the quarter.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 4; Actuals 2: 15; Actuals 3: 13; Actuals 4: 1; Actuals 1: 20; Actuals 2: 7; Actuals 3: 4; Actuals 4: 4; Actuals 1: 8; Actuals 2: 8; Actuals 3: 7; Actuals 4: 0; Actuals 1: 0; Actuals 2: 27 | 7 | 7 | 7 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 8; Actuals 2: 92; Actuals 3: 51; Actuals 4: 13; Actuals 1: 11; Actuals 2: 204; Actuals 3: 96; Actuals 4: 11; Actuals 1: 32; Actuals 2: 230; Actuals 3: 171; Actuals 4: 14; Actuals 1: 0; Actuals 2: 349 | 96 | 96 | 96 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 543; Actuals 2: 812; Actuals 3: 639; Actuals 4: 611; Actuals 1: 590; Actuals 2: 768; Actuals 3: 848; Actuals 4: 593; Actuals 1: 623; Actuals 2: 783; Actuals 3: 747; Actuals 4: 531; Actuals 1: 413; Actuals 2: 839 | 685 | 685 | 685 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 1: 22; Actuals 2: 21; Actuals 3: 25; Actuals 4: 26; Actuals 1: 40; Actuals 2: 32; Actuals 3: 30; Actuals 4: 9; Actuals 1: 22; Actuals 2: 22; Actuals 3: 12; Actuals 4: 5; Actuals 1: 7; Actuals 2: 18 | 13 | 12 | 10 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 41 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 776; Actuals 2: 1298; Actuals 3: 1971; Actuals 4: 1654; Actuals 1: 1359; Actuals 2: 2496; Actuals 3: 5898; Actuals 4: 686; Actuals 1: 3072; Actuals 2: 3846; Actuals 3: 3219; Actuals 4: 2757; Actuals 1: 2719; Actuals 2: 2888 | 3798 | 4011 | 4223 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 2796; Actuals 2: 3790; Actuals 3: 5093; Actuals 4: 7042; Actuals 1: 5297; Actuals 2: 4313; Actuals 3: 4565; Actuals 4: 744; Actuals 1: 1327; Actuals 2: 1393; Actuals 3: 1074; Actuals 4: 1095; Actuals 1: 2658; Actuals 2: 2844 | 687 | 299 | 300 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | Actuals 4: 1; Actuals 1: 2; Actuals 3: 1; Actuals 4: 1; Actuals 1: 6; Actuals 1: 1; Actuals 2: 0 | 6 | 7 | 7 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data. | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 2 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | Actuals 1: 914; Actuals 2: 293; Actuals 3: 575; Actuals 4: 1096; Actuals 1: 567; Actuals 2: 416; Actuals 3: 369; Actuals 4: 183; Actuals 1: 958; Actuals 2: 649; Actuals 3: 249; Actuals 4: 216; Actuals 1: 510; Actuals 2: 423 | 326 | 293 | 260 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | Actuals 1: 144; Actuals 2: 46; Actuals 3: 411; Actuals 4: 693; Actuals 1: 444; Actuals 2: 390; Actuals 3: 331; Actuals 4: 144; Actuals 1: 229; Actuals 2: 224; Actuals 3: 170; Actuals 4: 124; Actuals 1: 650; Actuals 2: 299 | 195 | 182 | 169 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 1; Actuals 2: 1; Actuals 3: 9; Actuals 4: 1; Actuals 1: 2; Actuals 2: 6; Actuals 3: 4; Actuals 4: 3; Actuals 1: 1; Actuals 2: 3; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 22 | 3 | 3 | 3 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 6; Actuals 2: 104; Actuals 3: 73; Actuals 4: 6; Actuals 1: 9; Actuals 2: 183; Actuals 3: 57; Actuals 4: 19; Actuals 1: 6; Actuals 2: 205; Actuals 3: 152; Actuals 4: 3; Actuals 1: 0; Actuals 2: 31 | 79 | 79 | 79 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 298; Actuals 2: 415; Actuals 3: 399; Actuals 4: 395; Actuals 1: 361; Actuals 2: 395; Actuals 3: 445; Actuals 4: 400; Actuals 1: 375; Actuals 2: 509; Actuals 3: 401; Actuals 4: 319; Actuals 1: 342; Actuals 2: 551 | 401 | 401 | 401 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 17; Actuals 2: 10; Actuals 3: 4; Actuals 4: 7; Actuals 1: 6; Actuals 2: 7; Actuals 3: 6; Actuals 4: 1; Actuals 1: 2; Actuals 3: 1; Actuals 4: 1; Actuals 1: 3; Actuals 2: 3 | 1 | 1 | 1 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 34 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 471; Actuals 2: 385; Actuals 3: 1035; Actuals 4: 792; Actuals 1: 522; Actuals 2: 2360; Actuals 3: 3603; Actuals 4: 763; Actuals 1: 1755; Actuals 2: 2770; Actuals 3: 3055; Actuals 4: 1796; Actuals 1: 2504; Actuals 2: 2745 | 2916 | 3118 | 3319 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 2103; Actuals 2: 1090; Actuals 3: 984; Actuals 4: 1129; Actuals 1: 842; Actuals 2: 1101; Actuals 3: 977; Actuals 4: 299; Actuals 1: 439; Actuals 2: 481; Actuals 3: 378; Actuals 4: 361; Actuals 1: 1653; Actuals 2: 1735 | 69 | 1 | 1 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | Actuals 1: 3; Actuals 2: 1; Actuals 4: 2; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0 | 1 | 1 | 1 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data. | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | Actuals 1: 678; Actuals 2: 151; Actuals 3: 198; Actuals 4: 362; Actuals 1: 215; Actuals 2: 163; Actuals 3: 206; Actuals 4: 114; Actuals 1: 281; Actuals 2: 282; Actuals 3: 135; Actuals 4: 96; Actuals 1: 1105; Actuals 2: 290 | 90 | 66 | 43 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | Actuals 1: 77; Actuals 2: 24; Actuals 3: 83; Actuals 4: 219; Actuals 1: 122; Actuals 2: 102; Actuals 3: 82; Actuals 4: 26; Actuals 1: 89; Actuals 2: 69; Actuals 3: 30; Actuals 4: 36; Actuals 1: 329; Actuals 2: 130 | 47 | 42 | 37 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 40; Actuals 2: 30; Actuals 3: 55; Actuals 4: 145; Actuals 1: 36; Actuals 2: 44; Actuals 3: 56; Actuals 4: 79; Actuals 1: 31; Actuals 2: 42; Actuals 3: 86; Actuals 4: 58; Actuals 1: 4; Actuals 2: 95 | 54 | 54 | 54 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 1 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 24; Actuals 2: 85; Actuals 3: 281; Actuals 4: 203; Actuals 1: 45; Actuals 2: 221; Actuals 3: 582; Actuals 4: 493; Actuals 1: 98; Actuals 2: 905; Actuals 3: 1200; Actuals 4: 689; Actuals 1: 6; Actuals 2: 1738 | 529 | 529 | 529 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 2885; Actuals 2: 3833; Actuals 3: 3449; Actuals 4: 3147; Actuals 1: 3052; Actuals 2: 3617; Actuals 3: 3451; Actuals 4: 3267; Actuals 1: 3226; Actuals 2: 3983; Actuals 3: 3691; Actuals 4: 3133; Actuals 1: 2312; Actuals 2: 3893 | 3428 | 3428 | 3428 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 172; Actuals 2: 139; Actuals 3: 151; Actuals 4: 252; Actuals 1: 155; Actuals 2: 144; Actuals 3: 89; Actuals 4: 96; Actuals 1: 168; Actuals 2: 71; Actuals 3: 55; Actuals 4: 51; Actuals 1: 59; Actuals 2: 53 | 54 | 42 | 31 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 11 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 3118; Actuals 2: 2770; Actuals 3: 3916; Actuals 4: 4764; Actuals 1: 4165; Actuals 2: 4514; Actuals 3: 4392; Actuals 4: 4142; Actuals 1: 5535; Actuals 2: 4358; Actuals 3: 4251; Actuals 4: 3616; Actuals 1: 2443; Actuals 2: 3025 | 4709 | 4799 | 4888 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 1915; Actuals 2: 1131; Actuals 3: 1130; Actuals 4: 1915; Actuals 1: 1471; Actuals 2: 1680; Actuals 3: 1564; Actuals 4: 1486; Actuals 1: 1431; Actuals 2: 1088; Actuals 3: 1150; Actuals 4: 977; Actuals 1: 2984; Actuals 2: 2125 | 1118 | 1072 | 1027 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | Actuals 1: 3; Actuals 2: 2; Actuals 3: 2; Actuals 4: 4; Actuals 1: 11; Actuals 2: 5; Actuals 3: 1; Actuals 1: 3; Actuals 2: 2; Actuals 4: 2; Actuals 1: 4; Actuals 2: 1 | 3 | 2 | 2 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 2 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | Actuals 1: 2483; Actuals 2: 892; Actuals 3: 1313; Actuals 4: 1301; Actuals 1: 2064; Actuals 2: 2258; Actuals 3: 1251; Actuals 4: 1354; Actuals 1: 1519; Actuals 2: 1091; Actuals 3: 473; Actuals 4: 761; Actuals 1: 637; Actuals 2: 379 | 799 | 707 | 615 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Distribution Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | Actuals 1: 247; Actuals 2: 57; Actuals 3: 52; Actuals 4: 37; Actuals 1: 107; Actuals 2: 94; Actuals 3: 52; Actuals 4: 66; Actuals 1: 94; Actuals 2: 86; Actuals 3: 49; Actuals 4: 60; Actuals 1: 1863; Actuals 2: 756 | 43 | 37 | 31 | # of asset inspection findings which have been fixed | Projected Data for 2023 - 2025 is a linear average forecast from previous quarterly data.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 1; Actuals 3: 21; Actuals 4: 1; Actuals 1: 28; Actuals 2: 1; Actuals 3: 2; Actuals 4: 7; Actuals 1: 2; Actuals 2: 2; Actuals 3: 5; Actuals 4: 1; Actuals 1: 7; Actuals 2: 1 | 26 | 29 | 27 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 9; Actuals 2: 10; Actuals 3: 18; Actuals 4: 29; Actuals 1: 17; Actuals 2: 6; Actuals 3: 13; Actuals 4: 20; Actuals 1: 14; Actuals 2: 9; Actuals 3: 17; Actuals 4: 5; Actuals 1: 67; Actuals 2: 13 | 56 | 60 | 57 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 8; Actuals 3: 10; Actuals 4: 0; Actuals 1: 13; Actuals 2: 17; Actuals 3: 3; Actuals 4: 0; Actuals 1: 18; Actuals 2: 30 | 67 | 19 | 18 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 3; Actuals 3: 3; Actuals 4: 1; Actuals 1: 0; Actuals 2: 6; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 5; Actuals 3: 3; Actuals 4: 0; Actuals 1: 1; Actuals 2: 9 | 7 | 8 | 7 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 2; Actuals 2: 8; Actuals 3: 21; Actuals 4: 7; Actuals 1: 8; Actuals 2: 19; Actuals 3: 4; Actuals 4: 3; Actuals 1: 4; Actuals 2: 5; Actuals 3: 17; Actuals 4: 4; Actuals 1: 13; Actuals 2: 5 | 34 | 37 | 35 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | Actuals 1: 34; Actuals 2: 94; Actuals 3: 36; Actuals 4: 19; Actuals 1: 29; Actuals 2: 48; Actuals 3: 28; Actuals 4: 13; Actuals 1: 86; Actuals 2: 66; Actuals 3: 24; Actuals 4: 5; Actuals 1: 5; Actuals 2: 10 | 53 | 94 | 75 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 17; Actuals 2: 36; Actuals 3: 31; Actuals 4: 21; Actuals 1: 19; Actuals 2: 28; Actuals 3: 166; Actuals 4: 150; Actuals 1: 26; Actuals 2: 24; Actuals 3: 22; Actuals 4: 10; Actuals 1: 1; Actuals 2: 15 | 67 | 153 | 120 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 472; Actuals 3: 828; Actuals 4: 262; Actuals 1: 982; Actuals 2: 1867; Actuals 3: 1450; Actuals 4: 415; Actuals 1: 1401; Actuals 2: 2117 | 9644 | 5663 | 4432 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 855; Actuals 2: 1477; Actuals 3: 673; Actuals 4: 306; Actuals 1: 476; Actuals 2: 1200; Actuals 3: 837; Actuals 4: 221; Actuals 1: 462; Actuals 2: 724; Actuals 3: 575; Actuals 4: 207; Actuals 1: 477; Actuals 2: 823 | 3739 | 2211 | 1732 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 2876; Actuals 2: 4537; Actuals 3: 1875; Actuals 4: 1297; Actuals 1: 1491; Actuals 2: 2220; Actuals 3: 1217; Actuals 4: 317; Actuals 1: 616; Actuals 2: 531; Actuals 3: 333; Actuals 4: 134; Actuals 1: 84; Actuals 2: 177 | 752 | 484 | 379 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 7; Actuals 3: 3; Actuals 4: 1; Actuals 1: 3; Actuals 2: 6; Actuals 3: 3; Actuals 4: 1; Actuals 1: 1; Actuals 2: 2; Actuals 3: 0; Actuals 4: 0; Actuals 1: 2; Actuals 2: 2 | 3 | 1 | 1 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 1; Actuals 4: 2; Actuals 1: 4; Actuals 2: 2; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0 | 2 | 1 | 1 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 77; Actuals 3: 240; Actuals 4: 152; Actuals 1: 489; Actuals 2: 716; Actuals 3: 399; Actuals 4: 186; Actuals 1: 700; Actuals 2: 582 | 557 | 585 | 509 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | Actuals 1: 39; Actuals 2: 73; Actuals 3: 93; Actuals 4: 28; Actuals 1: 216; Actuals 2: 208; Actuals 3: 279; Actuals 4: 56; Actuals 1: 215; Actuals 2: 369; Actuals 3: 217; Actuals 4: 83; Actuals 1: 153; Actuals 2: 282 | 190 | 180 | 156 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals 1: 337; Actuals 2: 467; Actuals 3: 239; Actuals 4: 228; Actuals 1: 713; Actuals 2: 491; Actuals 3: 368; Actuals 4: 146; Actuals 1: 255; Actuals 2: 461; Actuals 3: 152; Actuals 4: 32; Actuals 1: 353; Actuals 2: 260 | 100 | 22 | 19 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | Actuals 1: 1; Actuals 2: 0; Actuals 3: 132; Actuals 4: 9; Actuals 1: 8; Actuals 2: 1; Actuals 3: 0; Actuals 4: 3; Actuals 1: 3; Actuals 2: 0; Actuals 3: 1; Actuals 4: 1; Actuals 1: 9; Actuals 2: 1 | 4 | 4 | 4 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 9; Actuals 2: 9; Actuals 3: 26; Actuals 4: 18; Actuals 1: 12; Actuals 2: 7; Actuals 3: 14; Actuals 4: 13; Actuals 1: 31; Actuals 2: 2; Actuals 3: 4; Actuals 4: 4; Actuals 1: 39; Actuals 2: 0 | 19 | 18 | 20 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 6; Actuals 3: 7; Actuals 4: 0; Actuals 1: 3; Actuals 2: 8; Actuals 3: 0; Actuals 4: 0; Actuals 1: 5; Actuals 2: 5 | 5 | 5 | 5 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 0; Actuals 2: 1; Actuals 3: 3; Actuals 4: 1; Actuals 1: 3; Actuals 2: 5; Actuals 3: 1; Actuals 4: 0; Actuals 1: 0; Actuals 2: 4; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1 | 4 | 3 | 3 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 4; Actuals 2: 9; Actuals 3: 40; Actuals 4: 5; Actuals 1: 3; Actuals 2: 27; Actuals 3: 4; Actuals 4: 2; Actuals 1: 22; Actuals 2: 1; Actuals 3: 6; Actuals 4: 2; Actuals 1: 4; Actuals 2: 3 | 13 | 13 | 15 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | Actuals 1: 22; Actuals 2: 22; Actuals 3: 26; Actuals 4: 3; Actuals 1: 7; Actuals 2: 9; Actuals 3: 11; Actuals 4: 0; Actuals 1: 6; Actuals 2: 4; Actuals 3: 2; Actuals 4: 9; Actuals 1: 2; Actuals 2: 2 | 13 | 7 | 4 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 3; Actuals 2: 4; Actuals 3: 10; Actuals 4: 41; Actuals 1: 1; Actuals 2: 9; Actuals 3: 4; Actuals 4: 12; Actuals 1: 6; Actuals 2: 7; Actuals 3: 3; Actuals 4: 77; Actuals 1: 2; Actuals 2: 1 | 43 | 29 | 19 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 188; Actuals 3: 591; Actuals 4: 204; Actuals 1: 400; Actuals 2: 1081; Actuals 3: 583; Actuals 4: 275; Actuals 1: 312; Actuals 2: 711 | 3794 | 1335 | 897 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 182; Actuals 2: 402; Actuals 3: 155; Actuals 4: 133; Actuals 1: 364; Actuals 2: 528; Actuals 3: 417; Actuals 4: 126; Actuals 1: 245; Actuals 2: 386; Actuals 3: 195; Actuals 4: 87; Actuals 1: 95; Actuals 2: 419 | 1468 | 525 | 353 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 570; Actuals 2: 1318; Actuals 3: 469; Actuals 4: 364; Actuals 1: 782; Actuals 2: 921; Actuals 3: 571; Actuals 4: 156; Actuals 1: 209; Actuals 2: 205; Actuals 3: 59; Actuals 4: 116; Actuals 1: 25; Actuals 2: 72 | 415 | 167 | 112 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 1; Actuals 2: 3; Actuals 3: 1; Actuals 4: 1; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 1 | 0 | 0 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals 1: 6; Actuals 2: 2; Actuals 3: 1; Actuals 4: 1; Actuals 1: 3; Actuals 2: 0; Actuals 3: 0; Actuals 4: 1; Actuals 1: 1; Actuals 2: 1; Actuals 3: 0; Actuals 4: 1; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 115; Actuals 3: 229; Actuals 4: 146; Actuals 1: 262; Actuals 2: 450; Actuals 3: 206; Actuals 4: 86; Actuals 1: 216; Actuals 2: 202 | 150 | 107 | 113 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | Actuals 1: 12; Actuals 2: 24; Actuals 3: 11; Actuals 4: 21; Actuals 1: 179; Actuals 2: 169; Actuals 3: 172; Actuals 4: 34; Actuals 1: 173; Actuals 2: 161; Actuals 3: 97; Actuals 4: 47; Actuals 1: 31; Actuals 2: 78 | 44 | 36 | 38 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals 1: 124; Actuals 2: 190; Actuals 3: 67; Actuals 4: 197; Actuals 1: 446; Actuals 2: 466; Actuals 3: 241; Actuals 4: 102; Actuals 1: 169; Actuals 2: 229; Actuals 3: 54; Actuals 4: 15; Actuals 1: 126; Actuals 2: 45 | 69 | 5 | 5 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | Actuals 1: 1; Actuals 2: 3; Actuals 3: 7; Actuals 4: 3; Actuals 1: 19; Actuals 2: 6; Actuals 3: 15; Actuals 4: 8; Actuals 1: 2; Actuals 2: 12; Actuals 3: 2; Actuals 4: 5; Actuals 1: 10; Actuals 2: 9 | 39 | 39 | 36 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 36; Actuals 2: 34; Actuals 3: 57; Actuals 4: 36; Actuals 1: 52; Actuals 2: 59; Actuals 3: 34; Actuals 4: 37; Actuals 1: 33; Actuals 2: 42; Actuals 3: 45; Actuals 4: 20; Actuals 1: 181; Actuals 2: 23 | 188 | 186 | 169 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 2; Actuals 3: 52; Actuals 4: 17; Actuals 1: 5; Actuals 2: 1; Actuals 3: 34; Actuals 4: 5; Actuals 1: 8; Actuals 2: 6 | 70 | 70 | 63 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 1; Actuals 2: 1; Actuals 3: 11; Actuals 4: 17; Actuals 1: 2; Actuals 2: 14; Actuals 3: 8; Actuals 4: 1; Actuals 1: 3; Actuals 2: 10; Actuals 3: 9; Actuals 4: 10; Actuals 1: 9; Actuals 2: 6 | 34 | 34 | 31 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 30; Actuals 2: 80; Actuals 3: 76; Actuals 4: 116; Actuals 1: 79; Actuals 2: 67; Actuals 3: 45; Actuals 4: 33; Actuals 1: 17; Actuals 2: 49; Actuals 3: 31; Actuals 4: 33; Actuals 1: 65; Actuals 2: 20 | 204 | 203 | 184 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | Actuals 1: 102; Actuals 2: 93; Actuals 3: 104; Actuals 4: 66; Actuals 1: 66; Actuals 2: 85; Actuals 3: 72; Actuals 4: 69; Actuals 1: 130; Actuals 2: 93; Actuals 3: 114; Actuals 4: 73; Actuals 1: 32; Actuals 2: 27 | 92 | 92 | 92 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 111; Actuals 2: 109; Actuals 3: 73; Actuals 4: 65; Actuals 1: 55; Actuals 2: 95; Actuals 3: 86; Actuals 4: 78; Actuals 1: 104; Actuals 2: 59; Actuals 3: 150; Actuals 4: 93; Actuals 1: 18; Actuals 2: 19 | 37 | 37 | 37 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 3; Actuals 2: 216; Actuals 3: 983; Actuals 4: 1805; Actuals 1: 1616; Actuals 2: 1063; Actuals 3: 1069; Actuals 4: 1009; Actuals 1: 1357; Actuals 2: 587 | 1751 | 1751 | 1751 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 425; Actuals 2: 325; Actuals 3: 430; Actuals 4: 557; Actuals 1: 582; Actuals 2: 929; Actuals 3: 669; Actuals 4: 680; Actuals 1: 1305; Actuals 2: 1114; Actuals 3: 770; Actuals 4: 933; Actuals 1: 730; Actuals 2: 375 | 1156 | 1156 | 1156 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 773; Actuals 2: 1070; Actuals 3: 1547; Actuals 4: 1896; Actuals 1: 1197; Actuals 2: 1128; Actuals 3: 650; Actuals 4: 642; Actuals 1: 1314; Actuals 2: 611; Actuals 3: 598; Actuals 4: 631; Actuals 1: 384; Actuals 2: 257 | 1241 | 1241 | 1241 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | Actuals 1: 8; Actuals 2: 7; Actuals 3: 3; Actuals 4: 4; Actuals 1: 8; Actuals 2: 22; Actuals 3: 8; Actuals 4: 10; Actuals 1: 13; Actuals 2: 4; Actuals 3: 9; Actuals 4: 3; Actuals 1: 6; Actuals 2: 2 | 2 | 2 | 2 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | Actuals 1: 4; Actuals 2: 12; Actuals 3: 2; Actuals 4: 1; Actuals 1: 31; Actuals 2: 5; Actuals 3: 5; Actuals 4: 10; Actuals 1: 6; Actuals 2: 5; Actuals 3: 3; Actuals 4: 9; Actuals 1: 1; Actuals 2: 13 | 0 | 0 | 0 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 47; Actuals 3: 308; Actuals 4: 463; Actuals 1: 494; Actuals 2: 240; Actuals 3: 262; Actuals 4: 236; Actuals 1: 242; Actuals 2: 213 | 55 | 55 | 55 | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | Actuals 1: 91; Actuals 2: 85; Actuals 3: 66; Actuals 4: 78; Actuals 1: 320; Actuals 2: 571; Actuals 3: 738; Actuals 4: 928; Actuals 1: 500; Actuals 2: 305; Actuals 3: 539; Actuals 4: 353; Actuals 1: 182; Actuals 2: 123 | 125 | 125 | 125 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed | Projections are approximate and actual fixes will be dependent on actual future find rates, in-year timing of finds, and other factors. 2024 and 2025 projection is based on 2023 projected data. Data reported for 2022 Q4 and 2023 Q1 only include fixes that were formally closed in SAP by the end of the quarter; repairs awaiting work verification before formal SAP closure are not included. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections. | bar: Actuals 1 to Actuals 4
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals 1: 131; Actuals 2: 172; Actuals 3: 217; Actuals 4: 301; Actuals 1: 750; Actuals 2: 1047; Actuals 3: 711; Actuals 4: 666; Actuals 1: 514; Actuals 2: 263; Actuals 3: 371; Actuals 4: 270; Actuals 1: 158; Actuals 2: 124 | 229 | 229 | 229 | # of asset inspection findings which have been fixed |  | These metrics are not applicable for the Transmission Inspections.
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR | Actuals 1: 0; Actuals 2: 15; Actuals 3: 1447; Actuals 4: 5640; Actuals 1: 5915; Actuals 2: 1885; Actuals 3: 11415; Actuals 4: 318; Actuals 1: 375; Actuals 2: 76; Actuals 3: 662; Actuals 4: 368; Actuals 1: 544; Actuals 2: 1 | 483 | 0 | 0 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Projections account for there being no current workplan for Distribution GBL.
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | Actuals 1: 108355.2; Actuals 2: 115107.1; Actuals 3: 115520.2; Actuals 4: 113590.7; Actuals 1: 124315.4; Actuals 2: 139632.9; Actuals 3: 149972.2; Actuals 4: 113717.9; Actuals 1: 113349; Actuals 2: 97039.2; Actuals 3: 100979.9; Actuals 4: 40445; Actuals 1: 99782.9; Actuals 2: 123561 | 409746 | 435440 | 435440 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial | Actuals 1: 320; Actuals 2: 652; Actuals 3: 527; Actuals 4: 394; Actuals 1: 153; Actuals 2: 392; Actuals 3: 884; Actuals 4: 1093; Actuals 1: 610; Actuals 2: 1196; Actuals 3: 1096; Actuals 4: 711; Actuals 1: 243; Actuals 2: 1141 | 3033 | 2765 | 2765 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other | Actuals 1: 2038; Actuals 2: 2086; Actuals 3: 2143; Actuals 4: 3142; Actuals 1: 4109.5; Actuals 2: 2883; Actuals 3: 3462; Actuals 4: 7373; Actuals 1: 9164; Actuals 2: 4434; Actuals 3: 6072; Actuals 4: 4222; Actuals 1: 4912.5; Actuals 2: 10185 | 21611 | 18185 | 18185 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other | Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 4; Actuals 4: 11; Actuals 1: 0; Actuals 2: 0 | 5 | 5 | 5 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR | Actuals 1: 0; Actuals 2: 0; Actuals 3: 70; Actuals 4: 212; Actuals 1: 86; Actuals 2: 38; Actuals 3: 367; Actuals 4: 17; Actuals 1: 172; Actuals 2: 22; Actuals 3: 129; Actuals 4: 112; Actuals 1: 20; Actuals 2: 0 | 0 | 0 | 0 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Projections account for there being no current workplan for Distribution GBL.
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | Actuals 1: 3051.3; Actuals 2: 5567.1; Actuals 3: 8298.5; Actuals 4: 5173.9; Actuals 1: 3147.6; Actuals 2: 4539.2; Actuals 3: 5466.4; Actuals 4: 3369.3; Actuals 1: 3079.2; Actuals 2: 3668.6; Actuals 3: 5186; Actuals 4: 2942; Actuals 1: 2416; Actuals 2: 6267 | 17830 | 17830 | 17830 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 4
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 4
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR | Actuals 1: 0; Actuals 2: 17; Actuals 3: 316; Actuals 4: 3647; Actuals 1: 6218; Actuals 2: 1737; Actuals 3: 8742; Actuals 4: 18; Actuals 1: 1137; Actuals 2: 819; Actuals 3: 129; Actuals 4: 277; Actuals 1: 534; Actuals 2: 4 | 505 | 0 | 0 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Projections account for there being no current workplan for Distribution GBL.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | Actuals 1: 75985.2; Actuals 2: 92297.7; Actuals 3: 58513; Actuals 4: 52568.2; Actuals 1: 80105.6; Actuals 2: 92444.8; Actuals 3: 92712.2; Actuals 4: 42964.8; Actuals 1: 74489.4; Actuals 2: 90259.7; Actuals 3: 67837.2; Actuals 4: 26668.6; Actuals 1: 49428.2; Actuals 2: 106712 | 285188 | 283000 | 283000 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial | Actuals 1: 30; Actuals 2: 44; Actuals 3: 150; Actuals 4: 518; Actuals 1: 80; Actuals 2: 108; Actuals 3: 59; Actuals 4: 214; Actuals 1: 136; Actuals 2: 264; Actuals 3: 214; Actuals 4: 314; Actuals 1: 96; Actuals 2: 3 | 772 | 725 | 725 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other | Actuals 1: 2208; Actuals 2: 2039; Actuals 3: 2174.5; Actuals 4: 4884; Actuals 1: 5509; Actuals 2: 2358; Actuals 3: 3057; Actuals 4: 10013.6; Actuals 1: 8682; Actuals 2: 5195; Actuals 3: 7327.1; Actuals 4: 10562; Actuals 1: 5236; Actuals 2: 6523 | 27200 | 22802 | 22802 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other | Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 4; Actuals 1: 1; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 2 | 2 | 2 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR | Actuals 1: 0; Actuals 2: 0; Actuals 3: 5; Actuals 4: 172; Actuals 1: 147; Actuals 2: 17; Actuals 3: 484; Actuals 4: 6; Actuals 1: 220; Actuals 2: 128; Actuals 3: 56; Actuals 4: 73; Actuals 1: 26; Actuals 2: 0 | 0 | 0 | 0 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Projections account for there being no current workplan for Distribution GBL.
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | Actuals 1: 2567.7; Actuals 2: 5441.1; Actuals 3: 4440.1; Actuals 4: 3065.2; Actuals 1: 3050.7; Actuals 2: 2954.6; Actuals 3: 4199; Actuals 4: 1900.3; Actuals 1: 2391.3; Actuals 2: 3422.1; Actuals 3: 4585; Actuals 4: 2121; Actuals 1: 2194; Actuals 2: 6481 | 13380 | 13380 | 13380 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR | Actuals 1: 0; Actuals 2: 0; Actuals 3: 203; Actuals 4: 727; Actuals 1: 812; Actuals 2: 228; Actuals 3: 1298; Actuals 4: 63; Actuals 1: 105; Actuals 2: 48; Actuals 3: 52; Actuals 4: 115; Actuals 1: 43; Actuals 2: 0 | 35 | 0 | 0 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Projections account for there being no current workplan for Distribution GBL.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | other | Actuals 1: 157922.4; Actuals 2: 114811.3; Actuals 3: 121758.3; Actuals 4: 250172.9; Actuals 1: 159427.2; Actuals 2: 145056; Actuals 3: 221121.4; Actuals 4: 258497.3; Actuals 1: 145041.1; Actuals 2: 116971.7; Actuals 3: 189518.6; Actuals 4: 143057.2; Actuals 1: 200448.7; Actuals 2: 181861 | 717468 | 685206 | 685206 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial | Actuals 1: 32; Actuals 2: 106; Actuals 3: 62; Actuals 4: 49; Actuals 1: 24; Actuals 2: 169; Actuals 3: 215; Actuals 4: 261; Actuals 1: 144; Actuals 2: 304; Actuals 3: 221; Actuals 4: 231; Actuals 1: 177; Actuals 2: 458 | 766 | 708 | 708 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other | Actuals 1: 939; Actuals 2: 837; Actuals 3: 710.5; Actuals 4: 836; Actuals 1: 1376; Actuals 2: 1226; Actuals 3: 1191; Actuals 4: 1995; Actuals 1: 2325; Actuals 2: 2147; Actuals 3: 2029; Actuals 4: 1335; Actuals 1: 2297; Actuals 2: 8302 | 7118 | 6015 | 6015 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other | Actuals 1: 0; Actuals 2: 21; Actuals 3: 3; Actuals 4: 2; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 1; Actuals 3: 0; Actuals 4: 0; Actuals 1: 0; Actuals 2: 0 | 9 | 9 | 9 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR | Actuals 1: 0; Actuals 2: 0; Actuals 3: 10; Actuals 4: 23; Actuals 1: 19; Actuals 2: 3; Actuals 3: 49; Actuals 4: 2; Actuals 1: 36; Actuals 2: 5; Actuals 3: 15; Actuals 4: 37; Actuals 1: 0; Actuals 2: 0 | 0 | 0 | 0 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Projections account for there being no current workplan for Distribution GBL.
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | other | Actuals 1: 5767; Actuals 2: 6432.6; Actuals 3: 11786.7; Actuals 4: 16467.3; Actuals 1: 6383.1; Actuals 2: 6054.1; Actuals 3: 11225.5; Actuals 4: 8871.2; Actuals 1: 4261.2; Actuals 2: 4519; Actuals 3: 11697; Actuals 4: 6936; Actuals 1: 6605; Actuals 2: 8964 | 33465 | 33465 | 33465 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR | Actuals 1: 5849910; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 5839506; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 5933330; Actuals 2: 0; Actuals 3: 0; Actuals 4: 0; Actuals 1: 5847518; Actuals 2: 0 | >5,500,000 | >5,500,000 | >5,500,000 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | The count provided in the Q1 slot for each calendar year is the total count based on the Project Year.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | Actuals 1: 6077; Actuals 2: 12013; Actuals 3: 16842; Actuals 4: 3707; Actuals 1: 6433; Actuals 2: 16799; Actuals 3: 7166; Actuals 4: 3287; Actuals 1: 6703; Actuals 2: 10376; Actuals 3: 6623; Actuals 4: 131; Actuals 1: 6457; Actuals 2: 8386 | See Comments | See Comments | See Comments | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | We are unable to pull forecasted numbers by HFTD tier. We've have placed all forecasted units in Non-HFTD
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR | Actuals 1: 103; Actuals 1: 34; Actuals 1: 9; Actuals 1: 1; Actuals 2: 0 | 5 | 3 | 2 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | The count provided in the Q1 slot for each calendar year is the total count based on the Project Year.
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | Actuals 1: 52; Actuals 1: 11; Actuals 1: 4; Actuals 1: 0; Actuals 2: 0 | 3 | 2 | 1 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR | Actuals 1: 2440491; Actuals 1: 2407120; Actuals 1: 2398660; Actuals 1: 2356383; Actuals 2: 0 | >2,100,000 | >2,100,000 | >2,100,000 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | The count provided in the Q1 slot for each calendar year is the total count based on the Project Year.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | Actuals 1: 4149; Actuals 2: 6397; Actuals 3: 6041; Actuals 4: 1095; Actuals 1: 3124; Actuals 2: 9981; Actuals 3: 6195; Actuals 4: 2381; Actuals 1: 4179; Actuals 2: 5498; Actuals 3: 2108; Actuals 4: 136; Actuals 1: 3871; Actuals 2: 6424 | See Comments | See Comments | See Comments | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | We are unable to pull forecasted numbers by HFTD tier. We've have placed all forecasted units in NonHFTD. Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR | Actuals 1: 106; Actuals 1: 20; Actuals 1: 5; Actuals 1: 46; Actuals 2: 0 | 47 | 25 | 10 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | The count provided in the Q1 slot for each calendar year is the total count based on the Project Year.
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | Actuals 1: 25; Actuals 1: 8; Actuals 1: 3; Actuals 1: 2; Actuals 2: 0 | 3 | 2 | 1 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR | Actuals 1: 11502631; Actuals 1: 12015596; Actuals 1: 12014276; Actuals 1: 11828973; Actuals 2: 0 | >11,000,000 | >11,000,000 | >11,000,000 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | The count provided in the Q1 slot for each calendar year is the total count based on the Project Year.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | other | Actuals 1: 9676; Actuals 2: 12072; Actuals 3: 14975; Actuals 4: 3150; Actuals 1: 10332; Actuals 2: 15410; Actuals 3: 10379; Actuals 4: 6167; Actuals 1: 9943; Actuals 2: 11571; Actuals 3: 6932; Actuals 4: 938; Actuals 1: 8176; Actuals 2: 11206 | 64550 | 64550 | 64550 | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | These are forecasted numbers for all HFTD tiers. We are unable to pull forecasted data by HFTD tier. Inspection Method "Other" includes ground patrols.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A: PG&E does not perform this inspection type by this inspection method | bar: Actuals 1 to Actuals 4
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR | Actuals 1: 373; Actuals 1: 275; Actuals 1: 190; Actuals 1: 89; Actuals 2: 0 | 90 | 60 | 30 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | The count provided in the Q1 slot for each calendar year is the total count based on the Project Year.
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | other | Actuals 1: 133; Actuals 1: 68; Actuals 1: 26; Actuals 1: 21; Actuals 2: 0 | 22 | 15 | 10 | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. | Inspection Method "Other" includes ground patrols.
| 17. Community outreach metrics | 17.a. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | N/A | N/A | N/A | N/A | N/A | N/A | [27 empty] | Percentage of customers notified of evacuation |  | PG&E does not issue wildfire evacuation notices to customers and does not maintain metrics on the number of customers in an evacuation zone or the number of customers notified of evacuation orders. Because of this, PG&E is unable to report on evacuation related requirements in this table. PG&E anticipates this to be a recurring challenge going forward.

## Table 3
Utility | PG&E
Table No. | 3
Date Modified | 2023-08-01
[5 empty] | Actual | [7 empty] | Note: These columns are placeholders for future QR submissions. | [7 empty] | Projected
Table 3: List and description of additional metrics |  |  |  |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
Customer Hours of PSPS per RFW OH Circuit Mile Day |  |  |  |  | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0 | 25.1 | 24.8 | 24.5

## Table 4
Utility | PG&E
Table No. | 4
Date Modified | 2023-08-01
Note: These columns are placeholders for future QR submissions.
Table 4: Weather patterns |  |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Metric name | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | Unit(s) | Comments | Blank Meaning
1. Red flag warning only overhead circuit mile days | 1.a. | Red Flag Warning Only overhead circuit mile days - HFTD tier 2 | 1: 0; 2: 38182.28; 3: 2774.88; 4: 0; 1: 0; 2: 0 | Sum of overhead circuit miles of utility grid subject to red flag warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW multiplied by the number of days those circuit miles were under said RFW. For example, if 100 overhead circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW OH circuit mile days would be 110.
| 1.b. | Red Flag Warning Only overhead circuit mile days - HFTD tier 3 | 1: 0; 2: 8339.14; 3: 749.27; 4: 0; 1: 0; 2: 0 | Red flag warning overhead circuit mile days, see above for definition
| 1.c. | Red Flag Warning Only overhead circuit mile days - non-HFTD | 1: 0; 2: 65952.69; 3: 199.87; 4: 0; 1: 0; 2: 0 | Red flag warning overhead circuit mile days, see above for definition
2. Wind condition overhead circuit mile days | 2.a. | High Wind Warning Only overhead circuit mile days - HFTD tier 2 | 1: 0; 2: 289.03; 3: 0; 4: 1430.19; 1: 32399.88; 2: 150.37 | Sum of overhead circuit miles of utility grid subject to high wind warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of overhead circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 overhead circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW OH circuit mile days would be 110.
| 2.b. | High Wind Warning Only overhead circuit mile days - HFTD tier 3 | 1: 0; 2: 337.23; 3: 0; 4: 752.14; 1: 12457.96; 2: 0 | High wind warning overhead circuit mile days, see above for definition
| 2.c. | High Wind Warning Only overhead circuit mile days - non-HFTD | 1: 0; 2: 2.22; 3: 0; 4: 423.82; 1: 92965.76; 2: 138.38 | High wind warning overhead circuit mile days, see above for definition
3. Wind condition and Red flag warning overhead circuit mile days | 3.a. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 2 | 1: 0; 2: 38471.31; 3: 2774.88; 4: 1430.19; 1: 32399.88; 2: 150.37 | Sum of overhead circuit miles of utility grid subject to concurrent red flag warning and a high wind warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW and HWW multiplied by the number of days those circuit miles were under said RFW and HWW. For example, if 100 overhead circuit miles were under an RFW and HWW for 1 day, and 10 of those miles were under RFW and HWW for an additional day, then the total RFW and HWW OH circuit mile days would be 110.
| 3.b. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 3 | 1: 0; 2: 8676.37; 3: 749.27; 4: 752.14; 1: 12457.96; 2: 0 | High wind warning and red flag warning overhead circuit mile days, see above for definition
| 3.c. | High Wind Warning and Red Flag Warning overhead circuit mile days - non-HFTD | 1: 0; 2: 65954.91; 3: 199.87; 4: 423.82; 1: 92965.76; 2: 138.38 | High wind warning and red flag warning overhead circuit mile days, see above for definition
4. Fire potential index overhead circuit mile days | 4.a. | Fire potential index circuit mile days - HFTD tier 2 | 1: 3859.7; 2: 503899; 3: 1333407.9; 4: 395757; 1: 0; 2: 137233.9 | Sum of overhead circuit miles of utility grid subject to high fire potential index (FPI, as defined by the utility in its WMP) each day within a given time period, calculated as the number of overhead circuit miles that were under a high FPI multiplied by the number of days those miles were under said FPI. For example, if 100 overhead circuit miles were under a high FPI for 1 day, and 10 of those miles were under a high FPI for an additional day, then the total FPI OH circuit mile days would be 110.
| 4.b. | Fire potential index circuit mile days - HFTD tier 3 | 1: 1181.6; 2: 161044; 3: 482998; 4: 135880; 1: 0; 2: 37232.67 | Fire potential index overhead circuit mile days, see above for definition
| 4.c. | Fire potential index circuit mile days - non-HFTD | 1: 555.8; 2: 99862.5; 3: 282488.4; 4: 76714.6; 1: 0; 2: 28428.16 | Fire potential index overhead circuit mile days, see above for definition
5. Other | 5.a. | Other relevant weather pattern metrics tracked (add additional rows as needed)
Comments for Table 4: Table 4 shows the trends of National Weather Service (NWS) issued Red Flag Warnings (RFWs) and High Wind Warnings (HWWs) over the past year impacting PG&E circuits across the territory through the metrics RFW Circuit Mile Days and HWW Circuit Mile Days. NWS RFWs are a proxy for high fire danger conditions, while HWWs are issued for solely high wind threats, regardless of humidity values and fire danger. These values have changed from previous reports, which calculated RFW Day Circuit miles based on Fire Index Areas. For these metrics, circuit miles are now calculated by the NWS RFW and HWW polygons to give a more accurate and precise values for RFW Circuit Mile Days and HWW Circuit Mile Days.

## Table 5
| Utility | PG&E | Notes:
| Table No. | 5 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2023-08-01 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
[8 empty] | Actual number of risk events | [15 empty] | Projected risk events
| Table 5: Risk event drivers | [6 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
x | Risk event category | Metric type | # | Risk event driver | Line Type | HFTD Tier | Are risk events tracked for ignition driver? (yes / no) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
| Wire down event | 1. Fire | 1.a.d.0 | Fire | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 10; Actual number of risk events Q2: 19; Actual number of risk events Q3: 14; Actual number of risk events Q4: 21; Actual number of risk events Q1: 7; Actual number of risk events Q2: 1 | 66 | 66 | 66 | # risk events (excluding ignitions)
| Wire down event | 1. Fire | 1.a.d.2 | Fire | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Wire down event | 1. Fire | 1.a.d.3 | Fire | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 1. Fire | 1.a.t.0 | Fire | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 1. Fire | 1.a.t.2 | Fire | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 1. Fire | 1.a.t.3 | Fire | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 21; Actual number of risk events Q2: 18; Actual number of risk events Q3: 22; Actual number of risk events Q4: 21; Actual number of risk events Q1: 22; Actual number of risk events Q2: 18 | 91 | 91 | 91 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0 | 9 | 9 | 9 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 16; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3; Actual number of risk events Q1: 6; Actual number of risk events Q2: 6 | 39 | 39 | 39 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 117; Actual number of risk events Q2: 129; Actual number of risk events Q3: 151; Actual number of risk events Q4: 149; Actual number of risk events Q1: 158; Actual number of risk events Q2: 118 | 554 | 554 | 554 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 5; Actual number of risk events Q3: 5; Actual number of risk events Q4: 5; Actual number of risk events Q1: 3; Actual number of risk events Q2: 9 | 36 | 36 | 36 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2; Actual number of risk events Q1: 4; Actual number of risk events Q2: 7 | 16 | 16 | 16 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 5; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 6 | 6 | 6 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 4; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2; Actual number of risk events Q1: 4; Actual number of risk events Q2: 1 | 11 | 11 | 11 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 22; Actual number of risk events Q2: 21; Actual number of risk events Q3: 18; Actual number of risk events Q4: 22; Actual number of risk events Q1: 158; Actual number of risk events Q2: 6 | 65 | 65 | 65 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 3; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3; Actual number of risk events Q1: 8; Actual number of risk events Q2: 3 | 11 | 11 | 11 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0; Actual number of risk events Q1: 6; Actual number of risk events Q2: 0 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 8; Actual number of risk events Q3: 7; Actual number of risk events Q4: 2; Actual number of risk events Q1: 109; Actual number of risk events Q2: 2 | 17 | 17 | 17 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 12; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 6; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 22; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | Non-HFTD | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 140; Actual number of risk events Q2: 166; Actual number of risk events Q3: 118; Actual number of risk events Q4: 430; Actual number of risk events Q1: 3332; Actual number of risk events Q2: 54 | 1205 | 1205 | 1205 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 35; Actual number of risk events Q2: 49; Actual number of risk events Q3: 30; Actual number of risk events Q4: 74; Actual number of risk events Q1: 226; Actual number of risk events Q2: 37 | 416 | 416 | 416 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 31; Actual number of risk events Q2: 42; Actual number of risk events Q3: 23; Actual number of risk events Q4: 87; Actual number of risk events Q1: 151; Actual number of risk events Q2: 16 | 372 | 372 | 372 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 6; Actual number of risk events Q2: 0 | 4 | 4 | 4 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 104; Actual number of risk events Q2: 117; Actual number of risk events Q3: 108; Actual number of risk events Q4: 195; Actual number of risk events Q1: 682; Actual number of risk events Q2: 95 | 567 | 567 | 567 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 12; Actual number of risk events Q3: 1; Actual number of risk events Q4: 13; Actual number of risk events Q1: 25; Actual number of risk events Q2: 8 | 50 | 50 | 50 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 3; Actual number of risk events Q3: 2; Actual number of risk events Q4: 7; Actual number of risk events Q1: 18; Actual number of risk events Q2: 3 | 32 | 32 | 32 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 2; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.d.0 | Connector device | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.d.2 | Connector device | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.d.3 | Connector device | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.t.0 | Connector device | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.t.2 | Connector device | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 4 | 4 | 4 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.t.3 | Connector device | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 6; Actual number of risk events Q2: 10; Actual number of risk events Q3: 7; Actual number of risk events Q4: 14; Actual number of risk events Q1: 43; Actual number of risk events Q2: 5 | 49 | 49 | 49 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 2 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Ignition driver would be included in Fuse failures since we don't have specific call out for cutouts
| Wire down event | 4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Ignition driver would be included in Fuse failures since we don't have specific call out for cutouts
| Wire down event | 4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Ignition driver would be included in Fuse failures since we don't have specific call out for cutouts
| Wire down event | 4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and bushing | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 5; Actual number of risk events Q2: 5 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and bushing | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrester | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrester | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrester | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrester | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrester | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrester | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 20; Actual number of risk events Q2: 32; Actual number of risk events Q3: 19; Actual number of risk events Q4: 60; Actual number of risk events Q1: 194; Actual number of risk events Q2: 14 | 129 | 129 | 129 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 7; Actual number of risk events Q2: 1 | 13 | 13 | 13 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 4; Actual number of risk events Q2: 0 | 4 | 4 | 4 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 4 | 4 | 4 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 35; Actual number of risk events Q2: 46; Actual number of risk events Q3: 37; Actual number of risk events Q4: 47; Actual number of risk events Q1: 71; Actual number of risk events Q2: 28 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 2; Actual number of risk events Q3: 5; Actual number of risk events Q4: 8; Actual number of risk events Q1: 5; Actual number of risk events Q2: 3 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 3; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 6; Actual number of risk events Q2: 3 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 3; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 5; Actual number of risk events Q2: 2 | 4 | 4 | 4 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 4; Actual number of risk events Q4: 3; Actual number of risk events Q1: 0; Actual number of risk events Q2: 2 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 7; Actual number of risk events Q3: 5; Actual number of risk events Q4: 5; Actual number of risk events Q1: 8; Actual number of risk events Q2: 4 | 19 | 19 | 19 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.t.0 | Lightning | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.t.2 | Lightning | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.t.3 | Lightning | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.d.0 | Unknown | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 22; Actual number of risk events Q2: 11 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.d.2 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 10 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 7 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.t.0 | Unknown | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 13; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.t.2 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 11; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 11; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.d.0 | All Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 84; Actual number of risk events Q2: 66; Actual number of risk events Q3: 23; Actual number of risk events Q4: 0; Actual number of risk events Q1: 12; Actual number of risk events Q2: 6 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.d.2 | All Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.d.3 | All Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.t.0 | All Other | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 12; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.t.2 | All Other | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 9; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.t.3 | All Other | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 7; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
x | Unplanned Outage | 11. Dig-in | 11.a.d.0 | Dig-in | Distribution | Non-HFTD | No | Actual number of risk events Q1: 11; Actual number of risk events Q2: 28; Actual number of risk events Q3: 28; Actual number of risk events Q4: 15; Actual number of risk events Q1: 9; Actual number of risk events Q2: 14 | 82 | 82 | 82 | # risk events (excluding ignitions)
| Unplanned Outage | 11. Dig-in | 11.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2; Actual number of risk events Q1: 2; Actual number of risk events Q2: 2 | 6 | 6 | 6 | # risk events (excluding ignitions)
| Unplanned Outage | 11. Dig-in | 11.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 2; Actual number of risk events Q2: 3; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 4 | 6 | 6 | 6 | # risk events (excluding ignitions)
| Unplanned Outage | 11. Dig-in | 11.a.t.0 | Dig-in | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 11. Dig-in | 11.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 11. Dig-in | 11.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 12. Fire | 12.a.d.0 | Fire | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 63; Actual number of risk events Q2: 170; Actual number of risk events Q3: 200; Actual number of risk events Q4: 113; Actual number of risk events Q1: 3; Actual number of risk events Q2: 19 | 546 | 546 | 546 | # risk events (excluding ignitions)
| Unplanned Outage | 12. Fire | 12.a.d.2 | Fire | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 5; Actual number of risk events Q3: 13; Actual number of risk events Q4: 4; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1 | 26 | 26 | 26 | # risk events (excluding ignitions)
| Unplanned Outage | 12. Fire | 12.a.d.3 | Fire | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 6; Actual number of risk events Q4: 2; Actual number of risk events Q1: 0; Actual number of risk events Q2: 2 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Unplanned Outage | 12. Fire | 12.a.t.0 | Fire | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 4; Actual number of risk events Q4: 2; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 7 | 7 | 7 | # risk events (excluding ignitions)
| Unplanned Outage | 12. Fire | 12.a.t.2 | Fire | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 12; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 14 | 14 | 14 | # risk events (excluding ignitions)
| Unplanned Outage | 12. Fire | 12.a.t.3 | Fire | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 6; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 7 | 7 | 7 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 237; Actual number of risk events Q2: 517; Actual number of risk events Q3: 465; Actual number of risk events Q4: 349; Actual number of risk events Q1: 269; Actual number of risk events Q2: 573 | 1411.2 | 1411.2 | 1411.2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 31; Actual number of risk events Q2: 94; Actual number of risk events Q3: 111; Actual number of risk events Q4: 47; Actual number of risk events Q1: 45; Actual number of risk events Q2: 72 | 254.7 | 254.7 | 254.7 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 19; Actual number of risk events Q2: 28; Actual number of risk events Q3: 33; Actual number of risk events Q4: 22; Actual number of risk events Q1: 11; Actual number of risk events Q2: 21 | 91.8 | 91.8 | 91.8 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 6; Actual number of risk events Q2: 10; Actual number of risk events Q3: 13; Actual number of risk events Q4: 3; Actual number of risk events Q1: 6; Actual number of risk events Q2: 9 | 32 | 32 | 32 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 5 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 94; Actual number of risk events Q2: 183; Actual number of risk events Q3: 98; Actual number of risk events Q4: 68; Actual number of risk events Q1: 75; Actual number of risk events Q2: 139 | 443 | 443 | 443 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 3; Actual number of risk events Q3: 4; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 2 | 7 | 7 | 7 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 2 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 373; Actual number of risk events Q2: 467; Actual number of risk events Q3: 517; Actual number of risk events Q4: 397; Actual number of risk events Q1: 421; Actual number of risk events Q2: 365 | 1754 | 1754 | 1754 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 17; Actual number of risk events Q2: 30; Actual number of risk events Q3: 28; Actual number of risk events Q4: 20; Actual number of risk events Q1: 37; Actual number of risk events Q2: 47 | 95 | 95 | 95 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 7; Actual number of risk events Q2: 17; Actual number of risk events Q3: 8; Actual number of risk events Q4: 13; Actual number of risk events Q1: 17; Actual number of risk events Q2: 19 | 45 | 45 | 45 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 18; Actual number of risk events Q2: 9; Actual number of risk events Q3: 17; Actual number of risk events Q4: 10; Actual number of risk events Q1: 15; Actual number of risk events Q2: 16 | 54 | 54 | 54 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 6 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 2 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.d.0 | 3rd party contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 66; Actual number of risk events Q2: 89; Actual number of risk events Q3: 75; Actual number of risk events Q4: 65; Actual number of risk events Q1: 82; Actual number of risk events Q2: 30 | 294 | 294 | 294 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.d.2 | 3rd party contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 17; Actual number of risk events Q3: 12; Actual number of risk events Q4: 6; Actual number of risk events Q1: 4; Actual number of risk events Q2: 10 | 38 | 38 | 38 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 3; Actual number of risk events Q3: 4; Actual number of risk events Q4: 3; Actual number of risk events Q1: 2; Actual number of risk events Q2: 2 | 15 | 15 | 15 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.t.0 | 3rd party contact | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 8 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.t.2 | 3rd party contact | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 31; Actual number of risk events Q2: 49; Actual number of risk events Q3: 55; Actual number of risk events Q4: 24; Actual number of risk events Q1: 61; Actual number of risk events Q2: 48 | 159 | 159 | 159 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 5; Actual number of risk events Q3: 5; Actual number of risk events Q4: 3; Actual number of risk events Q1: 10; Actual number of risk events Q2: 9 | 17 | 17 | 17 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 3 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 10; Actual number of risk events Q3: 4; Actual number of risk events Q4: 2; Actual number of risk events Q1: 12; Actual number of risk events Q2: 0 | 20 | 20 | 20 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.g.d.0 | Unknown | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.g.d.2 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.g.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.g.t.0 | Unknown | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.g.t.2 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.g.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 397; Actual number of risk events Q2: 601; Actual number of risk events Q3: 431; Actual number of risk events Q4: 834; Actual number of risk events Q1: 6675; Actual number of risk events Q2: 277 | 2263 | 2263 | 2263 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 111; Actual number of risk events Q2: 159; Actual number of risk events Q3: 112; Actual number of risk events Q4: 198; Actual number of risk events Q1: 681; Actual number of risk events Q2: 122 | 580 | 580 | 580 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 134; Actual number of risk events Q2: 162; Actual number of risk events Q3: 96; Actual number of risk events Q4: 228; Actual number of risk events Q1: 598; Actual number of risk events Q2: 88 | 620 | 620 | 620 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 7; Actual number of risk events Q1: 28; Actual number of risk events Q2: 0 | 20 | 20 | 20 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 4; Actual number of risk events Q1: 18; Actual number of risk events Q2: 1 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 12; Actual number of risk events Q2: 0 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 10; Actual number of risk events Q3: 15; Actual number of risk events Q4: 17; Actual number of risk events Q1: 22; Actual number of risk events Q2: 12 | 47 | 47 | 47 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0 | 4 | 4 | 4 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 3 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 13; Actual number of risk events Q2: 17; Actual number of risk events Q3: 11; Actual number of risk events Q4: 11; Actual number of risk events Q1: 12; Actual number of risk events Q2: 9 | 52 | 52 | 52 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.0 | Capacitor bank | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 247; Actual number of risk events Q2: 412; Actual number of risk events Q3: 468; Actual number of risk events Q4: 440; Actual number of risk events Q1: 1323; Actual number of risk events Q2: 517 | 1567 | 1567 | 1567 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 19; Actual number of risk events Q2: 39; Actual number of risk events Q3: 25; Actual number of risk events Q4: 26; Actual number of risk events Q1: 80; Actual number of risk events Q2: 77 | 109 | 109 | 109 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 10; Actual number of risk events Q2: 16; Actual number of risk events Q3: 18; Actual number of risk events Q4: 13; Actual number of risk events Q1: 43; Actual number of risk events Q2: 33 | 57 | 57 | 57 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 5; Actual number of risk events Q2: 2 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 5; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.0 | Connection device | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 32; Actual number of risk events Q2: 46; Actual number of risk events Q3: 39; Actual number of risk events Q4: 67; Actual number of risk events Q1: 271; Actual number of risk events Q2: 142 | 184 | 184 | 184 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.2 | Connection device | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 21; Actual number of risk events Q2: 10 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.3 | Connection device | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 8; Actual number of risk events Q2: 6 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.0 | Connection device | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 4; Actual number of risk events Q3: 0; Actual number of risk events Q4: 3; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.2 | Connection device | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.3 | Connection device | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 122; Actual number of risk events Q2: 221; Actual number of risk events Q3: 175; Actual number of risk events Q4: 158; Actual number of risk events Q1: 341; Actual number of risk events Q2: 196 | 677 | 677 | 677 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 19; Actual number of risk events Q2: 21; Actual number of risk events Q3: 23; Actual number of risk events Q4: 11; Actual number of risk events Q1: 23; Actual number of risk events Q2: 45 | 74 | 74 | 74 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 20; Actual number of risk events Q3: 7; Actual number of risk events Q4: 3; Actual number of risk events Q1: 14; Actual number of risk events Q2: 16 | 38 | 38 | 38 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 111; Actual number of risk events Q2: 181; Actual number of risk events Q3: 282; Actual number of risk events Q4: 229; Actual number of risk events Q1: 392; Actual number of risk events Q2: 312 | 803 | 803 | 803 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 13; Actual number of risk events Q2: 19; Actual number of risk events Q3: 24; Actual number of risk events Q4: 16; Actual number of risk events Q1: 30; Actual number of risk events Q2: 26 | 72 | 72 | 72 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 14; Actual number of risk events Q2: 5; Actual number of risk events Q3: 18; Actual number of risk events Q4: 12; Actual number of risk events Q1: 24; Actual number of risk events Q2: 11 | 49 | 49 | 49 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.0 | Fuse | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.2 | Fuse | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.3 | Fuse | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.0 | Cutout | Distribution | Non-HFTD | No | Actual number of risk events Q1: 63; Actual number of risk events Q2: 87; Actual number of risk events Q3: 80; Actual number of risk events Q4: 92; Actual number of risk events Q1: 126; Actual number of risk events Q2: 0 | 322 | 322 | 322 | # risk events (excluding ignitions) | Ignition driver would be included in Fuse failures since PG&E does not have a specific call out for cutouts
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.2 | Cutout | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 8; Actual number of risk events Q2: 14; Actual number of risk events Q3: 13; Actual number of risk events Q4: 12; Actual number of risk events Q1: 12; Actual number of risk events Q2: 0 | 47 | 47 | 47 | # risk events (excluding ignitions) | Ignition driver would be included in Fuse failures since PG&E does not have a specific call out for cutouts
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.3 | Cutout | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 4; Actual number of risk events Q2: 5; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2; Actual number of risk events Q1: 10; Actual number of risk events Q2: 0 | 14 | 14 | 14 | # risk events (excluding ignitions) | Ignition driver would be included in Fuse failures since PG&E does not have a specific call out for cutouts
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.0 | Cutout | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.2 | Cutout | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.3 | Cutout | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.0 | Insulator and bushing | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 41; Actual number of risk events Q2: 65; Actual number of risk events Q3: 50; Actual number of risk events Q4: 68; Actual number of risk events Q1: 118; Actual number of risk events Q2: 57 | 224 | 224 | 224 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 23; Actual number of risk events Q3: 8; Actual number of risk events Q4: 11; Actual number of risk events Q1: 25; Actual number of risk events Q2: 25 | 50 | 50 | 50 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 12; Actual number of risk events Q2: 13; Actual number of risk events Q3: 5; Actual number of risk events Q4: 4; Actual number of risk events Q1: 7; Actual number of risk events Q2: 18 | 34 | 34 | 34 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.0 | Insulator and bushing | Transmission | Non-HFTD | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 4; Actual number of risk events Q3: 6; Actual number of risk events Q4: 2; Actual number of risk events Q1: 2; Actual number of risk events Q2: 8 | 20 | 20 | 20 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 5 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.0 | Lightning arrester | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 19; Actual number of risk events Q2: 18; Actual number of risk events Q3: 26; Actual number of risk events Q4: 47; Actual number of risk events Q1: 42; Actual number of risk events Q2: 21 | 110 | 110 | 110 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.2 | Lightning arrester | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 4; Actual number of risk events Q4: 13; Actual number of risk events Q1: 10; Actual number of risk events Q2: 3 | 20 | 20 | 20 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.3 | Lightning arrester | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 3; Actual number of risk events Q3: 1; Actual number of risk events Q4: 6; Actual number of risk events Q1: 5; Actual number of risk events Q2: 1 | 14 | 14 | 14 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.0 | Lightning arrester | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 8; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 8 | 8 | 8 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.2 | Lightning arrester | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.3 | Lightning arrester | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 136; Actual number of risk events Q2: 213; Actual number of risk events Q3: 191; Actual number of risk events Q4: 407; Actual number of risk events Q1: 840; Actual number of risk events Q2: 194 | 947 | 947 | 947 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 21; Actual number of risk events Q2: 46; Actual number of risk events Q3: 56; Actual number of risk events Q4: 47; Actual number of risk events Q1: 72; Actual number of risk events Q2: 55 | 170 | 170 | 170 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 18; Actual number of risk events Q2: 14; Actual number of risk events Q3: 18; Actual number of risk events Q4: 26; Actual number of risk events Q1: 35; Actual number of risk events Q2: 22 | 76 | 76 | 76 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 4; Actual number of risk events Q3: 2; Actual number of risk events Q4: 2; Actual number of risk events Q1: 6; Actual number of risk events Q2: 1 | 15 | 15 | 15 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 15; Actual number of risk events Q2: 13; Actual number of risk events Q3: 21; Actual number of risk events Q4: 31; Actual number of risk events Q1: 31; Actual number of risk events Q2: 17 | 80 | 80 | 80 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 8; Actual number of risk events Q3: 4; Actual number of risk events Q4: 7; Actual number of risk events Q1: 10; Actual number of risk events Q2: 3 | 21 | 21 | 21 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 10; Actual number of risk events Q1: 7; Actual number of risk events Q2: 1 | 13 | 13 | 13 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.0 | Recloser | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.2 | Recloser | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.3 | Recloser | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.0 | Relay | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 2; Actual number of risk events Q2: 2 | 4 | 4 | 4 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.2 | Relay | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.3 | Relay | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.0 | Relay | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 12 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.2 | Relay | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.3 | Relay | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.0 | Sectionalizer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 3; Actual number of risk events Q2: 1 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.0 | Sectionalizer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.0 | Splice | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 137; Actual number of risk events Q2: 218; Actual number of risk events Q3: 203; Actual number of risk events Q4: 165; Actual number of risk events Q1: 271; Actual number of risk events Q2: 157 | 723 | 723 | 723 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.2 | Splice | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 13; Actual number of risk events Q2: 18; Actual number of risk events Q3: 15; Actual number of risk events Q4: 20; Actual number of risk events Q1: 31; Actual number of risk events Q2: 28 | 66 | 66 | 66 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.3 | Splice | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 10; Actual number of risk events Q2: 7; Actual number of risk events Q3: 5; Actual number of risk events Q4: 4; Actual number of risk events Q1: 8; Actual number of risk events Q2: 7 | 26 | 26 | 26 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.0 | Splice | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.2 | Splice | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.3 | Splice | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 30; Actual number of risk events Q2: 56; Actual number of risk events Q3: 57; Actual number of risk events Q4: 56; Actual number of risk events Q1: 30; Actual number of risk events Q2: 35 | 199 | 199 | 199 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 4; Actual number of risk events Q1: 2; Actual number of risk events Q2: 3 | 6 | 6 | 6 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 4 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 5 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 2 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.0 | Tap | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.2 | Tap | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.3 | Tap | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.0 | Tap | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.2 | Tap | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.3 | Tap | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.0 | Tie wire | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.0 | Tie wire | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 625; Actual number of risk events Q2: 1059; Actual number of risk events Q3: 1459; Actual number of risk events Q4: 745; Actual number of risk events Q1: 758; Actual number of risk events Q2: 893 | 3888 | 3888 | 3888 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 75; Actual number of risk events Q2: 122; Actual number of risk events Q3: 140; Actual number of risk events Q4: 93; Actual number of risk events Q1: 31; Actual number of risk events Q2: 178 | 430 | 430 | 430 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 36; Actual number of risk events Q2: 56; Actual number of risk events Q3: 61; Actual number of risk events Q4: 26; Actual number of risk events Q1: 28; Actual number of risk events Q2: 64 | 179 | 179 | 179 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 9; Actual number of risk events Q2: 12; Actual number of risk events Q3: 23; Actual number of risk events Q4: 12; Actual number of risk events Q1: 11; Actual number of risk events Q2: 15 | 56 | 56 | 56 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 6; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 3; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1 | 12 | 12 | 12 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 3 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.0 | Unknown | Distribution | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.2 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.0 | Unknown | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.2 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 17; Actual number of risk events Q2: 39; Actual number of risk events Q3: 30; Actual number of risk events Q4: 22; Actual number of risk events Q1: 48; Actual number of risk events Q2: 144 | 108 | 108 | 108 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 4; Actual number of risk events Q3: 2; Actual number of risk events Q4: 5; Actual number of risk events Q1: 8; Actual number of risk events Q2: 22 | 15 | 15 | 15 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 8 | 6 | 6 | 6 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 3; Actual number of risk events Q3: 1; Actual number of risk events Q4: 27; Actual number of risk events Q1: 11; Actual number of risk events Q2: 3 | 34 | 34 | 34 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1627; Actual number of risk events Q2: 2193; Actual number of risk events Q3: 1865; Actual number of risk events Q4: 2156; Actual number of risk events Q1: 3956; Actual number of risk events Q2: 0 | 7605.77 | 7605.77 | 7605.77 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 289; Actual number of risk events Q2: 377; Actual number of risk events Q3: 338; Actual number of risk events Q4: 402; Actual number of risk events Q1: 565; Actual number of risk events Q2: 0 | 1363.82 | 1363.82 | 1363.82 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 123; Actual number of risk events Q2: 169; Actual number of risk events Q3: 105; Actual number of risk events Q4: 182; Actual number of risk events Q1: 336; Actual number of risk events Q2: 0 | 561.63 | 561.63 | 561.63 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 8 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.t.0 | Contamination | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 11; Actual number of risk events Q3: 1; Actual number of risk events Q4: 3; Actual number of risk events Q1: 8; Actual number of risk events Q2: 17 | 17 | 17 | 17 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.t.2 | Contamination | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1 | 3 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.t.3 | Contamination | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 16; Actual number of risk events Q2: 28; Actual number of risk events Q3: 23; Actual number of risk events Q4: 19; Actual number of risk events Q1: 18; Actual number of risk events Q2: 40 | 86 | 86 | 86 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 7; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 11 | 11 | 11 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 35; Actual number of risk events Q2: 86; Actual number of risk events Q3: 20; Actual number of risk events Q4: 17; Actual number of risk events Q1: 212; Actual number of risk events Q2: 98 | 158 | 158 | 158 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 5; Actual number of risk events Q3: 3; Actual number of risk events Q4: 11; Actual number of risk events Q1: 49; Actual number of risk events Q2: 54 | 20 | 20 | 20 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 5; Actual number of risk events Q4: 2; Actual number of risk events Q1: 14; Actual number of risk events Q2: 44 | 11 | 11 | 11 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.t.0 | Lightning | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 25; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3; Actual number of risk events Q1: 6; Actual number of risk events Q2: 15 | 20 | 20 | 20 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.t.2 | Lightning | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 10; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2; Actual number of risk events Q1: 12; Actual number of risk events Q2: 11 | 10 | 10 | 10 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.t.3 | Lightning | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 20. Government agency request | 20.a.d.0 | Government agency request | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 20. Government agency request | 20.a.d.2 | Government agency request | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 20. Government agency request | 20.a.d.3 | Government agency request | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 20. Government agency request | 20.a.t.0 | Government agency request | Transmission | Non-HFTD | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 20. Government agency request | 20.a.t.2 | Government agency request | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 20. Government agency request | 20.a.t.3 | Government agency request | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 21. Customer request | 21.a.d.0 | Customer request | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 21. Customer request | 21.a.d.2 | Customer request | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 21. Customer request | 21.a.d.3 | Customer request | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 21. Customer request | 21.a.t.0 | Customer request | Transmission | Non-HFTD | No | Actual number of risk events Q1: 3; Actual number of risk events Q2: 3; Actual number of risk events Q3: 6; Actual number of risk events Q4: 8; Actual number of risk events Q1: 13; Actual number of risk events Q2: 4 | 20 | 20 | 20 | # risk events (excluding ignitions)
| Unplanned Outage | 21. Customer request | 21.a.t.2 | Customer request | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 5; Actual number of risk events Q4: 4; Actual number of risk events Q1: 11; Actual number of risk events Q2: 2 | 11 | 11 | 11 | # risk events (excluding ignitions)
| Unplanned Outage | 21. Customer request | 21.a.t.3 | Customer request | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 8; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0 | 8 | 8 | 8 | # risk events (excluding ignitions)
| Unplanned Outage | 22. Emergency repairs | 22.a.d.0 | Emergency repairs | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 42; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 47.46 | 47.46 | 47.46 | # risk events (excluding ignitions)
| Unplanned Outage | 22. Emergency repairs | 22.a.d.2 | Emergency repairs | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 3; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 3.39 | 3.39 | 3.39 | # risk events (excluding ignitions)
| Unplanned Outage | 22. Emergency repairs | 22.a.d.3 | Emergency repairs | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0 | 1.13 | 1.13 | 1.13 | # risk events (excluding ignitions)
| Unplanned Outage | 22. Emergency repairs | 22.a.t.0 | Emergency repairs | Transmission | Non-HFTD | No | Actual number of risk events Q1: 27; Actual number of risk events Q2: 43; Actual number of risk events Q3: 40; Actual number of risk events Q4: 55; Actual number of risk events Q1: 56; Actual number of risk events Q2: 77 | 165 | 165 | 165 | # risk events (excluding ignitions)
| Unplanned Outage | 22. Emergency repairs | 22.a.t.2 | Emergency repairs | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 12; Actual number of risk events Q2: 24; Actual number of risk events Q3: 5; Actual number of risk events Q4: 9; Actual number of risk events Q1: 24; Actual number of risk events Q2: 16 | 50 | 50 | 50 | # risk events (excluding ignitions)
| Unplanned Outage | 22. Emergency repairs | 22.a.t.3 | Emergency repairs | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 4; Actual number of risk events Q2: 10; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 4 | 16 | 16 | 16 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.d.0 | Unknown | Distribution | Non-HFTD | No | Actual number of risk events Q1: 2251; Actual number of risk events Q2: 3217; Actual number of risk events Q3: 2629; Actual number of risk events Q4: 2864; Actual number of risk events Q1: 4007; Actual number of risk events Q2: 2706 | 10632.17 | 10632.17 | 10632.17 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.d.2 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of risk events Q1: 291; Actual number of risk events Q2: 358; Actual number of risk events Q3: 316; Actual number of risk events Q4: 405; Actual number of risk events Q1: 632; Actual number of risk events Q2: 494 | 1328.9 | 1328.9 | 1328.9 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of risk events Q1: 114; Actual number of risk events Q2: 155; Actual number of risk events Q3: 129; Actual number of risk events Q4: 160; Actual number of risk events Q1: 375; Actual number of risk events Q2: 257 | 541.26 | 541.26 | 541.26 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.t.0 | Unknown | Transmission | Non-HFTD | No | Actual number of risk events Q1: 21; Actual number of risk events Q2: 30; Actual number of risk events Q3: 18; Actual number of risk events Q4: 21; Actual number of risk events Q1: 116; Actual number of risk events Q2: 28 | 90 | 90 | 90 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.t.2 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 8; Actual number of risk events Q2: 3; Actual number of risk events Q3: 2; Actual number of risk events Q4: 13; Actual number of risk events Q1: 120; Actual number of risk events Q2: 17 | 26 | 26 | 26 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 3; Actual number of risk events Q2: 12; Actual number of risk events Q3: 0; Actual number of risk events Q4: 3; Actual number of risk events Q1: 59; Actual number of risk events Q2: 4 | 18 | 18 | 18 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.d.0 | All Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 166; Actual number of risk events Q2: 285 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.d.2 | All Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 19; Actual number of risk events Q2: 73 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.d.3 | All Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 4; Actual number of risk events Q2: 22 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.t.0 | All Other | Transmission | Non-HFTD | No | Actual number of risk events Q1: 21; Actual number of risk events Q2: 25; Actual number of risk events Q3: 20; Actual number of risk events Q4: 80; Actual number of risk events Q1: 38; Actual number of risk events Q2: 22 | 80 | 80 | 80 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.t.2 | All Other | Transmission | HFTD Tier 2 | No | Actual number of risk events Q1: 6; Actual number of risk events Q2: 6; Actual number of risk events Q3: 9; Actual number of risk events Q4: 49; Actual number of risk events Q1: 12; Actual number of risk events Q2: 3 | 60 | 60 | 60 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.t.3 | All Other | Transmission | HFTD Tier 3 | No | Actual number of risk events Q1: 8; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3; Actual number of risk events Q1: 22; Actual number of risk events Q2: 1 | 14 | 14 | 14 | # risk events (excluding ignitions)
Comments for Table 5 Risk Event Drivers (Distribution System): To the extent available, PG&E’s Integrated Logging Information System – Operations Data Base (ILIS-ODB) was used to provide the level of detail contained in Table 7.1 (Distribution) that includes both sustained and momentary outages experienced on our distribution system. When reviewing this data, the following should be noted: Based on PG&E’s standard definition, a distribution wire down event results in a reportable outage event and occurs when a normally energized electric primary distribution conductor is broken, or stays intact, and falls from its intended position to rest on the ground or a foreign object. PG&E used this standard definition in this year’s report and thus it does not include any secondary related wire down events. However, it should also be noted that any primary or secondary wire down condition that resulted in an outage event is also reported in the distribution outage results. Due to their relatively small contribution, the Commission does not require transformer-only outages be reported in the annual electric system reliability metrics. However, transformer-only outages are reported within PG&E’s Field Automation System (FAS) and most were also reported in PG&E’s ILIS-ODB outage data base. PG&E is including these transformer-only outages in the WMP reporting to reflect the full picture of outage incidents which could have represented ignition potential. PG&E also further enhanced our reporting process/controls in September 2020 to ensure future transformer-only outages are fully reported in our ILIS-ODB outage data base and is working to improve outage cause reporting. In Table 5 (Distribution), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based off analysis of trends on data from 2017-2022 Comments for Table 5 Risk Event Drivers (Transmission System): PG&E’s Transmission Operations Tracking & Logging (TOTL) application was used as the primary data source for Table 5 (Transmission) which includes unplanned outages experienced on the transmission (i.e., >50 kV) system. Unplanned outages include those due to an “automatic” operation (i.e., the transmission line relayed automatically by a protective device (typically a circuit breaker) and either automatically tested OK, tested no good, or was set up not to test (e.g., automatics disabled or cut out for wildfire risk mitigation)). Unplanned outages also include those where the line was manually removed from service by Operations on an “emergency” basis, usually to repair or replace an imminent failure of an asset. Such emergency forced outages (EFOs) are taken without securing approval from the California Independent System Operator (CAISO). Planned or “scheduled” outages are not included. Scheduled outages differ from EFOs in that PG&E garnered CAISO approval prior to the line being removed from service. Based on PG&E’s standard definition, a transmission wire down event (similar to distribution) results in a reportable outage event (note: customers may or may not have been de-energized) and occurs when a normally energized electric transmission conductor fails in service and falls from its intended position to rest on the ground or a foreign object. In Table 5 (Transmission), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based off analysis of trends on data from 2017-2022

## Table 6
| Utility | PG&E | Notes:
| Table No. | 6 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2023-08-01 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
[7 empty] | Actual number of ignitions | [15 empty] | Projected ignitions
| Table 6: Ignition drivers | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
| Metric type | # | Ignition driver | Line Type | HFTD Tier | Are ignitions tracked for ignition driver? (yes / no) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
| 1. Dig-in | 1.a.d.0 | Dig-in | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 1. Dig-in | 1.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 1. Dig-in | 1.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 1. Dig-in | 1.a.t.0 | Dig-in | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 1. Dig-in | 1.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 1. Dig-in | 1.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
x | 2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 11; Actual number of ignitions Q3: 17; Actual number of ignitions Q4: 6; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 15 | 34 | 34 | 34 | # ignitions
| 2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 5; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0 | 6.8747 | 6.7076 | 6.5406 | # ignitions
| 2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2 | 3 | 3 | 3 | # ignitions
| 2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 10; Actual number of ignitions Q3: 5; Actual number of ignitions Q4: 4; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 5 | 20 | 20 | 20 | # ignitions
| 2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 2 | 2 | 2 | # ignitions
| 2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 4; Actual number of ignitions Q2: 16; Actual number of ignitions Q3: 12; Actual number of ignitions Q4: 6; Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 10 | 36 | 36 | 36 | # ignitions
| 2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 3; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 6 | 6 | 6 | # ignitions
| 2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 2 | 2 | 2 | # ignitions
| 2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.e.d.0 | 3rd party facility | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 4; Actual number of ignitions Q3: 4; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.e.d.2 | 3rd party facility | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.e.d.3 | 3rd party facility | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.e.t.0 | 3rd party facility | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.e.t.2 | 3rd party facility | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.e.t.3 | 3rd party facility | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.f.d.0 | Unknown | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by contact from an unidentified object would be included under the following drivers 2.g Other or 10. Unknown.
| 2. Contact from object | 2.f.d.2 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by contact from an unidentified object would be included under the following drivers 2.g Other or 10. Unknown.
| 2. Contact from object | 2.f.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by contact from an unidentified object would be included under the following drivers 2.g Other or 10. Unknown.
| 2. Contact from object | 2.f.t.0 | Unknown | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by contact from an unidentified object would be included under the following drivers 2.g Other or 10. Unknown.
| 2. Contact from object | 2.f.t.2 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by contact from an unidentified object would be included under the following drivers 2.g Other or 10. Unknown.
| 2. Contact from object | 2.f.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by contact from an unidentified object would be included under the following drivers 2.g Other or 10. Unknown.
| 2. Contact from object | 2.g.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 6; Actual number of ignitions Q2: 6; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 2; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 5 | 23 | 23 | 23 | # ignitions
| 2. Contact from object | 2.g.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 4.9105 | 4.7912 | 4.6719 | # ignitions
| 2. Contact from object | 2.g.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 2. Contact from object | 2.g.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.g.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.g.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 28; Actual number of ignitions Q3: 26; Actual number of ignitions Q4: 4; Actual number of ignitions Q1: 4; Actual number of ignitions Q2: 14 | 57 | 57 | 57 | # ignitions
| 3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 3; Actual number of ignitions Q2: 8; Actual number of ignitions Q3: 11; Actual number of ignitions Q4: 3; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 4 | 25.5346 | 24.9141 | 24.2937 | # ignitions
| 3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 9; Actual number of ignitions Q3: 5; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 2 | 16.6957 | 16.29 | 15.8844 | # ignitions
| 3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment/facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 2 | 2 | 2 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 4; Actual number of ignitions Q4: 2; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 9 | 9 | 9 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 4; Actual number of ignitions Q2: 12; Actual number of ignitions Q3: 20; Actual number of ignitions Q4: 4; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 6 | 43 | 43 | 43 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0 | 2.9463 | 2.8747 | 2.8031 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 1 | 1 | 1 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.d.0 | Connection device | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 13; Actual number of ignitions Q3: 13; Actual number of ignitions Q4: 3; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 30 | 30 | 30 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.d.2 | Connection device | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 2.9463 | 2.8747 | 2.8031 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.d.3 | Connection device | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.t.0 | Connection device | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.t.2 | Connection device | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.t.3 | Connection device | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 4; Actual number of ignitions Q4: 2; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 8 | 8 | 8 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions related to cutout failure are characterized as fuse failures in PG&E's ignitions database.
| 4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions related to cutout failure are characterized as fuse failures in PG&E's ignitions database.
| 4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions related to cutout failure are characterized as fuse failures in PG&E's ignitions database.
| 4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions related to cutout failure are characterized as fuse failures in PG&E's ignitions database.
| 4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions related to cutout failure are characterized as fuse failures in PG&E's ignitions database.
| 4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions related to cutout failure are characterized as fuse failures in PG&E's ignitions database.
| 4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and brushing | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2 | 3 | 3 | 3 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and brushing | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and brushing | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and brushing | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and brushing | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and brushing | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrestor | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrestor | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrestor | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrestor | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrestor | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrestor | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2; Actual number of ignitions Q3: 3; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 1 | 6 | 6 | 6 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2 | 0 | 0 | 0 | # ignitions | With the exception of automatic wire splices, ignitions related to splice failures are characterized as connection device failures in PG&E's ignitions database. Because of this, ignitions caused by automatic wire splice failures have been included in Connection Devices 4.d.d.
| 4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | With the exception of automatic wire splices, ignitions related to splice failures are characterized as connection device failures in PG&E's ignitions database. Because of this, ignitions caused by automatic wire splice failures have been included in Connection Devices 4.d.d.
| 4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | With the exception of automatic wire splices, ignitions related to splice failures are characterized as connection device failures in PG&E's ignitions database. Because of this, ignitions caused by automatic wire splice failures have been included in Connection Devices 4.d.d.
| 4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | With the exception of automatic wire splices, ignitions related to splice failures are characterized as connection device failures in PG&E's ignitions database. Because of this, ignitions caused by automatic wire splice failures have been included in Connection Devices 4.d.d.
| 4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | With the exception of automatic wire splices, ignitions related to splice failures are characterized as connection device failures in PG&E's ignitions database. Because of this, ignitions caused by automatic wire splice failures have been included in Connection Devices 4.d.d.
| 4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | With the exception of automatic wire splices, ignitions related to splice failures are characterized as connection device failures in PG&E's ignitions database. Because of this, ignitions caused by automatic wire splice failures have been included in Connection Devices 4.d.d.
| 4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 8; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2 | 8 | 8 | 8 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 5; Actual number of ignitions Q3: 6; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 6 | 13 | 13 | 13 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by an unidentified equipment failure would be included under the following drivers 2.g Other or 10. Unknown.
| 4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by an unidentified equipment failure would be included under the following drivers 2.g Other or 10. Unknown.
| 4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by an unidentified equipment failure would be included under the following drivers 2.g Other or 10. Unknown.
| 4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by an unidentified equipment failure would be included under the following drivers 2.g Other or 10. Unknown.
| 4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by an unidentified equipment failure would be included under the following drivers 2.g Other or 10. Unknown.
| 4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | Ignitions caused by an unidentified equipment failure would be included under the following drivers 2.g Other or 10. Unknown.
| 4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 6; Actual number of ignitions Q3: 10; Actual number of ignitions Q4: 4; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 1 | 20 | 20 | 20 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 3; Actual number of ignitions Q2: 1 | 4.9105 | 4.7912 | 4.6719 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 3; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0 | 3.9284 | 3.8329 | 3.7375 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | [16 empty] | 7 | 7 | 7 | # ignitions | bar: Actual number of ignitions Q1 to Actual number of ignitions Q2
| 5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 3; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 8 | 8 | 8 | # ignitions
| 6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1.9642 | 1.9165 | 1.8687 | # ignitions
| 6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 7. Protective device operation | 7.a.d.0 | Protective device operation | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 7. Protective device operation | 7.a.d.2 | Protective device operation | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 7. Protective device operation | 7.a.d.3 | Protective device operation | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 7. Protective device operation | 7.a.t.0 | Protective device operation | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 7. Protective device operation | 7.a.t.2 | Protective device operation | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 7. Protective device operation | 7.a.t.3 | Protective device operation | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions | To PG&E's knowledge, there have been 0 ignitions observed involving PG&E assets that were a direct result of this ignition driver in 2022.
| 8. Vandalism/theft | 8.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 3; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0 | 2 | 2 | 2 | # ignitions
| 8. Vandalism/theft | 8.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 9. Lightning | 9.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 0 | 0 | 0 | # ignitions
| 9. Lightning | 9.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 9. Lightning | 9.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 9. Lightning | 9.a.t.0 | Lightning | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 2 | 2 | 2 | # ignitions
| 9. Lightning | 9.a.t.2 | Lightning | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 9. Lightning | 9.a.t.3 | Lightning | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 10. Unknown | 10.a.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0 | 0 | 0 | # ignitions
| 11. Other | 11.a.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 3; Actual number of ignitions Q2: 18; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 2; Actual number of ignitions Q2: 2 | 28 | 28 | 28 | # ignitions
| 11. Other | 11.a.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1.9642 | 1.9165 | 1.8687 | # ignitions
| 11. Other | 11.a.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 0.9821 | 0.95823 | 0.93437 | # ignitions
| 11. Other | 11.a.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
| 11. Other | 11.a.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1 | 1 | 1 | 1 | # ignitions
| 11. Other | 11.a.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0 | 1 | 1 | 1 | # ignitions
Comments for Table 6: The fire ignition data provided in this table is based on fire incident reports filed with the CPUC annually in accordance with D.14-02-015. The ignition data provided in these tables was pulled from PG&E’s systems in January 2023 and reflects preliminary data for two reasons: first, PG&E’s final 2022 fire ignition report is due on April 1, 2023 and 2022 data will be further reviewed in advance of that filing. The System HFTD Tier metric is the sum of Non HFTD, HFTD Zone 1, HFTD Tier 2, and HFTD Tier 3. 2023 HFTD Distribution: Values show decreases as compared to 2022 HFTD distribution based on preliminary undergrounding modelling forecast.

## Table 7
| Utility | PG&E
| Table No. | 7
| Date Modified | 2023-08-01
[7 empty] | Actual | [15 empty] | Projected
| Table 7: State of service territory and utility equipment | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 4348.5699; Actual Q2: 4345.3411; Actual Q3: 4631.3445; Actual Q4: 4628.6061; Actual Q1: 4633.0789; Actual Q2: 4636.0657 | 4626.8062 | 4610.5173 | 4610.5173 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 9716.6576; Actual Q2: 9715.6693; Actual Q3: 9428.8116; Actual Q4: 9427.7867; Actual Q1: 9432.685; Actual Q2: 9447.6988 | 9427.7867 | 9424.2185 | 9424.2185 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 6957.1301; Actual Q2: 6954.6518; Actual Q3: 7029.7223; Actual Q4: 7025.8764; Actual Q1: 7029.1447; Actual Q2: 7030.6881 | 6964.8843 | 6935.6647 | 6928.6185 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 29022.6951; Actual Q2: 29025.4167; Actual Q3: 28947.5391; Actual Q4: 28936.0333; Actual Q1: 28939.4634; Actual Q2: 28952.9704 | 28918.0957 | 28913.1777 | 28898.4328 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 426.5629; Actual Q2: 424.3796; Actual Q3: 421.7475; Actual Q4: 421.3767; Actual Q1: 420.31; Actual Q2: 420.1116 | 417.2495 | 417.2495 | 415.961 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 4852.2035; Actual Q2: 4853.0973; Actual Q3: 4858.1717; Actual Q4: 4859.0601; Actual Q1: 4859.7624; Actual Q2: 4860.4298 | 4850.496 | 4840.6048 | 4824.5795 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 647.0469; Actual Q2: 646.9476; Actual Q3: 683.6973; Actual Q4: 683.2701; Actual Q1: 682.6899; Actual Q2: 683.0467 | 676.2417 | 675.1267 | 675.1267 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 157.7631; Actual Q2: 156.3281; Actual Q3: 119.1924; Actual Q4: 118.5082; Actual Q1: 118.4988; Actual Q2: 118.6382 | 111.8676 | 111.8676 | 111.8676 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 8693.1045; Actual Q2: 8692.5594; Actual Q3: 8638.5246; Actual Q4: 8623.0156; Actual Q1: 8621.9341; Actual Q2: 8621.1233 | 8542.8162 | 8417.4326 | 8292.8664 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 5374.1373; Actual Q2: 5369.9503; Actual Q3: 5417.8917; Actual Q4: 5411.1054; Actual Q1: 5409.2593; Actual Q2: 5407.5905 | 5382.2062 | 5370.1752 | 5310.4533 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 888.9491; Actual Q2: 882.6836; Actual Q3: 799.9587; Actual Q4: 797.8877; Actual Q1: 795.8354; Actual Q2: 795.9632 | 791.5735 | 789.9104 | 788.2999 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 2360.5897; Actual Q2: 2341.8904; Actual Q3: 2415.2306; Actual Q4: 2404.0742; Actual Q1: 2395.6416; Actual Q2: 2395.4204 | 2354.5008 | 2333.8078 | 2294.8048 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 271.6586; Actual Q2: 270.8524; Actual Q3: 272.356; Actual Q4: 271.9752; Actual Q1: 272.0436; Actual Q2: 272.1962 | 267.8224 | 258.8721 | 255.6349 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 35.7873; Actual Q2: 35.7585; Actual Q3: 33.5971; Actual Q4: 33.3088; Actual Q1: 33.324; Actual Q2: 33.4114 | 33.3088 | 30.8609 | 30.8609 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 4297.583; Actual Q2: 4282.2151; Actual Q3: 4207.4348; Actual Q4: 4187.6568; Actual Q1: 4185.9489; Actual Q2: 4181.477 | 4128.5518 | 3951.4149 | 3745.9146 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1662.7455; Actual Q2: 1653.3888; Actual Q3: 1720.2677; Actual Q4: 1707.5367; Actual Q1: 1706.0152; Actual Q2: 1704.4036 | 1694.6322 | 1657.939 | 1580.6831 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 333.3048; Actual Q2: 332.1065; Actual Q3: 330.4929; Actual Q4: 329.3895; Actual Q1: 329.6038; Actual Q2: 329.5128 | 329.315 | 329.315 | 329.315 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 352.9192; Actual Q2: 350.5431; Actual Q3: 351.5567; Actual Q4: 343.7054; Actual Q1: 343.875; Actual Q2: 344.0042 | 342.0181 | 342.0181 | 342.0181 | Circuit miles | For Projected data, PG&E reduced the OH Circuit miles based on the increase of the UG circuit miles forcasted
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 532.9372; Actual Q2: 534.6115; Actual Q3: 585.2357; Actual Q4: 588.3099; Actual Q1: 588.1276; Actual Q2: 588.1206 | 588.3099 | 588.3099 | 588.3099 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 1654.3772; Actual Q2: 1653.3822; Actual Q3: 1593.5476; Actual Q4: 1594.5712; Actual Q1: 1593.4292; Actual Q2: 1593.0676 | 1594.5712 | 1594.5712 | 1594.5712 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 887.7087; Actual Q2: 887.7578; Actual Q3: 880.5545; Actual Q4: 882.4176; Actual Q1: 882.2855; Actual Q2: 882.204 | 882.4176 | 882.4176 | 882.4176 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 7928.1657; Actual Q2: 7927.0245; Actual Q3: 7949.1786; Actual Q4: 7952.5809; Actual Q1: 7918.0738; Actual Q2: 7918.2738 | 7952.5809 | 7952.5809 | 7952.5809 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 45.105; Actual Q2: 45.105; Actual Q3: 45.8319; Actual Q4: 45.8319; Actual Q1: 45.8319; Actual Q2: 45.8321 | 45.8319 | 45.8319 | 45.8319 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 1541.7771; Actual Q2: 1541.7829; Actual Q3: 1541.0559; Actual Q4: 1541.0439; Actual Q1: 1535.9382; Actual Q2: 1535.9327 | 1541.0439 | 1541.0439 | 1541.0439 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 85.2227; Actual Q2: 86.0816; Actual Q3: 96.3273; Actual Q4: 99.8541; Actual Q1: 99.8541; Actual Q2: 99.9 | 99.8541 | 99.8541 | 99.8541 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 133.7272; Actual Q2: 134.3674; Actual Q3: 115.2935; Actual Q4: 119.926; Actual Q1: 119.9369; Actual Q2: 119.9354 | 119.926 | 119.926 | 119.926 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 835.8007; Actual Q2: 836.5236; Actual Q3: 858.8134; Actual Q4: 862.0742; Actual Q1: 860.9841; Actual Q2: 860.9655 | 862.0742 | 862.0742 | 862.0742 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 2084.0941; Actual Q2: 2084.1624; Actual Q3: 2056.7798; Actual Q4: 2067.8761; Actual Q1: 2061.7109; Actual Q2: 2061.6547 | 2067.8761 | 2067.8761 | 2067.8761 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 79.0616; Actual Q2: 77.8902; Actual Q3: 72.8263; Actual Q4: 72.8263; Actual Q1: 72.7267; Actual Q2: 72.7009 | 72.8263 | 72.8263 | 72.8263 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 1010.0679; Actual Q2: 999.3293; Actual Q3: 996.3023; Actual Q4: 996.3023; Actual Q1: 979.5375; Actual Q2: 979.5335 | 996.3023 | 996.3023 | 996.3023 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 32.1786; Actual Q2: 32.1786; Actual Q3: 35.0025; Actual Q4: 35.0025; Actual Q1: 35.0025; Actual Q2: 35.0024 | 35.0025 | 35.0025 | 35.0025 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 25.9505; Actual Q2: 25.9811; Actual Q3: 23.1582; Actual Q4: 23.1582; Actual Q1: 23.1582; Actual Q2: 23.1581 | 23.1582 | 23.1582 | 23.1582 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 293.3891; Actual Q2: 293.3521; Actual Q3: 305.6531; Actual Q4: 305.6539; Actual Q1: 300.9997; Actual Q2: 300.995 | 305.6539 | 305.6539 | 305.6539 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 771.8024; Actual Q2: 769.9943; Actual Q3: 757.9361; Actual Q4: 757.9541; Actual Q1: 754.0889; Actual Q2: 754.1003 | 757.9541 | 757.9541 | 757.9541 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 22.8332; Actual Q2: 22.8332; Actual Q3: 27.036; Actual Q4: 27.036; Actual Q1: 27.037; Actual Q2: 27.0371 | 27.036 | 27.036 | 27.036 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 145.6196; Actual Q2: 145.6182; Actual Q3: 138.4021; Actual Q4: 138.4021; Actual Q1: 133.1501; Actual Q2: 133.1496 | 138.4021 | 138.4021 | 138.4021 | Circuit miles | For Projected data, PG&E used Q4 2022 metrics and projecting it to be flat delta
x | 2. Underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 5796.4058; Actual Q2: 5807.8832; Actual Q3: 6458.6199; Actual Q4: 6474.3866; Actual Q1: 6481.1385; Actual Q2: 6494.6988 | 6476.1865 | 6492.4754 | 6492.4754 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 12680.6917; Actual Q2: 12706.4541; Actual Q3: 12079.1919; Actual Q4: 12097.9196; Actual Q1: 12114.8782; Actual Q2: 12148.0258 | 12097.9196 | 12101.4878 | 12101.4878 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 2486.9413; Actual Q2: 2496.8179; Actual Q3: 2733.4712; Actual Q4: 2743.782; Actual Q1: 2748.6715; Actual Q2: 2759.7651 | 2804.774 | 2833.9936 | 2841.0399 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 3539.8856; Actual Q2: 3563.7755; Actual Q3: 3364.1547; Actual Q4: 3382.5812; Actual Q1: 3399.0455; Actual Q2: 3432.5195 | 3400.5188 | 3405.4369 | 3420.1817 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 53.6397; Actual Q2: 53.8587; Actual Q3: 57.3393; Actual Q4: 57.8976; Actual Q1: 58.7868; Actual Q2: 59.5479 | 62.0248 | 62.0248 | 63.3133 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 154.1344; Actual Q2: 158.2163; Actual Q3: 156.421; Actual Q4: 157.7913; Actual Q1: 158.225; Actual Q2: 158.4379 | 166.3555 | 176.2467 | 192.2719 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 296.0595; Actual Q2: 296.2649; Actual Q3: 333.2007; Actual Q4: 333.5923; Actual Q1: 333.6695; Actual Q2: 334.3165 | 340.6206 | 341.7357 | 341.7357 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 74.586; Actual Q2: 76.1494; Actual Q3: 39.9902; Actual Q4: 42.7733; Actual Q1: 42.7749; Actual Q2: 42.7602 | 49.4138 | 49.4138 | 49.4138 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 997.8451; Actual Q2: 1000.4192; Actual Q3: 1035.0633; Actual Q4: 1057.1284; Actual Q1: 1057.9727; Actual Q2: 1060.3177 | 1137.3278 | 1262.7114 | 1387.2776 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 453.4979; Actual Q2: 454.9782; Actual Q3: 431.0027; Actual Q4: 441.6947; Actual Q1: 442.9484; Actual Q2: 446.4102 | 470.5939 | 482.625 | 542.3468 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 63.7808; Actual Q2: 63.788; Actual Q3: 64.2903; Actual Q4: 64.8714; Actual Q1: 64.8573; Actual Q2: 64.8412 | 71.1856 | 72.8486 | 74.4592 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 135.8752; Actual Q2: 136.0232; Actual Q3: 136.4735; Actual Q4: 139.9058; Actual Q1: 139.8772; Actual Q2: 140.8197 | 189.4792 | 210.1722 | 249.1752 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 111.1707; Actual Q2: 113.4251; Actual Q3: 115.5915; Actual Q4: 115.8151; Actual Q1: 115.8896; Actual Q2: 115.8658 | 119.9679 | 128.9182 | 132.1555 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 8.5977; Actual Q2: 8.6831; Actual Q3: 7.7935; Actual Q4: 7.7861; Actual Q1: 7.7721; Actual Q2: 7.7714 | 7.7861 | 10.234 | 10.234 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 460.4259; Actual Q2: 480.7232; Actual Q3: 482.618; Actual Q4: 503.4972; Actual Q1: 507.9587; Actual Q2: 518.9901 | 562.6023 | 739.7391 | 945.2395 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 152.0049; Actual Q2: 160.7969; Actual Q3: 168.4299; Actual Q4: 175.9107; Actual Q1: 178.2035; Actual Q2: 182.3667 | 188.8152 | 225.5083 | 302.7642 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 20.2613; Actual Q2: 20.1679; Actual Q3: 20.3196; Actual Q4: 20.5408; Actual Q1: 20.571; Actual Q2: 20.5696 | 20.6153 | 20.6153 | 20.6153 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 30.715; Actual Q2: 31.373; Actual Q3: 31.2229; Actual Q4: 31.9197; Actual Q1: 32.0047; Actual Q2: 31.9987 | 33.607 | 33.607 | 33.607 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates.
|  | 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 20.8916; Actual Q2: 20.8916; Actual Q3: 10.8741; Actual Q4: 10.8746; Actual Q1: 20.8916; Actual Q2: 23.5341 | 10.8746 | 10.8746 | 10.8746 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 102.3832; Actual Q2: 102.3832; Actual Q3: 36.3202; Actual Q4: 36.3202; Actual Q1: 102.3832; Actual Q2: 100.4429 | 36.3202 | 36.3202 | 36.3202 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 8.1396; Actual Q2: 8.1396; Actual Q3: 23.3964; Actual Q4: 23.3964; Actual Q1: 8.1396; Actual Q2: 10.8746 | 23.3964 | 23.3964 | 23.3964 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 39.0546; Actual Q2: 39.0546; Actual Q3: 99.8783; Actual Q4: 99.8783; Actual Q1: 39.0546; Actual Q2: 36.3201 | 99.8783 | 99.8783 | 99.8783 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 1.3204; Actual Q2: 1.3204; Actual Q3: 1.1211; Actual Q4: 1.1211; Actual Q1: 1.3204; Actual Q2: 1.6533 | 1.1211 | 1.1211 | 1.1211 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0.48189; Actual Q2: 0.48189; Actual Q3: 7.8594; Actual Q4: 7.8594; Actual Q1: 0.48189; Actual Q2: 0.14894 | 7.8594 | 7.8594 | 7.8594 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 0.49677; Actual Q2: 0.49677; Actual Q3: 1.6534; Actual Q4: 1.6534; Actual Q1: 0.49677; Actual Q2: 1.1211 | 1.6534 | 1.6534 | 1.6534 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 8.4837; Actual Q2: 8.4837; Actual Q3: 0.14894; Actual Q4: 0.14894; Actual Q1: 8.4837; Actual Q2: 7.8593 | 0.14894 | 0.14894 | 0.14894 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 0.548; Actual Q2: 0.548; Actual Q3: 0.58353; Actual Q4: 0.58353; Actual Q1: 0.548; Actual Q2: 0.58353 | 0.58353 | 0.58353 | 0.58353 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0.38604; Actual Q2: 0.38604; Actual Q3: 0.35051; Actual Q4: 0.35051; Actual Q1: 0.38604; Actual Q2: 0.35051 | 0.35051 | 0.35051 | 0.35051 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
|  | 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles | 2023 - 2025 projected data is same as Q4 2022.
| 3. Critical facilities | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 14202; Actual Q2: 14194; Actual Q3: 15368; Actual Q4: 15539; Actual Q1: 15499; Actual Q2: 15379 | 15539 | 15539 | 15539 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 38262; Actual Q2: 38251; Actual Q3: 37015; Actual Q4: 37488; Actual Q1: 37493; Actual Q2: 37143 | 37488 | 37488 | 37488 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 7062; Actual Q2: 7059; Actual Q3: 7354; Actual Q4: 7423; Actual Q1: 7420; Actual Q2: 7374 | 7423 | 7423 | 7423 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 12783; Actual Q2: 12765; Actual Q3: 12442; Actual Q4: 12596; Actual Q1: 12592; Actual Q2: 12507 | 12596 | 12596 | 12596 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 231; Actual Q2: 229; Actual Q3: 240; Actual Q4: 241; Actual Q1: 239; Actual Q2: 238 | 241 | 241 | 241 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 804; Actual Q2: 804; Actual Q3: 793; Actual Q4: 796; Actual Q1: 798; Actual Q2: 795 | 796 | 796 | 796 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 1052; Actual Q2: 1052; Actual Q3: 1137; Actual Q4: 1141; Actual Q1: 1142; Actual Q2: 1139 | 1141 | 1141 | 1141 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 306; Actual Q2: 305; Actual Q3: 217; Actual Q4: 221; Actual Q1: 219; Actual Q2: 217 | 221 | 221 | 221 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 3534; Actual Q2: 3530; Actual Q3: 3565; Actual Q4: 3578; Actual Q1: 3575; Actual Q2: 3575 | 3578 | 3578 | 3578 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 1708; Actual Q2: 1707; Actual Q3: 1663; Actual Q4: 1690; Actual Q1: 1692; Actual Q2: 1682 | 1690 | 1690 | 1690 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 365; Actual Q2: 362; Actual Q3: 355; Actual Q4: 352; Actual Q1: 352; Actual Q2: 352 | 352 | 352 | 352 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 469; Actual Q2: 467; Actual Q3: 472; Actual Q4: 473; Actual Q1: 474; Actual Q2: 473 | 473 | 473 | 473 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 422; Actual Q2: 421; Actual Q3: 427; Actual Q4: 426; Actual Q1: 427; Actual Q2: 426 | 426 | 426 | 426 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 61; Actual Q2: 61; Actual Q3: 56; Actual Q4: 56; Actual Q1: 56; Actual Q2: 56 | 56 | 56 | 56 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 1926; Actual Q2: 1929; Actual Q3: 1953; Actual Q4: 1960; Actual Q1: 1958; Actual Q2: 1948 | 1960 | 1960 | 1960 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 726; Actual Q2: 720; Actual Q3: 697; Actual Q4: 697; Actual Q1: 700; Actual Q2: 696 | 697 | 697 | 697 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 210; Actual Q2: 209; Actual Q3: 212; Actual Q4: 213; Actual Q1: 213; Actual Q2: 213 | 213 | 213 | 213 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 113; Actual Q2: 114; Actual Q3: 110; Actual Q4: 110; Actual Q1: 110; Actual Q2: 109 | 110 | 110 | 110 | Number of critical facilities | 2023 - 2025 projected data is same as Q4 2022.
| 4. Residential customers | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q4: 1228424; Actual Q1: 1229724; Actual Q2: 1231399 | 1228424 | 1228424 | 1228424 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q4: 2546192; Actual Q1: 2549096; Actual Q2: 2553229 | 2546192 | 2546192 | 2546192 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q4: 403265; Actual Q1: 404074; Actual Q2: 405118 | 403265 | 403265 | 403265 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q4: 312685; Actual Q1: 313767; Actual Q2: 315321 | 312685 | 312685 | 312685 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q4: 10408; Actual Q1: 10394; Actual Q2: 10432 | 10408 | 10408 | 10408 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 10820; Actual Q1: 10834; Actual Q2: 10844 | 10820 | 10820 | 10820 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q4: 72042; Actual Q1: 72080; Actual Q2: 72145 | 72042 | 72042 | 72042 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 3444; Actual Q1: 3450; Actual Q2: 3448 | 3444 | 3444 | 3444 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q4: 195912; Actual Q1: 196090; Actual Q2: 196559 | 195912 | 195912 | 195912 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 27026; Actual Q1: 27087; Actual Q2: 27096 | 27026 | 27026 | 27026 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 17101; Actual Q1: 17051; Actual Q2: 17037 | 17101 | 17101 | 17101 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 8508; Actual Q1: 8508; Actual Q2: 8517 | 8508 | 8508 | 8508 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q4: 27234; Actual Q1: 27267; Actual Q2: 27317 | 27234 | 27234 | 27234 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 1868; Actual Q1: 1869; Actual Q2: 1865 | 1868 | 1868 | 1868 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q4: 105782; Actual Q1: 105924; Actual Q2: 106039 | 105782 | 105782 | 105782 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 9687; Actual Q1: 9683; Actual Q2: 9690 | 9687 | 9687 | 9687 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 9558; Actual Q1: 9559; Actual Q2: 9568 | 9558 | 9558 | 9558 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 1602; Actual Q1: 1603; Actual Q2: 1602 | 1602 | 1602 | 1602 | Number of residential customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
| 5. Commercial customers | 5.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q4: 107089; Actual Q1: 107064; Actual Q2: 107190 | 107089 | 107089 | 107089 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q4: 322682; Actual Q1: 322608; Actual Q2: 323043 | 322682 | 322682 | 322682 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q4: 60055; Actual Q1: 60032; Actual Q2: 60091 | 60055 | 60055 | 60055 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q4: 165601; Actual Q1: 165618; Actual Q2: 165897 | 165601 | 165601 | 165601 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q4: 1990; Actual Q1: 1983; Actual Q2: 1979 | 1990 | 1990 | 1990 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 12653; Actual Q1: 12661; Actual Q2: 12651 | 12653 | 12653 | 12653 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q4: 3952; Actual Q1: 3945; Actual Q2: 3942 | 3952 | 3952 | 3952 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 750; Actual Q1: 752; Actual Q2: 756 | 750 | 750 | 750 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q4: 19648; Actual Q1: 19648; Actual Q2: 19655 | 19648 | 19648 | 19648 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 10370; Actual Q1: 10370; Actual Q2: 10395 | 10370 | 10370 | 10370 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 1921; Actual Q1: 1913; Actual Q2: 1916 | 1921 | 1921 | 1921 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 3174; Actual Q1: 3183; Actual Q2: 3188 | 3174 | 3174 | 3174 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q4: 1717; Actual Q1: 1707; Actual Q2: 1706 | 1717 | 1717 | 1717 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 200; Actual Q1: 200; Actual Q2: 193 | 200 | 200 | 200 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q4: 8774; Actual Q1: 8765; Actual Q2: 8776 | 8774 | 8774 | 8774 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 3252; Actual Q1: 3255; Actual Q2: 3260 | 3252 | 3252 | 3252 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 786; Actual Q1: 782; Actual Q2: 778 | 786 | 786 | 786 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 5.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 503; Actual Q1: 500; Actual Q2: 503 | 503 | 503 | 503 | Number of commercial customers | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
| 6. AFN customers | 6.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 57130; Actual Q2: 57517; Actual Q3: 62046; Actual Q4: 342839; Actual Q1: 341635; Actual Q2: 341606 | 342839 | 342839 | 342839 | Number of customers belonging to access and functional needs populations | Unable to provide data for previous quarters due to system limitation of PG&E's GIS Real Time Database. The customer projection is the same as Q4 2022 Metric.
|  | 6.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 116384; Actual Q2: 116958; Actual Q3: 115578; Actual Q4: 868502; Actual Q1: 859948; Actual Q2: 859852 | 868502 | 868502 | 868502 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 23983; Actual Q2: 24103; Actual Q3: 25519; Actual Q4: 113761; Actual Q1: 113019; Actual Q2: 112973 | 113761 | 113761 | 113761 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 19689; Actual Q2: 19819; Actual Q3: 19353; Actual Q4: 119491; Actual Q1: 117964; Actual Q2: 117928 | 119491 | 119491 | 119491 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 472; Actual Q2: 472; Actual Q3: 516; Actual Q4: 3083; Actual Q1: 3016; Actual Q2: 3016 | 3083 | 3083 | 3083 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 502; Actual Q2: 504; Actual Q3: 494; Actual Q4: 3324; Actual Q1: 3270; Actual Q2: 3269 | 3324 | 3324 | 3324 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 3370; Actual Q2: 3389; Actual Q3: 3716; Actual Q4: 13473; Actual Q1: 13535; Actual Q2: 13534 | 13473 | 13473 | 13473 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 387; Actual Q2: 386; Actual Q3: 167; Actual Q4: 634; Actual Q1: 629; Actual Q2: 628 | 634 | 634 | 634 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 14192; Actual Q2: 14307; Actual Q3: 14779; Actual Q4: 57174; Actual Q1: 55940; Actual Q2: 55962 | 57174 | 57174 | 57174 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 1519; Actual Q2: 1539; Actual Q3: 1479; Actual Q4: 6113; Actual Q1: 6001; Actual Q2: 5992 | 6113 | 6113 | 6113 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 955; Actual Q2: 944; Actual Q3: 942; Actual Q4: 4747; Actual Q1: 4656; Actual Q2: 4651 | 4747 | 4747 | 4747 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 337; Actual Q2: 341; Actual Q3: 368; Actual Q4: 1995; Actual Q1: 1936; Actual Q2: 1927 | 1995 | 1995 | 1995 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 1276; Actual Q2: 1303; Actual Q3: 1337; Actual Q4: 4563; Actual Q1: 4601; Actual Q2: 4602 | 4563 | 4563 | 4563 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 90; Actual Q2: 91; Actual Q3: 89; Actual Q4: 399; Actual Q1: 399; Actual Q2: 398 | 399 | 399 | 399 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 7115; Actual Q2: 7171; Actual Q3: 7333; Actual Q4: 28288; Actual Q1: 28091; Actual Q2: 28043 | 28288 | 28288 | 28288 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 394; Actual Q2: 400; Actual Q3: 456; Actual Q4: 2002; Actual Q1: 1975; Actual Q2: 1969 | 2002 | 2002 | 2002 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 334; Actual Q2: 335; Actual Q3: 351; Actual Q4: 1906; Actual Q1: 1864; Actual Q2: 1863 | 1906 | 1906 | 1906 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
|  | 6.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 70; Actual Q2: 72; Actual Q3: 73; Actual Q4: 348; Actual Q1: 356; Actual Q2: 356 | 348 | 348 | 348 | Number of customers belonging to access and functional needs populations | AFN Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Previous quarter's data were carried over from the previous QDR submissions. 2023 - 2025 projection is the same as Q4 2022 Metric.
| 7. Substations | 7.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 87; Actual Q2: 87; Actual Q3: 98; Actual Q4: 87; Actual Q1: 87; Actual Q2: 87 | 87 | 87 | 87 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 216; Actual Q2: 216; Actual Q3: 205; Actual Q4: 216; Actual Q1: 216; Actual Q2: 216 | 216 | 216 | 216 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 67; Actual Q2: 67; Actual Q3: 69; Actual Q4: 67; Actual Q1: 67; Actual Q2: 67 | 67 | 67 | 67 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 305; Actual Q2: 305; Actual Q3: 303; Actual Q4: 305; Actual Q1: 305; Actual Q2: 305 | 305 | 305 | 305 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 4; Actual Q2: 4; Actual Q3: 6; Actual Q4: 4; Actual Q1: 4; Actual Q2: 4 | 4 | 4 | 4 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 61; Actual Q2: 61; Actual Q3: 59; Actual Q4: 61; Actual Q1: 61; Actual Q2: 61 | 61 | 61 | 61 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 11; Actual Q2: 11; Actual Q3: 12; Actual Q4: 11; Actual Q1: 11; Actual Q2: 11 | 11 | 11 | 11 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 5; Actual Q2: 5; Actual Q3: 4; Actual Q4: 5; Actual Q1: 5; Actual Q2: 5 | 5 | 5 | 5 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 35; Actual Q2: 35; Actual Q3: 35; Actual Q4: 34; Actual Q1: 34; Actual Q2: 35 | 34 | 34 | 34 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 64; Actual Q2: 64; Actual Q3: 64; Actual Q4: 65; Actual Q1: 65; Actual Q2: 64 | 65 | 65 | 65 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 17; Actual Q2: 17; Actual Q3: 15; Actual Q4: 17; Actual Q1: 17; Actual Q2: 17 | 17 | 17 | 17 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 54; Actual Q2: 54; Actual Q3: 56; Actual Q4: 52; Actual Q1: 52; Actual Q2: 52 | 52 | 52 | 52 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 18; Actual Q2: 18; Actual Q3: 22; Actual Q4: 18; Actual Q1: 18; Actual Q2: 18 | 18 | 18 | 18 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 28; Actual Q2: 28; Actual Q3: 24; Actual Q4: 28; Actual Q1: 28; Actual Q2: 28 | 28 | 28 | 28 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 4; Actual Q2: 4; Actual Q3: 5; Actual Q4: 4; Actual Q1: 4; Actual Q2: 4 | 4 | 4 | 4 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
|  | 7.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 16; Actual Q2: 16; Actual Q3: 15; Actual Q4: 17; Actual Q1: 17; Actual Q2: 16 | 17 | 17 | 17 | Number of substations | 2023 - 2025 projected data is same as Q4 2022.
| 8. Weather stations | 8.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 15; Actual Q2: 18; Actual Q3: 18; Actual Q4: 20; Actual Q1: 21; Actual Q2: 23 | 20 | 20 | 20 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 7; Actual Q2: 8; Actual Q3: 11; Actual Q4: 20; Actual Q1: 20; Actual Q2: 25 | 20 | 20 | 20 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 57; Actual Q2: 58; Actual Q3: 64; Actual Q4: 61; Actual Q1: 61; Actual Q2: 63 | 61 | 61 | 61 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 141; Actual Q2: 136; Actual Q3: 139; Actual Q4: 150; Actual Q1: 150; Actual Q2: 166 | 150 | 150 | 150 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 7; Actual Q2: 9; Actual Q3: 8; Actual Q4: 10; Actual Q1: 10; Actual Q2: 10 | 10 | 10 | 10 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 43; Actual Q2: 49; Actual Q3: 53; Actual Q4: 53; Actual Q1: 53; Actual Q2: 57 | 53 | 53 | 53 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 10; Actual Q2: 9; Actual Q3: 9; Actual Q4: 9; Actual Q1: 9; Actual Q2: 9 | 9 | 9 | 9 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 8; Actual Q2: 7; Actual Q3: 7; Actual Q4: 7; Actual Q1: 7; Actual Q2: 7 | 7 | 7 | 7 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 174; Actual Q2: 179; Actual Q3: 180; Actual Q4: 182; Actual Q1: 182; Actual Q2: 182 | 182 | 182 | 182 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 355; Actual Q2: 339; Actual Q3: 354; Actual Q4: 355; Actual Q1: 357; Actual Q2: 362 | 355 | 355 | 355 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 31; Actual Q2: 31; Actual Q3: 30; Actual Q4: 33; Actual Q1: 33; Actual Q2: 33 | 33 | 33 | 33 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 177; Actual Q2: 203; Actual Q3: 228; Actual Q4: 221; Actual Q1: 220; Actual Q2: 220 | 221 | 221 | 221 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 6; Actual Q2: 7; Actual Q3: 7; Actual Q4: 7; Actual Q1: 7; Actual Q2: 7 | 7 | 7 | 7 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 3; Actual Q2: 4; Actual Q3: 2; Actual Q4: 5; Actual Q1: 5; Actual Q2: 5 | 5 | 5 | 5 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 114; Actual Q2: 113; Actual Q3: 111; Actual Q4: 115; Actual Q1: 114; Actual Q2: 115 | 115 | 115 | 115 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 139; Actual Q2: 136; Actual Q3: 147; Actual Q4: 138; Actual Q1: 139; Actual Q2: 145 | 138 | 138 | 138 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 13; Actual Q2: 12; Actual Q3: 12; Actual Q4: 12; Actual Q1: 12; Actual Q2: 12 | 12 | 12 | 12 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
|  | 8.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 23; Actual Q2: 30; Actual Q3: 33; Actual Q4: 34; Actual Q1: 35; Actual Q2: 35 | 34 | 34 | 34 | Number of weather stations | 2023 - 2025 projected data is same as Q4 2022.
Updated comments for Table 7 (2/1/2023): AFN Data in Q4 2022 onward has been adjusted to reflect the AFN definition as stated in the 2022 WMP. Residental and Commerical Customer data has been provided starting with out Q4 2022 submsision. PG&E’s GIS system is a dynamic ‘real-time’ system that reflects the current assets in PG&E’s service territory, hence data will continue to change as our system evolves. Projected Data are missing inthis submission. PG&E plans to continue to work on providing this level of detail in future quarterly submissions as we enhance our backend reporting. Updated comments for Table 7 (11/1/2022): Updated WUI Dataset that was released in Sept 2022 for data as of 2020 provided by the University of Wisconsin-Madison SILVIS Lab, available here: http://silvis.forest.wisc.edu/data/wui-change/ and https://www.fs.usda.gov/rds/archive/catalog/RDS-2015-0012-3 Updated comments for Table 7 (5/2/2022): Please note that we added Undergrounding mileage starting with our Q1 2022 submission. PG&E is using 2020 Census data and which has impacted the Urban, Rural and Highly Rural layers starting with our Q1 2022 submission. Comments for Table 7: Table 7 seeks information regarding the current baseline state of HFTD and non-HFTD service territory, as located in urban versus rural versus highly rural areas, including a subset with the Wildland-Urban Interface (WUI). The WUI is defined as areas where homes are built near or among lands prone to wildland fires. PG&E identifies WUI areas within PG&E’s service territory based upon data provided by the University of Wisconsin-Madison SILVIS Lab, available here: http://silvis.forest.wisc.edu/data/wui-change/, shows the WUI areas within California as of 2020. Customers belonging to AFN (Access and Functional Needs) population dataset is based on Medical Baseline Customers only and does not reflect the revision of AFN definition in the 2022 WMP for data prior to Q3 2022. This is due to the system limitation of the data within the various systems that are not currently connected to the enterprise GIS database. Data in Q4 2022 onward has been adusted to reflect the AFN definition as stated in the 2022 WMP. Substation count includes facility type: Distribution Switching station, Junction, Power House, Power Plant, Substation & Transmission Switching Station. PG&E’s GIS system is a dynamic ‘real-time’ system that reflects the current assets in PG&E’s service territory, hence data will continue to change as our system evolves.

## Table 8
| Utility | PG&E |  |  |  |  | Notes:
| Table No. | 8 |  |  |  |  | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
| Date Modified | 2023-08-01 |  |  |  |  | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
[7 empty] | Actual | [15 empty] | Projected
| Table 8: Location of utility equipment additions or removal | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Planned net addition (or removal) - overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 77.7539; Actual Q2: 216.7905; Actual Q3: 362.8445; Actual Q4: 364.3071; Actual Q1: 284.509; Actual Q2: 290.7246 | -1.7999 | -16.2889 | 0 | Circuit miles
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: -122.7144; Actual Q2: 310.7988; Actual Q3: -402.6884; Actual Q4: -398.1833; Actual Q1: -283.9726; Actual Q2: -267.9704 | 0 | -3.5683 | 0 | Circuit miles
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: -54.2679; Actual Q2: -136.4592; Actual Q3: 18.2223; Actual Q4: 15.4164; Actual Q1: 72.0146; Actual Q2: 76.0363 | -60.992 | -29.2196 | -7.0463 | Circuit miles
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 294.3551; Actual Q2: -152.1228; Actual Q3: 218.0391; Actual Q4: 208.1333; Actual Q1: -83.2317; Actual Q2: -72.4463 | -17.9376 | -4.9181 | -14.7448 | Circuit miles
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: -31.7962; Actual Q2: -100.6808; Actual Q3: -38.6525; Actual Q4: -38.9735; Actual Q1: -6.2529; Actual Q2: -4.268 | -4.1272 | 0 | -1.2885 | Circuit miles
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: -208.4805; Actual Q2: -191.771; Actual Q3: -203.7283; Actual Q4: -201.6449; Actual Q1: 7.5589; Actual Q2: 7.3325 | -8.5642 | -9.8912 | -16.0253 | Circuit miles
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: -18.1806; Actual Q2: 4.8202; Actual Q3: 17.9973; Actual Q4: 17.5283; Actual Q1: 35.643; Actual Q2: 36.099 | -7.0284 | -1.115 | 0 | Circuit miles
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: -12.8572; Actual Q2: 11.0539; Actual Q3: -50.4076; Actual Q4: -51.2465; Actual Q1: -39.2643; Actual Q2: -37.6899 | -6.6406 | 0 | 0 | Circuit miles
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: -21.2125; Actual Q2: 34.6079; Actual Q3: -72.4754; Actual Q4: -85.7584; Actual Q1: -71.1704; Actual Q2: -71.4361 | -80.1994 | -125.3836 | -124.5661 | Circuit miles
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: -252.1787; Actual Q2: 16.0334; Actual Q3: -189.5083; Actual Q4: -193.0276; Actual Q1: 35.122; Actual Q2: 37.6402 | -28.8992 | -12.0311 | -59.7219 | Circuit miles
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 27.2217; Actual Q2: -54.1224; Actual Q3: -58.4413; Actual Q4: -60.0349; Actual Q1: -93.1137; Actual Q2: -86.7204 | -6.3142 | -1.6631 | -1.6106 | Circuit miles
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 244.0487; Actual Q2: -46.8645; Actual Q3: 302.9306; Actual Q4: 291.7032; Actual Q1: 35.0519; Actual Q2: 53.5299 | -49.5734 | -20.693 | -39.003 | Circuit miles
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: -8.2618; Actual Q2: -17.8923; Actual Q3: -5.344; Actual Q4: -5.5396; Actual Q1: 0.38504; Actual Q2: 1.3437 | -4.1528 | -8.9503 | -3.2373 | Circuit miles
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: -2.5126; Actual Q2: -1.8301; Actual Q3: -4.5029; Actual Q4: -4.8021; Actual Q1: -2.4633; Actual Q2: -2.3471 | 0 | -2.448 | 0 | Circuit miles
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: -101.588; Actual Q2: -58.4767; Actual Q3: -187.0652; Actual Q4: -191.1782; Actual Q1: -111.6341; Actual Q2: -100.7381 | -59.1051 | -177.1368 | -205.5004 | Circuit miles
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: -84.1945; Actual Q2: -22.7458; Actual Q3: -16.4323; Actual Q4: -22.5273; Actual Q1: 43.2696; Actual Q2: 51.0148 | -12.9045 | -36.6931 | -77.2559 | Circuit miles
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 83.1338; Actual Q2: 36.7417; Actual Q3: 79.8929; Actual Q4: 79.4229; Actual Q1: -3.701; Actual Q2: -2.5937 | -0.074433 | 0 | 0 | Circuit miles
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 64.5528; Actual Q2: 1.1892; Actual Q3: 64.1567; Actual Q4: 56.439; Actual Q1: -9.0443; Actual Q2: -6.5389 | -1.6873 | 0 | 0 | Circuit miles
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 20.0007; Actual Q2: 31.6373; Actual Q3: 72.8357; Actual Q4: 73.2506; Actual Q1: 55.1904; Actual Q2: 53.5091 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 3.3702; Actual Q2: 124.7566; Actual Q3: -58.0524; Actual Q4: -59.3888; Actual Q1: -60.9481; Actual Q2: -60.3146 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: -27.6167; Actual Q2: -25.2866; Actual Q3: -31.4455; Actual Q4: -27.5075; Actual Q1: -5.4232; Actual Q2: -5.5538 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 104.3117; Actual Q2: -22.103; Actual Q3: 128.0786; Actual Q4: 145.4369; Actual Q1: -10.0919; Actual Q2: -8.7507 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 4.2774; Actual Q2: -4.8176; Actual Q3: 5.0319; Actual Q4: 5.0048; Actual Q1: 0.72688; Actual Q2: 0.72712 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: -109.1609; Actual Q2: -132.2514; Actual Q3: -135.4441; Actual Q4: -122.2861; Actual Q1: -5.8389; Actual Q2: -5.8502 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: -3.328; Actual Q2: 1.8031; Actual Q3: 7.8273; Actual Q4: 10.4522; Actual Q1: 14.6314; Actual Q2: 13.8184 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: -4.5495; Actual Q2: 9.544; Actual Q3: -23.0065; Actual Q4: -18.6986; Actual Q1: -13.7904; Actual Q2: -14.4319 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 6.6771; Actual Q2: 22.427; Actual Q3: 31.1134; Actual Q4: 35.2134; Actual Q1: 25.1834; Actual Q2: 24.4419 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: -49.4159; Actual Q2: 23.3978; Actual Q3: -78.2202; Actual Q4: -65.2379; Actual Q1: -22.3832; Actual Q2: -22.5077 | 0 | 0 | 0 | Circuit miles
x |  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: -4.7889; Actual Q2: -24.127; Actual Q3: -11.0737; Actual Q4: -11.0059; Actual Q1: -6.3349; Actual Q2: -5.1894 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 54.7943; Actual Q2: -42.7461; Actual Q3: 41.3023; Actual Q4: 41.1937; Actual Q1: -30.5305; Actual Q2: -19.7958 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: -4.6073; Actual Q2: -2.3899; Actual Q3: -1.1975; Actual Q4: -1.1521; Actual Q1: 2.8239; Actual Q2: 2.8237 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 1.1631; Actual Q2: 9.0251; Actual Q3: -1.5418; Actual Q4: -1.6292; Actual Q1: -2.7923; Actual Q2: -2.8229 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 2.6716; Actual Q2: 9.2725; Actual Q3: 16.6531; Actual Q4: 18.3112; Actual Q1: 7.6106; Actual Q2: 7.6429 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: -32.9284; Actual Q2: -16.0498; Actual Q3: -47.9639; Actual Q4: -44.928; Actual Q1: -17.7135; Actual Q2: -15.894 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: -1.4016; Actual Q2: -8.4327; Actual Q3: 2.136; Actual Q4: 2.146; Actual Q1: 4.2039; Actual Q2: 4.2039 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 34.4729; Actual Q2: 1.3622; Actual Q3: 21.9021; Actual Q4: 21.9081; Actual Q1: -12.4695; Actual Q2: -12.4686 | 0 | 0 | 0 | Circuit miles
x | 2. Planned net addition (or removal) - underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 684.7326; Actual Q2: 686.8156 | 1.7999 | 16.2889 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: -565.8135; Actual Q2: -558.4283 | 0 | 3.5683 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 261.7303; Actual Q2: 262.9472 | 60.992 | 29.2196 | 7.0463 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: -140.8401; Actual Q2: -131.2561 | 17.9376 | 4.9181 | 14.7448 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 5.1471; Actual Q2: 5.6892 | 4.1272 | 0 | 1.2885 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 4.0906; Actual Q2: 0.22163 | 8.5642 | 9.8912 | 16.0253 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 37.61; Actual Q2: 38.0516 | 7.0284 | 1.115 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: -31.8111; Actual Q2: -33.3892 | 6.6406 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 60.1276; Actual Q2: 59.8985 | 80.1994 | 125.3836 | 124.5661 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: -10.5495; Actual Q2: -8.568 | 28.8992 | 12.0311 | 59.7219 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 1.0765; Actual Q2: 1.0532 | 6.3142 | 1.6631 | 1.6106 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 4.002; Actual Q2: 4.7965 | 49.5734 | 20.693 | 39.003 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 4.7188; Actual Q2: 2.4406 | 4.1528 | 8.9503 | 3.2373 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: -0.82557; Actual Q2: -0.91165 | 0 | 2.448 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 47.5328; Actual Q2: 38.2669 | 59.1051 | 177.1368 | 205.5004 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 26.1985; Actual Q2: 21.5698 | 12.9045 | 36.6931 | 77.2559 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0.30974; Actual Q2: 0.40164 | 0.074433 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 1.2897; Actual Q2: 0.62571 | 1.6873 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 0; Actual Q2: 2.6425 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 0; Actual Q2: -1.9403 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 2.7349 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: -2.7346 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0.33294 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: -0.33294 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 0; Actual Q2: 0.62432 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: -0.62435 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 0; Actual Q2: 0.035523 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: -0.035526 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
|  | 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit miles |  | See note 3 for columns I - L.
| 3. Planned net addition (or removal) - Substations | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q3: 13; Actual Q4: 54; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q3: -7; Actual Q4: -48; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q3: 1; Actual Q4: -9; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q3: -3; Actual Q4: 7; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q3: 2; Actual Q4: -3; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q3: -6; Actual Q4: -1; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q3: 1; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q3: -2; Actual Q4: -1; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q3: 0; Actual Q4: -1; Actual Q1: -1; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q3: -3; Actual Q4: -4; Actual Q1: 1; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q3: -2; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q3: 8; Actual Q4: 4; Actual Q1: -2; Actual Q2: -2 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q3: 4; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q3: -8; Actual Q4: -4; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q3: 1; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q3: 3; Actual Q4: 5; Actual Q1: 1; Actual Q2: 0 | 0 | 0 | 0 | Number of substations |  | See note 2 for columns I - J.
| 4. Planned net addition (or removal) - Weather stations | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 3; Actual Q2: 5; Actual Q3: 4; Actual Q4: 5; Actual Q1: 6; Actual Q2: 5 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 1; Actual Q2: 2; Actual Q3: 4; Actual Q4: 13; Actual Q1: 13; Actual Q2: 17 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 15; Actual Q2: 12; Actual Q3: 10; Actual Q4: 4; Actual Q1: 4; Actual Q2: 5 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 36; Actual Q2: 18; Actual Q3: 0; Actual Q4: 10; Actual Q1: 9; Actual Q2: 30 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 2; Actual Q2: 3; Actual Q3: 1; Actual Q4: 3; Actual Q1: 3; Actual Q2: 1 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 9; Actual Q2: 10; Actual Q3: 11; Actual Q4: 10; Actual Q1: 10; Actual Q2: 8 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: -1; Actual Q3: -1; Actual Q4: -1; Actual Q1: -1; Actual Q2: 0 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 1; Actual Q2: 0; Actual Q3: -1; Actual Q4: -1; Actual Q1: -1; Actual Q2: 0 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 45; Actual Q2: 26; Actual Q3: 9; Actual Q4: 8; Actual Q1: 8; Actual Q2: 3 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 77; Actual Q2: 22; Actual Q3: 10; Actual Q4: 2; Actual Q1: 2; Actual Q2: 23 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 2; Actual Q2: 0; Actual Q3: -1; Actual Q4: 2; Actual Q1: 2; Actual Q2: 2 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 39; Actual Q2: 47; Actual Q3: 63; Actual Q4: 46; Actual Q1: 43; Actual Q2: 17 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 1; Actual Q3: 1; Actual Q4: 1; Actual Q1: 1; Actual Q2: 0 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 1; Actual Q2: 2; Actual Q3: -1; Actual Q4: 2; Actual Q1: 2; Actual Q2: 1 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 22; Actual Q2: 11; Actual Q3: 1; Actual Q4: 1; Actual Q1: 0; Actual Q2: 2 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 23; Actual Q2: 6; Actual Q3: 11; Actual Q4: -1; Actual Q1: 0; Actual Q2: 9 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 5; Actual Q2: 3; Actual Q3: 0; Actual Q4: -1; Actual Q1: -1; Actual Q2: 0 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
|  | 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 4; Actual Q2: 11; Actual Q3: 10; Actual Q4: 11; Actual Q1: 12; Actual Q2: 5 | 0 | 0 | 0 | Number of weather stations |  | See note 1 for columns Y - AA
Comments for Table 8: The 2022 Actual Data was derived by subtracting the 2021 data from the 2022 data in Table 8, and reflects the total net change in the system year-over-year. Data for net change for underground is not provided since PG&E did not provide underground data in 2021. The data presented for 2020 and 2021 Transmission and Distribution removals/additions represents the work for removal of idle facilities. There are many other reasons that conductor may be added or removed. The same layers used in Table 7 have been used to determine Population Density, HFTD, and WUI. Notes for Table 8: The data presented in this table are based on the best knowledge that PG&E has as of January 31, 2023. As better data becomes available, this will be updated in the quarterly updates. Note 1: PG&E's has reached its weather station goal of the installation of 1,300 by the end of 2021. For Weather Station additional and removals for 2023, project prioritization and timing have not been fully determined or mapped. Note 2: The substation count was refined after the submission of our May 5, 2021 self-identification letter relating to substation inspections. Since substations are facilities in which significant amounts of equipment is installed, a single installation date for this field cannot be provided. As a result, PG&E is unable to provide year-over-year data for 2021 because the dataset used in 2021 is different than that from 2020 and would cause discrepancies in the data set. However, PG&E will be able to report the year-over-year data for 2022 and all future years since this standardized counting method will allow for an accurate comparison of annual substation data going forward. Note 3: Data for net change for underground is not provided since PG&E did not provide underground data in 2021. PG&E’s GIS system is a dynamic ‘real-time’ system that reflects the current assets in PG&E’s service territory, therefore our GIS data does not reflect data from previous years that we had not report on / previously extracted.

## Table 9
| Utility | PG&E
| Table No. | 9
| Date Modified | 2023-08-01
[7 empty] | Actual | [15 empty] | Projected
| Table 9: Location of utility infrastructure upgrades | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Number of overhead circuit miles planned for upgrade | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | [16 empty] | 0 | 2.9463 | 0.63921 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q2: 0.10265 | 0.072307 | 0.054043 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 1.4504; Actual Q2: 7.8223 | 5.8877 | 1.1039 | 7.7555 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 1.4716; Actual Q2: 5.0186 | 8.2065 | 3.9307 | 3.4888 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | [16 empty] | 0 | 0 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0.32292; Actual Q2: 2.2975 | 2.8335 | 0 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q2: 0.64432 | 0 | 0 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q2: 0.46629 | 0 | 0 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 4.2989; Actual Q2: 26.1799 | 56.5624 | 40.6489 | 23.5525 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0.91269; Actual Q2: 7.7521 | 14.8522 | 17.7973 | 10.2544 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q2: 1.2106 | 4.7387 | 8.2083 | 0.39468 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0.73902; Actual Q2: 12.1119 | 8.691 | 0.094941 | 2.5838 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | [16 empty] | 0 | 0 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | [16 empty] | 0 | 0 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 0.36193; Actual Q2: 5.0915 | 3.3797 | 0.14314 | 0.41062 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1.1286; Actual Q2: 5.7307 | 3.0906 | 0.072582 | 0.88178 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0.28977; Actual Q2: 0.13617 | 0.17603 | 0 | 0.038701 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q2: 1.1403 | 1.5094 | 0 | 0 | Circuit miles | Projected data for 2023-2025 is based on the level of work assumed for WMP target commitment. PG&E plans to update this data in future quarterly submissions as we refine our workplan that will account for project planning, readiness, and execution schedule updates. | See note 5 for columns I - L.
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | [19 empty] | Circuit miles |  | See note 1 for columns I - X. See note 4 for columns Y - AA.
x | 2. Number of substations planned for upgrades | 2.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 1; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 1; Actual Q2: 0 | 1 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 1; Actual Q4: 0; Actual Q1: 0; Actual Q2: 1 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
|  | 2.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 |  |  | Number of substations |  | PG&E is in the process of refining the substation upgrade plan for 2024 - 2025 and will provide any updates in future submissions.
| 3. Number of weather stations planned for upgrades | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | [19 empty] | Number of weather stations |  | See note 2 for columns I - AA
Comments for Table 9: The data presented in this table are based on the best knowledge that PG&E has as of January 31, 2023. As better data becomes available, this will be updated in the quarterly updates. Note 1: PG&E replaced or removed approximately 38 miles of transmission conductor in 2022, but all jobs have not been mapped into the GIS system in order to break the data down as required by this table. Note 2: PG&E plans to do some power upgrades on some weather stations in 2023, but projects have not been mapped as of March 2023 therefore its' projection will not be included in this dataset. If we have any planned upgrades, we'll provide it in the future quarterly updates. PG&E does not track weather station upgrades in this granularity and will provide any updates in future submissions. Note 3: PG&E is in the process of planning the Distribution system hardening work for 2023 - 2025. Note 4: PG&E does not have an equivalent "system hardening" program for transmission conductor, but PG&E is planning to replace or remove 43 HFTD miles in 2023, and 5 HFTD miles in 2025. The preliminarily planned jobs have not been mapped in order to break the data down for this table. Note 5: PG&E hardened 483 miles in 2022, but not all projects have been mapped as of January 2023 and therefore may not be included in this data. Other comments: 1) The same layers used in Table 8 have been used to determine Population Density, HFTD, and WUI.

## Table 10
Utility | PG&E |  | Notes:
Table No. | 10 |  | "PSPS" = Public Safety Power Shutoff
Date Modified | 2023-08-01 |  | In future submissions update planned upgrade numbers with actuals
|  |  |  | Actual | [15 empty] | Projected
Table 10: Recent use of PSPS and other PSPS metrics |  |  |  | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Wind Warning Status | Metric name | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Recent use of PSPS and fast-trip | 1.a. | RFW only | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 2 | 2 | 2 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
|  | HWW only | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
|  | HWW & RFW | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 1.8 | 1.8 | 1.8 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
|  | All (regardless of RFW/HWW status) | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 3.8 | 3.8 | 3.8 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
| 1.b. | RFW only | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 134.4 | 134.4 | 134.4 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
|  | HWW only | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
|  | HWW & RFW | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 324.6 | 324.6 | 324.6 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
|  | All (regardless of RFW/HWW status) | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 459 | 459 | 459 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
| 1.c. | RFW only | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 2795135.801 | 2763550.7661 | 2724861.055 | Customer hours per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022. Assumes 11 hours of non-weather outage duration, comprised of 1 hour of switching time prior to weather start and 10 hours of patrol and restoration time after weather All Clear. Total durations decrease each year 2023-2025 due to additional mitigations (MSO Device Replacements and Undergrounding) planned for implementation in each of these years.
|  | HWW only | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Customer hours per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022. Assumes 11 hours of non-weather outage duration, comprised of 1 hour of switching time prior to weather start and 10 hours of patrol and restoration time after weather All Clear. Total durations decrease each year 2023-2025 due to additional mitigations (MSO Device Replacements and Undergrounding) planned for implementation in each of these years.
|  | HWW & RFW | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 9526845.295 | 9419171.854 | 9287303.448 | Customer hours per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022. Assumes 11 hours of non-weather outage duration, comprised of 1 hour of switching time prior to weather start and 10 hours of patrol and restoration time after weather All Clear. Total durations decrease each year 2023-2025 due to additional mitigations (MSO Device Replacements and Undergrounding) planned for implementation in each of these years.
|  | All (regardless of RFW/HWW status) | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 12321981.096 | 12182722.6201 | 12012164.503 | Customer hours per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022. Assumes 11 hours of non-weather outage duration, comprised of 1 hour of switching time prior to weather start and 10 hours of patrol and restoration time after weather All Clear. Total durations decrease each year 2023-2025 due to additional mitigations (MSO Device Replacements and Undergrounding) planned for implementation in each of these years.
| 1.d. | RFW only | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 31; Actual Q3: 6; Actual Q4: 1; Actual Q1: 0; Actual Q2: 0 | 37.6 | 36.8 | 36 | Number of events | These forecasts are based on an estimated annual decrease of 2%.
|  | HWW only | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of events | These forecasts are based on an estimated annual decrease of 2%.
|  | HWW & RFW | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Number of events | These forecasts are based on an estimated annual decrease of 2%.
|  | None | Frequency of fast-trip events (total) | Actual Q1: 4; Actual Q2: 548; Actual Q3: 1319; Actual Q4: 466; Actual Q1: 7; Actual Q2: 228 | 2312.4 | 2263.2 | 2214 | Number of events | These forecasts are based on an estimated annual decrease of 2%.
| 1.e | RFW only | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 391; Actual Q3: 10091; Actual Q4: 104693; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit mile days | Meterological technology to forecast more than 1-2 weeks into the future still does not exist; EPSS does not have enough data for a 3-year historical average
|  | HWW only | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 20; Actual Q2: 16; Actual Q3: 0; Actual Q4: 75; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit mile days | Meterological technology to forecast more than 1-2 weeks into the future still does not exist; EPSS does not have enough data for a 3-year historical average
|  | HWW & RFW | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 80; Actual Q1: 0; Actual Q2: 0 | 0 | 0 | 0 | Circuit mile days | Meterological technology to forecast more than 1-2 weeks into the future still does not exist; EPSS does not have enough data for a 3-year historical average
|  | None | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 10239; Actual Q2: 1962929; Actual Q3: 3999301; Actual Q4: 1848540; Actual Q1: 4462; Actual Q2: 683207 | 0 | 0 | 0 | Circuit mile days | Meterological technology to forecast more than 1-2 weeks into the future still does not exist; EPSS does not have enough data for a 3-year historical average
2. Customer hours of PSPS and other outages | 2.a. | N/A | Customer hours of planned outages including PSPS (total) | Actual Q1: 1019782.4; Actual Q2: 1108699.9667; Actual Q3: 1032835.8333; Actual Q4: 867315.0167; Actual Q1: 427466.25; Actual Q2: 1270111.35 | 11265868.55 | 11265868.55 | 11265868.55 | Total customer hours of planned outages per year | For Actual: Historical PSPS and non-PSPS outage data. For Projected: Based on 3-year historical average.
| 2.b. | N/A | Customer hours of unplanned outages, not including PSPS or fast-trip (total) | Actual Q1: 2890302.1167; Actual Q2: 3777409.0667; Actual Q3: 4371825.4167; Actual Q4: 9390476.3333; Actual Q1: 48817792.4167; Actual Q2: 2794520.8833 | 33804724.6167 | 33804724.6167 | 33804724.6167 | Total customer hours of unplanned outages, not including PSPS or fast-trip, per year | For Actual: Historical PSPS and non-PSPS outage data. For Projected: Based on 3-year historical average.
| 2.c. | N/A | Customer hours of unplanned outages resulting from fast-trip | Actual Q1: 4635.8167; Actual Q2: 1808385.2; Actual Q3: 3893762.8; Actual Q4: 911271.1333; Actual Q1: 18301.6333; Actual Q2: 687038.8333 | 0 | 0 | 0 | Total customer hours of outages due to fast-trip per year | For Actual: Historical PSPS and non-PSPS outage data. For Projected: Based on 3-year historical average.
| 2.d. | N/A | System Average Interruption Duration Index (SAIDI) (including PSPS) | Actual Q1: 41.1; Actual Q2: 70.3; Actual Q3: 97.6; Actual Q4: 117.3; Actual Q1: 517.4; Actual Q2: 50.3 | 7.9494 | 7.9494 | 7.9494 | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | For Actual: Historical PSPS and non-PSPS outage data. For Projected: Based on 3-year historical average. Data is reported in minutes.
| 2.e. | N/A | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | Actual Q1: 41.1; Actual Q2: 70.3; Actual Q3: 97.6; Actual Q4: 117.3; Actual Q1: 517.4; Actual Q2: 50.3 | 6.4578 | 6.4578 | 6.4578 | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served | For Actual: Historical PSPS and non-PSPS outage data. For Projected: Based on 3-year historical average. Data is reported in minutes.
| 2.f. | N/A | System Average Interruption Frequency Index (SAIFI) (including PSPS) | Actual Q1: 0.3; Actual Q2: 0.5; Actual Q3: 0.6; Actual Q4: 0.464; Actual Q1: 0.988; Actual Q2: 0.344 | 1.7237 | 1.7237 | 1.7237 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | For Actual: Historical PSPS and non-PSPS outage data. For Projected: Based on 3-year historical average.
| 2.g. | N/A | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | Actual Q1: 0.3; Actual Q2: 0.5; Actual Q3: 0.6; Actual Q4: 0.464; Actual Q1: 0.988; Actual Q2: 0.344 | 1.678 | 1.678 | 1.678 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | For Actual: Historical PSPS and non-PSPS outage data. For Projected: Based on 3-year historical average.
3. Critical infrastructure impacted by PSPS | 3.a. | N/A | Critical infrastructure impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 231908.4893 | 229287.7073 | 226077.6795 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
4. Community outreach of PSPS metrics | 4.a. | N/A | # of customers impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 317151.1924 | 313527.2054 | 309137.8245 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022. Customer counts decrease each year 2023-2025 due to additional mitigations (MSO Device Replacements and Undergrounding) planned for implementation in each of these years.
| 4.b. | N/A | # of medical baseline customers impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 24586.4934 | 24307.802 | 23967.4928 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022. Medical Baseline customer counts decrease each year 2023-2025 due to additional mitigations (MSO Device Replacements and Undergrounding) planned for implementation in each of these years.
| 4.c. | N/A | # of customers notified prior to initiation of PSPS event | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 456339.1389 | 451124.695 | 444808.9492 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | For Actual: No PSPS events that required de-energization in 2022. Consistent with past reporting, does not include events in which no customers were de-energized. For Projected: This is larger than the number of customers impacted (4a), because it includes additional customers who were notified but not de-energized.
| 4.d. | N/A | # of medical baseline customers notified prior to initiation of PSPS event | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 35054.0358 | 34656.6933 | 34171.4996 | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | For Actual: No PSPS events that required de-energization in 2022. Consistent with past reporting, does not include events in which no customers were de-energized. For Projected: This is larger than the number of Medical Baseline customers impacted (4b), because it includes additional customers who were notified but not de-energized.
| 4.e. | N/A | # of customers notified prior to a PSPS event impacting them | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 317151.1924 | 313527.2054 | 309137.8245 | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | For Actual: No PSPS events that required de-energization in 2022. Consistent with past reporting, does not include events in which no customers were de-energized. For Projected: PG&E plans to notify all customers prior to their de-energization in a PSPS event.
| 4.f. | N/A | # of medical baseline customers notified prior to a PSPS event impacting them | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 24586.4934 | 24307.802 | 23967.4928 | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | For Actual: No PSPS events that required de-energization in 2022. Consistent with past reporting, does not include events in which no customers were de-energized. For Projected: PG&E plans to notify all Medical Baseline customers prior to their de-energization in a PSPS event.
5. Other PSPS metrics | 5.a. | N/A | Number of PSPS events in which a notification was sent but no de-energization occurred | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1; Actual Q1: 0; Actual Q2: 0 | 1 | 1 | 1 | Number of events | For Actual: Based on the October 22, 2022 Weather Event, which did not result in de-energization. For Projected: Based on the historical average of Weather Events which resulted in notifications but not de-energization, in the years 2020-2022.
| 5.b. | N/A | Average number of customers located on de-energized circuit | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 3525.567 | 3525.567 | 3525.567 | Number of customers | For Actual: No PSPS events that required de-energization in 2022. For Projected: This was calculated by summing the total active customers on de-energized circuits for all events in a given quarter, divided by the number of de-energized circuit-events in the same quarter. The list of impacted circuits is based on 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
| 5.c. | N/A | Customer hours of PSPS per RFW OH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 57.8194 | 57.1659 | 56.3656 | =1.c. / RFW OH circuit mile days in time period | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year historical average.
|  | N/A | Customer hours of PSPS per HWW OH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 1170.2931 | 1157.0665 | 1140.8675 | =1.c. / HWW OH circuit mile days in time period | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year historical average.
|  | N/A | Customer hours of PSPS per high FPIOH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 11.1452 | 11.0192 | 10.865 | =1.c. / FPI OH circuit mile days in time period | For Actual: No PSPS events that required de-energization in 2022. For Projected: Based on 5-year historical average.
| 5.d. | N/A | Median time between de-energization, due to PSPS, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 50 | 50 | 50 | Time between de-energization and inspection on a circuit-segment basis in hours | For Actual: No PSPS events that required de-energization in 2022. For Projected: This is calculated based on the time between the start of de-energization due to PSPS, and the start of inspection. Durations are based on the 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
| 5.e. | N/A | 95 percentile of time between de-energization, due to PSPS, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 88 | 88 | 88 | Time between de-energization and inspection on a circuit-segment basis in hours | For Actual: No PSPS events that required de-energization in 2022. For Projected: This is calculated based on the time between the start of de-energization due to PSPS, and the start of inspection. Durations are based on the 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022.
| 5.f. | N/A | Median time between de-energization, due to fast-trip, and inspection of a circuit segment | Actual Q1: 1.3167; Actual Q2: 3.5333; Actual Q3: 3.2833; Actual Q4: 3.1167; Actual Q1: 0.8; Actual Q2: 38 | 0 | 0 | 0 | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.g. | N/A | 95 percentile of time between de-energization, due to fast-trip, and inspection of a circuit segment | Actual Q1: 4.6; Actual Q2: 15.6; Actual Q3: 15.2; Actual Q4: 16.9; Actual Q1: 2.35; Actual Q2: 87.1 | 0 | 0 | 0 | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.h. | N/A | Number of risk events occurring on a de-energized circuit | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0 | 225.0284 | 225.0284 | 225.0284 | Number of risk events | For Actual: No PSPS events that required de-energization in 2022. For Projected: The number of risk events is based on the number of damages and hazards, as reported in post de-energization reports for past PSPS events. The list of events is based on the 5-year lookback analysis, which applies 2022 PSPS guidance and existing mitigations to the weather conditions seen in 2018-2022. For lookback events which do not align with a past PSPS event, the number of risk events is approximated using the number of sustained outages which occured during the hypothetical lookback event scope and duration, filtered to only include the types of outages which would have resulted in a damage or hazard (as reported in post de-energization reports).
Comments for Table 10: PG&E has outlined the past and forecasted PSPS metrics in Table 10, which is utilizing historic recorded data for actuals and an analysis of the past ten years of weather data to provide the forecasted metrics. Please see the Comments column of Table 10 for specific details regarding the actual and projected methodology for each metric.

## Table 11
Utility | PG&E | Notes:
Table No. | 11 | Territory spend refers to the sum total of initiative spending across all areas, including HFTDs. HFTD spend refers to initiative spending applied to HFTDs, and is a subset of territory spend.
Date Modified | 2023-08-01 | CAPEX = Capital expenditure; OPEX = Operating expenditure. | [9 empty] | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
|  | As data is submitted each reporting period, replace projections for the current reporting period with actuals. | [9 empty] | 15: Actual; 31: Projected
The units for the spend data are thousands of dollars.
Table 11: Mitigation initiative financials | [11 empty] | 15: CAPEX ($ thousands); 17: OPEX ($ thousands); 19: CAPEX ($ thousands); 21: OPEX ($ thousands); 23: CAPEX ($ thousands); 25: OPEX ($ thousands); 27: CAPEX ($ thousands); 29: OPEX ($ thousands); 31: CAPEX ($ thousands); 33: OPEX ($ thousands); 35: CAPEX ($ thousands); 37: OPEX ($ thousands); 39: CAPEX ($ thousands); 41: OPEX ($ thousands)
[12 empty] | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | Primary driver targeted | Secondary driver targeted | Year initiated | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compiance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Comments | 15: 2019; 19: 2020; 23: 2021; 27: 2022; 31: 2023; 35: 2024; 39: 2025 | Blank Meaning
Grid Design, Operations, and Maintenance | Asset Inspections | AI-01, AI-03 | Equipment / facility failure |  | Distribution - 2016 (focused on WMP work) Transmission - 2019 (when WSIP program started in full) Substation - 2019 Wildfire Safety Plan | Distribution - 2023 GRC Transmission - TO Rate Case Substation - 2023 GRC | n/a | Distribution - In compliance with WMP and GO 165 regulations. (Missed Inspections will be tracked and reported to the CPUC) Transmission - Exceeding compliance Substation - Supplemental substation inspections are performed in addition to routine based substation inspections thus exceeding GO 174 compliance. | Distribution - GO 95; GO 165 Transmission - GO 165 IV; GO 95 Rules 18B and 31.2 Substation - GO 174 |  |  | 0 | 0 | 268481.7516 | 225769.2108 | 0 | 0 | 249830.2165 | 92716.8533 | 0 | 0 | 244084.3952 | 112983.8177 | 0 | 0 | 247659.3054 | 138512.8669 | 0 | 0 | 199898.7232 | 96621.1166 | 0 | 0 | 171701.0994 | 79599.6894 | 0 | 0 | 177189.1585 | 82199.6877
Grid Design, Operations, and Maintenance | Asset management and inspection enterprise system(s) | AI-11 | N/A - Foundational | N/A - Foundational | n/a | n/a | n/a | n/a | n/a | Wildfire technology costs are aggregated in financials for "Other - Wildfire" |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Community Outreach and Engagement | Public outreach and education awareness program | CO-01, CO-02 | N/A - Foundational |  | 2018 | De-energization OIR – Phase 3 | n/a | In compliance | De-energization OIR – Phase 3 |  |  | 0 | 0 | 22117.8353 | 22117.8353 | 0 | 0 | 23431.6173 | 23431.6173 | 0 | 0 | 18326.4913 | 18326.4913 | 0 | 0 | 13095.0186 | 13095.0186 | 0 | 0 | 14931.7992 | 14931.7992 | 0 | 0 | 15379.7532 | 15379.7532 | 0 | 0 | 15841.1458 | 15841.1458
Emergency Preparedness | Preparedness and planning for service restoration | EP-01 | All Consequences |  | refer to "Other - PSPS" section 9 | refer to "Other - PSPS" section 9 | refer to "Other - PSPS" section 9 | refer to "Other - PSPS" section 9 | refer to "Other - PSPS" section 9 |  |  | 0 | 0 | 189.1269 | 189.1269 | 0 | 0 | 16156.1589 | 16156.1589 | 0 | 0 | 17796.4476 | 17796.4476 | 0 | 0 | 10351.3177 | 10351.3177 | 0 | 0 | 8700 | 8700 | 0 | 0 | 8961 | 8961 | 0 | 0 | 9229.83 | 9229.83
Emergency Preparedness | Emergency preparedness plan | EP-02, EP-03, EP-04, EP-05, EP-06 | All Consequences |  | <2018 | 2023 GRC | n/a | In Compliance | GO 166; R.96-11-004; R.18-12-005 |  |  | 0 | 0 | 2390.613 | 2390.613 | 0 | 0 | 2988.3181 | 2988.3181 | 0 | 0 | 2964.0722 | 2964.0722 | 0 | 0 | 1621.8857 | 1621.8857 | 0 | 0 | 4119 | 4119 | 0 | 0 | 4242.57 | 4242.57 | 0 | 0 | 4369.8471 | 4369.8471
Grid Design, Operations, and Maintenance | Covered conductor installation | GH-01, GH-02, GH-03 | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, CC - Seismic Scenario |  | 2018 | 2023 GRC | n/a | In Compliance | TD-9001M CH 15 “Fire Area Design Guidance” in addition to all relevant standards; All projects in HFTD/HFRA/Buffer Zones |  |  | 251136.0575 | 251136.0575 | 0 | 0 | 444029.9827 | 444029.9827 | 0 | 0 | 112596.2775 | 112596.2775 | 0 | 0 | 285543.7965 | 285543.7965 | 0 | 0 | 67504.2203 | 67504.2203 | 0 | 0 | 59301.8571 | 59301.8571 | 0 | 0 | 41432.3404 | 41432.3404 | 0 | 0
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | GH-04, GH-05 | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, CC - Seismic Scenario |  | 2019 | 2023 GRC | n/a | In Compliance | UG Design and Construction Standards; All projects in HFTD/HFRA/Buffer Zones |  |  | 66496.895 | 66331.5516 | 0 | 0 | 77562.1 | 72874.2798 | 0 | 0 | 262146.6108 | 252222.4578 | 0 | 0 | 558068.2384 | 550224.5857 | 0 | 0 | 1186600 | 1157350 | 0 | 0 | 1624232.6624 | 1594105.1624 | 0 | 0 | 1878931.225 | 1863415.5625 | 0 | 0
Grid Design, Operations, and Maintenance | Traditional overhead hardening | GH-06, GH-07 | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, CC - Seismic Scenario |  | Distribution - refer to Maintenance program in 8.1.4 Transmission before 2018 | Distribution - refer to Maintenance program in 8.1.4 Transmission - TO rate case | Distribution - refer to Maintenance program in 8.1.4 Transmission - n/a | Distribution - refer to Maintenance program in 8.1.4 Transmission - n/a | Distribution - refer to Maintenance program in 8.1.4 Transmission - n/a | Distribution costs covered in the Maintenance programs, under 8.1.4 |  | 508.0346 | 508.0346 | 0 | 0 | 1060.154 | 1060.154 | 0 | 0 | 24817.0913 | 24817.0913 | 0 | 0 | 7855.7489 | 7855.7489 | 0 | 0 | 19134.1732 | 19134.1732 | 0 | 0 | 8314.5099 | 8314.5099 | 0 | 0 | 20469.3304 | 20469.3304 | 0 | 0
Grid Design, Operations, and Maintenance | Installation of system automation equipment | GH-07 | N/A - Foundational | N/A - Foundational | 2019 | 2023 GRC | n/a | n/a | n/a |  |  | 41099.5935 | 6720.4368 | 0 | 0 | 15750.6482 | 1443.485 | 0 | 0 | 12577.5056 | 7730.8492 | 0 | 0 | 6490.4383 | 4275.0325 | 0 | 0 | 12679.2 | 12679.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | GH-08, GH-09, GH-10 | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, CC - Seismic Scenario |  | 2021 | 2023 GRC | n/a | Non-Exempt Expulsion Fuse Replacement portion - not in compliance, we have non-exempt fuse equipment installed in fire areas. | Non-Exempt Expulsion Fuse Replacement portion - Cal Fire Power Line Fire Prevention Field Guide establishes what is classified as non-exempt; TD-9100P-09 is the estimating standard for equipment in fire areas that references the above guide. |  |  | 82191.0327 | 82081.0393 | 0 | 0 | 141687.9436 | 141300.6067 | 0 | 0 | 121447.0999 | 122032.1985 | 0 | 0 | 90850.735 | 90783.4049 | 0 | 0 | 42299.4215 | 42299.4215 | 0 | 0 | 41058.0969 | 41058.0969 | 0 | 0 | 21928.7323 | 21928.7323 | 0 | 0
Grid Design, Operations, and Maintenance | Quality assurance / quality control | GM-01 | N/A - Foundational | N/A - Foundational | 2020 | 2023 GRC, 2022 WMP | n/a | In Compliance | GO 95 GO 128 GO 165 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 4349 | 2467 | 0 | 0 | 4349 | 2467 | 0 | 0 | 4349 | 2467 | 0 | 0 | 33808.8626 | 32977.9224 | 0 | 0 | 10977.1169 | 10977.1169 | 0 | 0 | 11306.4304 | 11306.4304
Grid Design, Operations, and Maintenance | Open work orders | GM-02, GM-03, GM-04 | Equipment / facility failure |  | refer to 8.1.4 | refer to 8.1.4 | refer to 8.1.4 | refer to 8.1.4 | refer to 8.1.4 | Most of the costs related to "Open Work Orders" are mapped to Maintenance section 8.1.4 |  | 0 | 0 | 5256.9386 | 5256.9386 | 0 | 0 | 3106.4294 | 3106.4294 | 0 | 0 | 5058.2168 | 5058.2168 | 0 | 0 | 1972.9466 | 1972.9466 | 0 | 0 | 3180.6093 | 3180.6093 | 0 | 0 | 3276.0275 | 3276.0275 | 0 | 0 | 3374.3084 | 3374.3084
Grid Design, Operations, and Maintenance | Equipment Settings to Reduce Wildfire Risk (Grid Ops) | GM-06, GM-07 | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, CC - Seismic Scenario |  | 2021 | 2023 GRC | n/a | n/a | n/a |  |  | 56.6213 | 56.6213 | 1835.4004 | 1835.4004 | 4798.2197 | 4798.2197 | 6425.3295 | 6425.3295 | 719.8351 | 719.8351 | 24027.2564 | 24027.2564 | 18049.9693 | 18049.9693 | 87916.0239 | 87916.0239 | 42108.7201 | 42108.7201 | 133428.7944 | 133428.7944 | 39582.1379 | 39582.1379 | 137431.6582 | 137431.6582 | 35708.3443 | 35708.3443 | 141554.6079 | 141554.6079
PSPS | Other - PSPS | PS-01, PS-02, PS-06, PS-07 | Consequence - PSPS | No other consequences reflected | 2018 – PSPS program initiated | 2023 GRC and 2022 WMCE | n/a | In compliance | R.18-12-005 |  |  | 1399.1783 | 1399.1783 | 209124.556 | 209124.556 | 9163.3797 | 9163.3797 | 249248.5438 | 249248.5438 | 6268.9049 | 6268.9049 | 195707.8959 | 195707.8959 | 1862.7631 | 1862.7631 | 41042.292 | 41042.292 | 3963.1799 | 3963.1799 | 93112.0087 | 93112.0087 | 4082.0753 | 4082.0753 | 95905.3689 | 95905.3689 | 4204.5375 | 4204.5375 | 98782.53 | 98782.53
Situational Awareness and Forecasting | Environmental monitoring systems | SA-01 | N/A - Foundational | N/A - Foundational | 2018 | 2023 GRC | n/a | exceeding compliance with regulations | n/a |  |  | 6933.6763 | 6933.6763 | 606.9244 | 606.9244 | 8314.9397 | 8314.9397 | 111.2093 | 111.2093 | 7719.7701 | 7719.7701 | 145.2292 | 145.2292 | 5625.0762 | 5625.0762 | 99.0722 | 99.0722 | 3286.1036 | 3286.1036 | 3126.5412 | 3126.5412 | 3384.6867 | 3384.6867 | 3220.3374 | 3220.3374 | 3486.2274 | 3486.2274 | 3316.9476 | 3316.9476
Situational Awareness and Forecasting | Grid monitoring systems | SA-02, SA-03 | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, CC - Seismic Scenario |  | 2019 | 2023 GRC | n/a | n/a | GO 95 |  |  | 2944.8728 | 2944.8728 | 455.1574 | 455.1574 | 2594.0074 | 2594.0074 | 1469.8419 | 1469.8419 | 8596.9917 | 8596.9917 | 932.4317 | 932.4317 | 11088.2435 | 11088.2435 | 1497.522 | 1497.522 | 7798.159 | 7798.159 | 3329.768 | 3329.768 | 10092.1037 | 10092.1037 | 3429.6611 | 3429.6611 | 10394.8668 | 10394.8668 | 3532.5509 | 3532.5509
Situational Awareness and Forecasting | Weather forecasting | SA-04, SA-05 | N/A - Foundational | N/A - Foundational | 2014 | 2023 GRC | n/a | exceeding compliance with regulations | n/a |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1627.0829 | 1627.0829 | 0 | 0 | 1797.3967 | 1797.3967 | 0 | 0 | 2067.4111 | 2067.4111 | 0 | 0 | 1976.0114 | 1976.0114 | 0 | 0 | 2035.2918 | 2035.2918 | 0 | 0 | 2096.3505 | 2096.3505
Vegetation Management and Inspection | Vegetation Inspections - Transmission | VM-01 | Vegetation Contact |  | <2018 | TO Rate Case | n/a | In compliance | "NERC Standard FAC-003-04; GO 95 Rule 35; PRC 4292; PRC 4293; Transmission Non-Orchard Routine Patrol Procedure (TD-7103P-01)" |  |  | 0 | 0 | 21034.22 | 6394.7002 | 0 | 0 | 22860.655 | 6949.9623 | 0 | 0 | 23507.405 | 23507.405 | 0 | 0 | 24917.176 | 24917.176 | 0 | 0 | 35443.09 | 35443.09 | 0 | 0 | 32890.6 | 32890.6 | 0 | 0 | 32890.6 | 32890.6
Vegetation Management and Inspection | Pole clearing | VM-02 | Vegetation Contact |  | <2018, 2021 | 2023 GRC, 2022 WMP | n/a | In compliance | PRC 4292; Vegetation Control Program Standard (TD-7112S); Vegetation Control Procedure (TD-7112P-01); Vegetation Management Utility Defensible Space Standard (TD-7109S) |  |  | 0 | 0 | 24583.8637 | 18900.1694 | 0 | 0 | 28252.2558 | 18061.7614 | 0 | 0 | 35083.2187 | 26808.3763 | 0 | 0 | 52195.7622 | 41521.75 | 0 | 0 | 31000 | 17049.5 | 0 | 0 | 30228.4774 | 16625.175 | 0 | 0 | 28787.2071 | 15832.4996
Vegetation Management and Inspection | Clearance | VM-03 | Vegetation Contact |  | n/a | n/a | n/a | n/a | n/a | refer to 8.2.3.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Fall-in mitigation | VM-04 | Vegetation Contact |  | 2023 | n/a | n/a | n/a | GO 95 Rule 35; PRC 4292; PRC 4293 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123997 | 123997 | 0 | 0 | 156365.8066 | 156365.8066 | 0 | 0 | 148910.4066 | 148910.4066
Vegetation Management and Inspection | Substation defensible space | VM-05, VM-06, VM-07 | Vegetation Contact |  | 2019 | 2023 GRC, 2022 WMP | n/a | In compliance | California PRC 4291; Substation Defensible Space Procedure LAND-4001P-01 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 4327.6907 | 4327.6907 | 0 | 0 | 6160.8633 | 6160.8633 | 0 | 0 | 5091.1372 | 5091.1372 | 0 | 0 | 4836.0004 | 4836.0004 | 0 | 0 | 4981.0804 | 4932.8804 | 0 | 0 | 5130.5128 | 5138.7301
Vegetation Management and Inspection | Quality assurance / quality control | VM-08 | N/A - Foundational | N/A - Foundational | <2018, 2019, 2021 | 2023 GRC, 2022 WMP | n/a | n/a | n/a |  |  | 0 | 0 | 9059.5332 | 6288.7141 | 0 | 0 | 8083.0297 | 4358.345 | 0 | 0 | 54549.9209 | 35052.1436 | 0 | 0 | 58849.3422 | 42487.0432 | 0 | 0 | 49251 | 35187.2867 | 0 | 0 | 83460.7858 | 60302.7137 | 0 | 0 | 79481.4404 | 57427.5272
Vegetation Management and Inspection | Open work orders | VM-09 | Vegetation Contact |  | n/a | n/a | n/a | n/a | n/a | cost embedded in 8.2.2.1 and 8.2.2.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Engagement with access and functional needs populations |  | N/A - Foundational |  | 2019 | De-energization OIR – Phase 3 | n/a | In compliance | De-energization OIR – Phase 3, GO 166 |  |  | 0 | 0 | 1798.9138 | 1798.9138 | 255.1762 | 255.1762 | 24890.6211 | 24890.6211 | 36.4711 | 36.4711 | 25774.44 | 25774.44 | 5874.3394 | 5874.3394 | 30836.7581 | 30836.7581 | 4062.5 | 4062.5 | 23346.5806 | 23346.5806 | 4062.5 | 4062.5 | 15546.5806 | 15546.5806 | 4184.375 | 4184.375 | 16012.978 | 16012.978
Community Outreach and Engagement | Collaboration on local wildfire mitigation planning |  | N/A - Foundational |  | 2018 | De-energization OIR – Phase 3 | n/a | In compliance | De-energization OIR – Phase 3 |  |  | 0 | 0 | 7900.0555 | 7900.0555 | 0 | 0 | 9036.1912 | 9036.1912 | 0 | 0 | 10566.0131 | 10566.0131 | 0 | 0 | 10315.173 | 10315.173 | 0 | 0 | 11834.5776 | 11834.5776 | 0 | 0 | 12189.615 | 12189.615 | 0 | 0 | 12555.3034 | 12555.3034
Community Outreach and Engagement | Best practice sharing with other utilities |  | N/A - Foundational |  | 2021 | PSPS OII | n/a | In compliance | Customer Care portion: PSPS OII |  |  | 0 | 0 | 2346.6931 | 2346.6931 | 0 | 0 | 2716.4217 | 2716.4217 | 0 | 0 | 3112.9697 | 3112.9697 | 0 | 0 | 3033.6193 | 3033.6193 | 0 | 0 | 3496.1115 | 3496.1115 | 0 | 0 | 3600.9949 | 3600.9949 | 0 | 0 | 3709.0247 | 3709.0247
Emergency Preparedness | External collaboration and coordination |  | All Consequences |  | 2018 | De-energization OIR – Phase 3 | n/a | In compliance | De-energization OIR – Phase 3 |  |  | 0 | 0 | 11389.1299 | 11389.1299 | 0 | 0 | 13050.336 | 13050.336 | 0 | 0 | 15197.7335 | 15197.7335 | 0 | 0 | 14815.7448 | 14815.7448 | 0 | 0 | 17043.1514 | 17043.1514 | 0 | 0 | 17554.4459 | 17554.4459 | 0 | 0 | 18081.0793 | 18081.0793
Emergency Preparedness | Public emergency communication strategy |  | All Consequences |  | 2018 | De-energization OIR – Phase 3 | n/a | In compliance | De-energization OIR – Phase 3 |  |  | 0 | 0 | 3840.253 | 3840.253 | 0 | 0 | 7224.2167 | 7224.2167 | 0 | 0 | 6879.2394 | 6879.2394 | 0 | 0 | 5978.6615 | 5978.6615 | 0 | 0 | 8109.3037 | 8109.3037 | 0 | 0 | 8352.5828 | 8352.5828 | 0 | 0 | 8603.1603 | 8603.1603
Emergency Preparedness | Customer support in wildfire and PSPS emergencies |  | All Consequences |  | 2018 | De-energization OIR – Phase 3 | n/a | In compliance | De-energization OIR – Phase 3 |  |  | 0 | 0 | 2073.6491 | 2073.6491 | 765.5286 | 765.5286 | 14521.6002 | 14521.6002 | 109.4134 | 109.4134 | 11928.6446 | 11928.6446 | -12.0189 | -12.0189 | 9311.2938 | 9311.2938 | 187.5 | 187.5 | 14780.0164 | 14780.0164 | 193.125 | 193.125 | 15223.4169 | 15223.4169 | 198.9187 | 198.9187 | 15680.1194 | 15680.1194
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events |  | Consequence - PSPS |  | - Distribution - 2019 - Transmission - 2019/2020 | -Distribution - 2023 GRC - Transmission - TO Rate Case | n/a | - Distribution - In compliance per WMP commitments for replacements - Transmission - n/a | n/a |  |  | 33100 | 28491.1392 | 0 | 0 | 44700 | 38475.9494 | 0 | 0 | 24700 | 21260.7595 | 0 | 0 | 28242.9333 | 25901.145 | 0 | 0 | 1455.9022 | 0 | 0 | 0 | 1499.5793 | 0 | 0 | 0 | 1544.5667 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above |  | Contact from object |  | Pertaining to Substation Animal Abatement: 2019 – Wildfire Safety Plan | Pertaining to Substation Animal Abatement: 2023 GRC | n/a | Pertaining to Substation Animal Abatement: Exceeds minimum substation maintenance and inspection requirements within GO 174 | Pertaining to Substation Animal Abatement: GO 174 |  |  | 1708.9731 | 1708.9731 | 457.1145 | 335.6557 | 5960.8386 | 5960.8386 | 1234.79 | 974.0114 | 6598.9343 | 6598.9343 | 649.5368 | 242.2372 | 3443.3024 | 3443.3024 | 616.2575 | 365.8081 | 0 | 0 | 1024.1647 | 764.1681 | 0 | 0 | 1054.8896 | 787.0931 | 0 | 0 | 1086.5363 | 810.7059
Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements |  | Equipment / facility failure |  | <2018 | 2023 GRC | n/a | Not in compliance - due to the backlog of poles to be replaced and reinforced; but have plan to reduce backlog | GO 95 Rule 18 |  |  | 361157.977 | 105813.4526 | 3764.3247 | 0 | 248054.7576 | 127940.7329 | 4783.4683 | 0 | 413620.3631 | 338323.4499 | 2800.1469 | 104.771 | 506322.0386 | 408396.5809 | 3362.5204 | 543.7312 | 425534.6043 | 350306.252 | 5809.3098 | 0 | 903039.8762 | 828396.5163 | 5983.5891 | 0 | 930131.0725 | 853248.4118 | 6163.0968 | 0
Grid Design, Operations, and Maintenance | Transmission pole/tower replacements and reinforcements |  | Equipment / facility failure |  | <2018 | TO Rate Case | n/a | Refer to section 8.1.7.1 and associated target 8.1.1.2 GM-09 for information regarding transmission maintenance notifications. | GO 95 Rule 18 |  |  | 41694.6543 | 22950.0251 | 167411.8598 | 114551.4348 | 63740.489 | 14707.8029 | 93657.0663 | 49029.1608 | 81032.7963 | 12990.9465 | 105907.949 | 45196.9636 | 143534.7034 | 30619.1346 | 93770.5882 | 54595.9668 | 90847.6275 | 18447.657 | 99279.8781 | 10184.1633 | 93573.0563 | 19001.0867 | 102258.2745 | 10489.6882 | 96380.248 | 19571.1193 | 105326.0227 | 10804.3789
Grid Design, Operations, and Maintenance | Emerging grid hardening technology installations and pilots |  | Equipment / facility failure |  | 2020 | 2022 WMP | n/a | not in compliance – we have non-exempt fuse equipment installed in fire areas. | Cal Fire Power Line Fire Prevention Field Guide establishes what is classified as non-exempt. TD-9100P-09 is the estimating standard for equipment in fire areas that references the above guide. |  |  | 0 | 0 | 0 | 0 | 5569.1325 | 5569.1325 | 0 | 0 | 13504.7715 | 13504.7715 | 0 | 0 | 1983.4017 | 1983.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Microgrids |  | Consequence - PSPS |  | 2019 - Dist. Micro, CMEP, MIP, Clean Substation 2019 - Remote Grid | - Dist. Micro, CMEP, MIP, Clean Substation: Microgrid OIR, 2020 GRC, EPIC 3 - Remote Grid: 2023 GRC | - CMEP, MIP, Clean Substation: MGMA/MGBA - Remote Grid: n/a | - Dist. Micro, CMEP, MIP, Clean Substation: In compliance - Remote Grid: in compliance with required filing (Resolution E-5132) | n/a |  |  | 3283.1713 | 3283.1713 | 725.9452 | 725.9452 | 13901.6863 | 13901.6863 | 2149.9013 | 2149.9013 | 15532.2255 | 15532.2255 | 7257.8435 | 7257.8435 | 5226.3028 | 5226.3028 | 5053.9473 | 5053.9473 | 5940.2315 | 5940.2315 | 8338.2782 | 8338.2782 | 4742.361 | 4742.361 | 27935.7745 | 27935.7745 | 6008.213 | 6008.213 | 38299.4646 | 38299.4646
Grid Design, Operations, and Maintenance | Line removals (in HFTD) |  | Contact from object, Vegetation Contact, Contamination, Equipment / facility failure, Other, Unknown, Wire-to-wire contact, Vandalism / Theft, CC - Seismic Scenario |  | Distribution - 2019 Transmission < 2018 | Distribution - 2023 GRC Transmission - Res.SED 6 | n/a | Distribution - In Compliance Transmission - In Compliance | Distribution: De-energization and removal of OH conductor in HFTD/HFRA; Utility Procedure: TD-2459P-01 “Idle Facility Program” Transmission: GO-95 rule 31.6 |  |  | 0 | 0 | 0 | 0 | 196.8593 | 196.8593 | 0 | 0 | 3209.2233 | 3209.2233 | 0 | 0 | 29546.6298 | 12842.9691 | 0 | 0 | 64023.161 | 21568.0233 | 0 | 0 | 2250 | 2250 | 0 | 0 | 2250 | 2250 | 0 | 0
Grid Design, Operations, and Maintenance | Equipment inspections, maintenance, and repair |  | Equipment / facility failure |  | - Distribution < 2018 - Transmission < 2018 - Substation - Circuit Breaker Maintenance and Installation initiative was introduced in the 2020 WMP. | - Distribution and Substation: 2023 GRC - Transmission: TO Rate Case | n/a | - Distribution - Not currently in compliance. Refer to Section 8.1.7.2 and associated target in 8.1.1.X GM-10 for information regarding transmission maintenance notifications. - Transmission - Not currently in compliance. Refer to Section 8.1.7.1 and associated target in 8.1.1.2 GM-09 for information regarding transmission maintenance notifications. - Substation - In Compliance with regulations | - Distribution - GO 95 Rule 18 - Transmission - GO 95 Rule 18 - Substation – CPUC General Order 174; WECC-FAC-501 |  |  | 763889.6811 | 307279.7471 | 385147.2314 | 80620.4247 | 808343.258 | 302200.7298 | 188653.0883 | 86011.5952 | 858659.7323 | 350490.4794 | 196118.5844 | 92508.762 | 989383.1782 | 339110.1198 | 174951.115 | 81067.9249 | 953221.4698 | 455039.1133 | 194884.9182 | 76645.0114 | 935723.2463 | 444679.7828 | 321606.4718 | 204604.5661 | 963794.9437 | 458020.1763 | 331254.6659 | 210742.703
Grid Design, Operations, and Maintenance | Grid Response Procedures and Notifications (Grid Ops) |  | N/A - Foundational | N/A - Foundational | n/a - refer to other sections (8.1.8.1 - EPSS, 8.1.8.2 - Inspections) | n/a - refer to other sections (8.1.8.1 - EPSS, 8.1.8.2 - Inspections) | n/a - refer to other sections (8.1.8.1 - EPSS, 8.1.8.2 - Inspections) | n/a - refer to other sections (8.1.8.1 - EPSS, 8.1.8.2 - Inspections) | n/a - refer to other sections (8.1.8.1 - EPSS, 8.1.8.2 - Inspections) | Refer to 8.1.8.1 where EPSS financials are aggregated, also 8.1.8.2 Inspections |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Grid Design, Operations, and Maintenance | Personnel Work Procedures and Training in Conditions of Elevated Fire Risk (Grid Ops) |  | N/A - Foundational | N/A - Foundational | <2018 | 2022 WMP | n/a | In Compliance | 2021 California Code Public Resources Code - PRC, sections 4427, 4428, 4431 | General Operations |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Grid Design, Operations, and Maintenance | Workforce Planning |  | N/A - Foundational | N/A - Foundational | <2018 | 2023 GRC | n/a | n/a - support function | n/a - support function | General Operations |  | 0 | 0 | 1384.7294 | 1384.7294 | 0 | 0 | 839.8231 | 839.8231 | 0 | 0 | 966.4419 | 966.4419 | 0 | 0 | 808.4113 | 808.4113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overview of the Service Territory | Environmental compliance and permitting |  | N/A - Foundational | N/A - Foundational | <2018 | 2023 GRC | n/a | In Compliance | n/a - governed by various state, federal, local legislation | General Operations - costs are allocated to projects across the company when mitigations happen; so costs are already embedded in various programs and MWCs/MATs |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Risk Methodology and Assessment | Risk Methodology and Assessment |  | N/A - Foundational | N/A - Foundational | 2019 | 2022 WMP | n/a | Risk models - in compliance | n/a |  |  | 6250 | 1933.5264 | 0 | 0 | 6950 | 2150.0814 | 0 | 0 | 8550 | 2645.0641 | 0 | 0 | 10150 | 3140.0469 | 0 | 0 | 10750 | 3325.6654 | 0 | 0 | 11072.5 | 3425.4354 | 0 | 0 | 11404.675 | 3528.1984 | 0 | 0
Situational Awareness and Forecasting | Ignition detection systems |  | N/A - Foundational | N/A - Foundational | 2017 | 2023 GRC | n/a | exceeding compliance with regulations | n/a |  |  | 198.2271 | 198.2271 | 6196.5384 | 6196.5384 | 898.8112 | 898.8112 | 12667.292 | 12667.292 | 14.032 | 14.032 | 13969.7842 | 13969.7842 | 3.5106 | 3.5106 | 18744.056 | 18744.056 | 0 | 0 | 15324.18 | 15324.18 | 0 | 0 | 15783.9054 | 15783.9054 | 0 | 0 | 16257.4226 | 16257.4226
Situational Awareness and Forecasting | Fire potential index |  | N/A - Foundational | N/A - Foundational | 2015 | 2023 GRC | n/a | exceeding compliance with regulations | n/a |  |  | 0 | 0 | 85.8259 | 85.8259 | 0 | 0 | 93.1869 | 93.1869 | 0 | 0 | 134.1519 | 134.1519 | 0 | 0 | 132.1787 | 132.1787 | 0 | 0 | 150.4726 | 150.4726 | 0 | 0 | 154.9867 | 154.9867 | 0 | 0 | 159.6363 | 159.6363
Vegetation Management and Inspection | Vegetation Inspections - Distribution |  | Vegetation Contact |  | <2018 | 2023 GRC, 2022 WMP | n/a | In compliance | GO 95 Rule 35; PRC 4292; PRC 4293; Distribution Routine Patrol Procedure (TD-7102P-01); Distribution Vegetation Management Standard (DVMS) (TD-7102S); ESRB-4; GO 95 Rule 18; Vegetation Management Second Patrol Procedure (TD-7102P-23) |  |  | 0 | 0 | 811978.0915 | 625072.1894 | 0 | 0 | 1110306.8252 | 757404.7133 | 0 | 0 | 1371367.373 | 1043531.6169 | 0 | 0 | 1330439.6905 | 992889.1518 | 0 | 0 | 795246 | 432220.4341 | 0 | 0 | 792337.9285 | 430639.8817 | 0 | 0 | 754559.8725 | 410107.3072
Vegetation Management and Inspection | Vegetation Inspections - Substation |  | Vegetation Contact |  | Substation - 2019 Wildfire Safety Plan | Substation - 2023 GRC | N/A | Substation – Defensible Space inspections and mitigation are performed in addition to routine and supplemental based substation inspections thus exceeding GO 174 compliance. | Substation - GO 174 |  |  | 0 | 0 | 2224.6 | 2224.6 | 0 | 0 | 23.2685 | 23.2685 | 0 | 0 | 2921.5027 | 2921.5027 | 0 | 0 | 2580.7539 | 2580.7539 | 0 | 0 | 3356.6698 | 3356.6698 | 0 | 0 | 3457.3699 | 3457.3699 | 0 | 0 | 3561.091 | 3561.091
Vegetation Management and Inspection | Wood and slash management |  | Vegetation Contact |  | <2018 | 2023 GRC, 2022 WMP | n/a | In compliance | Best Management Practices (BMP) for Vegetation Management Activities (TD-7102P-01-JA01); Wood Management (TD-7102P-26) |  |  | 0 | 0 | 69731.5711 | 68849.9362 | 0 | 0 | 95658.1151 | 94318.2654 | 0 | 0 | 61215.1751 | 60129.9236 | 0 | 0 | 160447.3519 | 158128.1768 | 0 | 0 | 80400 | 79889.9338 | 0 | 0 | 102581.8007 | 101931.0108 | 0 | 0 | 97690.7802 | 97071.0195
Vegetation Management and Inspection | High-risk species |  | Vegetation Contact |  | n/a | n/a | n/a | n/a | n/a | cost embedded in 8.2.2.1 and 8.2.2.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Fire-resilient rights-of-way |  | Vegetation Contact |  | <2018 | TO Rate Case | n/a | In compliance | PG&E 2016 Transmission Maintenance Agreement, approved and enforced by the California Independent System Operator (CAISO); ANSI A300 (Part 7)-2018 Integrated Vegetation Management; State, county, and city weed abatement ordinances |  |  | 0 | 0 | 10156.145 | 3087.6116 | 0 | 0 | 13935.693 | 4236.6477 | 0 | 0 | 14566.504 | 14566.504 | 0 | 0 | 10557.411 | 10557.411 | 0 | 0 | 12837.958 | 12837.958 | 0 | 0 | 12680 | 12680 | 0 | 0 | 12680 | 12680
Vegetation Management and Inspection | Emergency response vegetation management |  | Vegetation Contact |  | <2018 | 2023 GRC, 2022 WMP | n/a | In compliance | Vegetation Management Priority Tag Procedure (TD-7102P-17); Preventing and Mitigating Fires While Performing PG&E Work (TD-1464S) |  |  | 0 | 0 | 3427.6906 | 1828.2037 | 0 | 0 | 5047.0188 | 2735.8267 | 0 | 0 | 8803.926 | 5460.5051 | 0 | 0 | 11314.5479 | 6545.4195 | 0 | 0 | 13000 | 7577.6 | 0 | 0 | 12676.4583 | 7389.01 | 0 | 0 | 12072.0546 | 7036.7078
Vegetation Management and Inspection | Vegetation management enterprise system |  | N/A - Foundational | N/A - Foundational | 2021 | 2023 GRC, 2022 WMP | n/a | n/a | n/a |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8962.0837 | 7868.0096 | 0 | 0 | 16932.7155 | 16614.225 | 0 | 0 | 38798 | 38798 | 0 | 0 | 17552.0191 | 17552.0191 | 0 | 0 | 16715.1525 | 16715.1525
Vegetation Management and Inspection | Workforce Planning |  | N/A - Foundational | N/A - Foundational | n/a | n/a | n/a | n/a | n/a | cost embedded in 8.2.2.1 and 8.2.2.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy Development |  | N/A - Foundational | All Drivers, All Consequences | n/a | n/a | n/a | n/a | n/a | cost partially in Section 6 - Risk Methodology and Assessment |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Other | Other - Wildfire |  | N/A - Foundational | N/A - Foundational | n/a - this section are support projects and programs | 2023 GRC for Wildfire Technology | n/a | n/a - this section are support projects and programs | n/a - this section are support projects and programs |  |  | 52135.3649 | 52135.3649 | 61760.7516 | 61760.7516 | 88804.6079 | 88804.6079 | 71245.0584 | 71245.0584 | 113582.4769 | 113582.4769 | 120538.9625 | 120538.9625 | 89732.4724 | 89732.4724 | 110720.1985 | 110720.1985 | 109538.4214 | 109538.4214 | 115625.5227 | 115625.5227 | 121029.246 | 121029.246 | 118420.832 | 118420.832 | 124660.1233 | 124660.1233 | 121973.457 | 121973.457
Note: The Utility Initiative Tracking ID were provide to align with the provided WMP Initiative Activities, note that not all 2023 WMP Initiative Activities are listed so the Utility Initiative Tracking IDs were match to the most appropriate Initiative Activity. | [11 empty] | 30: Total above; 31: 3050934.5953; 32: 2324538.5413; 33: 2206824.3016; 34: 1492338.5815
[27 empty] | My File | 3050934.5953 | 2324538.5413 | 2206824.3016 | 1492338.5815
[27 empty] | Check | 0 | 0 | 0 | 0

## Table 12
Utility | PG&E | Notes:
Table No. | 12
Date Modified | 2023-08-01
Table 12: WMP Midyear & End-of-Year Targets
Targets
[5 empty] | YTD end of Q2 | YTD end of Q3 | End of year | YTD end of Q2 | YTD end of Q3 | End of year | End of year
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | TargetType | Units | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2025 | Method of Verification | Comments
Grid Design, Operations and Maintenance | Detailed Inspection Transmission – Ground | AI-02 | Quantitative | Transmission Structures | 22417 | 27000 | 27000 | 14400 | 20000 | 20000 | 22000 | Completed work orders
Grid Design, Operations and Maintenance | Detailed Inspection Transmission – Climbing | AI-05 | Quantitative | Transmission Structures | 1429 | 1700 | 1700 | 960 | 1200 | 1200 | 1200 | Completed work orders
Grid Design, Operations and Maintenance | Detailed Inspection Transmission – Aerial | AI-04 | Quantitative | Transmission Structures | 19000 | 24000 | 24000 | 19000 | 20000 | 20000 | 19000 | Completed work orders
Grid Design, Operations and Maintenance | Perform transmission infrared inspections | AI-06 | Quantitative | Miles | 1650 | 3250 | 4000 | 1600 | 3100 | 4000 | 3500 | Completed work orders
Grid Design, Operations and Maintenance | Detailed Inspections - Distribution | AI-07 | Quantitative | Distribution Poles | 30000 | 72532 | 234648 | 190805 | 233501 | 233501 | 244000 | Completed work orders
Grid Design, Operations and Maintenance | Supplemental Inspections - Substation Distribution | AI-08 | Quantitative | Distribution Substations | 46 | 52 | 52 | 68 | 76 | 76 | 78 | Pronto report listing out the three (3) inspection methods, ground, aerial, and infrared
Grid Design, Operations and Maintenance | Supplemental Inspections - Substation Transmission | AI-09 | Quantitative | Transmission Substations | 31 | 34 | 34 | 33 | 36 | 36 | 41 | Pronto report listing out the three (3) inspection methods, ground, aerial, and infrared
Grid Design, Operations and Maintenance | Supplemental Inspections - Hydroelectric Substations and Powerhouses | AI-10 | Quantitative | Hydroelectric Substations and Powerhouses | 41 | 41 | 41 | 45 | 46 | 46 | 40 | Pronto report listing out the three (3) inspection methods, ground, aerial, and infrared | Tule River sub sold to SCE
Community Outreach and Engagement | Community Engagement - Surveys | CO-02 | Quantitative | Surveys | 1 | 1 | 2 | 1 | 1 | 2 | 2 | Survey results and analyses.
Vegetation Management and Inspection | LiDAR Routine Inspections - Transmission | VM-01 | Quantitative | Circuit Miles | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | LiDAR Contractor Work Complete Attestation - (Vegetation Management Project Management Database). Data is uploaded to VMPI2 mobile device for Pre-Inspectors
Vegetation Management and Inspection | Pole Clearing Program | VM-02 | Quantitative | Distribution poles | 57750 | 77503 | 77503 | 47250 | 63000 | 63000 | 52000 | List of all poles in VM database as of October 1, 2022. (PCD2 App) All exceptions must be accordingly documented in the system of record
Vegetation Management and Inspection | Defensible Space Inspections - Distribution Substation | VM-05 | Quantitative | Distribution Substations | 130 | 131 | 131 | 130 | 131 | 131 | 131 | Preventative Notification numbers for each defensible space inspection
Vegetation Management and Inspection | Defensible Space Inspections - Transmission Substation | VM-06 | Quantitative | Transmission Substations | 55 | 55 | 55 | 55 | 55 | 55 | 55 | Preventative Notification numbers for each defensible space inspection
Vegetation Management and Inspection | Defensible Space Inspections - Hydroelectric Substations and Powerhouses | VM-07 | Quantitative | Hydroelectric Substations and Powerhouses | 61 | 61 | 61 | 60 | 60 | 60 | 60 | Preventative Notification numbers for each defensible space inspection | Tule River sub sold to SCE
Grid Design, Operations and Maintenance | Covered conductor installation | GH-01 | Quantitative | Circuit Miles |  |  | 420 |  |  | 470 | 580 | Post-construction projects, use as-built job package and Fire Safe Spans Inspection report (QA report from I-Auditor). In-construction projects, use design construction drawing and Fire Safe Spans Inspection report (QA report from I-Auditor).
Grid Design, Operations and Maintenance | Undergrounding of electric lines and/or equipment | GH-04 | Quantitative | Circuit Miles |  |  | 350 |  |  | 450 | 550 | Post-construction projects, use as-built job package and Fire Safe Spans Inspection report (QA report from I-Auditor). In-construction projects, use design construction drawing and Fire Safe Spans Inspection report (QA report from I-Auditor).
Grid Design, Operations and Maintenance | Traditional overhead hardening - Transmission | GH-05 | Quantitative | Circuit Miles |  |  | 43 |  |  | 0 | 5 | As-built job package.
Grid Design, Operations and Maintenance | Traditional overhead hardening - Transmission | GH-06 | Quantitative | Transmission Lines |  |  | 20 |  |  | 22 | 25 | As-built job package
Grid Design, Operations and Maintenance | Motor Switch Operator (MSO) Switch Replacement | GH-09 | Quantitative | MSOs replacements |  |  | 20 |  |  | 47 | N/A | As-built job package
Grid Design, Operations and Maintenance | Other grid topology improvements to minimize risk of ignitions | GH-08 | Quantitative | Surge Arrestors |  |  | 663 |  |  | N/A | N/A | Completed work orders
Grid Design, Operations and Maintenance | Installation of System Automation Equipment – Distribution EPSS Protective Devices | GH-07 | Quantitative | Distribution Sectionalizing Devices |  |  | 75 |  |  | N/A | N/A | Completed work orders
Grid Design, Operations and Maintenance | Non-Exempt Expulsion Fuses | GH-10 | Quantitative | Fuses |  |  | 3000 |  |  | 3000 | 1500 | Completed work orders
Grid Design, Operations and Maintenance | Open Work Orders - Transmission | GM-02 | Quantitative | Transmission LC Tags |  |  | 16831 |  |  | N/A | N/A | Completed notifications
Grid Design, Operations and Maintenance | Open Work Orders - Distribution | GM-03 | Quantitative | Percent Risk Reduction |  |  | 48% |  |  | 68% | 77% | Completed notifications
Grid Design, Operations and Maintenance | Protective Equipment and Device Settings | GM-06 | Quantitative | Protective Device Controllers or Relays that are DCD capable |  |  | 500 |  |  | 400 | 250 | Report with the number of protective device controllers or relays that were DCD capable
Situational Awareness and Forecasting | Planned Improvements | SA-02 | Quantitative | Circuits |  |  | 40 |  |  | 40 | 40 | Completed job packages
Vegetation Management and Inspection | Fall-in Mitigation | VM-04 | Quantitative | Trees Removed |  |  | 15000 |  |  | 20000 | 25000 | Completed work orders
Vegetation Management and Inspection | Quality Assurance / Quality Control | VM-08 | Quantitative | % Pass Rate |  |  | 0.95 |  |  | 0.95 | 0.95 | QV VM final reports
Emergency Preparedness Plan | Emergency Planning | EP-06 | Quantitative | 1 CERP and 2 wildfire related annexes |  |  | 3 |  |  | 3 | 3 | 1 CERP and 2 wildfire related annexes
Public Safety Power Shutuff | Customer Support in Wildfire and PSPS Emergencies | PS-06 | Quantitative | # of batteries |  |  | 4000 |  |  | 4000 | 4000 | Received waiver from customer. Contractor provided monthly log of deliveries with Account number.
Public Safety Power Shutuff | Performance Metrics Identified by the Electrical Corporation | PS-07 | Quantitative | # of Customer events |  |  | 15000 |  |  | 18000 | 22000 | Customer event reductions as measured by the static 5 year look back impacted by PSPS

## Table 14
Notes
Utility | PG&E | [7 empty] | 1) Ignition likelihood scaled from WDRM v3 to historical CPUC reportable probabilities
Table No. | 14 | [7 empty] | 2) PSPS likelihood is aggregated at the number of annual PSPS events and is represented as the same value for both HFTD and non-HFTD
Date Modified | 2023-03-01
Table 14: HFTD Area Risk Summary
*EC to add all other risk categories to right of last required category.
HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
Non-HFTD Distribution | 855.524 | 656.744 | 198.7799 | 284.7828 | 163.0337 | 42.0053 | 79.7438 | n/a | 4.75 | 2.3061 | n/a | n/a | n/a | 41.8484 | n/a | n/a
HFTD 2 Distribution | 24291.0179 | 22425.256 | 1865.7619 | 177.0372 | 74.7102 | 75.3981 | 26.9288 | n/a | 4.75 | 126.6698 | n/a | n/a | n/a | 392.792 | n/a | n/a
HFTD 3 Distribution | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a* | n/a*
Non-HFTD Transmission | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2
HFTD 2 Transmision | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2
HFTD 3 Transmision | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2 | Note 2
Comments for Table 14: The data presented in this table are based on the best knowledge that PG&E has as of January 31, 2023. As better data becomes available, this will be updated in the quarterly updates. Note 1: Ignition Likelihood Metric: Ignition likelihood scaled from WDRM v3 to historical CPUC reportable probabilities. Note 2: The WTRM currently does not output results in the categories defined in this table. While the WTRM is used to represent risk across PG&E's Transmission System, the WTRM is not currently calibrated with the WDRM and is not fit for use for comparison of risks across multiple domains. Note 3: PSPS Likelihood Metric: PSPS likelihood is aggregated at the number of annual PSPS events and is represented as the same value for both HFTD and non-HFTD. Note 4: PG&E's risk models does not uniquely differentiate HFTD Tier 2 vs Tier 3 in its results, as PG&E sees a wide range of risk consequence in Tier 2 and Tier3. As such PG&E assesses each risk consequence at each pixel, regardless of the Tier 2 and Tier 3 designation. N/A*: Per note 4, PG&E has provided its data in HFTD 2 Distribution row but note that the results also include HFTD 3 Distribution. As such PG&E assesses each risk consequence at each pixel, regardless of the Tier 2 and Tier 3 designation.

## Table 15
Notes
Utility | PG&E | [11 empty] | 1) As described in Section 6.2, Burn Probability is a preliminary step in wildfire calculation, PG&E does not break this apart separately
Table No. | 15 | [11 empty] | 2) PG&E interprets this as Technosylva's Terrain Difficulty Index (TDI), but is not in the current WDRM v3.
Date Modified | 2023-03-01 | [11 empty] | 3) PG&E interprets this as Technosylva's Risk and Associated Value Exposure (RAVE), but is not in the current WDRM v3 and PSPS.
4) ignition likelihood scaled from WDRM v3 to historical CPUC reportable probabilities
Table 15: Top Risk Circuit Scores
*EC to add all other risk categories to right of last required category.
[9 empty] | Note 4 |  |  |  | Note 1 |  |  | Note 2 | Note 3 | Note 3 |  | Note 3 | Note 3
Top- Risk Circuit/ Segment/ Span ID | Risk Granularity | Line Class | Circuit/ Segment/ Span Length (mi) | Inclusion Reason | HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
INDIAN FLAT 1104CB | Circuit Segment | Distribution | 13.7984 | Top 5% Risk | HFTD T2/T3 | 118.4654 | 118.4654 | 0 | 0.092864 | 0.052375 | 0.023498 | 0.016991 | n/a | 0 | 1275.6892 | n/a | n/a | n/a | 0 | n/a | n/a
BONNIE NOOK 1101CB | Circuit Segment | Distribution | 17.8044 | Top 5% Risk | HFTD T2/T3 | 91.2757 | 85.7859 | 5.49 | 0.12592 | 0.049897 | 0.061604 | 0.014418 | n/a | 1.0833 | 681.277 | n/a | n/a | n/a | 5.0676 | n/a | n/a
ALLEGHANY 1102CB | Circuit Segment | Distribution | 18.911 | Top 5% Risk | HFTD T2/T3 | 88.6057 | 86.0352 | 2.57 | 0.13492 | 0.075839 | 0.047435 | 0.01165 | n/a | 0.91667 | 637.6545 | n/a | n/a | n/a | 2.8042 | n/a | n/a
OAKHURST 110310140 | Circuit Segment | Distribution | 18.7573 | Top 5% Risk | HFTD T2/T3 | 88.4072 | 87.6743 | 0.73 | 0.1444 | 0.067327 | 0.061028 | 0.016049 | n/a | 0.16667 | 607.1449 | n/a | n/a | n/a | 4.397 | n/a | n/a
SILVERADO 2104515946 | Circuit Segment | Distribution | 19.0559 | Top 5% Risk | HFTD T2/T3 | 85.6002 | 80.7385 | 4.86 | 0.1818 | 0.077638 | 0.086109 | 0.018052 | n/a | 1.6667 | 444.1088 | n/a | n/a | n/a | 2.917 | n/a | n/a
HIGHLANDS 1102628 | Circuit Segment | Distribution | 15.7833 | Top 5% Risk | HFTD T2/T3 | 75.5797 | 75.4228 | 0.16 | 0.054274 | 0.031724 | 0.0096317 | 0.012919 | n/a | 0.83333 | 1389.6546 | n/a | n/a | n/a | 0.18832 | n/a | n/a
UPPER LAKE 11011276 | Circuit Segment | Distribution | 12.2879 | Top 5% Risk | HFTD T2/T3 | 67.2154 | 67.2154 | 0 | 0.081244 | 0.040321 | 0.031675 | 0.0092482 | n/a | 0 | 827.3291 | n/a | n/a | n/a | 0 | n/a | n/a
MIDDLETOWN 110148212 | Circuit Segment | Distribution | 9.8342 | Top 5% Risk | HFTD T2/T3 | 58.8187 | 58.3023 | 0.52 | 0.061009 | 0.022972 | 0.03152 | 0.0065178 | n/a | 0.41667 | 955.6277 | n/a | n/a | n/a | 1.2392 | n/a | n/a
APPLE HILL 21026552 | Circuit Segment | Distribution | 13.0241 | Top 5% Risk | HFTD T2/T3 | 57.1112 | 55.7622 | 1.35 | 0.073447 | 0.030361 | 0.032036 | 0.01105 | n/a | 0.58333 | 759.2213 | n/a | n/a | n/a | 2.3126 | n/a | n/a
NOTRE DAME 11042028 | Circuit Segment | Distribution | 11.3904 | Top 5% Risk | HFTD T2/T3 | 50.0967 | 49.5273 | 0.57 | 0.055547 | 0.018694 | 0.030871 | 0.0059816 | n/a | 0.83333 | 891.6258 | n/a | n/a | n/a | 0.68325 | n/a | n/a
CLAYTON 221296224 | Circuit Segment | Distribution | 10.1751 | Top 5% Risk | HFTD T2/T3 | 47.284 | 46.8169 | 0.47 | 0.050286 | 0.02571 | 0.016527 | 0.008049 | n/a | 0.66667 | 931.0051 | n/a | n/a | n/a | 0.70065 | n/a | n/a
ANTLER 11011384 | Circuit Segment | Distribution | 10.3375 | Top 5% Risk | HFTD T2/T3 | 46.8765 | 46.4286 | 0.45 | 0.089103 | 0.033176 | 0.043007 | 0.012921 | n/a | 0.083333 | 521.0645 | n/a | n/a | n/a | 5.3748 | n/a | n/a
MONTICELLO 1101654 | Circuit Segment | Distribution | 8.302 | Top 5% Risk | HFTD T2/T3 | 43.061 | 42.0937 | 0.97 | 0.043932 | 0.021006 | 0.013379 | 0.0095464 | n/a | 0.91667 | 958.167 | n/a | n/a | n/a | 1.0552 | n/a | n/a
BALCH NO 1 1101105414 | Circuit Segment | Distribution | 7.471 | Top 5% Risk | HFTD T2/T3 | 42.1929 | 42.179 | 0.01 | 0.02666 | 0.014398 | 0.0047943 | 0.0074682 | n/a | 0.083333 | 1582.0883 | n/a | n/a | n/a | 0.16639 | n/a | n/a
CURTIS 170356972 | Circuit Segment | Distribution | 8.4156 | Top 5% Risk | HFTD T2/T3 | 41.0987 | 40.9418 | 0.16 | 0.032244 | 0.016023 | 0.0053831 | 0.010838 | n/a | 0.083333 | 1269.7508 | n/a | n/a | n/a | 1.8821 | n/a | n/a
MONTICELLO 1101630 | Circuit Segment | Distribution | 4.9383 | Top 5% Risk | HFTD T2/T3 | 41.0785 | 40.1799 | 0.9 | 0.041905 | 0.020098 | 0.013381 | 0.0084256 | n/a | 0.91667 | 958.8298 | n/a | n/a | n/a | 0.98028 | n/a | n/a
PINE GROVE 1101CB | Circuit Segment | Distribution | 5.0523 | Top 5% Risk | HFTD T2/T3 | 31.9963 | 30.9366 | 1.06 | 0.044131 | 0.020752 | 0.01559 | 0.0077891 | n/a | 0.41667 | 701.0238 | n/a | n/a | n/a | 2.5434 | n/a | n/a
BUCKS CREEK 1101CB | Circuit Segment | Distribution | 4.8133 | Top 5% Risk | HFTD T2/T3 | 28.5059 | 28.5059 | 0 | 0.030079 | 0.020746 | 0.006401 | 0.0029323 | n/a | 0 | 947.6914 | n/a | n/a | n/a | 0 | n/a | n/a
SILVERADO 2104646776 | Circuit Segment | Distribution | 5.6861 | Top 5% Risk | HFTD T2/T3 | 26.5899 | 22.9267 | 3.66 | 0.063662 | 0.022366 | 0.035897 | 0.0053984 | n/a | 1.5 | 360.1334 | n/a | n/a | n/a | 2.4421 | n/a | n/a
CALISTOGA 1102131531 | Circuit Segment | Distribution | 5.042 | Top 5% Risk | HFTD T2/T3 | 26.0276 | 25.3574 | 0.67 | 0.054215 | 0.016667 | 0.034367 | 0.0031813 | n/a | 0.83333 | 467.7204 | n/a | n/a | n/a | 0.8042 | n/a | n/a
APPLE HILL 1104CB | Circuit Segment | Distribution | 5.6478 | Top 5% Risk | HFTD T2/T3 | 16.8603 | 15.7803 | 1.08 | 0.042343 | 0.020006 | 0.015804 | 0.0065331 | n/a | 0.5 | 372.6777 | n/a | n/a | n/a | 2.16 | n/a | n/a
MIDDLETOWN 1101171414 | Circuit Segment | Distribution | 3.5913 | Top 5% Risk | HFTD T2/T3 | 16.553 | 16.5203 | 0.03 | 0.023449 | 0.011498 | 0.010033 | 0.0019176 | n/a | 1 | 704.5098 | n/a | n/a | n/a | 0.032703 | n/a | n/a
ELECTRA 1102CB | Circuit Segment | Distribution | 2.6041 | Top 5% Risk | HFTD T2/T3 | 13.9336 | 13.9321 | 0 | 0.021292 | 0.013965 | 0.0026691 | 0.0046577 | n/a | 0.25 | 654.3409 | n/a | n/a | n/a | 0.0061624 | n/a | n/a
ORO FINO 1102CB | Circuit Segment | Distribution | 2.7342 | Top 5% Risk | HFTD T2/T3 | 12.5973 | 12.3594 | 0.24 | 0.020689 | 0.0094052 | 0.009169 | 0.002115 | n/a | 0.91667 | 597.3859 | n/a | n/a | n/a | 0.25945 | n/a | n/a
FRENCH GULCH 1101CB | Circuit Segment | Distribution | 2.7103 | Top 5% Risk | HFTD T2/T3 | 12.2201 | 11.8723 | 0.35 | 0.016126 | 0.010391 | 0.0022013 | 0.0035338 | n/a | 0.16667 | 736.2099 | n/a | n/a | n/a | 2.0868 | n/a | n/a
PARADISE 1103283794 | Circuit Segment | Distribution | 2.5507 | Top 5% Risk | HFTD T2/T3 | 12.1216 | 11.7003 | 0.42 | 0.017189 | 0.0083857 | 0.0054943 | 0.003309 | n/a | 1.25 | 680.6834 | n/a | n/a | n/a | 0.33701 | n/a | n/a
PARADISE 11061212 | Circuit Segment | Distribution | 2.3681 | Top 5% Risk | HFTD T2/T3 | 12.042 | 8.9653 | 3.08 | 0.022286 | 0.010355 | 0.0083336 | 0.0035978 | n/a | 1.0833 | 402.2767 | n/a | n/a | n/a | 2.8401 | n/a | n/a
CRESTA 1101103126 | Circuit Segment | Distribution | 0.87202 | Top 5% Risk | HFTD T2/T3 | 4.9548 | 4.9123 | 0.04 | 0.006334 | 0.0035102 | 0.0022348 | 0.00058905 | n/a | 1.5833 | 775.5367 | n/a | n/a | n/a | 0.026835 | n/a | n/a
CRESTA 1101546650 | Circuit Segment | Distribution | 0.89675 | Top 5% Risk | HFTD T2/T3 | 4.3588 | 4.3447 | 0.01 | 0.0062118 | 0.0041788 | 0.0014636 | 0.0005694 | n/a | 1.5833 | 699.4236 | n/a | n/a | n/a | 0.0089451 | n/a | n/a
MONTICELLO 1101CB | Circuit Segment | Distribution | 0.53696 | Top 5% Risk | HFTD T2/T3 | 3.063 | 3.063 | 0 | 0.0031223 | 0.0018583 | 0.00066244 | 0.00060162 | n/a | 0 | 980.9878 | n/a | n/a | n/a | 0 | n/a | n/a
TIGER CREEK 0201CB | Circuit Segment | Distribution | 0.39611 | Top 5% Risk | HFTD T2/T3 | 2.3021 | 2.2984 | 0 | 0.0025515 | 0.0013444 | 0.001006 | 0.00020108 | n/a | 0.5 | 900.8369 | n/a | n/a | n/a | 0.0072479 | n/a | n/a
INDIAN FLAT 11044440 | Circuit Segment | Distribution | 0.23656 | Top 5% Risk | HFTD T2/T3 | 1.7414 | 1.7414 | 0 | 0.0017945 | 0.0010988 | 0.00037872 | 0.00031702 | n/a | 0 | 970.3859 | n/a | n/a | n/a | 0 | n/a | n/a
CALPINE 1144304 | Circuit Segment | Distribution | 0.046358 | Top 5% Risk | HFTD T2/T3 | 1.714 | 1.703 | 0.01 | 0.0021465 | 0.0016636 | 0.0002979 | 0.00018491 | n/a | 1.4167 | 793.4165 | n/a | n/a | n/a | 0.007736 | n/a | n/a
APPLE HILL 2102CB | Circuit Segment | Distribution | 0.16914 | Top 5% Risk | HFTD T2/T3 | 1.4303 | 1.3798 | 0.05 | 0.0017415 | 0.00083934 | 0.00057424 | 0.00032797 | n/a | 0.58333 | 792.2561 | n/a | n/a | n/a | 0.086734 | n/a | n/a
MIDDLETOWN 1103CB | Circuit Segment | Distribution | 0.052964 | Top 5% Risk | HFTD T2/T3 | 1.0905 | 1.0905 | 0 | 0.0025189 | 0.0016727 | 0.00038566 | 0.00046059 | n/a | 0 | 432.9305 | n/a | n/a | n/a | 0 | n/a | n/a
PLACERVILLE 210658118 | Circuit Segment | Distribution | 0.10823 | Top 5% Risk | HFTD T2/T3 | 0.90325 | 0.89064 | 0.01 | 0.0010404 | 0.00063595 | 0.00016606 | 0.00023836 | n/a | 0.58333 | 856.0784 | n/a | n/a | n/a | 0.021609 | n/a | n/a
BALCH NO 1 1101CB | Circuit Segment | Distribution | 0.0137 | Top 5% Risk | HFTD T2/T3 | 0.81633 | 0.81633 | 0 | 0.00049446 | 0.00023641 | 0.00016333 | 9.4717e-05 | n/a | 0 | 1650.9566 | n/a | n/a | n/a | 0 | n/a | n/a
ALLEGHANY 11021101/2 | Circuit Segment | Distribution | 0.014692 | Top 5% Risk | HFTD T2/T3 | 0.33724 | 0.33724 | 0 | 0.00046721 | 0.00028559 | 0.00013775 | 4.387e-05 | n/a | 0 | 721.8028 | n/a | n/a | n/a | 0 | n/a | n/a
CALPINE 1144962 | Circuit Segment | Distribution | 0.039372 | Top 5% Risk | HFTD T2/T3 | 0.20797 | 0.20797 | 0 | 0.00024846 | 0.00020162 | 1.8626e-05 | 2.8214e-05 | n/a | 0 | 837.0146 | n/a | n/a | n/a | 0 | n/a | n/a
CAMP EVERS 2105BL 2101 | Circuit Segment | Distribution | 0.0032255 | Top 5% Risk | HFTD T2/T3 | 0.091574 | 0.091574 | 0 | 0.006562 | 0.0010484 | 0.0054105 | 0.00010305 | n/a | 0 | 13.9552 | n/a | n/a | n/a | 0 | n/a | n/a
MARIPOSA 2101929360 | Circuit Segment | Distribution | 0.067118 | Top 5% Risk | HFTD T2/T3 | 0.085249 | 0.085249 | 0 | 0.00016024 | 0.00013154 | 5.7355e-06 | 2.2965e-05 | n/a | 0 | 531.9936 | n/a | n/a | n/a | 0 | n/a | n/a