## Effectiveness Analysis Summary
Effectiveness Assesment Interval
Outages From: | 2015
Outages Through: | 2024
Total # of Outage Years | 10
Line No. | System Hardening Mitigations | Blended Average Effectiveness (a) | Notes
2015-2024
1 | Undergrounding All (b) | 99.11% | See "Effectiveness Analysis" tab for supporting data
2 | Undergrounding Primary Distribution Lines (c ) | 97.51% | See "Effectiveness Analysis" tab for supporting data
3 | Line Removal with Remote Grid | 97.51% | See "Effectiveness Analysis" tab for supporting data
4 | Covered Conductor + EPSS + PSPS (d) | 96.57% | Calculated value using formula outlined in footnote (d). See 4a. And 4b. for input data for the calculation and the associated data sources
4a. | Covered Conductor + EPSS + DCD | 78.6% | See "Effectiveness Analysis" tab for supporting data
4b. | PSPS Effectiveness | 84% | See "PSPS_effectiveness_calculation" for supporting data
5 | Covered Conductor + EPSS + DCD | 78.6% | See "Effectiveness Analysis" tab for supporting data
6 | Covered Conductor | 67.07% | See "Effectiveness Analysis" tab for supporting data
(a) This effectiveness evaluation is based on an assessment of each mitigation’s prevention of an ignition from active faults of known cause on overhead assets. Company-initiated outages, including PSPS outages, outages of unknown cause, as well as outages on existing underground assets are not applicable to this study and are excluded from calculation results as “N/A.” (b) Includes distribution primary, secondary, and services line(s). (c) Includes distribution secondary and services parallel to targeted primary line(s). (d) The combined “Overhead with EPSS and PSPS” effectiveness differs from others in the table as it is the result of two independent studies. The first study yields PSPS effectiveness alone to be approximately 84% effective at mitigating wildfire risk. Subsequently, the combined effectiveness of approximately 79% for “Overhead with EPSS” is applied on top of the PSPS reduction, resulting in: Mitigation Effectiveness = 84% + (100% - 84%) * 79% = 97%

## Effectiveness Analysis Detail
|  |  | 1 |  |  |  | 2 |  |  |  | 3 |  |  |  | 4 |  |  |  | 5
|  |  | Undergrounding All |  |  |  | Undergrounding Primary Distribution Lines |  |  |  | Line Removal with Remote Grid |  |  |  | Covered Conductor + EPSS + DCD |  |  |  | Covered Conductor |  |  |  | Average from/through Interval Years
WDRM V4 Subdriver | GRC Driver | GRC Subdriver | Effectiveness | % Eff | 2015 PctVal | Interval PctVal | Effectiveness | % Eff | 2015 PctVal | Interval PctVal | Effectiveness | % Eff | 2015 PctVal | Interval PctVal | Effectiveness | % Eff | 2015 PctVal | Interval PctVal | Effectiveness | % Eff | 2015 PctVal | Interval PctVal | 2015-2024
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.7
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 3.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.5
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.9
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.5
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.5
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.3
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.8
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.6
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.8
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.5
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.6
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.9
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.5
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.8
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | Very High | 90% | 1.44 | 1.44 | 1.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | Medium High | 60% | 0.9 | 0.9 | Medium | 40% | 0.6 | 0.6 | 1.5
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | Medium High | 60% | 0.12 | 0.12 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | Medium High | 60% | 0.12 | 0.12 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Third Party (Balloon) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Balloon) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | Very High | 90% | 0.9 | 0.9 | 1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 7.2 | 7.2 | All | 100% | 7.2 | 7.2 | All | 100% | 7.2 | 7.2 | Very High | 90% | 6.48 | 6.48 | Very High | 90% | 6.48 | 6.48 | 7.2
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Third Party (Balloon) | Contact from object | Balloon contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | HIgh | 70% | 0.07 | 0.07 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Balloon) | Contact from object | Balloon contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | Very High | 90% | 1.71 | 1.71 | Very High | 90% | 1.71 | 1.71 | 1.9
Third Party (other) | Contact from object | Other contact from object | All | 100% | 6.1 | 6.1 | All | 100% | 6.1 | 6.1 | All | 100% | 6.1 | 6.1 | Very High | 90% | 5.49 | 5.49 | Very High | 90% | 5.49 | 5.49 | 6.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | Very High | 90% | 0.9 | 0.9 | 1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | High | 70% | 0.77 | 0.77 | 1.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Third Party (other) | Contact from object | Other contact from object | All | 100% | 17.6 | 17.6 | All | 100% | 17.6 | 17.6 | All | 100% | 17.6 | 17.6 | Medium High | 60% | 10.56 | 10.56 | Medium | 40% | 7.04 | 7.04 | 17.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Third Party (other) | Contact from object | Other contact from object | All | 100% | 19.6 | 19.6 | All | 100% | 19.6 | 19.6 | All | 100% | 19.6 | 19.6 | Very High | 90% | 17.64 | 17.64 | Very High | 90% | 17.64 | 17.64 | 19.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Medium High | 60% | 0.54 | 0.54 | Medium | 40% | 0.36 | 0.36 | 0.9
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | Very High | 90% | 3.15 | 3.15 | Very High | 90% | 3.15 | 3.15 | 3.5
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | Very High | 90% | 0.9 | 0.9 | 1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Medium High | 60% | 0.72 | 0.72 | Medium | 40% | 0.48 | 0.48 | 1.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | Very High | 90% | 2.07 | 2.07 | Very High | 90% | 2.07 | 2.07 | 2.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Medium High | 60% | 0.84 | 0.84 | Medium | 40% | 0.56 | 0.56 | 1.4
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.6 | 0.6 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | 0.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium High | 60% | 0.18 | 0.18 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.9 | 0.9 | Medium High | 60% | 0.54 | 0.54 | Medium High | 60% | 0.54 | 0.54 | Medium High | 60% | 0.54 | 0.54 | Medium | 40% | 0.36 | 0.36 | 0.9
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Third Party (other) | Contact from object | Other contact from object | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Vandalism / Theft | Vandalism / Theft | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (other) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Third Party (other) | Vandalism / Theft | Vandalism / Theft | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | Very High | 90% | 1.08 | 1.08 | 1.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 8.2 | 8.2 | All | 100% | 8.2 | 8.2 | All | 100% | 8.2 | 8.2 | Very High | 90% | 7.38 | 7.38 | Very High | 90% | 7.38 | 7.38 | 8.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Medium High | 60% | 0.54 | 0.54 | Medium | 40% | 0.36 | 0.36 | 0.9
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 2.9 | 2.9 | All | 100% | 2.9 | 2.9 | All | 100% | 2.9 | 2.9 | Very High | 90% | 2.61 | 2.61 | Very High | 90% | 2.61 | 2.61 | 2.9
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Medium High | 60% | 0.66 | 0.66 | Medium | 40% | 0.44 | 0.44 | 1.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 7.9 | 7.9 | All | 100% | 7.9 | 7.9 | All | 100% | 7.9 | 7.9 | Medium High | 60% | 4.74 | 4.74 | Medium | 40% | 3.16 | 3.16 | 7.9
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 6.5 | 6.5 | All | 100% | 6.5 | 6.5 | All | 100% | 6.5 | 6.5 | Very High | 90% | 5.85 | 5.85 | Very High | 90% | 5.85 | 5.85 | 6.5
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | Very High | 90% | 1.89 | 1.89 | Very High | 90% | 1.89 | 1.89 | 2.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | Very High | 90% | 2.43 | 2.43 | Very High | 90% | 2.43 | 2.43 | 2.7
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | Very High | 90% | 1.89 | 1.89 | Very High | 90% | 1.89 | 1.89 | 2.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 2.2 | 2.2 | All | 100% | 2.2 | 2.2 | All | 100% | 2.2 | 2.2 | Very High | 90% | 1.98 | 1.98 | Very High | 90% | 1.98 | 1.98 | 2.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/a | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 5.9 | 5.9 | All | 100% | 5.9 | 5.9 | All | 100% | 5.9 | 5.9 | Very High | 90% | 5.31 | 5.31 | High | 70% | 4.13 | 4.13 | 5.9
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 92.3 | 92.3 | All | 100% | 92.3 | 92.3 | All | 100% | 92.3 | 92.3 | Very High | 90% | 83.07 | 83.07 | High | 70% | 64.61 | 64.61 | 92.3
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | Medium High | 60% | 1.44 | 1.44 | Medium | 40% | 0.96 | 0.96 | 2.4
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 45.8 | 45.8 | All | 100% | 45.8 | 45.8 | All | 100% | 45.8 | 45.8 | Medium High | 60% | 27.48 | 27.48 | Medium | 40% | 18.32 | 18.32 | 45.8
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 3.7 | 3.7 | All | 100% | 3.7 | 3.7 | All | 100% | 3.7 | 3.7 | Medium High | 60% | 2.22 | 2.22 | Medium | 40% | 1.48 | 1.48 | 3.7
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 6 | 6 | All | 100% | 6 | 6 | All | 100% | 6 | 6 | Very High | 90% | 5.4 | 5.4 | High | 70% | 4.2 | 4.2 | 6
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Medium High | 60% | 0.66 | 0.66 | Medium | 40% | 0.44 | 0.44 | 1.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.5 | 0.5 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | 0.5
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.5 | 0.5 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | 0.5
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.3 | 0.3 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | 0.3
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Third Party (Vehicle) | Contact from object | Other contact from object | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Third Party (Vehicle) | Contact from object | Vehicle Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Medium High | 60% | 0.48 | 0.48 | Medium | 40% | 0.32 | 0.32 | 0.8
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | Medium High | 60% | 3.84 | 3.84 | Medium | 40% | 2.56 | 2.56 | 6.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 10.4 | 10.4 | All | 100% | 10.4 | 10.4 | All | 100% | 10.4 | 10.4 | Very High | 90% | 9.36 | 9.36 | Very High | 90% | 9.36 | 9.36 | 10.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 78.5 | 78.5 | All | 100% | 78.5 | 78.5 | All | 100% | 78.5 | 78.5 | Very High | 90% | 70.65 | 70.65 | Very High | 90% | 70.65 | 70.65 | 78.5
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 3.9 | 3.9 | All | 100% | 3.9 | 3.9 | All | 100% | 3.9 | 3.9 | Very High | 90% | 3.51 | 3.51 | Very High | 90% | 3.51 | 3.51 | 3.9
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | High | 70% | 0.7 | 0.7 | 1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | High | 70% | 0.7 | 0.7 | 1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | High | 70% | 0.77 | 0.77 | 1.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 2.2 | 2.2 | All | 100% | 2.2 | 2.2 | All | 100% | 2.2 | 2.2 | Very High | 90% | 1.98 | 1.98 | High | 70% | 1.54 | 1.54 | 2.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 26.9 | 26.9 | All | 100% | 26.9 | 26.9 | All | 100% | 26.9 | 26.9 | Very High | 90% | 24.21 | 24.21 | High | 70% | 18.83 | 18.83 | 26.9
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 3.8 | 3.8 | All | 100% | 3.8 | 3.8 | All | 100% | 3.8 | 3.8 | Very High | 90% | 3.42 | 3.42 | High | 70% | 2.66 | 2.66 | 3.8
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Bird) | 0 | 0 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | High | 70% | 0.84 | 0.84 | 1.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Bird) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | High | 70% | 1.12 | 1.12 | 1.6
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 3 | 3 | All | 100% | 3 | 3 | All | 100% | 3 | 3 | Very High | 90% | 2.7 | 2.7 | High | 70% | 2.1 | 2.1 | 3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | High | 70% | 0.84 | 0.84 | 1.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 10.3 | 10.3 | All | 100% | 10.3 | 10.3 | All | 100% | 10.3 | 10.3 | Very High | 90% | 9.27 | 9.27 | High | 70% | 7.21 | 7.21 | 10.3
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | High | 70% | 0.91 | 0.91 | 1.3
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Bird) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Animal (other) | Contact from object | Animal Contact | All | 100% | 8.8 | 8.8 | All | 100% | 8.8 | 8.8 | All | 100% | 8.8 | 8.8 | Very High | 90% | 7.92 | 7.92 | Very High | 90% | 7.92 | 7.92 | 8.8
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (other) | Contact from object | Animal Contact | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (other) | Contact from object | Animal Contact | All | 100% | 5.1 | 5.1 | All | 100% | 5.1 | 5.1 | All | 100% | 5.1 | 5.1 | Very High | 90% | 4.59 | 4.59 | Very High | 90% | 4.59 | 4.59 | 5.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/a | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | Very High | 90% | 2.43 | 2.43 | High | 70% | 1.89 | 1.89 | 2.7
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Medium High | 60% | 0.6 | 0.6 | Medium | 40% | 0.4 | 0.4 | 1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Animal (other) | Contact from object | Animal Contact | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | Very High | 90% | 1.62 | 1.62 | High | 70% | 1.26 | 1.26 | 1.8
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | High | 70% | 0.21 | 0.21 | Medium High | 60% | 0.18 | 0.18 | 0.3
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 3.7 | 3.7 | All | 100% | 3.7 | 3.7 | All | 100% | 3.7 | 3.7 | Very High | 90% | 3.33 | 3.33 | High | 70% | 2.59 | 2.59 | 3.7
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Animal (other) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (other) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/a | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/a | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Medium High | 60% | 0.54 | 0.54 | Medium | 40% | 0.36 | 0.36 | 0.9
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Medium High | 60% | 0.54 | 0.54 | Medium | 40% | 0.36 | 0.36 | 0.9
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | Very High | 90% | 3.15 | 3.15 | Very High | 90% | 3.15 | 3.15 | 3.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 33.1 | 33.1 | All | 100% | 33.1 | 33.1 | All | 100% | 33.1 | 33.1 | Very High | 90% | 29.79 | 29.79 | Very High | 90% | 29.79 | 29.79 | 33.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | Very High | 90% | 1.71 | 1.71 | High | 70% | 1.33 | 1.33 | 1.9
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | Very High | 90% | 1.35 | 1.35 | High | 70% | 1.05 | 1.05 | 1.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | Very High | 90% | 2.79 | 2.79 | High | 70% | 2.17 | 2.17 | 3.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 7.3 | 7.3 | All | 100% | 7.3 | 7.3 | All | 100% | 7.3 | 7.3 | Very High | 90% | 6.57 | 6.57 | High | 70% | 5.11 | 5.11 | 7.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | High | 70% | 0.77 | 0.77 | 1.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | Very High | 90% | 5.76 | 5.76 | High | 70% | 4.48 | 4.48 | 6.4
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | High | 70% | 1.12 | 1.12 | 1.6
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 45.9 | 45.9 | All | 100% | 45.9 | 45.9 | All | 100% | 45.9 | 45.9 | Very High | 90% | 41.31 | 41.31 | High | 70% | 32.13 | 32.13 | 45.9
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 10.3 | 10.3 | All | 100% | 10.3 | 10.3 | All | 100% | 10.3 | 10.3 | Very High | 90% | 9.27 | 9.27 | High | 70% | 7.21 | 7.21 | 10.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | Very High | 90% | 2.07 | 2.07 | High | 70% | 1.61 | 1.61 | 2.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Medium High | 60% | 0.72 | 0.72 | Medium | 40% | 0.48 | 0.48 | 1.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | High | 70% | 0.63 | 0.63 | 0.9
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 7.9 | 7.9 | All | 100% | 7.9 | 7.9 | All | 100% | 7.9 | 7.9 | Very High | 90% | 7.11 | 7.11 | High | 70% | 5.53 | 5.53 | 7.9
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium High | 60% | 0.06 | 0.06 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | Medium High | 60% | 0.12 | 0.12 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | Very High | 90% | 0.99 | 0.99 | 1.1
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | 0 | 0 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | Very High | 90% | 1.62 | 1.62 | High | 70% | 1.26 | 1.26 | 1.8
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | Very High | 90% | 3.15 | 3.15 | High | 70% | 2.45 | 2.45 | 3.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 7.7 | 7.7 | All | 100% | 7.7 | 7.7 | All | 100% | 7.7 | 7.7 | Very High | 90% | 6.93 | 6.93 | High | 70% | 5.39 | 5.39 | 7.7
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 19.9 | 19.9 | All | 100% | 19.9 | 19.9 | All | 100% | 19.9 | 19.9 | Very High | 90% | 17.91 | 17.91 | High | 70% | 13.93 | 13.93 | 19.9
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | Very High | 90% | 3.78 | 3.78 | High | 70% | 2.94 | 2.94 | 4.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Animal (Squirrel) | Contact from object | Animal Contact | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Animal (Squirrel) | Contact from object | Animal Contact | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Animal (Squirrel) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Primary Conductor - Other | Other | All Other | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.5
Primary Conductor - Line Slap | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Wire Down | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Line Slap | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Wire Down | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Wire Down | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Voltage Control) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Voltage Control) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Switch) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Switch) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Switch) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Wire Down | Other | All Other | All | 100% | 4 | 4 | All | 100% | 4 | 4 | All | 100% | 4 | 4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 4
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.3
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Primary Conductor - Line Slap | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Primary Conductor - Other | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Wire Down | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 2 | 2 | All | 100% | 2 | 2 | All | 100% | 2 | 2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2
Equipment (Support Structure) | Other | All Other | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.5
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5
Equipment (Support Structure) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Switch) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (Transformer) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (DPD) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Primary Conductor - Other | Other | All Other | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.3
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.5
Primary Conductor - Wire Down | Other | All Other | All | 100% | 12.7 | 12.7 | All | 100% | 12.7 | 12.7 | All | 100% | 12.7 | 12.7 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 12.7
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Primary Conductor - Other | Other | All Other | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 5.3
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Line Slap | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Line Slap | Other | All Other | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.2
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (Support Structure) | Other | All Other | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.7
Equipment (Support Structure) | Other | All Other | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.7
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Equipment (Fuse) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Fuse) | Other | All Other | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.3
Equipment (other) | Other | All Other | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Equipment (other) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.2
Equipment (Support Structure) | Other | All Other | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 3.4
Equipment (Support Structure) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (DPD) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Secondary Conductor | Other | All Other | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Secondary Conductor | Other | All Other | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Secondary Conductor | Other | All Other | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Secondary Conductor | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Secondary Conductor | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Secondary Conductor | Other | All Other | All | 100% | 0.4 | 0.4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (Switch) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.2
Equipment (Transformer) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Capacitor) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Capacitor) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Capacitor) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (DPD) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Primary Conductor - Wire Down | Other | All Other | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.3
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.2
Primary Conductor - Other | Other | All Other | All | 100% | 8.6 | 8.6 | All | 100% | 8.6 | 8.6 | All | 100% | 8.6 | 8.6 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 8.6
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Line Slap | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Fuse) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.9
Equipment (Fuse) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.7
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 13.4 | 13.4 | All | 100% | 13.4 | 13.4 | All | 100% | 13.4 | 13.4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 13.4
Equipment (Fuse) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (other) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (other) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.9
Equipment (other) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Primary Conductor - Other | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (other) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (other) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Other | All Other | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (DPD) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (DPD) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (DPD) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Voltage Control) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Secondary Conductor | Other | All Other | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | none | 0% | 0 | 0 | none | 0% | 0 | 0 | 0.1
Secondary Conductor | Other | All Other | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | none | 0% | 0 | 0 | none | 0% | 0 | 0 | 0.1
Secondary Conductor | Other | All Other | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | none | 0% | 0 | 0 | none | 0% | 0 | 0 | 0.2
Equipment (other) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Switch) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Switch) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Switch) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Switch) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | Other | All Other | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | Very High | 90% | 3.24 | 3.24 | High | 70% | 2.52 | 2.52 | 3.6
Equipment (Transformer) | Other | All Other | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Equipment (Transformer) | Other | All Other | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | High | 70% | 0.91 | 0.91 | 1.3
Equipment (Transformer) | Other | All Other | All | 100% | 6.2 | 6.2 | All | 100% | 6.2 | 6.2 | All | 100% | 6.2 | 6.2 | Very High | 90% | 5.58 | 5.58 | High | 70% | 4.34 | 4.34 | 6.2
Equipment (Transformer) | Other | All Other | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | High | 70% | 0.63 | 0.63 | 0.9
Equipment (Transformer) | Other | All Other | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | Very High | 90% | 2.79 | 2.79 | High | 70% | 2.17 | 2.17 | 3.1
Equipment (Transformer) | Other | All Other | All | 100% | 50.7 | 50.7 | All | 100% | 50.7 | 50.7 | All | 100% | 50.7 | 50.7 | Very High | 90% | 45.63 | 45.63 | High | 70% | 35.49 | 35.49 | 50.7
Equipment (Transformer) | Other | All Other | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | High | 70% | 0.84 | 0.84 | 1.2
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Equipment (Transformer) | Other | All Other | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | Very High | 90% | 1.62 | 1.62 | High | 70% | 1.26 | 1.26 | 1.8
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Other | All Other | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | High | 70% | 0.77 | 0.77 | 1.1
Equipment (Transformer) | Other | All Other | All | 100% | 66.5 | 66.5 | All | 100% | 66.5 | 66.5 | All | 100% | 66.5 | 66.5 | Very High | 90% | 59.85 | 59.85 | High | 70% | 46.55 | 46.55 | 66.5
Equipment (Transformer) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Primary Conductor - Wire Down | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Other | All Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Support Structure) | Other | All Other | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (Support Structure) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Support Structure) | Other | All Other | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Support Structure) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (DPD) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | 0 | 0 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Other | All Other | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | Other | All Other | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Primary Conductor - Line Slap | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Wire Down | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Equipment (Support Structure) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | Very High | 90% | 2.79 | 2.79 | Very High | 90% | 2.79 | 2.79 | 3.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Equipment (Voltage Control) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.4 | 0.4 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | 0.4
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | Very High | 90% | 1.35 | 1.35 | High | 70% | 1.05 | 1.05 | 1.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 10.8 | 10.8 | All | 100% | 10.8 | 10.8 | All | 100% | 10.8 | 10.8 | Very High | 90% | 9.72 | 9.72 | High | 70% | 7.56 | 7.56 | 10.8
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | High | 70% | 0.77 | 0.77 | 1.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 3 | 3 | All | 100% | 3 | 3 | All | 100% | 3 | 3 | Very High | 90% | 2.7 | 2.7 | High | 70% | 2.1 | 2.1 | 3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | High | 70% | 0.91 | 0.91 | 1.3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 23.8 | 23.8 | All | 100% | 23.8 | 23.8 | All | 100% | 23.8 | 23.8 | Very High | 90% | 21.42 | 21.42 | High | 70% | 16.66 | 16.66 | 23.8
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | High | 70% | 1.12 | 1.12 | 1.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | High | 70% | 0.91 | 0.91 | 1.3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | Very High | 90% | 1.71 | 1.71 | High | 70% | 1.33 | 1.33 | 1.9
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | High | 70% | 0.28 | 0.28 | Medium High | 60% | 0.24 | 0.24 | 0.4
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | Very High | 90% | 2.52 | 2.52 | Very High | 90% | 2.52 | 2.52 | 2.8
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Medium High | 60% | 0.66 | 0.66 | Medium | 40% | 0.44 | 0.44 | 1.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | High | 70% | 0.49 | 0.49 | Medium High | 60% | 0.42 | 0.42 | 0.7
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 10.5 | 10.5 | All | 100% | 10.5 | 10.5 | All | 100% | 10.5 | 10.5 | High | 70% | 7.35 | 7.35 | Medium High | 60% | 6.3 | 6.3 | 10.5
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | High | 70% | 0.35 | 0.35 | Medium | 40% | 0.2 | 0.2 | 0.5
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | Very High | 90% | 2.52 | 2.52 | High | 70% | 1.96 | 1.96 | 2.8
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | Medium High | 60% | 1.56 | 1.56 | Medium | 40% | 1.04 | 1.04 | 2.6
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Primary Conductor - Line Slap | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Primary Conductor - Wire Down | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | Very High | 90% | 1.35 | 1.35 | Very High | 90% | 1.35 | 1.35 | 1.5
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | High | 70% | 0.84 | 0.84 | 1.2
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | High | 70% | 1.19 | 1.19 | 1.7
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Medium High | 60% | 0.48 | 0.48 | Medium | 40% | 0.32 | 0.32 | 0.8
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | High | 70% | 0.84 | 0.84 | 1.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Contamination | Contamination | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | High | 70% | 1.12 | 1.12 | 1.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 7.7 | 7.7 | All | 100% | 7.7 | 7.7 | All | 100% | 7.7 | 7.7 | Very High | 90% | 6.93 | 6.93 | High | 70% | 5.39 | 5.39 | 7.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 6.2 | 6.2 | All | 100% | 6.2 | 6.2 | All | 100% | 6.2 | 6.2 | Very High | 90% | 5.58 | 5.58 | High | 70% | 4.34 | 4.34 | 6.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | Very High | 90% | 4.77 | 4.77 | Very High | 90% | 4.77 | 4.77 | 5.3
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Equipment (Support Structure) | Equipment / facility failure | Anchor / guy damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (Voltage Control) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Medium High | 60% | 0.6 | 0.6 | Medium | 40% | 0.4 | 0.4 | 1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 5 | 5 | All | 100% | 5 | 5 | All | 100% | 5 | 5 | Medium High | 60% | 3 | 3 | Medium | 40% | 2 | 2 | 5
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Medium High | 60% | 0.6 | 0.6 | Medium | 40% | 0.4 | 0.4 | 1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Equipment (Capacitor) | Equipment / facility failure | Capacitor bank damage or failure | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Medium High | 60% | 0.78 | 0.78 | Medium | 40% | 0.52 | 0.52 | 1.3
Equipment (Capacitor) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | Very High | 90% | 2.25 | 2.25 | Very High | 90% | 2.25 | 2.25 | 2.5
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | Very High | 90% | 2.25 | 2.25 | Very High | 90% | 2.25 | 2.25 | 2.5
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 5 | 5 | All | 100% | 5 | 5 | All | 100% | 5 | 5 | Very High | 90% | 4.5 | 4.5 | Very High | 90% | 4.5 | 4.5 | 5
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | Very High | 90% | 2.25 | 2.25 | Very High | 90% | 2.25 | 2.25 | 2.5
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 29 | 29 | All | 100% | 29 | 29 | All | 100% | 29 | 29 | Very High | 90% | 26.1 | 26.1 | Very High | 90% | 26.1 | 26.1 | 29
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 4.9 | 4.9 | All | 100% | 4.9 | 4.9 | All | 100% | 4.9 | 4.9 | Medium High | 60% | 2.94 | 2.94 | Medium | 40% | 1.96 | 1.96 | 4.9
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 104.7 | 104.7 | All | 100% | 104.7 | 104.7 | All | 100% | 104.7 | 104.7 | Medium High | 60% | 62.82 | 62.82 | Medium | 40% | 41.88 | 41.88 | 104.7
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | Medium High | 60% | 1.86 | 1.86 | Medium | 40% | 1.24 | 1.24 | 3.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 3 | 3 | All | 100% | 3 | 3 | All | 100% | 3 | 3 | Very High | 90% | 2.7 | 2.7 | Very High | 90% | 2.7 | 2.7 | 3
Primary Conductor - Other | Contamination | Contamination | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | Very High | 90% | 3.24 | 3.24 | Very High | 90% | 3.24 | 3.24 | 3.6
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 18.3 | 18.3 | All | 100% | 18.3 | 18.3 | All | 100% | 18.3 | 18.3 | Very High | 90% | 16.47 | 16.47 | Very High | 90% | 16.47 | 16.47 | 18.3
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 3 | 3 | All | 100% | 3 | 3 | All | 100% | 3 | 3 | Very High | 90% | 2.7 | 2.7 | Very High | 90% | 2.7 | 2.7 | 3
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | All | 100% | 19.8 | 19.8 | All | 100% | 19.8 | 19.8 | All | 100% | 19.8 | 19.8 | Very High | 90% | 17.82 | 17.82 | Very High | 90% | 17.82 | 17.82 | 19.8
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | All | 100% | 4.9 | 4.9 | All | 100% | 4.9 | 4.9 | All | 100% | 4.9 | 4.9 | Medium High | 60% | 2.94 | 2.94 | Medium | 40% | 1.96 | 1.96 | 4.9
Primary Conductor - Line Slap | Equipment / facility failure | Conductor damage or failure | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | Very High | 90% | 3.15 | 3.15 | Very High | 90% | 3.15 | 3.15 | 3.5
Primary Conductor - Line Slap | Equipment / facility failure | Conductor damage or failure | All | 100% | 29.1 | 29.1 | All | 100% | 29.1 | 29.1 | All | 100% | 29.1 | 29.1 | Very High | 90% | 26.19 | 26.19 | Very High | 90% | 26.19 | 26.19 | 29.1
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | Very High | 90% | 5.76 | 5.76 | Very High | 90% | 5.76 | 5.76 | 6.4
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | Very High | 90% | 2.16 | 2.16 | Very High | 90% | 2.16 | 2.16 | 2.4
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 30.5 | 30.5 | All | 100% | 30.5 | 30.5 | All | 100% | 30.5 | 30.5 | Very High | 90% | 27.45 | 27.45 | Very High | 90% | 27.45 | 27.45 | 30.5
Primary Conductor - Wire Down | Equipment / facility failure | Connection device damage or failure | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | Very High | 90% | 1.44 | 1.44 | 1.6
Primary Conductor - Wire Down | Equipment / facility failure | Connection device damage or failure | All | 100% | 24.3 | 24.3 | All | 100% | 24.3 | 24.3 | All | 100% | 24.3 | 24.3 | Very High | 90% | 21.87 | 21.87 | Very High | 90% | 21.87 | 21.87 | 24.3
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | Very High | 90% | 0.99 | 0.99 | 1.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 3.8 | 3.8 | All | 100% | 3.8 | 3.8 | All | 100% | 3.8 | 3.8 | Very High | 90% | 3.42 | 3.42 | Very High | 90% | 3.42 | 3.42 | 3.8
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 8 | 8 | All | 100% | 8 | 8 | All | 100% | 8 | 8 | Very High | 90% | 7.2 | 7.2 | Very High | 90% | 7.2 | 7.2 | 8
Primary Conductor - Other | Contamination | Contamination | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Contamination | Contamination | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | Very High | 90% | 0.9 | 0.9 | 1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 8.6 | 8.6 | All | 100% | 8.6 | 8.6 | All | 100% | 8.6 | 8.6 | Very High | 90% | 7.74 | 7.74 | Very High | 90% | 7.74 | 7.74 | 8.6
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | Very High | 90% | 0.9 | 0.9 | 1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 11.1 | 11.1 | All | 100% | 11.1 | 11.1 | All | 100% | 11.1 | 11.1 | Very High | 90% | 9.99 | 9.99 | Very High | 90% | 9.99 | 9.99 | 11.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 125 | 125 | All | 100% | 125 | 125 | All | 100% | 125 | 125 | Very High | 90% | 112.5 | 112.5 | Very High | 90% | 112.5 | 112.5 | 125
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 8.3 | 8.3 | All | 100% | 8.3 | 8.3 | All | 100% | 8.3 | 8.3 | Medium High | 60% | 4.98 | 4.98 | Medium | 40% | 3.32 | 3.32 | 8.3
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Medium High | 60% | 1.02 | 1.02 | Medium | 40% | 0.68 | 0.68 | 1.7
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | Very High | 90% | 4.77 | 4.77 | Very High | 90% | 4.77 | 4.77 | 5.3
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | Very High | 90% | 2.97 | 2.97 | Very High | 90% | 2.97 | 2.97 | 3.3
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 16.7 | 16.7 | All | 100% | 16.7 | 16.7 | All | 100% | 16.7 | 16.7 | Very High | 90% | 15.03 | 15.03 | Very High | 90% | 15.03 | 15.03 | 16.7
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Crossarm damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | none | 0% | 0 | 0 | none | 0% | 0 | 0 | none | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | Very High | 90% | 2.07 | 2.07 | Very High | 90% | 2.07 | 2.07 | 2.3
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | Very High | 90% | 3.78 | 3.78 | High | 70% | 2.94 | 2.94 | 4.2
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 45.4 | 45.4 | All | 100% | 45.4 | 45.4 | All | 100% | 45.4 | 45.4 | Very High | 90% | 40.86 | 40.86 | High | 70% | 31.78 | 31.78 | 45.4
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 5.6 | 5.6 | All | 100% | 5.6 | 5.6 | All | 100% | 5.6 | 5.6 | Very High | 90% | 5.04 | 5.04 | High | 70% | 3.92 | 3.92 | 5.6
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 7.6 | 7.6 | All | 100% | 7.6 | 7.6 | All | 100% | 7.6 | 7.6 | Very High | 90% | 6.84 | 6.84 | Very High | 90% | 6.84 | 6.84 | 7.6
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | High | 70% | 0.7 | 0.7 | 1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | Very High | 90% | 2.97 | 2.97 | High | 70% | 2.31 | 2.31 | 3.3
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | Very High | 90% | 1.35 | 1.35 | Very High | 90% | 1.35 | 1.35 | 1.5
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 4.4 | 4.4 | All | 100% | 4.4 | 4.4 | All | 100% | 4.4 | 4.4 | Very High | 90% | 3.96 | 3.96 | Very High | 90% | 3.96 | 3.96 | 4.4
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 22.9 | 22.9 | All | 100% | 22.9 | 22.9 | All | 100% | 22.9 | 22.9 | Very High | 90% | 20.61 | 20.61 | Very High | 90% | 20.61 | 20.61 | 22.9
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 8.2 | 8.2 | All | 100% | 8.2 | 8.2 | All | 100% | 8.2 | 8.2 | Very High | 90% | 7.38 | 7.38 | Very High | 90% | 7.38 | 7.38 | 8.2
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | Very High | 90% | 3.78 | 3.78 | Very High | 90% | 3.78 | 3.78 | 4.2
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 28.1 | 28.1 | All | 100% | 28.1 | 28.1 | All | 100% | 28.1 | 28.1 | Very High | 90% | 25.29 | 25.29 | Very High | 90% | 25.29 | 25.29 | 28.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | Very High | 90% | 0.99 | 0.99 | 1.1
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | All | 100% | 7.7 | 7.7 | All | 100% | 7.7 | 7.7 | All | 100% | 7.7 | 7.7 | Very High | 90% | 6.93 | 6.93 | Very High | 90% | 6.93 | 6.93 | 7.7
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | Very High | 90% | 1.89 | 1.89 | Very High | 90% | 1.89 | 1.89 | 2.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 6.3 | 6.3 | All | 100% | 6.3 | 6.3 | All | 100% | 6.3 | 6.3 | Very High | 90% | 5.67 | 5.67 | Very High | 90% | 5.67 | 5.67 | 6.3
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 66.6 | 66.6 | All | 100% | 66.6 | 66.6 | All | 100% | 66.6 | 66.6 | Very High | 90% | 59.94 | 59.94 | Very High | 90% | 59.94 | 59.94 | 66.6
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 4 | 4 | All | 100% | 4 | 4 | All | 100% | 4 | 4 | Medium High | 60% | 2.4 | 2.4 | Medium | 40% | 1.6 | 1.6 | 4
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 4 | 4 | All | 100% | 4 | 4 | All | 100% | 4 | 4 | Medium High | 60% | 2.4 | 2.4 | Medium | 40% | 1.6 | 1.6 | 4
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 5.5 | 5.5 | All | 100% | 5.5 | 5.5 | All | 100% | 5.5 | 5.5 | Very High | 90% | 4.95 | 4.95 | Very High | 90% | 4.95 | 4.95 | 5.5
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | All | 100% | 4.2 | 4.2 | Very High | 90% | 3.78 | 3.78 | Very High | 90% | 3.78 | 3.78 | 4.2
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | Very High | 90% | 1.26 | 1.26 | 1.4
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | Very High | 90% | 3.06 | 3.06 | High | 70% | 2.38 | 2.38 | 3.4
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | High | 70% | 1.19 | 1.19 | 1.7
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | Very High | 90% | 1.89 | 1.89 | High | 70% | 1.47 | 1.47 | 2.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 17.2 | 17.2 | All | 100% | 17.2 | 17.2 | All | 100% | 17.2 | 17.2 | Very High | 90% | 15.48 | 15.48 | High | 70% | 12.04 | 12.04 | 17.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | Very High | 90% | 2.52 | 2.52 | High | 70% | 1.96 | 1.96 | 2.8
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 3.2 | 3.2 | All | 100% | 3.2 | 3.2 | All | 100% | 3.2 | 3.2 | Very High | 90% | 2.88 | 2.88 | High | 70% | 2.24 | 2.24 | 3.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 41.2 | 41.2 | All | 100% | 41.2 | 41.2 | All | 100% | 41.2 | 41.2 | Very High | 90% | 37.08 | 37.08 | High | 70% | 28.84 | 28.84 | 41.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 6 | 6 | All | 100% | 6 | 6 | All | 100% | 6 | 6 | Very High | 90% | 5.4 | 5.4 | Very High | 90% | 5.4 | 5.4 | 6
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 3.7 | 3.7 | All | 100% | 3.7 | 3.7 | All | 100% | 3.7 | 3.7 | Very High | 90% | 3.33 | 3.33 | Very High | 90% | 3.33 | 3.33 | 3.7
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 14.2 | 14.2 | All | 100% | 14.2 | 14.2 | All | 100% | 14.2 | 14.2 | Very High | 90% | 12.78 | 12.78 | Very High | 90% | 12.78 | 12.78 | 14.2
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | Very High | 90% | 1.26 | 1.26 | 1.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.7
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Wire Down | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Line Slap | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Line Slap | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 18.2 | 18.2 | All | 100% | 18.2 | 18.2 | All | 100% | 18.2 | 18.2 | Very High | 90% | 16.38 | 16.38 | High | 70% | 12.74 | 12.74 | 18.2
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 127.6 | 127.6 | All | 100% | 127.6 | 127.6 | All | 100% | 127.6 | 127.6 | Very High | 90% | 114.84 | 114.84 | High | 70% | 89.32 | 89.32 | 127.6
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 20.3 | 20.3 | All | 100% | 20.3 | 20.3 | All | 100% | 20.3 | 20.3 | Medium High | 60% | 12.18 | 12.18 | Medium | 40% | 8.12 | 8.12 | 20.3
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | Very High | 90% | 4.77 | 4.77 | High | 70% | 3.71 | 3.71 | 5.3
Primary Conductor - Other | Contamination | Contamination | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 16.2 | 16.2 | All | 100% | 16.2 | 16.2 | All | 100% | 16.2 | 16.2 | Very High | 90% | 14.58 | 14.58 | High | 70% | 11.34 | 11.34 | 16.2
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 57.6 | 57.6 | All | 100% | 57.6 | 57.6 | All | 100% | 57.6 | 57.6 | Very High | 90% | 51.84 | 51.84 | High | 70% | 40.32 | 40.32 | 57.6
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | Very High | 90% | 3.06 | 3.06 | High | 70% | 2.38 | 2.38 | 3.4
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Medium High | 60% | 0.72 | 0.72 | Medium | 40% | 0.48 | 0.48 | 1.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | High | 70% | 0.77 | 0.77 | 1.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | High | 70% | 1.19 | 1.19 | 1.7
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | Very High | 90% | 2.43 | 2.43 | High | 70% | 1.89 | 1.89 | 2.7
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | HIgh | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | HIgh | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Medium High | 60% | 0.84 | 0.84 | Medium | 40% | 0.56 | 0.56 | 1.4
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Medium High | 60% | 0.84 | 0.84 | Medium | 40% | 0.56 | 0.56 | 1.4
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 8.4 | 8.4 | All | 100% | 8.4 | 8.4 | All | 100% | 8.4 | 8.4 | Medium High | 60% | 5.04 | 5.04 | Medium | 40% | 3.36 | 3.36 | 8.4
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Medium High | 60% | 0.48 | 0.48 | Medium | 40% | 0.32 | 0.32 | 0.8
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Medium High | 60% | 0.96 | 0.96 | Medium | 40% | 0.64 | 0.64 | 1.6
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.8
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.6
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 1.4 | 1.4 | High | 70% | 0.98 | 0.98 | High | 70% | 0.98 | 0.98 | High | 70% | 0.98 | 0.98 | High | 70% | 0.98 | 0.98 | 1.4
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.8 | 0.8 | High | 70% | 0.56 | 0.56 | High | 70% | 0.56 | 0.56 | High | 70% | 0.56 | 0.56 | High | 70% | 0.56 | 0.56 | 0.8
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 3.2 | 3.2 | Medium | 40% | 1.28 | 1.28 | Medium | 40% | 1.28 | 1.28 | Medium | 40% | 1.28 | 1.28 | Medium | 40% | 1.28 | 1.28 | 3.2
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 24.3 | 24.3 | Medium | 40% | 9.72 | 9.72 | Medium | 40% | 9.72 | 9.72 | Medium | 40% | 9.72 | 9.72 | Medium | 40% | 9.72 | 9.72 | 24.3
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 5.9 | 5.9 | Medium | 40% | 2.36 | 2.36 | Medium | 40% | 2.36 | 2.36 | Medium | 40% | 2.36 | 2.36 | Medium | 40% | 2.36 | 2.36 | 5.9
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.4 | 0.4 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | 0.4
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 2.4 | 2.4 | High | 70% | 1.68 | 1.68 | High | 70% | 1.68 | 1.68 | High | 70% | 1.68 | 1.68 | High | 70% | 1.68 | 1.68 | 2.4
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 2.2 | 2.2 | Medium | 40% | 0.88 | 0.88 | Medium | 40% | 0.88 | 0.88 | Medium | 40% | 0.88 | 0.88 | Medium | 40% | 0.88 | 0.88 | 2.2
Secondary Conductor | Contamination | Contamination | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Contamination | Contamination | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 2.5 | 2.5 | High | 70% | 1.75 | 1.75 | High | 70% | 1.75 | 1.75 | High | 70% | 1.75 | 1.75 | High | 70% | 1.75 | 1.75 | 2.5
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 6.8 | 6.8 | High | 70% | 4.76 | 4.76 | High | 70% | 4.76 | 4.76 | High | 70% | 4.76 | 4.76 | High | 70% | 4.76 | 4.76 | 6.8
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.8 | 0.8 | High | 70% | 0.56 | 0.56 | High | 70% | 0.56 | 0.56 | High | 70% | 0.56 | 0.56 | High | 70% | 0.56 | 0.56 | 0.8
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 2.9 | 2.9 | High | 70% | 2.03 | 2.03 | High | 70% | 2.03 | 2.03 | High | 70% | 2.03 | 2.03 | High | 70% | 2.03 | 2.03 | 2.9
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | All | 100% | 1.8 | 1.8 | High | 70% | 1.26 | 1.26 | High | 70% | 1.26 | 1.26 | High | 70% | 1.26 | 1.26 | High | 70% | 1.26 | 1.26 | 1.8
Equipment (DPD) | Equipment / facility failure | Sectionalizer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Equipment / facility failure | Sectionalizer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Equipment / facility failure | Sectionalizer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.5 | 0.5 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | 0.5
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.5 | 0.5 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | 0.5
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 4.5 | 4.5 | Medium | 40% | 1.8 | 1.8 | Medium | 40% | 1.8 | 1.8 | Medium | 40% | 1.8 | 1.8 | Medium | 40% | 1.8 | 1.8 | 4.5
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 1.5 | 1.5 | Medium | 40% | 0.6 | 0.6 | Medium | 40% | 0.6 | 0.6 | Medium | 40% | 0.6 | 0.6 | Medium | 40% | 0.6 | 0.6 | 1.5
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.4 | 0.4 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | 0.4
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.8 | 0.8 | Medium | 40% | 0.32 | 0.32 | Medium | 40% | 0.32 | 0.32 | Medium | 40% | 0.32 | 0.32 | Medium | 40% | 0.32 | 0.32 | 0.8
Secondary Conductor | 0 | 0 | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.5 | 0.5 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | 0.5
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 2 | 2 | High | 70% | 1.4 | 1.4 | High | 70% | 1.4 | 1.4 | High | 70% | 1.4 | 1.4 | High | 70% | 1.4 | 1.4 | 2
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.7 | 0.7 | High | 70% | 0.49 | 0.49 | High | 70% | 0.49 | 0.49 | High | 70% | 0.49 | 0.49 | High | 70% | 0.49 | 0.49 | 0.7
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Secondary Conductor | Contamination | Contamination | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | Very High | 90% | 1.71 | 1.71 | Very High | 90% | 1.71 | 1.71 | 1.9
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | High | 70% | 0.63 | 0.63 | 0.9
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 3.2 | 3.2 | All | 100% | 3.2 | 3.2 | All | 100% | 3.2 | 3.2 | Very High | 90% | 2.88 | 2.88 | High | 70% | 2.24 | 2.24 | 3.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 7.2 | 7.2 | All | 100% | 7.2 | 7.2 | All | 100% | 7.2 | 7.2 | Very High | 90% | 6.48 | 6.48 | High | 70% | 5.04 | 5.04 | 7.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 73.7 | 73.7 | All | 100% | 73.7 | 73.7 | All | 100% | 73.7 | 73.7 | Very High | 90% | 66.33 | 66.33 | High | 70% | 51.59 | 51.59 | 73.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 8.2 | 8.2 | All | 100% | 8.2 | 8.2 | All | 100% | 8.2 | 8.2 | Very High | 90% | 7.38 | 7.38 | High | 70% | 5.74 | 5.74 | 8.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | High | 70% | 1.12 | 1.12 | 1.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 16.7 | 16.7 | All | 100% | 16.7 | 16.7 | All | 100% | 16.7 | 16.7 | Very High | 90% | 15.03 | 15.03 | High | 70% | 11.69 | 11.69 | 16.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 25.5 | 25.5 | All | 100% | 25.5 | 25.5 | All | 100% | 25.5 | 25.5 | Very High | 90% | 22.95 | 22.95 | High | 70% | 17.85 | 17.85 | 25.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 222.7 | 222.7 | All | 100% | 222.7 | 222.7 | All | 100% | 222.7 | 222.7 | Very High | 90% | 200.43 | 200.43 | High | 70% | 155.89 | 155.89 | 222.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 5.7 | 5.7 | All | 100% | 5.7 | 5.7 | All | 100% | 5.7 | 5.7 | Very High | 90% | 5.13 | 5.13 | High | 70% | 3.99 | 3.99 | 5.7
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 33.8 | 33.8 | All | 100% | 33.8 | 33.8 | All | 100% | 33.8 | 33.8 | Very High | 90% | 30.42 | 30.42 | High | 70% | 23.66 | 23.66 | 33.8
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 10.9 | 10.9 | All | 100% | 10.9 | 10.9 | All | 100% | 10.9 | 10.9 | Very High | 90% | 9.81 | 9.81 | High | 70% | 7.63 | 7.63 | 10.9
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | Very High | 90% | 1.35 | 1.35 | High | 70% | 1.05 | 1.05 | 1.5
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | Very High | 90% | 2.16 | 2.16 | High | 70% | 1.68 | 1.68 | 2.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 22.2 | 22.2 | All | 100% | 22.2 | 22.2 | All | 100% | 22.2 | 22.2 | Very High | 90% | 19.98 | 19.98 | High | 70% | 15.54 | 15.54 | 22.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | Medium High | 60% | 2.04 | 2.04 | Medium | 40% | 1.36 | 1.36 | 3.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 6.2 | 6.2 | All | 100% | 6.2 | 6.2 | All | 100% | 6.2 | 6.2 | Very High | 90% | 5.58 | 5.58 | High | 70% | 4.34 | 4.34 | 6.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | Very High | 90% | 1.62 | 1.62 | High | 70% | 1.26 | 1.26 | 1.8
Equipment (Transformer) | Contamination | Contamination | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Contamination | Contamination | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 9.9 | 9.9 | All | 100% | 9.9 | 9.9 | All | 100% | 9.9 | 9.9 | Very High | 90% | 8.91 | 8.91 | High | 70% | 6.93 | 6.93 | 9.9
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 5.1 | 5.1 | All | 100% | 5.1 | 5.1 | All | 100% | 5.1 | 5.1 | Very High | 90% | 4.59 | 4.59 | High | 70% | 3.57 | 3.57 | 5.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 229.8 | 229.8 | All | 100% | 229.8 | 229.8 | All | 100% | 229.8 | 229.8 | Very High | 90% | 206.82 | 206.82 | High | 70% | 160.86 | 160.86 | 229.8
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 7.3 | 7.3 | All | 100% | 7.3 | 7.3 | All | 100% | 7.3 | 7.3 | Very High | 90% | 6.57 | 6.57 | High | 70% | 5.11 | 5.11 | 7.3
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | Very High | 90% | 2.34 | 2.34 | High | 70% | 1.82 | 1.82 | 2.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 2 | 2 | All | 100% | 2 | 2 | All | 100% | 2 | 2 | Very High | 90% | 1.8 | 1.8 | High | 70% | 1.4 | 1.4 | 2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 6.9 | 6.9 | All | 100% | 6.9 | 6.9 | All | 100% | 6.9 | 6.9 | Very High | 90% | 6.21 | 6.21 | Very High | 90% | 6.21 | 6.21 | 6.9
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (Support Structure) | Equipment / facility failure | Pole damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.3
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Lightning arrestor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | All | 100% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Voltage Control) | Equipment / facility failure | Voltage regulator / booster damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Voltage Control) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Contamination | Contamination | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Insulator and brushing damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Contamination | Contamination | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Contamination | Contamination | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Equipment / facility failure | Connection device damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Fuse) | Equipment / facility failure | Fuse damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Line Slap | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (DPD) | Equipment / facility failure | Recloser damage or failure | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Contamination | Contamination | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Secondary damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Secondary Conductor | Equipment / facility failure | Conductor damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Equipment / facility failure | Other equipment / facility failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Switch) | Equipment / facility failure | Switch damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | 0.2
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Contamination | Contamination | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Transformer) | Equipment / facility failure | Transformer damage or failure | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Primary Conductor - Other | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Other | Unknown | Unknown | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Equipment (Support Structure) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Fuse) | Unknown | Unknown | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Equipment (Fuse) | Unknown | Unknown | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Equipment (other) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Equipment (Support Structure) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (DPD) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Equipment (DPD) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (DPD) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Equipment (Transformer) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Unknown | Unknown | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Equipment (Transformer) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (other) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Equipment (DPD) | Unknown | Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Primary Conductor - Other | Unknown | Unknown | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Primary Conductor - Wire Down | Unknown | Unknown | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Primary Conductor - Line Slap | Unknown | Unknown | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Equipment (other) | Unknown | Unknown | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Equipment (Fuse) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Support Structure) | Unknown | Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Equipment (Transformer) | Unknown | Unknown | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Equipment (Transformer) | Unknown | Unknown | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 4.3 | 4.3 | All | 100% | 4.3 | 4.3 | All | 100% | 4.3 | 4.3 | Very High | 90% | 3.87 | 3.87 | Very High | 90% | 3.87 | 3.87 | 4.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (other) | Vegetation Contact | Grow Into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 6.6 | 6.6 | All | 100% | 6.6 | 6.6 | All | 100% | 6.6 | 6.6 | Medium High | 60% | 3.96 | 3.96 | Medium | 40% | 2.64 | 2.64 | 6.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | Very High | 90% | 2.25 | 2.25 | Very High | 90% | 2.25 | 2.25 | 2.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 22.5 | 22.5 | All | 100% | 22.5 | 22.5 | All | 100% | 22.5 | 22.5 | Very High | 90% | 20.25 | 20.25 | Very High | 90% | 20.25 | 20.25 | 22.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | Very High | 90% | 2.25 | 2.25 | Very High | 90% | 2.25 | 2.25 | 2.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | All | 100% | 3.5 | 3.5 | Very High | 90% | 3.15 | 3.15 | Very High | 90% | 3.15 | 3.15 | 3.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Medium High | 60% | 0.48 | 0.48 | Medium | 40% | 0.32 | 0.32 | 0.8
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | 0 | 0 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Vegetation (Branch) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Branch) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 5.2 | 5.2 | All | 100% | 5.2 | 5.2 | All | 100% | 5.2 | 5.2 | Very High | 90% | 4.68 | 4.68 | Very High | 90% | 4.68 | 4.68 | 5.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | All | 100% | 3.4 | 3.4 | Very High | 90% | 3.06 | 3.06 | Very High | 90% | 3.06 | 3.06 | 3.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 8.6 | 8.6 | All | 100% | 8.6 | 8.6 | All | 100% | 8.6 | 8.6 | Very High | 90% | 7.74 | 7.74 | Very High | 90% | 7.74 | 7.74 | 8.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 7.8 | 7.8 | All | 100% | 7.8 | 7.8 | All | 100% | 7.8 | 7.8 | Medium High | 60% | 4.68 | 4.68 | Medium | 40% | 3.12 | 3.12 | 7.8
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 137 | 137 | All | 100% | 137 | 137 | All | 100% | 137 | 137 | Medium High | 60% | 82.2 | 82.2 | Medium | 40% | 54.8 | 54.8 | 137
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | Medium High | 60% | 1.86 | 1.86 | Medium | 40% | 1.24 | 1.24 | 3.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | Very High | 90% | 2.97 | 2.97 | Very High | 90% | 2.97 | 2.97 | 3.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | All | 100% | 2.1 | 2.1 | Very High | 90% | 1.89 | 1.89 | Very High | 90% | 1.89 | 1.89 | 2.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 35.9 | 35.9 | All | 100% | 35.9 | 35.9 | All | 100% | 35.9 | 35.9 | Very High | 90% | 32.31 | 32.31 | Very High | 90% | 32.31 | 32.31 | 35.9
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 347.4 | 347.4 | All | 100% | 347.4 | 347.4 | All | 100% | 347.4 | 347.4 | Very High | 90% | 312.66 | 312.66 | Very High | 90% | 312.66 | 312.66 | 347.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 5.4 | 5.4 | All | 100% | 5.4 | 5.4 | All | 100% | 5.4 | 5.4 | Medium High | 60% | 3.24 | 3.24 | Medium | 40% | 2.16 | 2.16 | 5.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 33.6 | 33.6 | All | 100% | 33.6 | 33.6 | All | 100% | 33.6 | 33.6 | Very High | 90% | 30.24 | 30.24 | Very High | 90% | 30.24 | 30.24 | 33.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Primary Conductor - Wire Down | Vegetation Contact | Branch | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | Very High | 90% | 1.26 | 1.26 | 1.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 7.3 | 7.3 | All | 100% | 7.3 | 7.3 | All | 100% | 7.3 | 7.3 | Very High | 90% | 6.57 | 6.57 | Very High | 90% | 6.57 | 6.57 | 7.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 4.1 | 4.1 | All | 100% | 4.1 | 4.1 | All | 100% | 4.1 | 4.1 | Medium High | 60% | 2.46 | 2.46 | Medium | 40% | 1.64 | 1.64 | 4.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | High | 70% | 0.91 | 0.91 | 1.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | High | 70% | 0.7 | 0.7 | 1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | All | 100% | 1.6 | 1.6 | Very High | 90% | 1.44 | 1.44 | Very High | 90% | 1.44 | 1.44 | 1.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 41.6 | 41.6 | All | 100% | 41.6 | 41.6 | All | 100% | 41.6 | 41.6 | Very High | 90% | 37.44 | 37.44 | Very High | 90% | 37.44 | 37.44 | 41.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | All | 100% | 1.1 | 1.1 | Very High | 90% | 0.99 | 0.99 | Very High | 90% | 0.99 | 0.99 | 1.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 6.5 | 6.5 | All | 100% | 6.5 | 6.5 | All | 100% | 6.5 | 6.5 | Very High | 90% | 5.85 | 5.85 | Very High | 90% | 5.85 | 5.85 | 6.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | Very High | 90% | 2.34 | 2.34 | Very High | 90% | 2.34 | 2.34 | 2.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | All | 100% | 1.5 | 1.5 | Very High | 90% | 1.35 | 1.35 | High | 70% | 1.05 | 1.05 | 1.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Branch) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 5.5 | 5.5 | All | 100% | 5.5 | 5.5 | All | 100% | 5.5 | 5.5 | Very High | 90% | 4.95 | 4.95 | High | 70% | 3.85 | 3.85 | 5.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 6.7 | 6.7 | All | 100% | 6.7 | 6.7 | All | 100% | 6.7 | 6.7 | Medium High | 60% | 4.02 | 4.02 | Medium | 40% | 2.68 | 2.68 | 6.7
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | 0 | 0 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | HIgh | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.6 | 0.6 | High | 70% | 0.42 | 0.42 | High | 70% | 0.42 | 0.42 | High | 70% | 0.42 | 0.42 | High | 70% | 0.42 | 0.42 | 0.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.2 | 3.2 | Medium | 40% | 1.28 | 1.28 | Medium | 40% | 1.28 | 1.28 | Medium | 40% | 1.28 | 1.28 | Medium | 40% | 1.28 | 1.28 | 3.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.8 | 3.8 | Medium | 40% | 1.52 | 1.52 | Medium | 40% | 1.52 | 1.52 | Medium | 40% | 1.52 | 1.52 | Medium | 40% | 1.52 | 1.52 | 3.8
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 4.8 | 4.8 | High | 70% | 3.36 | 3.36 | High | 70% | 3.36 | 3.36 | High | 70% | 3.36 | 3.36 | High | 70% | 3.36 | 3.36 | 4.8
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.1 | 1.1 | High | 70% | 0.77 | 0.77 | High | 70% | 0.77 | 0.77 | High | 70% | 0.77 | 0.77 | High | 70% | 0.77 | 0.77 | 1.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.6 | 3.6 | Medium | 40% | 1.44 | 1.44 | Medium | 40% | 1.44 | 1.44 | Medium | 40% | 1.44 | 1.44 | Medium | 40% | 1.44 | 1.44 | 3.6
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.9 | 0.9 | Medium | 40% | 0.36 | 0.36 | Medium | 40% | 0.36 | 0.36 | Medium | 40% | 0.36 | 0.36 | Medium | 40% | 0.36 | 0.36 | 0.9
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 5.1 | 5.1 | Medium | 40% | 2.04 | 2.04 | Medium | 40% | 2.04 | 2.04 | Medium | 40% | 2.04 | 2.04 | Medium | 40% | 2.04 | 2.04 | 5.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.9 | 0.9 | High | 70% | 0.63 | 0.63 | High | 70% | 0.63 | 0.63 | High | 70% | 0.63 | 0.63 | High | 70% | 0.63 | 0.63 | 0.9
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | All | 100% | 2.5 | 2.5 | Very High | 90% | 2.25 | 2.25 | High | 70% | 1.75 | 1.75 | 2.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Medium High | 60% | 0.72 | 0.72 | Medium | 40% | 0.48 | 0.48 | 1.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | Very High | 90% | 2.43 | 2.43 | High | 70% | 1.89 | 1.89 | 2.7
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 4.5 | 4.5 | All | 100% | 4.5 | 4.5 | All | 100% | 4.5 | 4.5 | Very High | 90% | 4.05 | 4.05 | High | 70% | 3.15 | 3.15 | 4.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | All | 100% | 3.3 | 3.3 | Very High | 90% | 2.97 | 2.97 | High | 70% | 2.31 | 2.31 | 3.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 4.1 | 4.1 | All | 100% | 4.1 | 4.1 | All | 100% | 4.1 | 4.1 | Medium High | 60% | 2.46 | 2.46 | Medium | 40% | 1.64 | 1.64 | 4.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | All | 100% | 3.1 | 3.1 | Very High | 90% | 2.79 | 2.79 | High | 70% | 2.17 | 2.17 | 3.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1 | 1 | All | 100% | 1 | 1 | All | 100% | 1 | 1 | Very High | 90% | 0.9 | 0.9 | High | 70% | 0.7 | 0.7 | 1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | Very High | 90% | 1.62 | 1.62 | High | 70% | 1.26 | 1.26 | 1.8
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Medium High | 60% | 0.54 | 0.54 | Medium | 40% | 0.36 | 0.36 | 0.9
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | Medium High | 60% | 2.16 | 2.16 | Medium | 40% | 1.44 | 1.44 | 3.6
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 11.3 | 11.3 | All | 100% | 11.3 | 11.3 | All | 100% | 11.3 | 11.3 | Very High | 90% | 10.17 | 10.17 | Very High | 90% | 10.17 | 10.17 | 11.3
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (other) | Vegetation Contact | Other/Unknown | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Other/Unknown | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | Very High | 90% | 1.08 | 1.08 | 1.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Medium High | 60% | 0.72 | 0.72 | Medium | 40% | 0.48 | 0.48 | 1.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 6.1 | 6.1 | All | 100% | 6.1 | 6.1 | All | 100% | 6.1 | 6.1 | Very High | 90% | 5.49 | 5.49 | Very High | 90% | 5.49 | 5.49 | 6.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 11.8 | 11.8 | All | 100% | 11.8 | 11.8 | All | 100% | 11.8 | 11.8 | Very High | 90% | 10.62 | 10.62 | Very High | 90% | 10.62 | 10.62 | 11.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | All | 100% | 2.4 | 2.4 | Very High | 90% | 2.16 | 2.16 | Very High | 90% | 2.16 | 2.16 | 2.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 31.6 | 31.6 | All | 100% | 31.6 | 31.6 | All | 100% | 31.6 | 31.6 | Very High | 90% | 28.44 | 28.44 | Very High | 90% | 28.44 | 28.44 | 31.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 35.9 | 35.9 | All | 100% | 35.9 | 35.9 | All | 100% | 35.9 | 35.9 | Medium High | 60% | 21.54 | 21.54 | Medium | 40% | 14.36 | 14.36 | 35.9
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 707.3 | 707.3 | All | 100% | 707.3 | 707.3 | All | 100% | 707.3 | 707.3 | Medium High | 60% | 424.38 | 424.38 | Medium | 40% | 282.92 | 282.92 | 707.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 9.8 | 9.8 | All | 100% | 9.8 | 9.8 | All | 100% | 9.8 | 9.8 | Medium High | 60% | 5.88 | 5.88 | Medium | 40% | 3.92 | 3.92 | 9.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 6.1 | 6.1 | All | 100% | 6.1 | 6.1 | All | 100% | 6.1 | 6.1 | Very High | 90% | 5.49 | 5.49 | Very High | 90% | 5.49 | 5.49 | 6.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | All | 100% | 1.8 | 1.8 | Very High | 90% | 1.62 | 1.62 | Very High | 90% | 1.62 | 1.62 | 1.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 24.2 | 24.2 | All | 100% | 24.2 | 24.2 | All | 100% | 24.2 | 24.2 | Very High | 90% | 21.78 | 21.78 | Very High | 90% | 21.78 | 21.78 | 24.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 308.1 | 308.1 | All | 100% | 308.1 | 308.1 | All | 100% | 308.1 | 308.1 | Very High | 90% | 277.29 | 277.29 | Very High | 90% | 277.29 | 277.29 | 308.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 28.2 | 28.2 | All | 100% | 28.2 | 28.2 | All | 100% | 28.2 | 28.2 | Medium High | 60% | 16.92 | 16.92 | Medium | 40% | 11.28 | 11.28 | 28.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Very High | 90% | 1.53 | 1.53 | Very High | 90% | 1.53 | 1.53 | 1.7
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 66 | 66 | All | 100% | 66 | 66 | All | 100% | 66 | 66 | Very High | 90% | 59.4 | 59.4 | Very High | 90% | 59.4 | 59.4 | 66
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | n/a | 0% | 0 | 0 | n/a | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Primary Conductor - Wire Down | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Primary Conductor - Wire Down | Vegetation Contact | Fell into | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | All | 100% | 3.6 | 3.6 | Very High | 90% | 3.24 | 3.24 | Very High | 90% | 3.24 | 3.24 | 3.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | All | 100% | 0.9 | 0.9 | Very High | 90% | 0.81 | 0.81 | Very High | 90% | 0.81 | 0.81 | 0.9
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 24.8 | 24.8 | All | 100% | 24.8 | 24.8 | All | 100% | 24.8 | 24.8 | Very High | 90% | 22.32 | 22.32 | Very High | 90% | 22.32 | 22.32 | 24.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Medium High | 60% | 0.84 | 0.84 | Medium | 40% | 0.56 | 0.56 | 1.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 35 | 35 | All | 100% | 35 | 35 | All | 100% | 35 | 35 | Medium High | 60% | 21 | 21 | Medium | 40% | 14 | 14 | 35
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Medium High | 60% | 0.78 | 0.78 | Medium | 40% | 0.52 | 0.52 | 1.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | 0 | 0 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Medium High | 60% | 0.12 | 0.12 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 19.3 | 19.3 | All | 100% | 19.3 | 19.3 | All | 100% | 19.3 | 19.3 | Very High | 90% | 17.37 | 17.37 | Very High | 90% | 17.37 | 17.37 | 19.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | All | 100% | 2.6 | 2.6 | Very High | 90% | 2.34 | 2.34 | Very High | 90% | 2.34 | 2.34 | 2.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | All | 100% | 5.3 | 5.3 | Very High | 90% | 4.77 | 4.77 | Very High | 90% | 4.77 | 4.77 | 5.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Medium High | 60% | 0.24 | 0.24 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | Very High | 90% | 1.71 | 1.71 | High | 70% | 1.33 | 1.33 | 1.9
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 44.3 | 44.3 | All | 100% | 44.3 | 44.3 | All | 100% | 44.3 | 44.3 | Very High | 90% | 39.87 | 39.87 | High | 70% | 31.01 | 31.01 | 44.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | Medium High | 60% | 1.68 | 1.68 | Medium | 40% | 1.12 | 1.12 | 2.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 107 | 107 | All | 100% | 107 | 107 | All | 100% | 107 | 107 | Medium High | 60% | 64.2 | 64.2 | Medium | 40% | 42.8 | 42.8 | 107
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Medium High | 60% | 0.84 | 0.84 | Medium | 40% | 0.56 | 0.56 | 1.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | All | 100% | 1.9 | 1.9 | Very High | 90% | 1.71 | 1.71 | High | 70% | 1.33 | 1.33 | 1.9
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.1 | 1.1 | High | 70% | 0.77 | 0.77 | High | 70% | 0.77 | 0.77 | High | 70% | 0.77 | 0.77 | High | 70% | 0.77 | 0.77 | 1.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 7.5 | 7.5 | Medium | 40% | 3 | 3 | Medium | 40% | 3 | 3 | Medium | 40% | 3 | 3 | Medium | 40% | 3 | 3 | 7.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.2 | 1.2 | Medium | 40% | 0.48 | 0.48 | Medium | 40% | 0.48 | 0.48 | Medium | 40% | 0.48 | 0.48 | Medium | 40% | 0.48 | 0.48 | 1.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 12.6 | 12.6 | Medium | 40% | 5.04 | 5.04 | Medium | 40% | 5.04 | 5.04 | Medium | 40% | 5.04 | 5.04 | Medium | 40% | 5.04 | 5.04 | 12.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.6 | 0.6 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.9 | 0.9 | High | 70% | 0.63 | 0.63 | High | 70% | 0.63 | 0.63 | High | 70% | 0.63 | 0.63 | High | 70% | 0.63 | 0.63 | 0.9
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 4.5 | 4.5 | High | 70% | 3.15 | 3.15 | High | 70% | 3.15 | 3.15 | High | 70% | 3.15 | 3.15 | High | 70% | 3.15 | 3.15 | 4.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.5 | 0.5 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | Medium | 40% | 0.2 | 0.2 | 0.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.5 | 1.5 | High | 70% | 1.05 | 1.05 | High | 70% | 1.05 | 1.05 | High | 70% | 1.05 | 1.05 | High | 70% | 1.05 | 1.05 | 1.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.5 | 0.5 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | High | 70% | 0.35 | 0.35 | 0.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 7.6 | 7.6 | Medium | 40% | 3.04 | 3.04 | Medium | 40% | 3.04 | 3.04 | Medium | 40% | 3.04 | 3.04 | Medium | 40% | 3.04 | 3.04 | 7.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.1 | 1.1 | Medium | 40% | 0.44 | 0.44 | Medium | 40% | 0.44 | 0.44 | Medium | 40% | 0.44 | 0.44 | Medium | 40% | 0.44 | 0.44 | 1.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 14.1 | 14.1 | Medium | 40% | 5.64 | 5.64 | Medium | 40% | 5.64 | 5.64 | Medium | 40% | 5.64 | 5.64 | Medium | 40% | 5.64 | 5.64 | 14.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.1 | 1.1 | Medium | 40% | 0.44 | 0.44 | Medium | 40% | 0.44 | 0.44 | Medium | 40% | 0.44 | 0.44 | Medium | 40% | 0.44 | 0.44 | 1.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | 0 | 0 | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1 | 1 | High | 70% | 0.7 | 0.7 | High | 70% | 0.7 | 0.7 | High | 70% | 0.7 | 0.7 | High | 70% | 0.7 | 0.7 | 1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | All | 100% | 6.4 | 6.4 | Very High | 90% | 5.76 | 5.76 | High | 70% | 4.48 | 4.48 | 6.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 3 | 3 | All | 100% | 3 | 3 | All | 100% | 3 | 3 | Medium High | 60% | 1.8 | 1.8 | Medium | 40% | 1.2 | 1.2 | 3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 2 | 2 | All | 100% | 2 | 2 | All | 100% | 2 | 2 | Very High | 90% | 1.8 | 1.8 | High | 70% | 1.4 | 1.4 | 2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | High | 70% | 0.49 | 0.49 | 0.7
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | All | 100% | 1.4 | 1.4 | Very High | 90% | 1.26 | 1.26 | High | 70% | 0.98 | 0.98 | 1.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Medium High | 60% | 0.18 | 0.18 | Medium | 40% | 0.12 | 0.12 | 0.3
Vegetation (Trunk) | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 7.9 | 7.9 | All | 100% | 7.9 | 7.9 | All | 100% | 7.9 | 7.9 | Very High | 90% | 7.11 | 7.11 | High | 70% | 5.53 | 5.53 | 7.9
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Medium High | 60% | 0.36 | 0.36 | Medium | 40% | 0.24 | 0.24 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 14.2 | 14.2 | All | 100% | 14.2 | 14.2 | All | 100% | 14.2 | 14.2 | Medium High | 60% | 8.52 | 8.52 | Medium | 40% | 5.68 | 5.68 | 14.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Medium High | 60% | 0.3 | 0.3 | Medium | 40% | 0.2 | 0.2 | 0.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | High | 70% | 0.35 | 0.35 | 0.5
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | High | 70% | 0.42 | 0.42 | 0.6
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | All | 100% | 2.8 | 2.8 | Very High | 90% | 2.52 | 2.52 | High | 70% | 1.96 | 1.96 | 2.8
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | All | 100% | 2.3 | 2.3 | Very High | 90% | 2.07 | 2.07 | High | 70% | 1.61 | 1.61 | 2.3
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | All | 100% | 1.2 | 1.2 | Very High | 90% | 1.08 | 1.08 | High | 70% | 0.84 | 0.84 | 1.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Medium High | 60% | 0.42 | 0.42 | Medium | 40% | 0.28 | 0.28 | 0.7
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | All | 100% | 0.4 | 0.4 | Very High | 90% | 0.36 | 0.36 | Very High | 90% | 0.36 | 0.36 | 0.4
Vegetation (Trunk) | Vegetation Contact | Fell into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | All | 100% | 1.3 | 1.3 | Very High | 90% | 1.17 | 1.17 | Very High | 90% | 1.17 | 1.17 | 1.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | All | 100% | 1.7 | 1.7 | Medium High | 60% | 1.02 | 1.02 | Medium | 40% | 0.68 | 0.68 | 1.7
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | All | 100% | 0.7 | 0.7 | Very High | 90% | 0.63 | 0.63 | Very High | 90% | 0.63 | 0.63 | 0.7
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | All | 100% | 0.3 | 0.3 | Very High | 90% | 0.27 | 0.27 | Very High | 90% | 0.27 | 0.27 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | All | 100% | 0.5 | 0.5 | Very High | 90% | 0.45 | 0.45 | Very High | 90% | 0.45 | 0.45 | 0.5
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 6.3 | 6.3 | All | 100% | 6.3 | 6.3 | All | 100% | 6.3 | 6.3 | Very High | 90% | 5.67 | 5.67 | Very High | 90% | 5.67 | 5.67 | 6.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 35.2 | 35.2 | All | 100% | 35.2 | 35.2 | All | 100% | 35.2 | 35.2 | Very High | 90% | 31.68 | 31.68 | Very High | 90% | 31.68 | 31.68 | 35.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | All | 100% | 2.7 | 2.7 | Very High | 90% | 2.43 | 2.43 | Very High | 90% | 2.43 | 2.43 | 2.7
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | Very High | 90% | 0.18 | 0.18 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | Very High | 90% | 0.09 | 0.09 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | Very High | 90% | 0.72 | 0.72 | 0.8
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | All | 100% | 0.6 | 0.6 | Very High | 90% | 0.54 | 0.54 | Very High | 90% | 0.54 | 0.54 | 0.6
Vegetation (other) | Vegetation Contact | Grow Into | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | All | 100% | 0.2 | 0.2 | Very High | 90% | 0.18 | 0.18 | High | 70% | 0.14 | 0.14 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Medium High | 60% | 0.06 | 0.06 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.7 | 0.7 | High | 70% | 0.49 | 0.49 | High | 70% | 0.49 | 0.49 | High | 70% | 0.49 | 0.49 | High | 70% | 0.49 | 0.49 | 0.7
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.6 | 0.6 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | Medium | 40% | 0.24 | 0.24 | 0.6
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.3 | 0.3 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.3 | 0.3 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | High | 70% | 0.21 | 0.21 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 1.6 | 1.6 | High | 70% | 1.12 | 1.12 | High | 70% | 1.12 | 1.12 | High | 70% | 1.12 | 1.12 | High | 70% | 1.12 | 1.12 | 1.6
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.2 | 0.2 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | Medium | 40% | 0.08 | 0.08 | 0.2
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.4 | 0.4 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | High | 70% | 0.28 | 0.28 | 0.4
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.4 | 0.4 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | Medium | 40% | 0.16 | 0.16 | 0.4
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | Medium | 40% | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | All | 100% | 0.8 | 0.8 | Very High | 90% | 0.72 | 0.72 | High | 70% | 0.56 | 0.56 | 0.8
Vegetation (other) | Vegetation Contact | Grow Into | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | All | 100% | 0.1 | 0.1 | Very High | 90% | 0.09 | 0.09 | High | 70% | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.3 | 0.3 | All | 1 | 0.3 | 0.3 | All | 1 | 0.3 | 0.3 | Very High | 0.9 | 0.27 | 0.27 | High | 0.7 | 0.21 | 0.21 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | High | 0.7 | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.4 | 0.4 | All | 1 | 0.4 | 0.4 | All | 1 | 0.4 | 0.4 | Very High | 0.9 | 0.36 | 0.36 | High | 0.7 | 0.28 | 0.28 | 0.4
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Medium High | 0.6 | 0.06 | 0.06 | Medium | 0.4 | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.6 | 0.6 | All | 1 | 0.6 | 0.6 | All | 1 | 0.6 | 0.6 | Medium High | 0.6 | 0.36 | 0.36 | Medium | 0.4 | 0.24 | 0.24 | 0.6
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Medium High | 0.6 | 0.06 | 0.06 | Medium | 0.4 | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | High | 0.7 | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | High | 0.7 | 0.07 | 0.07 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.3 | 0.3 | All | 1 | 0.3 | 0.3 | All | 1 | 0.3 | 0.3 | Very High | 0.9 | 0.27 | 0.27 | High | 0.7 | 0.21 | 0.21 | 0.3
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Medium High | 0.6 | 0.06 | 0.06 | Medium | 0.4 | 0.04 | 0.04 | 0.1
Vegetation (other) | Vegetation Contact | Grow Into | All | 1 | 0.2 | 0.2 | All | 1 | 0.2 | 0.2 | All | 1 | 0.2 | 0.2 | Very High | 0.9 | 0.18 | 0.18 | High | 0.7 | 0.14 | 0.14 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | Very High | 0.9 | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Medium High | 0.6 | 0.06 | 0.06 | Medium | 0.4 | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | Very High | 0.9 | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 2.3 | 2.3 | All | 1 | 2.3 | 2.3 | All | 1 | 2.3 | 2.3 | Very High | 0.9 | 2.07 | 2.07 | Very High | 0.9 | 2.07 | 2.07 | 2.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.2 | 0.2 | All | 1 | 0.2 | 0.2 | All | 1 | 0.2 | 0.2 | Very High | 0.9 | 0.18 | 0.18 | Very High | 0.9 | 0.18 | 0.18 | 0.2
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | Very High | 0.9 | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.3 | 0.3 | All | 1 | 0.3 | 0.3 | All | 1 | 0.3 | 0.3 | Very High | 0.9 | 0.27 | 0.27 | Very High | 0.9 | 0.27 | 0.27 | 0.3
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | Very High | 0.9 | 0.09 | 0.09 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | High | 0.7 | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | High | 0.7 | 0.07 | 0.07 | Medium | 0.4 | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | Medium | 0.4 | 0.04 | 0.04 | Medium | 0.4 | 0.04 | 0.04 | Medium | 0.4 | 0.04 | 0.04 | Medium | 0.4 | 0.04 | 0.04 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | High | 0.7 | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | High | 0.7 | 0.07 | 0.07 | 0.1
Vegetation (Branch) | Vegetation Contact | Branch | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | All | 1 | 0.1 | 0.1 | Very High | 0.9 | 0.09 | 0.09 | High | 0.7 | 0.07 | 0.07 | 0.1
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0
Company Initiated | Utility work / Operation | Utility work / Operation | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | n/a | 0 | 0 | 0 | n/a | 0 | 0 | 0 | 0

## RiskScore_Attribute
Case | Tranche | Outcome | Title | Risk_Score_2025
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 1 | Aggregated | Aggregated | 246.8042 | The Baseline_wPSPS data are based on the following PSPS mitigation program effectiveness inputs:
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 10 | Aggregated | Aggregated | 23.5412
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 2 | Aggregated | Aggregated | 249.942
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 3 | Aggregated | Aggregated | 247.2035
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 4 | Aggregated | Aggregated | 248.2658
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 5 | Aggregated | Aggregated | 250.7463
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 6 | Aggregated | Aggregated | 244.6774
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 7 | Aggregated | Aggregated | 246.5119
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 8 | Aggregated | Aggregated | 242.6165
Baseline_wPSPS | HFRA - Distribution - Primary - Tranche 9 | Aggregated | Aggregated | 189.3095
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 1 | Aggregated | Aggregated | 9.0125
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 10 | Aggregated | Aggregated | 0.52149
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 2 | Aggregated | Aggregated | 8.3042
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 3 | Aggregated | Aggregated | 8.2524
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 4 | Aggregated | Aggregated | 7.6169
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 5 | Aggregated | Aggregated | 8.8538
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 6 | Aggregated | Aggregated | 11.4589
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 7 | Aggregated | Aggregated | 10.0444
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 8 | Aggregated | Aggregated | 11.3088
Baseline_wPSPS | HFRA - Distribution - Secondary - Tranche 9 | Aggregated | Aggregated | 6.9642
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 1 | Aggregated | Aggregated | 5.7141
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 10 | Aggregated | Aggregated | 0.75737
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 2 | Aggregated | Aggregated | 7.2437
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 3 | Aggregated | Aggregated | 8.8955
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 4 | Aggregated | Aggregated | 8.526
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 5 | Aggregated | Aggregated | 9.3178
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 6 | Aggregated | Aggregated | 11.0481
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 7 | Aggregated | Aggregated | 9.98
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 8 | Aggregated | Aggregated | 11.0795
Baseline_wPSPS | HFRA - Distribution - Service - Tranche 9 | Aggregated | Aggregated | 7.3145
Baseline | HFRA - Distribution - Primary - Tranche 2 | Aggregated | Aggregated | 1576.0183
Baseline | HFRA - Distribution - Primary - Tranche 5 | Aggregated | Aggregated | 1574.0879
Baseline | HFRA - Distribution - Primary - Tranche 4 | Aggregated | Aggregated | 1562.468
Baseline | HFRA - Distribution - Primary - Tranche 3 | Aggregated | Aggregated | 1557.2015
Baseline | HFRA - Distribution - Primary - Tranche 1 | Aggregated | Aggregated | 1570.7201
Baseline | HFRA - Distribution - Primary - Tranche 6 | Aggregated | Aggregated | 1526.2048
Baseline | HFRA - Distribution - Primary - Tranche 7 | Aggregated | Aggregated | 1531.1112
Baseline | HFRA - Distribution - Primary - Tranche 8 | Aggregated | Aggregated | 1493.7665
Baseline | HFRA - Distribution - Primary - Tranche 9 | Aggregated | Aggregated | 1153.3023
Baseline | HFRA - Distribution - Primary - Tranche 10 | Aggregated | Aggregated | 141.98
Baseline | HFRA - Distribution - Secondary - Tranche 6 | Aggregated | Aggregated | 71.1755
Baseline | HFRA - Distribution - Service - Tranche 6 | Aggregated | Aggregated | 68.6861
Baseline | HFRA - Distribution - Secondary - Tranche 8 | Aggregated | Aggregated | 69.0913
Baseline | HFRA - Distribution - Service - Tranche 8 | Aggregated | Aggregated | 67.8719
Baseline | HFRA - Distribution - Secondary - Tranche 7 | Aggregated | Aggregated | 61.9926
Baseline | HFRA - Distribution - Service - Tranche 7 | Aggregated | Aggregated | 61.6732
Baseline | HFRA - Distribution - Service - Tranche 5 | Aggregated | Aggregated | 58.3124
Baseline | HFRA - Distribution - Service - Tranche 3 | Aggregated | Aggregated | 55.9097
Baseline | HFRA - Distribution - Secondary - Tranche 1 | Aggregated | Aggregated | 56.4697
Baseline | HFRA - Distribution - Secondary - Tranche 5 | Aggregated | Aggregated | 55.3519
Baseline | HFRA - Distribution - Service - Tranche 4 | Aggregated | Aggregated | 53.5239
Baseline | HFRA - Distribution - Secondary - Tranche 2 | Aggregated | Aggregated | 52.2388
Baseline | HFRA - Distribution - Secondary - Tranche 3 | Aggregated | Aggregated | 51.8605
Baseline | HFRA - Distribution - Secondary - Tranche 4 | Aggregated | Aggregated | 47.8257
Baseline | HFRA - Distribution - Service - Tranche 2 | Aggregated | Aggregated | 45.6231
Baseline | HFRA - Distribution - Service - Tranche 9 | Aggregated | Aggregated | 44.2816
Baseline | HFRA - Distribution - Secondary - Tranche 9 | Aggregated | Aggregated | 42.0126
Baseline | HFRA - Distribution - Service - Tranche 1 | Aggregated | Aggregated | 35.8996
Baseline | HFRA - Distribution - Service - Tranche 10 | Aggregated | Aggregated | 4.5766
Baseline | HFRA - Distribution - Secondary - Tranche 10 | Aggregated | Aggregated | 3.1408

## PSPS_effectiveness_calculation
| Case | Outcome | Title | Risk_Score_2025 | Notes |  | PSPS effectiveness = 1 - ((PostPSPS risk score - PrePSPS risk score)/PrePSPS risk score)
HFRA-Distribution | Baseline_wPSPS | Aggregated | Aggregated | 2351.8322 | These were calculated by summing the risk scores across all HFRA-Distribution tranches from tab "Risk_Score_Data" | Calculated_PSPS effectiveness = | 84%
HFRA-Distribution | Baseline | Aggregated | Aggregated | 14694.3778

## PSPS_effectiveness_validation
| Outcome | Outcome | Title | Baseline_risk_score_2025 | PSPS effectiveness | Calculated_Baseline_wPSPS_risk_score_2025 |  | PSPS effectiveness = 1 - ((PostPSPS risk score - PrePSPS risk score)/PrePSPS risk score)
HFRA-Distribution | Non-Red Flag Warning - Nonreportable Fires | Aggregated | Aggregated | 8.95 | 0 | 8.95 | Calculated_PSPS effectiveness = | 84%
HFRA-Distribution | Non-Red Flag Warning - OEIS Catastrophic - Destructive Fires | Aggregated | Aggregated | 1454.3976 | 0 | 1454.3976
HFRA-Distribution | Non-Red Flag Warning - OEIS Catastrophic - Large Fires | Aggregated | Aggregated | 3.5168 | 0 | 3.5168
HFRA-Distribution | Non-Red Flag Warning - OEIS Non-Catastrophic - Destructive Fires | Aggregated | Aggregated | 183.9472 | 0 | 183.9472
HFRA-Distribution | Non-Red Flag Warning - OEIS Non-Catastrophic - Large Fires | Aggregated | Aggregated | 8.8684 | 0 | 8.8684
HFRA-Distribution | Non-Red Flag Warning - Small Fires | Aggregated | Aggregated | 29.2009 | 0 | 29.2009
HFRA-Distribution | Red Flag Warning - Nonreportable Fires | Aggregated | Aggregated | 0.3385 | 0 | 0.3385
HFRA-Distribution | Red Flag Warning - OEIS Catastrophic - Destructive Fires | Aggregated | Aggregated | 12966.0392 | 0.95 | 648.302
HFRA-Distribution | Red Flag Warning - OEIS Catastrophic - Large Fires | Aggregated | Aggregated | 11.1661 | 0.91935 | 0.90049
HFRA-Distribution | Red Flag Warning - OEIS Non-Catastrophic - Destructive Fires | Aggregated | Aggregated | 0 | 0.95 | 0
HFRA-Distribution | Red Flag Warning - OEIS Non-Catastrophic - Large Fires | Aggregated | Aggregated | 13.1365 | 0.91935 | 1.0594
HFRA-Distribution | Red Flag Warning - Small Fires | Aggregated | Aggregated | 3.6306 | 0.6791 | 1.165
HFRA-Distribution | Seismic - Non-Red Flag Warning - OEIS Catastrophic - Destructive Fires | Aggregated | Aggregated | 1.131 | 0 | 1.131
HFRA-Distribution | Seismic - Non-Red Flag Warning - OEIS Non-Catastrophic - Destructive Fires | Aggregated | Aggregated | 0.14429 | 0 | 0.14429
HFRA-Distribution | Seismic - Red Flag Warning - OEIS Catastrophic - Destructive Fires | Aggregated | Aggregated | 9.9107 | 0 | 9.9107
HFRA-Distribution | Seismic - Red Flag Warning - OEIS Non-Catastrophic - Destructive Fires | Aggregated | Aggregated | 0 | 0 | 0
| Aggregated | Aggregated | Aggregated | 14694.3778 |  | 2351.8322