## Effectiveness Outputs
Dynamic Interval Effectiveness
2015-2024
[13 empty] | Covered Conductor | 52.29%
Dynamic Interval Assessment: 2015-2024
[13 empty] | WDRM V4 Subdriver | Covered Conductor Effectiveness | WDRM V4 SH ALL Risk Driver
[13 empty] | Vegetation (Branch) | 42.59% | epss_outage_risk_dollarized_vegetation_branch
[13 empty] | Vegetation (Trunk) | 40.08% | epss_outage_risk_dollarized_vegetation_trunk
[13 empty] | Vegetation (other) | 73.45% | epss_outage_risk_dollarized_vegetation_other
[13 empty] | Animal (Bird) | 78.9% | epss_outage_risk_dollarized_animal_bird
[13 empty] | Animal (Squirrel) | 72.9% | epss_outage_risk_dollarized_animal_squirrel
[13 empty] | Animal (other) | 74.59% | epss_outage_risk_dollarized_animal_other
[13 empty] | Third Party (Balloon) | 87.84% | epss_outage_risk_dollarized_third_party_balloon
[13 empty] | Third Party (Vehicle) | 48.08% | epss_outage_risk_dollarized_third_party_vehicle | [13 empty] | 0%
[13 empty] | Third Party (other) | 39.88% | epss_outage_risk_dollarized_third_party_other | [13 empty] | 0%
[13 empty] | Primary Conductor - Line Slap | 84.72% | epss_outage_risk_dollarized_primary_conductor_line_slap_cause | [13 empty] | 0%
[13 empty] | Primary Conductor - Wire Down | 45.31% | epss_outage_risk_dollarized_primary_conductor_wire_down_cause | [13 empty] | 0%
[13 empty] | Primary Conductor - Other | 62.84% | epss_outage_risk_dollarized_primary_conductor_other_cause | [13 empty] | 0%
[13 empty] | Secondary Conductor | 42.12% | epss_outage_risk_dollarized_secondary_conductor | [13 empty] | 0%
[13 empty] | Equipment (Support Structure) | 72.52% | epss_outage_risk_dollarized_support_structure_equipment_cause | [13 empty] | 0%
[13 empty] | Equipment (Transformer) | 55.02% | epss_outage_risk_dollarized_transformer_equipment_cause | [13 empty] | 0%
[13 empty] | Equipment (Voltage Control) | 32.47% | epss_outage_risk_dollarized_voltage_regulator_equipment_cause | [13 empty] | 0%
[13 empty] | Equipment (other) | 70.44% | epss_outage_risk_dollarized_other_equipment_type | [13 empty] | 0%
[13 empty] | Equipment (Capacitor) | 39.44% | epss_outage_risk_dollarized_capacitor_bank_equipment_cause | [13 empty] | 0%
[13 empty] | Equipment (DPD) | 35.46% | epss_outage_risk_dollarized_dpd_equipment_cause | [13 empty] | 0%
[13 empty] | Equipment (Fuse) | 71.36% | epss_outage_risk_dollarized_fuse_equipment_cause | [13 empty] | 0%
[13 empty] | Equipment (Switch) | 60% | epss_outage_risk_dollarized_switch_equipment_cause
Effectiveness Assesment Interval
[9 empty] | Outages From: | 2015
[9 empty] | Outages Through: | 2024
sum of PctVal
[9 empty] | Total # of Outage Years | 10 |  |  | Mom/Sus | Sus
| Status Quo |  |  |  | Covered Conductor |  |  |  | Averages from Year below up to 2024 |  |  | Average from/through Interval Years | Count of ODB_EVENT_LOG_ID |  |  |  |  | FNLYEAR
WDRM V4 Subdriver | Effectiveness | % Eff | 2015 PctVal | Interval PctVal | Effectiveness | % Eff | 2015 PctVal | Interval PctVal | 2018 | 2015 | 2020 | 2015-2024 | JointForLookup | BASIC_CAUSE | SUPPLEMENTAL_CAUSE | EQUIPINVOLVED | EQUIPCONDITION | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Grand Total
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 1 | 0.7 | 0.8 | 0.7 | 3rdParty¦Aircraft¦ConductorOverhead¦Brokenwireonground | 3rd Party | Aircraft | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2018: 3; FNLYEAR 2021: 1; FNLYEAR 2022: 3 | 7
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Aircraft¦ConductorOverhead¦Normal | 3rd Party | Aircraft | Conductor- Overhead | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦Aircraft¦ConductorOverhead¦Normal | 3rd Party | Aircraft | Conductor, Overhead | Normal | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Aircraft¦ConductorOverhead¦OnGround | 3rd Party | Aircraft | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Aircraft¦PoleWood¦Brokenwireonground | 3rd Party | Aircraft | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Annealed | 3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Annealed | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Brokenwireonground | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.57143 | 0.6 | 0.6 | 0.6 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Brokenwireonground | 3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Broken, wire on ground | [10 empty] | 6 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2019 to FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.14286 | 0.3 | 0.2 | 0.3 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Burnedflashed | 3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Burned/flashed | FNLYEAR 2015: 2; FNLYEAR 2023: 1 | 3
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 1.1429 | 0.9 | 1 | 0.9 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Normal | 3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Normal |  |  | 1 | 2 | 1 | 1 |  | 2 | 2 |  | 9
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Together | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.4 | 0.4 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Together | 3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Together | FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2022: 1 | 4
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorUnderground¦Broken | 3rd Party | Contact with High Voltage, 3rd party | Conductor, Underground | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦CrossarmWood¦Brokenwireonground | 3rd Party | Contact with High Voltage, 3rd party | Crossarm, Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦Cutoutfuseholder¦Normal | 3rd Party | Contact with High Voltage, 3rd party | Cutout, fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | 3rdParty¦ContactwithHighVoltage3rdparty¦Fuse¦FailedFaulted | 3rd Party | Contact with High Voltage, 3rd party | Fuse | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦PoleWood¦Broken | 3rd Party | Contact with High Voltage, 3rd party | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦PoleWood¦Brokenwireonground | 3rd Party | Contact with High Voltage, 3rd party | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦Pothead(RiserTermination)¦Broken | 3rd Party | Contact with High Voltage, 3rd party | Pothead(Riser Termination) | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦Secondary¦Brokenwireonground | 3rd Party | Contact with High Voltage, 3rd party | Secondary | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦ContactwithHighVoltage3rdparty¦Secondary¦BurnedOpen | 3rd Party | Contact with High Voltage, 3rd party | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦¦FailedFaulted | 3rd Party | Customer Equipment |  | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦AnchororGuy¦Brokenwireonground | 3rd Party | Customer Equipment | Anchor or Guy | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Bus¦Burnedflashed | 3rd Party | Customer Equipment | Bus | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Bus¦FailedFaulted | 3rd Party | Customer Equipment | Bus | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Arcing | 3rd Party | Customer Equipment | Circuit Breaker | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Broken | 3rd Party | Customer Equipment | Circuit Breaker | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦CustomerEquipment¦CircuitBreaker¦FailedFaulted | 3rd Party | Customer Equipment | Circuit Breaker | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Malfunctioning | 3rd Party | Customer Equipment | Circuit Breaker | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Malfunctioning | 3rd Party | Customer Equipment | Circuit Breaker | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.4 | 0.4 | 0.4 | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Normal | 3rd Party | Customer Equipment | Circuit Breaker | Normal | FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2023: 2 | 4
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.7 | 0 | 0.7 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Broken | 3rd Party | Customer Equipment | Conductor, Overhead | Broken | FNLYEAR 2015: 4; FNLYEAR 2017: 2; FNLYEAR 2018: 1 | 7
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.6 | 0.2 | 0.6 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Brokenwireonground | 3rd Party | Customer Equipment | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2022: 1 | 6
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Burnedflashed | 3rd Party | Customer Equipment | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Deteriorated | 3rd Party | Customer Equipment | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal | 3rd Party | Customer Equipment | Conductor- Overhead | Normal | FNLYEAR 2024: 4 | 4
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 3.8571 | 3.1 | 4.4 | 3.1 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal | 3rd Party | Customer Equipment | Conductor, Overhead | Normal | 1 | 1 | 2 | 4 | 1 | 6 | 1 | 10 | 5 |  | 31
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦OnGround | 3rd Party | Customer Equipment | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Together | 3rd Party | Customer Equipment | Conductor, Overhead | Together | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.6 | 1 | 0.6 | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Broken | 3rd Party | Customer Equipment | Conductor, Underground | Broken | FNLYEAR 2015: 1; FNLYEAR 2022: 4; FNLYEAR 2023: 1 | 6
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Contaminated | 3rd Party | Customer Equipment | Conductor- Underground | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Deteriorated | 3rd Party | Customer Equipment | Conductor, Underground | Deteriorated | FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 4
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Normal | 3rd Party | Customer Equipment | Conductor- Underground | Normal | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Normal | 3rd Party | Customer Equipment | Conductor, Underground | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦ConnectororSplice(OH)¦Broken | 3rd Party | Customer Equipment | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦ConnectororSplice(OH)¦Normal | 3rd Party | Customer Equipment | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦ConnectororSplice(UG)¦Normal | 3rd Party | Customer Equipment | Connector or Splice (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦ConnectororSplice(UG)¦Normal | 3rd Party | Customer Equipment | Connector or Splice (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦CrossarmWood¦Broken | 3rd Party | Customer Equipment | Crossarm- Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 0.4 | 0.5 | 3rdParty¦CustomerEquipment¦CrossarmWood¦Broken | 3rd Party | Customer Equipment | Crossarm, Wood | Broken | FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2023: 1 | 5
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦CT¦Burnedflashed | 3rd Party | Customer Equipment | CT | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦CT¦FailedFaulted | 3rd Party | Customer Equipment | CT | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.3 | 0.2 | 0.3 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Arcing | 3rd Party | Customer Equipment | Customer Equipment | Arcing | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦BentorTwisted | 3rd Party | Customer Equipment | Customer Equipment | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Broken | 3rd Party | Customer Equipment | Customer Equipment | Broken | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.8571 | 1.9 | 2.2 | 1.9 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Broken | 3rd Party | Customer Equipment | Customer Equipment | Broken | 1 | 1 | 4 |  | 2 | 4 | 1 | 4 | 2 |  | 19
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 0.6 | 0.5 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Burnedflashed | 3rd Party | Customer Equipment | Customer Equipment | Burned/flashed | FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 5
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.5 | 0.6 | 0.5 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦BurnedOpen | 3rd Party | Customer Equipment | Customer Equipment | Burned Open | FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 5
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Deteriorated | 3rd Party | Customer Equipment | Customer Equipment | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦FailedFaulted | 3rd Party | Customer Equipment | Customer Equipment | Failed/Faulted | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.3 | 2.2 | 1.3 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦FailedFaulted | 3rd Party | Customer Equipment | Customer Equipment | Failed/Faulted | 1 | 1 |  |  |  | 2 | 2 | 4 | 3 |  | 13
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.1 | 2.2 | 1.1 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Malfunctioning | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | FNLYEAR 2024: 11 | 11
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2 | 1.8 | 2 | 1.8 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Malfunctioning | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | 1 |  | 3 | 1 | 3 | 4 | 1 | 3 | 2 |  | 18
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Normal | 3rd Party | Customer Equipment | Customer Equipment | Normal | FNLYEAR 2024: 3 | 3
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.4286 | 1.1 | 1.4 | 1.1 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Normal | 3rd Party | Customer Equipment | Customer Equipment | Normal | 1 |  |  | 3 |  | 1 | 3 | 1 | 2 |  | 11
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Together | 3rd Party | Customer Equipment | Customer Equipment | Together | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Cutoutfuseholder¦Burnedflashed | 3rd Party | Customer Equipment | Cutout, fuse holder | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦Cutoutfuseholder¦FailedFaulted | 3rd Party | Customer Equipment | Cutout, fuse holder | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Fuse¦Broken | 3rd Party | Customer Equipment | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | 3rdParty¦CustomerEquipment¦Fuse¦BurnedOpen | 3rd Party | Customer Equipment | Fuse | Burned Open | FNLYEAR 2021: 2; FNLYEAR 2022: 2 | 4
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Fuse¦FailedFaulted | 3rd Party | Customer Equipment | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 1.6 | 0.4 | 1.6 | 3rdParty¦CustomerEquipment¦Fuse¦FailedFaulted | 3rd Party | Customer Equipment | Fuse | Failed/Faulted | 3 | 2 | 3 | 4 | 2 |  |  | 1 | 1 |  | 16
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1 | 0.8 | 0.8 | 0.8 | 3rdParty¦CustomerEquipment¦Fuse¦Normal | 3rd Party | Customer Equipment | Fuse | Normal |  |  | 1 | 1 | 2 | 1 |  | 2 | 1 |  | 8
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Generator¦Normal | 3rd Party | Customer Equipment | Generator | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 0.8 | 0.5 | 3rdParty¦CustomerEquipment¦Generator¦Normal | 3rd Party | Customer Equipment | Generator | Normal | FNLYEAR 2018: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 5
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Insulator¦Broken | 3rd Party | Customer Equipment | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦Insulator¦Broken | 3rd Party | Customer Equipment | Insulator | Broken | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦LightningArrestor¦Arcing | 3rd Party | Customer Equipment | Lightning Arrestor | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦LightningArrestor¦Burnedflashed | 3rd Party | Customer Equipment | Lightning Arrestor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦LightningArrestor¦FailedFaulted | 3rd Party | Customer Equipment | Lightning Arrestor | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Arcing | 3rd Party | Customer Equipment | Metering Equipment | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Broken | 3rd Party | Customer Equipment | Metering Equipment | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.4 | 0.2 | 0.4 | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Burnedflashed | 3rd Party | Customer Equipment | Metering Equipment | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦CustomerEquipment¦MeteringEquipment¦FailedFaulted | 3rd Party | Customer Equipment | Metering Equipment | Failed/Faulted | FNLYEAR 2020: 1; FNLYEAR 2023: 2 | 3
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Malfunctioning | 3rd Party | Customer Equipment | Metering Equipment | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Malfunctioning | 3rd Party | Customer Equipment | Metering Equipment | Malfunctioning | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Normal | 3rd Party | Customer Equipment | Metering Equipment | Normal | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Broken | 3rd Party | Customer Equipment | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Broken | 3rd Party | Customer Equipment | Other | Broken | FNLYEAR 2016: 1; FNLYEAR 2019: 3; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 6
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Burnedflashed | 3rd Party | Customer Equipment | Other | Burned/flashed | FNLYEAR 2018: 3 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Contaminated | 3rd Party | Customer Equipment | Other | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Deteriorated | 3rd Party | Customer Equipment | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Deteriorated | 3rd Party | Customer Equipment | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦FailedFaulted | 3rd Party | Customer Equipment | Other | Failed/Faulted | [10 empty] | 6 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2020 to FNLYEAR 2021; FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Malfunctioning | 3rd Party | Customer Equipment | Other | Malfunctioning | FNLYEAR 2024: 3 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Malfunctioning | 3rd Party | Customer Equipment | Other | Malfunctioning | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2019: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 6
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Normal | 3rd Party | Customer Equipment | Other | Normal | FNLYEAR 2024: 3 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦CustomerEquipment¦Other¦Normal | 3rd Party | Customer Equipment | Other | Normal |  | 2 | 2 |  |  | 1 | 2 | 3 | 1 |  | 11
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦PoleWood¦Broken | 3rd Party | Customer Equipment | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.8571 | 1.6 | 2 | 1.6 | 3rdParty¦CustomerEquipment¦PoleWood¦Broken | 3rd Party | Customer Equipment | Pole-Wood | Broken | 1 | 2 |  | 1 | 2 | 2 | 6 | 2 |  |  | 16
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦PoleWood¦Brokenwireonground | 3rd Party | Customer Equipment | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦PoleWood¦Burnedflashed | 3rd Party | Customer Equipment | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦PoleWood¦Deteriorated | 3rd Party | Customer Equipment | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦PoleWood¦Deteriorated | 3rd Party | Customer Equipment | Pole-Wood | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦PoleWood¦Normal | 3rd Party | Customer Equipment | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦PoleWood¦OnGround | 3rd Party | Customer Equipment | Pole-Wood | On Ground | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦PTCCVT¦FailedFaulted | 3rd Party | Customer Equipment | PT/CCVT | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Recloser¦FailedFaulted | 3rd Party | Customer Equipment | Recloser | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Recloser¦Malfunctioning | 3rd Party | Customer Equipment | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Recloser¦Normal | 3rd Party | Customer Equipment | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.6 | 1 | 0.6 | 3rdParty¦CustomerEquipment¦Recloser¦Normal | 3rd Party | Customer Equipment | Recloser | Normal | FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 6
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Relay¦Malfunctioning | 3rd Party | Customer Equipment | Relay | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Relay¦Normal | 3rd Party | Customer Equipment | Relay | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦CustomerEquipment¦Secondary¦Arcing | 3rd Party | Customer Equipment | Secondary | Arcing | FNLYEAR 2017: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Secondary¦BentorTwisted | 3rd Party | Customer Equipment | Secondary | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.9 | 0.6 | 0.9 | 3rdParty¦CustomerEquipment¦Secondary¦Broken | 3rd Party | Customer Equipment | Secondary | Broken | FNLYEAR 2017: 3; FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 9
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Secondary¦Brokenwireonground | 3rd Party | Customer Equipment | Secondary | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Secondary¦Burnedflashed | 3rd Party | Customer Equipment | Secondary | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.5 | 0.6 | 0.5 | 3rdParty¦CustomerEquipment¦Secondary¦Burnedflashed | 3rd Party | Customer Equipment | Secondary | Burned/flashed | [10 empty] | 5 | bar: FNLYEAR 2015; FNLYEAR 2019 to FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Secondary¦BurnedOpen | 3rd Party | Customer Equipment | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Secondary¦Deteriorated | 3rd Party | Customer Equipment | Secondary | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 1 | 1.2 | 1 | 3rdParty¦CustomerEquipment¦Secondary¦Normal | 3rd Party | Customer Equipment | Secondary | Normal | FNLYEAR 2015: 2; FNLYEAR 2017: 2; FNLYEAR 2020: 4; FNLYEAR 2021: 2 | 10
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Serviceconductor¦Broken | 3rd Party | Customer Equipment | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Serviceconductor¦Burnedflashed | 3rd Party | Customer Equipment | Service conductor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Serviceconductor¦Normal | 3rd Party | Customer Equipment | Service conductor | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Switch(OH)¦Arcing | 3rd Party | Customer Equipment | Switch (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦CustomerEquipment¦Switch(OH)¦Normal | 3rd Party | Customer Equipment | Switch (OH) | Normal | FNLYEAR 2020: 1; FNLYEAR 2023: 2 | 3
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Switch(UG)¦FailedFaulted | 3rd Party | Customer Equipment | Switch (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Broken | 3rd Party | Customer Equipment | Transformer (OH) | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Burnedflashed | 3rd Party | Customer Equipment | Transformer (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Deteriorated | 3rd Party | Customer Equipment | Transformer (OH) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦CustomerEquipment¦Transformer(OH)¦FailedFaulted | 3rd Party | Customer Equipment | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.6 | 1.2 | 0.6 | 3rdParty¦CustomerEquipment¦Transformer(OH)¦FailedFaulted | 3rd Party | Customer Equipment | Transformer (OH) | Failed/Faulted | FNLYEAR 2020: 2; FNLYEAR 2021: 3; FNLYEAR 2022: 1 | 6
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.6 | 1 | 0.6 | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Normal | 3rd Party | Customer Equipment | Transformer (OH) | Normal | FNLYEAR 2016: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2023: 2 | 6
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer(UG)¦FailedFaulted | 3rd Party | Customer Equipment | Transformer (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.6 | 1 | 0.6 | 3rdParty¦CustomerEquipment¦Transformer(UG)¦Normal | 3rd Party | Customer Equipment | Transformer (UG) | Normal | FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 6
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer¦Annealed | 3rd Party | Customer Equipment | Transformer | Annealed | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer¦Arcing | 3rd Party | Customer Equipment | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer¦Broken | 3rd Party | Customer Equipment | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | 3rdParty¦CustomerEquipment¦Transformer¦Brokenwireonground | 3rd Party | Customer Equipment | Transformer | Broken, wire on ground | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2022 to FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.2 | 0.3 | 3rdParty¦CustomerEquipment¦Transformer¦Burnedflashed | 3rd Party | Customer Equipment | Transformer | Burned/flashed | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2019 to FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 0.8 | 1.4 | 0.8 | 3rdParty¦CustomerEquipment¦Transformer¦FailedFaulted | 3rd Party | Customer Equipment | Transformer | Failed/Faulted | FNLYEAR 2018: 1; FNLYEAR 2020: 5; FNLYEAR 2021: 1; FNLYEAR 2022: 1 | 8
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer¦Normal | 3rd Party | Customer Equipment | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦CustomerEquipment¦Transformer¦Normal | 3rd Party | Customer Equipment | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦Digin3rdparty¦Bushing¦Broken | 3rd Party | Dig in, 3rd party | Bushing | Broken | [10 empty] | 2 | bar: FNLYEAR 2015 to FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Digin3rdparty¦ConductorOverhead¦Broken | 3rd Party | Dig in, 3rd party | Conductor, Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦ConductorOverhead¦Burnedflashed | 3rd Party | Dig in, 3rd party | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken | 3rd Party | Dig in- 3rd party | Conductor- Underground | Broken | FNLYEAR 2024: 4 | 4
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 4.4286 | 4.5 | 4 | 4.5 | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 5 | 8 | 1 | 7 | 4 | 3 | 6 | 6 | 5 |  | 45
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.6 | 0.4 | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Burnedflashed | 3rd Party | Dig in, 3rd party | Conductor, Underground | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2019 to FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1 | 0.7 | 1.2 | 0.7 | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Normal | 3rd Party | Dig in, 3rd party | Conductor, Underground | Normal | FNLYEAR 2019: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 7
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦ConnectororSplice(OH)¦Broken | 3rd Party | Dig in, 3rd party | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦ConnectororSplice(UG)¦FailedFaulted | 3rd Party | Dig in, 3rd party | Connector or Splice (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.4 | 0.4 | 3rdParty¦Digin3rdparty¦CustomerEquipment¦Broken | 3rd Party | Dig in, 3rd party | Customer Equipment | Broken | FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 1 | 4
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦Elbow¦Broken | 3rd Party | Dig in, 3rd party | Elbow | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦Fuse¦FailedFaulted | 3rd Party | Dig in, 3rd party | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Digin3rdparty¦Other¦Broken | 3rd Party | Dig in, 3rd party | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Digin3rdparty¦Other¦FailedFaulted | 3rd Party | Dig in, 3rd party | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Digin3rdparty¦Secondary¦Broken | 3rd Party | Dig in- 3rd party | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 1.1 | 1.2 | 1.1 | 3rdParty¦Digin3rdparty¦Secondary¦Broken | 3rd Party | Dig in, 3rd party | Secondary | Broken | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 |  | 11
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Digin3rdparty¦Secondary¦Deteriorated | 3rd Party | Dig in, 3rd party | Secondary | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Digin3rdparty¦Serviceconductor¦Annealed | 3rd Party | Dig in, 3rd party | Service conductor | Annealed | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Digin3rdparty¦Serviceconductor¦BentorTwisted | 3rd Party | Dig in, 3rd party | Service conductor | Bent or Twisted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0.2 | 0.3 | 3rdParty¦Digin3rdparty¦Serviceconductor¦Broken | 3rd Party | Dig in, 3rd party | Service conductor | Broken | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2018; FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦Serviceconductor¦BurnedOpen | 3rd Party | Dig in, 3rd party | Service conductor | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | 3rdParty¦Digin3rdparty¦Transformer(OH)¦FailedFaulted | 3rd Party | Dig in, 3rd party | Transformer (OH) | Failed/Faulted | FNLYEAR 2017: 1; FNLYEAR 2021: 2 | 3
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Broken | 3rd Party | Dig in, 3rd party | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Burnedflashed | 3rd Party | Dig in, 3rd party | Transformer (UG) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Leaking | 3rd Party | Dig in, 3rd party | Transformer (UG) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Normal | 3rd Party | Dig in, 3rd party | Transformer (UG) | Normal | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Digin3rdparty¦Transformer¦Arcing | 3rd Party | Dig in, 3rd party | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 0.8 | 1.2 | 0.8 | 3rdParty¦Digin3rdparty¦Transformer¦Broken | 3rd Party | Dig in, 3rd party | Transformer | Broken | FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 2 | 8
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦Transformer¦Burnedflashed | 3rd Party | Dig in, 3rd party | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Digin3rdparty¦Transformer¦BurnedOpen | 3rd Party | Dig in, 3rd party | Transformer | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Digin3rdparty¦Transformer¦FailedFaulted | 3rd Party | Dig in, 3rd party | Transformer | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦¦FailedFaulted | 3rd Party | Fire, house or bldg. |  | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Capacitor¦Burnedflashed | 3rd Party | Fire- house or bldg. | Capacitor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Brokenwireonground | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2016: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 1 | 4
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Burnedflashed | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Burnedflashed | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2018: 2; FNLYEAR 2020: 2 | 6
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Normal | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Normal | FNLYEAR 2024: 3 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Normal | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Normal | 1 | 3 | 3 | 3 | 3 | 1 | 3 | 5 | 2 |  | 24
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Together | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorUnderground¦Burnedflashed | 3rd Party | Fire, house or bldg. | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConductorUnderground¦Normal | 3rd Party | Fire, house or bldg. | Conductor, Underground | Normal | FNLYEAR 2018: 2; FNLYEAR 2019: 1 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦ConnectororSplice(OH)¦BurnedOpen | 3rd Party | Fire, house or bldg. | Connector or Splice (OH) | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦CrossarmWood¦Broken | 3rd Party | Fire, house or bldg. | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦CrossarmWood¦Burnedflashed | 3rd Party | Fire, house or bldg. | Crossarm, Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Burnedflashed | 3rd Party | Fire, house or bldg. | Customer Equipment | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 4
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦BurnedOpen | 3rd Party | Fire, house or bldg. | Customer Equipment | Burned Open | FNLYEAR 2015: 2; FNLYEAR 2018: 1 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Contaminated | 3rd Party | Fire- house or bldg. | Customer Equipment | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Malfunctioning | 3rd Party | Fire, house or bldg. | Customer Equipment | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Cutoutfuseholder¦FailedFaulted | 3rd Party | Fire, house or bldg. | Cutout, fuse holder | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Fuse¦Normal | 3rd Party | Fire, house or bldg. | Fuse | Normal | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2018: 3 | 5
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Insulator¦FailedFaulted | 3rd Party | Fire- house or bldg. | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Jumper¦Broken | 3rd Party | Fire, house or bldg. | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Jumper¦Normal | 3rd Party | Fire, house or bldg. | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦MeteringEquipment¦Arcing | 3rd Party | Fire, house or bldg. | Metering Equipment | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦MeteringEquipment¦Burnedflashed | 3rd Party | Fire, house or bldg. | Metering Equipment | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦MeteringEquipment¦Normal | 3rd Party | Fire- house or bldg. | Metering Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Other¦Burnedflashed | 3rd Party | Fire, house or bldg. | Other | Burned/flashed | FNLYEAR 2017: 1; FNLYEAR 2020: 2 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Other¦Normal | 3rd Party | Fire, house or bldg. | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦PoleWood¦Broken | 3rd Party | Fire, house or bldg. | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦PoleWood¦Brokenwireonground | 3rd Party | Fire- house or bldg. | Pole-Wood | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦PoleWood¦Brokenwireonground | 3rd Party | Fire, house or bldg. | Pole-Wood | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦PoleWood¦Burnedflashed | 3rd Party | Fire- house or bldg. | Pole-Wood | Burned/flashed | FNLYEAR 2024: 2 | 2
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦PoleWood¦Burnedflashed | 3rd Party | Fire, house or bldg. | Pole-Wood | Burned/flashed | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 2; FNLYEAR 2022: 2 | 7
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦PoleWood¦Normal | 3rd Party | Fire, house or bldg. | Pole-Wood | Normal | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦Brokenwireonground | 3rd Party | Fire- house or bldg. | Secondary | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦Brokenwireonground | 3rd Party | Fire, house or bldg. | Secondary | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦Burnedflashed | 3rd Party | Fire- house or bldg. | Secondary | Burned/flashed | FNLYEAR 2024: 2 | 2
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦Burnedflashed | 3rd Party | Fire, house or bldg. | Secondary | Burned/flashed |  |  | 1 | 1 | 2 |  | 2 | 1 | 1 |  | 8
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦BurnedOpen | 3rd Party | Fire, house or bldg. | Secondary | Burned Open | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2021; FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦Normal | 3rd Party | Fire, house or bldg. | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦OnGround | 3rd Party | Fire, house or bldg. | Secondary | On Ground | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Secondary¦Together | 3rd Party | Fire, house or bldg. | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Broken | 3rd Party | Fire, house or bldg. | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Brokenwireonground | 3rd Party | Fire, house or bldg. | Service conductor | Broken, wire on ground | FNLYEAR 2022: 3; FNLYEAR 2023: 1 | 4
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Burnedflashed | 3rd Party | Fire, house or bldg. | Service conductor | Burned/flashed | FNLYEAR 2016: 2; FNLYEAR 2018: 3; FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 8
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Serviceconductor¦BurnedOpen | 3rd Party | Fire, house or bldg. | Service conductor | Burned Open | FNLYEAR 2020: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 1 | 4
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Normal | 3rd Party | Fire- house or bldg. | Service conductor | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Brokenwireonground | 3rd Party | Fire, house or bldg. | Transformer (OH) | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Burnedflashed | 3rd Party | Fire, house or bldg. | Transformer (OH) | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2019; FNLYEAR 2021 to FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦FailedFaulted | 3rd Party | Fire, house or bldg. | Transformer (OH) | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 2 | 4
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Normal | 3rd Party | Fire, house or bldg. | Transformer (OH) | Normal | 3 |  | 1 |  | 1 | 1 | 2 | 1 |  |  | 9
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer(UG)¦Normal | 3rd Party | Fire- house or bldg. | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer(UG)¦Normal | 3rd Party | Fire, house or bldg. | Transformer (UG) | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer¦Burnedflashed | 3rd Party | Fire, house or bldg. | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer¦BurnedOpen | 3rd Party | Fire, house or bldg. | Transformer | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Firehouseorbldg¦Transformer¦FailedFaulted | 3rd Party | Fire, house or bldg. | Transformer | Failed/Faulted | FNLYEAR 2015: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦GunShot¦ConductorOverhead¦Broken | 3rd Party | Gun Shot | Conductor- Overhead | Broken | FNLYEAR 2024: 3 | 3
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 1.44 | 1.44 | 2.1429 | 1.6 | 1.8 | 1.6 | 3rdParty¦GunShot¦ConductorOverhead¦Broken | 3rd Party | Gun Shot | Conductor, Overhead | Broken |  | 1 |  | 1 | 5 | 4 | 3 | 1 | 1 |  | 16
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.6 | 0.6 | 1.1429 | 1.5 | 0.6 | 1.5 | 3rdParty¦GunShot¦ConductorOverhead¦Brokenwireonground | 3rd Party | Gun Shot | Conductor, Overhead | Broken, wire on ground | 2 | 2 | 3 | 3 | 2 | 1 |  |  | 2 |  | 15
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.57143 | 0.6 | 0.4 | 0.6 | 3rdParty¦GunShot¦ConductorOverhead¦Deteriorated | 3rd Party | Gun Shot | Conductor, Overhead | Deteriorated | FNLYEAR 2017: 2; FNLYEAR 2019: 2; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 6
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦GunShot¦ConductorOverhead¦Together | 3rd Party | Gun Shot | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦GunShot¦ConductorUnderground¦Broken | 3rd Party | Gun Shot | Conductor, Underground | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦GunShot¦Fuse¦BurnedOpen | 3rd Party | Gun Shot | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦GunShot¦Insulator¦FailedFaulted | 3rd Party | Gun Shot | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦GunShot¦Pothead(RiserTermination)¦Burnedflashed | 3rd Party | Gun Shot | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦GunShot¦Regulator¦Leaking | 3rd Party | Gun Shot | Regulator | Leaking | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦GunShot¦Secondary¦Broken | 3rd Party | Gun Shot | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦GunShot¦Transformer(OH)¦Leaking | 3rd Party | Gun Shot | Transformer (OH) | Leaking | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦GunShot¦Transformer¦FailedFaulted | 3rd Party | Gun Shot | Transformer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Kite¦ConductorOverhead¦Contaminated | 3rd Party | Kite | Conductor- Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Kite¦ConductorOverhead¦Normal | 3rd Party | Kite | Conductor- Overhead | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.42857 | 0.5 | 0.6 | 0.5 | 3rdParty¦Kite¦ConductorOverhead¦Normal | 3rd Party | Kite | Conductor, Overhead | Normal | FNLYEAR 2015: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 5
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Arcing | 3rd Party | Metallic Balloon | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Broken | 3rd Party | Metallic Balloon | Conductor, Overhead | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Third Party (Balloon) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0.4 | 0.3 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Brokenwireonground | 3rd Party | Metallic Balloon | Conductor, Overhead | Broken, wire on ground | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2020 to FNLYEAR 2021
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Burnedflashed | 3rd Party | Metallic Balloon | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Contaminated | 3rd Party | Metallic Balloon | Conductor- Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.9 | 0.9 | 1.4286 | 1 | 2 | 1 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal | 3rd Party | Metallic Balloon | Conductor- Overhead | Normal | FNLYEAR 2024: 10 | 10
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 6.48 | 6.48 | 7.8571 | 7.2 | 6.8 | 7.2 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 4 | 8 | 5 | 13 | 8 | 12 | 11 | 7 | 4 |  | 72
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Together | 3rd Party | Metallic Balloon | Conductor- Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.28571 | 0.6 | 0.4 | 0.6 | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Together | 3rd Party | Metallic Balloon | Conductor, Overhead | Together | FNLYEAR 2015: 1; FNLYEAR 2017: 3; FNLYEAR 2021: 1; FNLYEAR 2022: 1 | 6
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦MetallicBalloon¦Cutoutfuseholder¦FailedFaulted | 3rd Party | Metallic Balloon | Cutout, fuse holder | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 1.53 | 1.53 | 0.71429 | 1.7 | 0.2 | 1.7 | 3rdParty¦MetallicBalloon¦Fuse¦FailedFaulted | 3rd Party | Metallic Balloon | Fuse | Failed/Faulted | 5 | 4 | 3 | 3 | 1 | 1 |  |  |  |  | 17
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦MetallicBalloon¦Fuse¦Normal | 3rd Party | Metallic Balloon | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Balloon) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.42857 | 0.4 | 0.4 | 0.4 | 3rdParty¦MetallicBalloon¦Fuse¦Normal | 3rd Party | Metallic Balloon | Fuse | Normal | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2018; FNLYEAR 2021; FNLYEAR 2023
Third Party (Balloon) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦MetallicBalloon¦Other¦Normal | 3rd Party | Metallic Balloon | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (Balloon) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦MetallicBalloon¦PoleWood¦Burnedflashed | 3rd Party | Metallic Balloon | Pole-Wood | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2023
Third Party (Balloon) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦MetallicBalloon¦Pothead(RiserTermination)¦Normal | 3rd Party | Metallic Balloon | Pothead(Riser Termination) | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (Balloon) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦MetallicBalloon¦Transformer(OH)¦Burnedflashed | 3rd Party | Metallic Balloon | Transformer (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (Balloon) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦MetallicBalloon¦Transformer(OH)¦Leaking | 3rd Party | Metallic Balloon | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (Balloon) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦MetallicBalloon¦Transformer(OH)¦Normal | 3rd Party | Metallic Balloon | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦AnchororGuy¦Broken | 3rd Party | Other | Anchor or Guy | Broken | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2020 to FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦AnchororGuy¦Normal | 3rd Party | Other | Anchor or Guy | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦CircuitBreaker¦Normal | 3rd Party | Other | Circuit Breaker | Normal | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦Arcing | 3rd Party | Other | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦BentorTwisted | 3rd Party | Other | Conductor, Overhead | Bent or Twisted | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦Broken | 3rd Party | Other | Conductor, Overhead | Broken | FNLYEAR 2016: 1; FNLYEAR 2017: 2; FNLYEAR 2020: 1; FNLYEAR 2022: 1 | 5
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦Brokenwireonground | 3rd Party | Other | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 2 | 2
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦Brokenwireonground | 3rd Party | Other | Conductor, Overhead | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2018 to FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Other¦ConductorOverhead¦Deteriorated | 3rd Party | Other | Conductor- Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦Normal | 3rd Party | Other | Conductor- Overhead | Normal | FNLYEAR 2024: 19 | 19
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦Normal | 3rd Party | Other | Conductor, Overhead | Normal | 1 | 6 | 6 | 5 | 5 | 3 | 8 | 8 | 19 |  | 61
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦OnGround | 3rd Party | Other | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorOverhead¦Together | 3rd Party | Other | Conductor, Overhead | Together |  | 1 | 1 | 2 | 1 | 3 |  | 1 | 1 |  | 10
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Other¦ConductorUnderground¦Burnedflashed | 3rd Party | Other | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦ConductorUnderground¦Normal | 3rd Party | Other | Conductor, Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦CrossarmWood¦Broken | 3rd Party | Other | Crossarm- Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦CrossarmWood¦Broken | 3rd Party | Other | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦CustomerEquipment¦Leaking | 3rd Party | Other | Customer Equipment | Leaking | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦CustomerEquipment¦Normal | 3rd Party | Other | Customer Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦CustomerEquipment¦Normal | 3rd Party | Other | Customer Equipment | Normal | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2022 to FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Cutoutfuseholder¦Normal | 3rd Party | Other | Cutout, fuse holder | Normal | FNLYEAR 2020: 2 | 2
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Cutoutfuseholder¦OnGround | 3rd Party | Other | Cutout, fuse holder | On Ground | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Fuse¦FailedFaulted | 3rd Party | Other | Fuse | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2020: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 7
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Fuse¦Normal | 3rd Party | Other | Fuse | Normal | FNLYEAR 2020: 4; FNLYEAR 2022: 2; FNLYEAR 2023: 3 | 9
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Generator¦Normal | 3rd Party | Other | Generator | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Generator¦Normal | 3rd Party | Other | Generator | Normal | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Insulator¦Broken | 3rd Party | Other | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Insulator¦Normal | 3rd Party | Other | Insulator | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Jumper¦ | 3rd Party | Other | Jumper | [11 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Jumper¦Broken | 3rd Party | Other | Jumper | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Jumper¦Normal | 3rd Party | Other | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦MeteringEquipment¦FailedFaulted | 3rd Party | Other | Metering Equipment | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦MeteringEquipment¦Normal | 3rd Party | Other | Metering Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Other¦Broken | 3rd Party | Other | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Other¦Brokenwireonground | 3rd Party | Other | Other | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Other¦Deteriorated | 3rd Party | Other | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Other¦FailedFaulted | 3rd Party | Other | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Other¦Malfunctioning | 3rd Party | Other | Other | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Other¦Normal | 3rd Party | Other | Other | Normal | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2021 to FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦PoleWood¦Broken | 3rd Party | Other | Pole-Wood | Broken | FNLYEAR 2016: 2; FNLYEAR 2017: 2; FNLYEAR 2021: 2; FNLYEAR 2023: 2 | 8
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦PoleWood¦Brokenwireonground | 3rd Party | Other | Pole-Wood | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2015 to FNLYEAR 2016
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦PoleWood¦Burnedflashed | 3rd Party | Other | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦PoleWood¦Contaminated | 3rd Party | Other | Pole-Wood | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦PoleWood¦Deteriorated | 3rd Party | Other | Pole-Wood | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Recloser¦Normal | 3rd Party | Other | Recloser | Normal | FNLYEAR 2015: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 4
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Secondary¦Burnedflashed | 3rd Party | Other | Secondary | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Secondary¦Normal | 3rd Party | Other | Secondary | Normal | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Serviceconductor¦Broken | 3rd Party | Other | Service conductor | Broken | FNLYEAR 2021: 1; FNLYEAR 2023: 2 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Serviceconductor¦Brokenwireonground | 3rd Party | Other | Service conductor | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Serviceconductor¦Burnedflashed | 3rd Party | Other | Service conductor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Serviceconductor¦Normal | 3rd Party | Other | Service conductor | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Serviceconductor¦Normal | 3rd Party | Other | Service conductor | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(OH)¦ | 3rd Party | Other | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(OH)¦Broken | 3rd Party | Other | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(OH)¦Contaminated | 3rd Party | Other | Transformer (OH) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(OH)¦FailedFaulted | 3rd Party | Other | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 3 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(OH)¦FailedFaulted | 3rd Party | Other | Transformer (OH) | Failed/Faulted | FNLYEAR 2020: 2; FNLYEAR 2021: 1; FNLYEAR 2023: 2 | 5
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(OH)¦Normal | 3rd Party | Other | Transformer (OH) | Normal |  | 2 | 1 | 1 | 1 | 2 | 3 | 1 |  |  | 11
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(UG)¦Broken | 3rd Party | Other | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(UG)¦Broken | 3rd Party | Other | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer(UG)¦Normal | 3rd Party | Other | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer¦Broken | 3rd Party | Other | Transformer | Broken | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer¦FailedFaulted | 3rd Party | Other | Transformer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer¦FailedFaulted | 3rd Party | Other | Transformer | Failed/Faulted | FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 3
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer¦Malfunctioning | 3rd Party | Other | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Other¦Transformer¦Normal | 3rd Party | Other | Transformer | Normal | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ThrownObject¦Bushing¦Normal | 3rd Party | Thrown Object | Bushing | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.57143 | 0.5 | 0.4 | 0.5 | 3rdParty¦ThrownObject¦ConductorOverhead¦Normal | 3rd Party | Thrown Object | Conductor, Overhead | Normal | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2022: 2 | 5
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦ThrownObject¦ConductorOverhead¦Together | 3rd Party | Thrown Object | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦ThrownObject¦Fuse¦Normal | 3rd Party | Thrown Object | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦ThrownObject¦Transformer¦Broken | 3rd Party | Thrown Object | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦AnchororGuy¦Broken | 3rd Party | Tree - cutting, 3rd party | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Treecutting3rdparty¦AnchororGuy¦Normal | 3rd Party | Tree - cutting, 3rd party | Anchor or Guy | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Bushing¦Broken | 3rd Party | Tree - cutting, 3rd party | Bushing | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Arcing | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Broken | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.42857 | 0.6 | 0.6 | 0.6 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Broken | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 1 | 6
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 1 | 0.7 | 1.4 | 0.7 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 7 | 7
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 7.04 | 7.04 | 15.1429 | 17.6 | 13.8 | 17.6 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 17 | 22 | 31 | 18 | 19 | 24 | 17 | 13 | 15 |  | 176
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.42857 | 0.4 | 0.4 | 0.4 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonobject | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on object | [10 empty] | 4 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2020 to FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.57143 | 0.5 | 0.6 | 0.5 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Burnedflashed | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Burned/flashed | [10 empty] | 5 | bar: FNLYEAR 2015; FNLYEAR 2019 to FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Deteriorated | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 1.53 | 1.53 | 2.4286 | 1.7 | 3.4 | 1.7 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Normal | FNLYEAR 2024: 17 | 17
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 17.64 | 17.64 | 21 | 19.6 | 18.8 | 19.6 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 17 | 18 | 14 | 25 | 28 | 34 | 13 | 25 | 22 |  | 196
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 0.71429 | 0.9 | 0.4 | 0.9 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦OnGround | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | On Ground | FNLYEAR 2016: 2; FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 2 | 9
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 3.15 | 3.15 | 2.4286 | 3.5 | 1.4 | 3.5 | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Together | 8 | 10 |  | 5 | 5 | 2 | 2 | 3 |  |  | 35
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦ConductorUnderground¦Normal | 3rd Party | Tree - cutting, 3rd party | Conductor, Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦ConnectororSplice(OH)¦Broken | 3rd Party | Tree - cutting- 3rd party | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦ConnectororSplice(OH)¦Broken | 3rd Party | Tree - cutting, 3rd party | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Treecutting3rdparty¦ConnectororSplice(OH)¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Connector or Splice (OH) | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Broken | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken | 1 |  | 2 |  | 2 | 1 | 1 | 2 | 1 |  | 10
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.48 | 0.48 | 1.4286 | 1.2 | 1 | 1.2 | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken, wire on ground | 1 | 1 |  | 4 | 1 | 3 |  | 2 |  |  | 12
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Brokenwireonobject | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken, wire on object | FNLYEAR 2017: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Cutoutfuseholder¦Normal | 3rd Party | Tree - cutting- 3rd party | Cutout- fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦Treecutting3rdparty¦Cutoutfuseholder¦Normal | 3rd Party | Tree - cutting, 3rd party | Cutout, fuse holder | Normal | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Fuse¦Broken | 3rd Party | Tree - cutting, 3rd party | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Fuse¦BurnedOpen | 3rd Party | Tree - cutting, 3rd party | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted | 3rd Party | Tree - cutting- 3rd party | Fuse | Failed/Faulted | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.92 | 0.92 | 1.7143 | 2.3 | 0.6 | 2.3 | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 1 | 5 | 5 | 5 | 4 | 1 | 2 |  |  |  | 23
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Fuse¦Normal | 3rd Party | Tree - cutting- 3rd party | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 0.71429 | 0.9 | 0.8 | 0.9 | 3rdParty¦Treecutting3rdparty¦Fuse¦Normal | 3rd Party | Tree - cutting, 3rd party | Fuse | Normal | 1 | 3 |  | 1 |  | 1 | 2 | 1 |  |  | 9
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Insulator¦Broken | 3rd Party | Tree - cutting- 3rd party | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0.2 | 0.4 | 3rdParty¦Treecutting3rdparty¦Insulator¦Broken | 3rd Party | Tree - cutting, 3rd party | Insulator | Broken | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2018; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Insulator¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Insulator | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Jumper¦BurnedOpen | 3rd Party | Tree - cutting, 3rd party | Jumper | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Jumper¦Normal | 3rd Party | Tree - cutting, 3rd party | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Treecutting3rdparty¦PoleWood¦Broken | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 0.57143 | 0.7 | 0.6 | 0.7 | 3rdParty¦Treecutting3rdparty¦PoleWood¦Broken | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken | FNLYEAR 2015: 1; FNLYEAR 2017: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 7
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonground | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken- wire on ground | FNLYEAR 2024: 3 | 3
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.56 | 0.56 | 1.5714 | 1.4 | 1.4 | 1.4 | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken, wire on ground |  | 2 | 1 | 3 | 1 | 1 | 2 | 4 |  |  | 14
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonobject | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦PoleWood¦Normal | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Recloser¦Malfunctioning | 3rd Party | Tree - cutting, 3rd party | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0 | 0.2 | 3rdParty¦Treecutting3rdparty¦Recloser¦Normal | 3rd Party | Tree - cutting, 3rd party | Recloser | Normal | [10 empty] | 2 | bar: FNLYEAR 2018 to FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Treecutting3rdparty¦Secondary¦Broken | 3rd Party | Tree - cutting- 3rd party | Secondary | Broken | FNLYEAR 2024: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.42857 | 0.6 | 0.4 | 0.6 | 3rdParty¦Treecutting3rdparty¦Secondary¦Broken | 3rd Party | Tree - cutting, 3rd party | Secondary | Broken | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2018: 1; FNLYEAR 2022: 2 | 6
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.14286 | 0.3 | 0.2 | 0.3 | 3rdParty¦Treecutting3rdparty¦Secondary¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Secondary | Broken, wire on ground | FNLYEAR 2016: 2; FNLYEAR 2020: 1 | 3
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Secondary¦Normal | 3rd Party | Tree - cutting, 3rd party | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Secondary¦OnGround | 3rd Party | Tree - cutting, 3rd party | Secondary | On Ground | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Secondary¦Together | 3rd Party | Tree - cutting, 3rd party | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | 3rdParty¦Treecutting3rdparty¦Serviceconductor¦Broken | 3rd Party | Tree - cutting, 3rd party | Service conductor | Broken | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1 | 0.9 | 1 | 0.9 | 3rdParty¦Treecutting3rdparty¦Serviceconductor¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Service conductor | Broken, wire on ground | 2 |  |  | 1 | 1 | 1 | 1 | 1 | 2 |  | 9
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Treecutting3rdparty¦Serviceconductor¦Normal | 3rd Party | Tree - cutting, 3rd party | Service conductor | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.4 | 0.3 | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Broken | 3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Broken | FNLYEAR 2018: 1; FNLYEAR 2022: 2 | 3
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Brokenwireonground | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦FailedFaulted | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.57143 | 0.6 | 0.6 | 0.6 | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦FailedFaulted | 3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Failed/Faulted | FNLYEAR 2015: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 6
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Leaking | 3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Leaking | FNLYEAR 2023: 2 | 2
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Normal | 3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer(UG)¦Normal | 3rd Party | Tree - cutting- 3rd party | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.28571 | 0.3 | 0.4 | 0.3 | 3rdParty¦Treecutting3rdparty¦Transformer¦Broken | 3rd Party | Tree - cutting, 3rd party | Transformer | Broken | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2020; FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer¦Brokenwireonground | 3rd Party | Tree - cutting, 3rd party | Transformer | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer¦Brokenwireonobject | 3rd Party | Tree - cutting, 3rd party | Transformer | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer¦Burnedflashed | 3rd Party | Tree - cutting, 3rd party | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer¦Contaminated | 3rd Party | Tree - cutting, 3rd party | Transformer | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer¦Deteriorated | 3rd Party | Tree - cutting, 3rd party | Transformer | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0 | 0.3 | 3rdParty¦Treecutting3rdparty¦Transformer¦FailedFaulted | 3rd Party | Tree - cutting, 3rd party | Transformer | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2017 to FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Transformer¦Leaking | 3rd Party | Tree - cutting, 3rd party | Transformer | Leaking | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Treecutting3rdparty¦Woodpin¦Broken | 3rd Party | Tree - cutting, 3rd party | Woodpin | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦Bushing¦Broken | 3rd Party | Vandalism | Bushing | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Vandalism¦CircuitBreaker¦Normal | 3rd Party | Vandalism | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Vandalism¦ConductorOverhead¦Brokenwireonground | 3rd Party | Vandalism | Conductor, Overhead | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦ConductorOverhead¦Normal | 3rd Party | Vandalism | Conductor, Overhead | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦ConductorUnderground¦Broken | 3rd Party | Vandalism | Conductor, Underground | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦ConductorUnderground¦Burnedflashed | 3rd Party | Vandalism | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vandalism¦Fuse¦FailedFaulted | 3rd Party | Vandalism | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦MeteringEquipment¦FailedFaulted | 3rd Party | Vandalism | Metering Equipment | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Vandalism¦Other¦Broken | 3rd Party | Vandalism | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Vandalism¦Other¦Burnedflashed | 3rd Party | Vandalism | Other | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦PoleWood¦Broken | 3rd Party | Vandalism | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.2 | 0.3 | 3rdParty¦Vandalism¦PoleWood¦Broken | 3rd Party | Vandalism | Pole-Wood | Broken | FNLYEAR 2019: 2; FNLYEAR 2021: 1 | 3
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vandalism¦PoleWood¦Brokenwireonground | 3rd Party | Vandalism | Pole-Wood | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦PoleWood¦Burnedflashed | 3rd Party | Vandalism | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦Recloser¦Broken | 3rd Party | Vandalism | Recloser | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦Secondary¦Broken | 3rd Party | Vandalism | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦Switch(OH)¦Normal | 3rd Party | Vandalism | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦Transformer(OH)¦Burnedflashed | 3rd Party | Vandalism | Transformer (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Vandalism¦Transformer(OH)¦FailedFaulted | 3rd Party | Vandalism | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦Transformer(UG)¦Broken | 3rd Party | Vandalism | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vandalism¦Transformer¦Contaminated | 3rd Party | Vandalism | Transformer | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vandalism¦Transformer¦FailedFaulted | 3rd Party | Vandalism | Transformer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (Vehicle) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Vehicle¦¦BurnedOpen | 3rd Party | Vehicle |  | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (Vehicle) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 3rdParty¦Vehicle¦¦Normal | 3rd Party | Vehicle |  | Normal | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2019
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.57143 | 0.5 | 0.8 | 0.5 | 3rdParty¦Vehicle¦AnchororGuy¦BentorTwisted | 3rd Party | Vehicle | Anchor or Guy | Bent or Twisted | FNLYEAR 2017: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 5
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 1.08 | 1.08 | 1.7143 | 1.2 | 2.4 | 1.2 | 3rdParty¦Vehicle¦AnchororGuy¦Broken | 3rd Party | Vehicle | Anchor or Guy | Broken | FNLYEAR 2024: 12 | 12
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 7.38 | 7.38 | 8.7143 | 8.2 | 8.2 | 8.2 | 3rdParty¦Vehicle¦AnchororGuy¦Broken | 3rd Party | Vehicle | Anchor or Guy | Broken | 6 | 10 | 5 | 11 | 9 | 9 | 8 | 15 | 9 |  | 82
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦AnchororGuy¦Brokenwireonground | 3rd Party | Vehicle | Anchor or Guy | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1.2857 | 0.9 | 1.4 | 0.9 | 3rdParty¦Vehicle¦AnchororGuy¦Brokenwireonground | 3rd Party | Vehicle | Anchor or Guy | Broken, wire on ground | FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 3; FNLYEAR 2022: 3; FNLYEAR 2023: 1 | 9
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦AnchororGuy¦Normal | 3rd Party | Vehicle | Anchor or Guy | Normal | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 2.61 | 2.61 | 2.2857 | 2.9 | 2.6 | 2.9 | 3rdParty¦Vehicle¦AnchororGuy¦Normal | 3rd Party | Vehicle | Anchor or Guy | Normal | 5 | 3 | 5 |  | 3 | 4 | 1 | 4 | 4 |  | 29
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Bushing¦Broken | 3rd Party | Vehicle | Bushing | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Capacitor¦Burnedflashed | 3rd Party | Vehicle | Capacitor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦ConductorOverhead¦BentorTwisted | 3rd Party | Vehicle | Conductor- Overhead | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vehicle¦ConductorOverhead¦BentorTwisted | 3rd Party | Vehicle | Conductor, Overhead | Bent or Twisted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2022
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 1 | 0.9 | 0.6 | 0.9 | 3rdParty¦Vehicle¦ConductorOverhead¦Broken | 3rd Party | Vehicle | Conductor, Overhead | Broken | FNLYEAR 2016: 2; FNLYEAR 2018: 2; FNLYEAR 2019: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 9
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 1.5714 | 1.1 | 2.2 | 1.1 | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground | 3rd Party | Vehicle | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 11 | 11
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 3.16 | 3.16 | 8 | 7.9 | 7 | 7.9 | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 8 | 7 | 8 | 9 | 12 | 9 | 12 | 6 | 8 |  | 79
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.71429 | 0.6 | 0.6 | 0.6 | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonobject | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on object | FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 6
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Vehicle¦ConductorOverhead¦Burnedflashed | 3rd Party | Vehicle | Conductor, Overhead | Burned/flashed | FNLYEAR 2020: 1; FNLYEAR 2023: 2 | 3
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦ConductorOverhead¦Contaminated | 3rd Party | Vehicle | Conductor, Overhead | Contaminated | FNLYEAR 2018: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦ConductorOverhead¦Deteriorated | 3rd Party | Vehicle | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 1.2 | 0.6 | 3rdParty¦Vehicle¦ConductorOverhead¦Normal | 3rd Party | Vehicle | Conductor- Overhead | Normal | FNLYEAR 2024: 6 | 6
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 5.85 | 5.85 | 6.5714 | 6.5 | 7.8 | 6.5 | 3rdParty¦Vehicle¦ConductorOverhead¦Normal | 3rd Party | Vehicle | Conductor, Overhead | Normal | 5 | 2 | 12 | 3 | 4 | 7 | 12 | 12 | 8 |  | 65
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0 | 0.4 | 0 | 0.4 | 3rdParty¦Vehicle¦ConductorOverhead¦OnGround | 3rd Party | Vehicle | Conductor, Overhead | On Ground | FNLYEAR 2015: 2; FNLYEAR 2016: 2 | 4
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Vehicle¦ConductorOverhead¦Together | 3rd Party | Vehicle | Conductor- Overhead | Together | FNLYEAR 2024: 3 | 3
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 1.89 | 1.89 | 2 | 2.1 | 1.4 | 2.1 | 3rdParty¦Vehicle¦ConductorOverhead¦Together | 3rd Party | Vehicle | Conductor, Overhead | Together | 1 | 2 | 4 | 5 | 2 | 2 | 2 | 1 | 2 |  | 21
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.5 | 0.2 | 0.5 | 3rdParty¦Vehicle¦ConductorUnderground¦Broken | 3rd Party | Vehicle | Conductor, Underground | Broken | FNLYEAR 2015: 2; FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2020: 1 | 5
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦ConductorUnderground¦Burnedflashed | 3rd Party | Vehicle | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦ConductorUnderground¦Normal | 3rd Party | Vehicle | Conductor- Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Broken | 3rd Party | Vehicle | Connector or Splice (OH) | Broken | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Brokenwireonground | 3rd Party | Vehicle | Connector or Splice (OH) | Broken, wire on ground | FNLYEAR 2017: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Normal | 3rd Party | Vehicle | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦ConnectororSplice(UG)¦Broken | 3rd Party | Vehicle | Connector or Splice (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦ConnectororSplice(UG)¦Burnedflashed | 3rd Party | Vehicle | Connector or Splice (UG) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦CrossarmWood¦Broken | 3rd Party | Vehicle | Crossarm- Wood | Broken | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 2.43 | 2.43 | 3 | 2.7 | 2.6 | 2.7 | 3rdParty¦Vehicle¦CrossarmWood¦Broken | 3rd Party | Vehicle | Crossarm, Wood | Broken |  | 4 | 2 | 2 | 6 | 5 | 4 | 2 | 2 |  | 27
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.71429 | 0.6 | 0.4 | 0.6 | 3rdParty¦Vehicle¦CrossarmWood¦Brokenwireonground | 3rd Party | Vehicle | Crossarm, Wood | Broken, wire on ground | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2022: 1 | 6
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦CrossarmWood¦Brokenwireonobject | 3rd Party | Vehicle | Crossarm, Wood | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦CrossarmWood¦Burnedflashed | 3rd Party | Vehicle | Crossarm- Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦CrossarmWood¦Normal | 3rd Party | Vehicle | Crossarm, Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦CustomerEquipment¦Broken | 3rd Party | Vehicle | Customer Equipment | Broken | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2017
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0.2 | 0.4 | 3rdParty¦Vehicle¦Cutoutfuseholder¦Broken | 3rd Party | Vehicle | Cutout, fuse holder | Broken | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2018; FNLYEAR 2021
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦Cutoutfuseholder¦FailedFaulted | 3rd Party | Vehicle | Cutout, fuse holder | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2018
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦Cutoutfuseholder¦Normal | 3rd Party | Vehicle | Cutout- fuse holder | Normal | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦Cutoutfuseholder¦Normal | 3rd Party | Vehicle | Cutout, fuse holder | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2019
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Elbow¦Broken | 3rd Party | Vehicle | Elbow | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Fuse¦BurnedOpen | 3rd Party | Vehicle | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.57143 | 0.5 | 0.8 | 0.5 | 3rdParty¦Vehicle¦Fuse¦BurnedOpen | 3rd Party | Vehicle | Fuse | Burned Open | FNLYEAR 2016: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 5
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 1.89 | 1.89 | 1.2857 | 2.1 | 0.6 | 2.1 | 3rdParty¦Vehicle¦Fuse¦FailedFaulted | 3rd Party | Vehicle | Fuse | Failed/Faulted | 6 | 1 | 5 | 5 | 1 | 1 | 1 | 1 |  |  | 21
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦Fuse¦Normal | 3rd Party | Vehicle | Fuse | Normal | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 1.98 | 1.98 | 2.8571 | 2.2 | 2.8 | 2.2 | 3rdParty¦Vehicle¦Fuse¦Normal | 3rd Party | Vehicle | Fuse | Normal |  |  | 2 | 2 | 4 | 2 |  | 3 | 9 |  | 22
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.28571 | 0.5 | 0 | 0.5 | 3rdParty¦Vehicle¦Insulator¦Broken | 3rd Party | Vehicle | Insulator | Broken | [10 empty] | 5 | bar: FNLYEAR 2015 to FNLYEAR 2019
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦Jumper¦Broken | 3rd Party | Vehicle | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦Jumper¦BurnedOpen | 3rd Party | Vehicle | Jumper | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2016
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦LightningArrestor¦FailedFaulted | 3rd Party | Vehicle | Lightning Arrestor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 1 | 1.1 | 1.2 | 1.1 | 3rdParty¦Vehicle¦Other¦Broken | 3rd Party | Vehicle | Other | Broken | 1 | 2 | 1 | 1 |  |  | 3 |  | 3 |  | 11
Third Party (Vehicle) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0.85714 | 0.7 | 0.6 | 0.7 | 3rdParty¦Vehicle¦Other¦Normal | 3rd Party | Vehicle | Other | Normal | FNLYEAR 2015: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 7
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vehicle¦PoleTowersteel¦Broken | 3rd Party | Vehicle | Pole - Tower, steel | Broken | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 2.36 | 2.36 | 8.4286 | 5.9 | 11.8 | 5.9 | 3rdParty¦Vehicle¦PoleWood¦Broken | 3rd Party | Vehicle | Pole-Wood | Broken | FNLYEAR 2024: 59 | 59
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 36.92 | 36.92 | 92.1429 | 92.3 | 85.4 | 92.3 | 3rdParty¦Vehicle¦PoleWood¦Broken | 3rd Party | Vehicle | Pole-Wood | Broken | 65 | 119 | 94 | 113 | 105 | 120 | 116 | 104 | 87 |  | 923
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.96 | 0.96 | 3.4286 | 2.4 | 4.8 | 2.4 | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground | 3rd Party | Vehicle | Pole-Wood | Broken- wire on ground | FNLYEAR 2024: 24 | 24
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 18.32 | 18.32 | 42.4286 | 45.8 | 36.8 | 45.8 | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 49 | 68 | 44 | 57 | 56 | 58 | 55 | 41 | 30 |  | 458
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonobject | 3rd Party | Vehicle | Pole-Wood | Broken- wire on object | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 1.48 | 1.48 | 3 | 3.7 | 2.2 | 3.7 | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonobject | 3rd Party | Vehicle | Pole-Wood | Broken, wire on object | 5 | 5 | 6 | 5 | 5 | 3 | 6 | 2 |  |  | 37
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦PoleWood¦Burnedflashed | 3rd Party | Vehicle | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vehicle¦PoleWood¦Burnedflashed | 3rd Party | Vehicle | Pole-Wood | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦PoleWood¦Deteriorated | 3rd Party | Vehicle | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦PoleWood¦Deteriorated | 3rd Party | Vehicle | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 1 | 0.7 | 1.4 | 0.7 | 3rdParty¦Vehicle¦PoleWood¦Normal | 3rd Party | Vehicle | Pole-Wood | Normal | FNLYEAR 2024: 7 | 7
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 4.2 | 4.2 | 5.8571 | 6 | 5.8 | 6 | 3rdParty¦Vehicle¦PoleWood¦Normal | 3rd Party | Vehicle | Pole-Wood | Normal | 6 | 7 | 6 | 7 | 5 | 13 | 9 | 3 | 4 |  | 60
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 0.85714 | 1.1 | 1 | 1.1 | 3rdParty¦Vehicle¦PoleWood¦OnGround | 3rd Party | Vehicle | Pole-Wood | On Ground | 3 | 2 |  |  | 1 | 2 | 2 | 1 |  |  | 11
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Pothead(RiserTermination)¦Broken | 3rd Party | Vehicle | Pothead(Riser Termination) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦Pothead(RiserTermination)¦Broken | 3rd Party | Vehicle | Pothead(Riser Termination) | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Recloser¦Broken | 3rd Party | Vehicle | Recloser | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦Recloser¦Burnedflashed | 3rd Party | Vehicle | Recloser | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦Secondary¦Broken | 3rd Party | Vehicle | Secondary | Broken | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vehicle¦Secondary¦Broken | 3rd Party | Vehicle | Secondary | Broken | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.42857 | 0.5 | 0.4 | 0.5 | 3rdParty¦Vehicle¦Secondary¦Brokenwireonground | 3rd Party | Vehicle | Secondary | Broken, wire on ground | [10 empty] | 5 | bar: FNLYEAR 2015; FNLYEAR 2017; FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2022
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Secondary¦Brokenwireonobject | 3rd Party | Vehicle | Secondary | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦Secondary¦Burnedflashed | 3rd Party | Vehicle | Secondary | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Secondary¦BurnedOpen | 3rd Party | Vehicle | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vehicle¦Secondary¦Normal | 3rd Party | Vehicle | Secondary | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Secondary¦Together | 3rd Party | Vehicle | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2021
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 0.6 | 0.5 | 3rdParty¦Vehicle¦Serviceconductor¦Broken | 3rd Party | Vehicle | Service conductor | Broken | [10 empty] | 5 | bar: FNLYEAR 2018 to FNLYEAR 2020; FNLYEAR 2022 to FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Vehicle¦Serviceconductor¦Brokenwireonground | 3rd Party | Vehicle | Service conductor | Broken, wire on ground | FNLYEAR 2021: 2; FNLYEAR 2023: 1 | 3
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | 3rdParty¦Vehicle¦Serviceconductor¦Normal | 3rd Party | Vehicle | Service conductor | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2022
Third Party (Vehicle) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦Switch¦Broken | 3rd Party | Vehicle | Switch | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦Transformer(OH)¦Broken | 3rd Party | Vehicle | Transformer (OH) | Broken | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 0.85714 | 0.8 | 1 | 0.8 | 3rdParty¦Vehicle¦Transformer(OH)¦Broken | 3rd Party | Vehicle | Transformer (OH) | Broken |  | 1 | 1 | 1 |  | 2 | 1 | 1 | 1 |  | 8
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Transformer(OH)¦FailedFaulted | 3rd Party | Vehicle | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Vehicle¦Transformer(OH)¦FailedFaulted | 3rd Party | Vehicle | Transformer (OH) | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2021 to FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Transformer(OH)¦Normal | 3rd Party | Vehicle | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.71429 | 0.6 | 1 | 0.6 | 3rdParty¦Vehicle¦Transformer(OH)¦Normal | 3rd Party | Vehicle | Transformer (OH) | Normal | FNLYEAR 2017: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 2 | 6
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | 3rdParty¦Vehicle¦Transformer(UG)¦Broken | 3rd Party | Vehicle | Transformer (UG) | Broken | FNLYEAR 2024: 2 | 2
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.4286 | 2.2 | 2.4 | 2.2 | 3rdParty¦Vehicle¦Transformer(UG)¦Broken | 3rd Party | Vehicle | Transformer (UG) | Broken | 1 | 2 | 2 | 4 | 1 | 3 | 4 | 3 | 2 |  | 22
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Transformer(UG)¦Deteriorated | 3rd Party | Vehicle | Transformer (UG) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.4 | 0.3 | 3rdParty¦Vehicle¦Transformer(UG)¦FailedFaulted | 3rd Party | Vehicle | Transformer (UG) | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2019; FNLYEAR 2021; FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | 3rdParty¦Vehicle¦Transformer(UG)¦Leaking | 3rd Party | Vehicle | Transformer (UG) | Leaking | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2020; FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Transformer(UG)¦Normal | 3rd Party | Vehicle | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Vehicle¦Transformer(UG)¦Normal | 3rd Party | Vehicle | Transformer (UG) | Normal | [10 empty] | 3 | bar: FNLYEAR 2020; FNLYEAR 2022 to FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Vehicle¦Transformer(UG)¦OnGround | 3rd Party | Vehicle | Transformer (UG) | On Ground | FNLYEAR 2024: 3 | 3
Third Party (Vehicle) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.6 | 0.4 | 0.6 | 3rdParty¦Vehicle¦Transformer(UG)¦OnGround | 3rd Party | Vehicle | Transformer (UG) | On Ground | FNLYEAR 2016: 2; FNLYEAR 2018: 2; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 6
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦Transformer¦ | 3rd Party | Vehicle | Transformer | [11 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | 3rdParty¦Vehicle¦Transformer¦Arcing | 3rd Party | Vehicle | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2019
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.57143 | 0.6 | 0.4 | 0.6 | 3rdParty¦Vehicle¦Transformer¦Broken | 3rd Party | Vehicle | Transformer | Broken | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2023: 1 | 6
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.42857 | 0.4 | 0.4 | 0.4 | 3rdParty¦Vehicle¦Transformer¦Brokenwireonground | 3rd Party | Vehicle | Transformer | Broken, wire on ground | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦Transformer¦FailedFaulted | 3rd Party | Vehicle | Transformer | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0 | 0.2 | 3rdParty¦Vehicle¦Transformer¦Leaking | 3rd Party | Vehicle | Transformer | Leaking | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2018
Third Party (Vehicle) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Transformer¦Malfunctioning | 3rd Party | Vehicle | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2023
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | 3rdParty¦Vehicle¦Transformer¦Normal | 3rd Party | Vehicle | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Third Party (Vehicle) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | 3rdParty¦Vehicle¦Transformer¦Normal | 3rd Party | Vehicle | Transformer | Normal | [10 empty] | 3 | bar: FNLYEAR 2021 to FNLYEAR 2023
Animal (Bird) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Birdfound¦¦ | Animal | Bird found | [12 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Animal (Bird) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Birdfound¦¦Broken | Animal | Bird found |  | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Bird) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Birdfound¦¦FailedFaulted | Animal | Bird found |  | Failed/Faulted | 5 | 4 | 3 | 2 |  | 1 | 1 |  |  |  | 16
Animal (Bird) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Birdfound¦¦Normal | Animal | Bird found |  | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Booster¦Normal | Animal | Bird found | Booster | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | Animal¦Birdfound¦Bus¦Burnedflashed | Animal | Bird found | Bus | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | Animal¦Birdfound¦Bus¦Normal | Animal | Bird found | Bus | Normal | FNLYEAR 2024: 4 | 4
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Bus¦Normal | Animal | Bird found | Bus | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Bushing¦Arcing | Animal | Bird found | Bushing | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Bushing¦Arcing | Animal | Bird found | Bushing | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Birdfound¦Bushing¦Burnedflashed | Animal | Bird found | Bushing | Burned/flashed | FNLYEAR 2024: 3 | 3
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.32 | 0.32 | 1 | 0.8 | 0.8 | 0.8 | Animal¦Birdfound¦Bushing¦Burnedflashed | Animal | Bird found | Bushing | Burned/flashed | 1 |  |  | 2 | 1 | 1 |  | 2 | 1 |  | 8
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0.2 | 0.3 | Animal¦Birdfound¦Bushing¦FailedFaulted | Animal | Bird found | Bushing | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2020
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Bushing¦Normal | Animal | Bird found | Bushing | Normal | FNLYEAR 2024: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Bushing¦Normal | Animal | Bird found | Bushing | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Capacitor¦Normal | Animal | Bird found | Capacitor | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Capacitor¦Normal | Animal | Bird found | Capacitor | Normal | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦CircuitBreaker¦Normal | Animal | Bird found | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.2 | 0.3 | Animal¦Birdfound¦CircuitBreaker¦Normal | Animal | Bird found | Circuit Breaker | Normal | [10 empty] | 3 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦ConductorOverhead¦Annealed | Animal | Bird found | Conductor, Overhead | Annealed | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.6 | 0.4 | Animal¦Birdfound¦ConductorOverhead¦BentorTwisted | Animal | Bird found | Conductor, Overhead | Bent or Twisted | FNLYEAR 2019: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 4
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.14286 | 0.4 | 0 | 0.4 | Animal¦Birdfound¦ConductorOverhead¦Broken | Animal | Bird found | Conductor, Overhead | Broken | FNLYEAR 2015: 3; FNLYEAR 2019: 1 | 4
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground | Animal | Bird found | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 2.56 | 2.56 | 5.8571 | 6.4 | 3.6 | 6.4 | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 5 | 13 | 5 | 13 | 10 | 7 | 4 | 2 | 5 |  | 64
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonobject | Animal | Bird found | Conductor, Overhead | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.71429 | 0.6 | 0.6 | 0.6 | Animal¦Birdfound¦ConductorOverhead¦Burnedflashed | Animal | Bird found | Conductor, Overhead | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 2 | 6
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦ConductorOverhead¦Contaminated | Animal | Bird found | Conductor, Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.71429 | 0.6 | 0.6 | 0.6 | Animal¦Birdfound¦ConductorOverhead¦Deteriorated | Animal | Bird found | Conductor, Overhead | Deteriorated | FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2020: 1; FNLYEAR 2022: 2 | 6
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 9.36 | 9.36 | 14.8571 | 10.4 | 20.8 | 10.4 | Animal¦Birdfound¦ConductorOverhead¦Normal | Animal | Bird found | Conductor- Overhead | Normal | FNLYEAR 2024: 104 | 104
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 70.65 | 70.65 | 93.1429 | 78.5 | 91.2 | 78.5 | Animal¦Birdfound¦ConductorOverhead¦Normal | Animal | Bird found | Conductor, Overhead | Normal | 32 | 39 | 62 | 95 | 101 | 113 | 120 | 124 | 99 |  | 785
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Animal¦Birdfound¦ConductorOverhead¦OnGround | Animal | Bird found | Conductor, Overhead | On Ground | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2018
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦ConductorOverhead¦Together | Animal | Bird found | Conductor- Overhead | Together | FNLYEAR 2024: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 3.51 | 3.51 | 4.1429 | 3.9 | 3.6 | 3.9 | Animal¦Birdfound¦ConductorOverhead¦Together | Animal | Bird found | Conductor, Overhead | Together | 3 | 1 | 6 | 8 | 3 | 4 | 10 | 3 | 1 |  | 39
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦ConductorUnderground¦Normal | Animal | Bird found | Conductor- Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Birdfound¦ConductorUnderground¦Normal | Animal | Bird found | Conductor, Underground | Normal | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦ConnectororSplice(OH)¦Arcing | Animal | Bird found | Connector or Splice (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦ConnectororSplice(OH)¦Burnedflashed | Animal | Bird found | Connector or Splice (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦ConnectororSplice(OH)¦Normal | Animal | Bird found | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0 | 0.4 | Animal¦Birdfound¦ConnectororSplice(OH)¦Normal | Animal | Bird found | Connector or Splice (OH) | Normal | [10 empty] | 4 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2018 to FNLYEAR 2019
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦CrossarmWood¦Broken | Animal | Bird found | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦CrossarmWood¦Burnedflashed | Animal | Bird found | Crossarm- Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.8 | 0.4 | Animal¦Birdfound¦Cutoutfuseholder¦Broken | Animal | Bird found | Cutout- fuse holder | Broken | FNLYEAR 2024: 4 | 4
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.7 | 0.7 | 1.2857 | 1 | 1.6 | 1 | Animal¦Birdfound¦Cutoutfuseholder¦Broken | Animal | Bird found | Cutout, fuse holder | Broken | FNLYEAR 2015: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 3; FNLYEAR 2021: 3; FNLYEAR 2022: 2 | 10
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 0.71429 | 0.7 | 0.4 | 0.7 | Animal¦Birdfound¦Cutoutfuseholder¦Burnedflashed | Animal | Bird found | Cutout, fuse holder | Burned/flashed | FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 1 | 7
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.7 | 0.7 | 0.42857 | 1 | 0.4 | 1 | Animal¦Birdfound¦Cutoutfuseholder¦FailedFaulted | Animal | Bird found | Cutout, fuse holder | Failed/Faulted | 2 | 2 | 3 |  | 1 |  |  | 1 | 1 |  | 10
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Cutoutfuseholder¦Normal | Animal | Bird found | Cutout- fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.77 | 0.77 | 1 | 1.1 | 1 | 1.1 | Animal¦Birdfound¦Cutoutfuseholder¦Normal | Animal | Bird found | Cutout, fuse holder | Normal | 2 | 2 |  | 2 |  |  | 1 | 2 | 2 |  | 11
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Fuse¦Broken | Animal | Bird found | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Fuse¦Broken | Animal | Bird found | Fuse | Broken | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | Animal¦Birdfound¦Fuse¦BurnedOpen | Animal | Bird found | Fuse | Burned Open | FNLYEAR 2024: 5 | 5
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 1.54 | 1.54 | 3.1429 | 2.2 | 4.4 | 2.2 | Animal¦Birdfound¦Fuse¦BurnedOpen | Animal | Bird found | Fuse | Burned Open | FNLYEAR 2020: 5; FNLYEAR 2021: 7; FNLYEAR 2022: 9; FNLYEAR 2023: 1 | 22
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | Animal¦Birdfound¦Fuse¦FailedFaulted | Animal | Bird found | Fuse | Failed/Faulted | FNLYEAR 2024: 5 | 5
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 18.83 | 18.83 | 19.7143 | 26.9 | 10.2 | 26.9 | Animal¦Birdfound¦Fuse¦FailedFaulted | Animal | Bird found | Fuse | Failed/Faulted | 37 | 46 | 48 | 47 | 40 | 30 | 6 | 6 | 9 |  | 269
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Birdfound¦Fuse¦Normal | Animal | Bird found | Fuse | Normal | FNLYEAR 2024: 3 | 3
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 2.66 | 2.66 | 3 | 3.8 | 3.2 | 3.8 | Animal¦Birdfound¦Fuse¦Normal | Animal | Bird found | Fuse | Normal | 8 | 5 | 4 | 2 | 3 | 2 | 4 | 3 | 7 |  | 38
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.28571 | 0.3 | 0.2 | 0.3 | Animal¦Birdfound¦Insulator¦Broken | Animal | Bird found | Insulator | Broken | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2019 to FNLYEAR 2020
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.57143 | 0.5 | 0.8 | 0.5 | Animal¦Birdfound¦Insulator¦Burnedflashed | Animal | Bird found | Insulator | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 1 | 5
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0 | 0.2 | 0 | 0.2 | Animal¦Birdfound¦Insulator¦FailedFaulted | Animal | Bird found | Insulator | Failed/Faulted | FNLYEAR 2017: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Insulator¦Normal | Animal | Bird found | Insulator | Normal | FNLYEAR 2024: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | Animal¦Birdfound¦Jumper¦BentorTwisted | Animal | Bird found | Jumper | Bent or Twisted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Jumper¦Burnedflashed | Animal | Bird found | Jumper | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 0.71429 | 0.7 | 0.8 | 0.7 | Animal¦Birdfound¦Jumper¦BurnedOpen | Animal | Bird found | Jumper | Burned Open | 1 |  | 1 |  | 1 | 1 | 2 | 1 |  |  | 7
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Jumper¦Normal | Animal | Bird found | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.6 | 0.4 | Animal¦Birdfound¦Jumper¦Normal | Animal | Bird found | Jumper | Normal | FNLYEAR 2019: 1; FNLYEAR 2021: 2; FNLYEAR 2023: 1 | 4
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦LightningArrestor¦Broken | Animal | Bird found | Lightning Arrestor | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦LightningArrestor¦Burnedflashed | Animal | Bird found | Lightning Arrestor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.57143 | 0.6 | 0.8 | 0.6 | Animal¦Birdfound¦LightningArrestor¦Burnedflashed | Animal | Bird found | Lightning Arrestor | Burned/flashed | FNLYEAR 2015: 2; FNLYEAR 2020: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 6
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.2 | 0.3 | Animal¦Birdfound¦LightningArrestor¦FailedFaulted | Animal | Bird found | Lightning Arrestor | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2018 to FNLYEAR 2020
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦LightningArrestor¦Normal | Animal | Bird found | Lightning Arrestor | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦MeteringEquipment¦Normal | Animal | Bird found | Metering Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Bird) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Birdfound¦Other¦Normal | Animal | Bird found | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Birdfound¦Other¦Normal | Animal | Bird found | Other | Normal | [10 empty] | 2 | bar: FNLYEAR 2015 to FNLYEAR 2016
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.28571 | 0.3 | 0 | 0.3 | Animal¦Birdfound¦PoleWood¦Broken | Animal | Bird found | Pole-Wood | Broken | FNLYEAR 2017: 1; FNLYEAR 2019: 2 | 3
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦PoleWood¦Brokenwireonground | Animal | Bird found | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦PoleWood¦Deteriorated | Animal | Bird found | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦PoleWood¦Normal | Animal | Bird found | Pole-Wood | Normal | FNLYEAR 2024: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.28571 | 0.4 | 0.2 | 0.4 | Animal¦Birdfound¦PoleWood¦Normal | Animal | Bird found | Pole-Wood | Normal | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2018; FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Animal¦Birdfound¦Pothead(RiserTermination)¦Arcing | Animal | Bird found | Pothead(Riser Termination) | Arcing | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2018
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Pothead(RiserTermination)¦Broken | Animal | Bird found | Pothead(Riser Termination) | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Pothead(RiserTermination)¦Burnedflashed | Animal | Bird found | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.42857 | 0.5 | 0.4 | 0.5 | Animal¦Birdfound¦Pothead(RiserTermination)¦Burnedflashed | Animal | Bird found | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 5 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2019 to FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.8 | 0.4 | Animal¦Birdfound¦Pothead(RiserTermination)¦Normal | Animal | Bird found | Pothead(Riser Termination) | Normal | FNLYEAR 2024: 4 | 4
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.84 | 0.84 | 1.4286 | 1.2 | 2 | 1.2 | Animal¦Birdfound¦Pothead(RiserTermination)¦Normal | Animal | Bird found | Pothead(Riser Termination) | Normal | FNLYEAR 2016: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 6; FNLYEAR 2023: 1 | 12
Animal (Bird) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Birdfound¦PTCCVT¦Burnedflashed | Animal | Bird found | PT/CCVT | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦PTCCVT¦FailedFaulted | Animal | Bird found | PT/CCVT | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0.2 | 0.3 | Animal¦Birdfound¦Recloser¦Burnedflashed | Animal | Bird found | Recloser | Burned/flashed | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2018; FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.2 | 0.3 | Animal¦Birdfound¦Recloser¦FailedFaulted | Animal | Bird found | Recloser | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Recloser¦Malfunctioning | Animal | Bird found | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Recloser¦Normal | Animal | Bird found | Recloser | Normal | FNLYEAR 2024: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 1.1429 | 0.9 | 1.6 | 0.9 | Animal¦Birdfound¦Recloser¦Normal | Animal | Bird found | Recloser | Normal | FNLYEAR 2017: 1; FNLYEAR 2020: 4; FNLYEAR 2022: 3; FNLYEAR 2023: 1 | 9
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Regulator¦Burnedflashed | Animal | Bird found | Regulator | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (Bird) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Regulator¦Normal | Animal | Bird found | Regulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Regulator¦Normal | Animal | Bird found | Regulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Relay¦Malfunctioning | Animal | Bird found | Relay | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Secondary¦Normal | Animal | Bird found | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Switch(OH)¦Normal | Animal | Bird found | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Switch(OH)¦Normal | Animal | Bird found | Switch (OH) | Normal | FNLYEAR 2022: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Switch(UG)¦Normal | Animal | Bird found | Switch (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Switch¦Burnedflashed | Animal | Bird found | Switch | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.8 | 0.4 | Animal¦Birdfound¦Transformer(OH)¦ | Animal | Bird found | Transformer (OH) |  | FNLYEAR 2020: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 4
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 0.8 | 0.5 | Animal¦Birdfound¦Transformer(OH)¦Broken | Animal | Bird found | Transformer (OH) | Broken | FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 5
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Transformer(OH)¦Burnedflashed | Animal | Bird found | Transformer (OH) | Burned/flashed | FNLYEAR 2024: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 1.12 | 1.12 | 1.8571 | 1.6 | 2 | 1.6 | Animal¦Birdfound¦Transformer(OH)¦Burnedflashed | Animal | Bird found | Transformer (OH) | Burned/flashed | 2 |  | 1 | 1 | 2 | 2 | 1 | 5 | 2 |  | 16
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Birdfound¦Transformer(OH)¦FailedFaulted | Animal | Bird found | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 3 | 3
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 2.1 | 2.1 | 3.2857 | 3 | 2.8 | 3 | Animal¦Birdfound¦Transformer(OH)¦FailedFaulted | Animal | Bird found | Transformer (OH) | Failed/Faulted | 3 | 3 | 1 | 5 | 4 | 3 | 4 | 3 | 4 |  | 30
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.84 | 0.84 | 1.7143 | 1.2 | 2.4 | 1.2 | Animal¦Birdfound¦Transformer(OH)¦Normal | Animal | Bird found | Transformer (OH) | Normal | FNLYEAR 2024: 12 | 12
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 7.21 | 7.21 | 10.5714 | 10.3 | 11 | 10.3 | Animal¦Birdfound¦Transformer(OH)¦Normal | Animal | Bird found | Transformer (OH) | Normal | 6 | 12 | 11 | 8 | 11 | 11 | 15 | 20 | 9 |  | 103
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Transformer(UG)¦FailedFaulted | Animal | Bird found | Transformer (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (Bird) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Transformer(UG)¦Normal | Animal | Bird found | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Transformer¦ | Animal | Bird found | Transformer | [11 empty] | 1 | bar: FNLYEAR 2017
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Transformer¦Broken | Animal | Bird found | Transformer | Broken | FNLYEAR 2023: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.57143 | 0.5 | 0.4 | 0.5 | Animal¦Birdfound¦Transformer¦Burnedflashed | Animal | Bird found | Transformer | Burned/flashed | [10 empty] | 5 | bar: FNLYEAR 2015; FNLYEAR 2018 to FNLYEAR 2020; FNLYEAR 2022
Animal (Bird) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Birdfound¦Transformer¦BurnedOpen | Animal | Bird found | Transformer | Burned Open | FNLYEAR 2023: 2 | 2
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.91 | 0.91 | 0.71429 | 1.3 | 0.6 | 1.3 | Animal¦Birdfound¦Transformer¦FailedFaulted | Animal | Bird found | Transformer | Failed/Faulted | 3 | 2 | 3 | 1 | 1 | 2 | 1 |  |  |  | 13
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Transformer¦Malfunctioning | Animal | Bird found | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Bird) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | Animal¦Birdfound¦Transformer¦Normal | Animal | Bird found | Transformer | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2021
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Birdfound¦Transformer¦OnGround | Animal | Bird found | Transformer | On Ground | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Bird) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Birdfound¦Transformer¦OnGround | Animal | Bird found | Transformer | On Ground | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Other¦¦BurnedOpen | Animal | Other |  | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Other¦¦FailedFaulted | Animal | Other |  | Failed/Faulted | 2 | 1 | 2 | 1 |  | 1 |  | 2 |  |  | 9
Animal (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Other¦¦Normal | Animal | Other |  | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0 | 0.2 | 0 | 0.2 | Animal¦Other¦AnchororGuy¦BentorTwisted | Animal | Other | Anchor or Guy | Bent or Twisted | FNLYEAR 2016: 2 | 2
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦AnchororGuy¦Broken | Animal | Other | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦AnchororGuy¦Normal | Animal | Other | Anchor or Guy | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Other¦AnchororGuy¦Normal | Animal | Other | Anchor or Guy | Normal | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | Animal¦Other¦Bus¦Normal | Animal | Other | Bus | Normal | FNLYEAR 2020: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 1 | 4
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Bushing¦Burnedflashed | Animal | Other | Bushing | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Bushing¦Contaminated | Animal | Other | Bushing | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Animal¦Other¦Bushing¦Normal | Animal | Other | Bushing | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2018
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Capacitor¦Broken | Animal | Other | Capacitor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Capacitor¦Burnedflashed | Animal | Other | Capacitor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦CircuitBreaker¦Normal | Animal | Other | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦CircuitBreaker¦Normal | Animal | Other | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦ConductorOverhead¦Arcing | Animal | Other | Conductor- Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦ConductorOverhead¦BentorTwisted | Animal | Other | Conductor, Overhead | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦ConductorOverhead¦Brokenwireonground | Animal | Other | Conductor- Overhead | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.57143 | 0.7 | 0.6 | 0.7 | Animal¦Other¦ConductorOverhead¦Brokenwireonground | Animal | Other | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2015: 1; FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 7
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.42857 | 0.4 | 0.4 | 0.4 | Animal¦Other¦ConductorOverhead¦Burnedflashed | Animal | Other | Conductor, Overhead | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2022 to FNLYEAR 2023
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦ConductorOverhead¦Contaminated | Animal | Other | Conductor, Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦ConductorOverhead¦FailedFaulted | Animal | Other | Conductor, Overhead | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 1.53 | 1.53 | 2.4286 | 1.7 | 3.4 | 1.7 | Animal¦Other¦ConductorOverhead¦Normal | Animal | Other | Conductor- Overhead | Normal | FNLYEAR 2024: 17 | 17
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 7.92 | 7.92 | 10.2857 | 8.8 | 10 | 8.8 | Animal¦Other¦ConductorOverhead¦Normal | Animal | Other | Conductor, Overhead | Normal | 3 | 3 | 10 | 13 | 9 | 10 | 10 | 14 | 16 |  | 88
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Other¦ConductorOverhead¦OnGround | Animal | Other | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2018
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.71429 | 0.6 | 0.2 | 0.6 | Animal¦Other¦ConductorOverhead¦Together | Animal | Other | Conductor, Overhead | Together | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 3; FNLYEAR 2023: 1 | 6
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦ConductorUnderground¦Broken | Animal | Other | Conductor, Underground | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦ConductorUnderground¦Burnedflashed | Animal | Other | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | Animal¦Other¦ConductorUnderground¦Deteriorated | Animal | Other | Conductor, Underground | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦ConductorUnderground¦Normal | Animal | Other | Conductor, Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦ConnectororSplice(OH)¦Arcing | Animal | Other | Connector or Splice (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0 | 0.2 | 0 | 0.2 | Animal¦Other¦ConnectororSplice(OH)¦BurnedOpen | Animal | Other | Connector or Splice (OH) | Burned Open | FNLYEAR 2016: 2 | 2
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦ConnectororSplice(OH)¦Normal | Animal | Other | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Other¦CrossarmSteel¦Normal | Animal | Other | Crossarm, Steel | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.42857 | 0.4 | 0.6 | 0.4 | Animal¦Other¦CrossarmWood¦Broken | Animal | Other | Crossarm, Wood | Broken | FNLYEAR 2016: 1; FNLYEAR 2020: 2; FNLYEAR 2022: 1 | 4
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.14286 | 0.3 | 0 | 0.3 | Animal¦Other¦CrossarmWood¦Burnedflashed | Animal | Other | Crossarm, Wood | Burned/flashed | FNLYEAR 2016: 2; FNLYEAR 2018: 1 | 3
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦CrossarmWood¦Normal | Animal | Other | Crossarm- Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.42857 | 0.5 | 0.4 | 0.5 | Animal¦Other¦CrossarmWood¦Normal | Animal | Other | Crossarm, Wood | Normal | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 2 | 5
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦CustomerEquipment¦Normal | Animal | Other | Customer Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Other¦Cutoutfuseholder¦Broken | Animal | Other | Cutout, fuse holder | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.4 | 0.3 | Animal¦Other¦Cutoutfuseholder¦FailedFaulted | Animal | Other | Cutout, fuse holder | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2023
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Cutoutfuseholder¦Normal | Animal | Other | Cutout- fuse holder | Normal | FNLYEAR 2024: 2 | 2
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 0.71429 | 0.8 | 0.6 | 0.8 | Animal¦Other¦Cutoutfuseholder¦Normal | Animal | Other | Cutout, fuse holder | Normal | 1 |  | 2 |  | 2 |  | 1 | 1 | 1 |  | 8
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Elbow¦FailedFaulted | Animal | Other | Elbow | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Fuse¦Broken | Animal | Other | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Fuse¦BurnedOpen | Animal | Other | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 0.8 | 0.5 | Animal¦Other¦Fuse¦BurnedOpen | Animal | Other | Fuse | Burned Open | FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 3 | 5
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Other¦Fuse¦FailedFaulted | Animal | Other | Fuse | Failed/Faulted | FNLYEAR 2024: 3 | 3
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 4.59 | 4.59 | 3 | 5.1 | 2.6 | 5.1 | Animal¦Other¦Fuse¦FailedFaulted | Animal | Other | Fuse | Failed/Faulted | 11 | 10 | 9 | 3 | 5 | 4 | 1 | 2 | 6 |  | 51
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Fuse¦Normal | Animal | Other | Fuse | Normal | FNLYEAR 2024: 2 | 2
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.63 | 0.63 | 0.57143 | 0.7 | 0.8 | 0.7 | Animal¦Other¦Fuse¦Normal | Animal | Other | Fuse | Normal | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 2 | 7
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Insulator¦Broken | Animal | Other | Insulator | Broken | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 0.85714 | 0.9 | 0.8 | 0.9 | Animal¦Other¦Insulator¦Burnedflashed | Animal | Other | Insulator | Burned/flashed | 1 | 1 | 1 |  | 2 | 1 | 1 | 1 | 1 |  | 9
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Other¦Insulator¦FailedFaulted | Animal | Other | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Other¦Insulator¦Normal | Animal | Other | Insulator | Normal | FNLYEAR 2024: 3 | 3
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.4 | 0.3 | Animal¦Other¦Insulator¦Normal | Animal | Other | Insulator | Normal | FNLYEAR 2018: 1; FNLYEAR 2020: 2 | 3
Animal (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Other¦Jumper¦ | Animal | Other | Jumper | [11 empty] | 1 | bar: FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Jumper¦Broken | Animal | Other | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Jumper¦Burnedflashed | Animal | Other | Jumper | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.28571 | 0.4 | 0.2 | 0.4 | Animal¦Other¦Jumper¦BurnedOpen | Animal | Other | Jumper | Burned Open | FNLYEAR 2017: 2; FNLYEAR 2019: 1; FNLYEAR 2023: 1 | 4
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Jumper¦Normal | Animal | Other | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦LightningArrestor¦Broken | Animal | Other | Lightning Arrestor | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Other¦LightningArrestor¦Burnedflashed | Animal | Other | Lightning Arrestor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Other¦LightningArrestor¦FailedFaulted | Animal | Other | Lightning Arrestor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.28571 | 0.3 | 0.2 | 0.3 | Animal¦Other¦LightningArrestor¦Normal | Animal | Other | Lightning Arrestor | Normal | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2018; FNLYEAR 2021
Animal (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Other¦Other¦Broken | Animal | Other | Other | Broken | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Animal (other) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Other¦FailedFaulted | Animal | Other | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Other¦Other¦Normal | Animal | Other | Other | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2023
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦PoleWood¦Broken | Animal | Other | Pole-Wood | Broken | FNLYEAR 2024: 2 | 2
Animal (other) | None | 0% | 0 | 0 | High | 70% | 1.89 | 1.89 | 2.7143 | 2.7 | 3.4 | 2.7 | Animal¦Other¦PoleWood¦Broken | Animal | Other | Pole-Wood | Broken | 3 | 4 | 1 |  | 2 | 12 | 2 | 2 | 1 |  | 27
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦PoleWood¦Brokenwireonground | Animal | Other | Pole-Wood | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.4 | 0.4 | 1 | 1 | 0.6 | 1 | Animal¦Other¦PoleWood¦Brokenwireonground | Animal | Other | Pole-Wood | Broken, wire on ground |  | 2 | 1 | 1 | 3 | 2 | 1 |  |  |  | 10
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦PoleWood¦Burnedflashed | Animal | Other | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 1 | 0.7 | 1.4 | 0.7 | Animal¦Other¦PoleWood¦Deteriorated | Animal | Other | Pole-Wood | Deteriorated | FNLYEAR 2024: 7 | 7
Animal (other) | None | 0% | 0 | 0 | High | 70% | 1.26 | 1.26 | 2.1429 | 1.8 | 2.4 | 1.8 | Animal¦Other¦PoleWood¦Deteriorated | Animal | Other | Pole-Wood | Deteriorated | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 4 | 5 |  | 18
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.71429 | 0.6 | 0.6 | 0.6 | Animal¦Other¦PoleWood¦Normal | Animal | Other | Pole-Wood | Normal | FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 2; FNLYEAR 2021: 1 | 6
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Other¦Pothead(RiserTermination)¦Burnedflashed | Animal | Other | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Pothead(RiserTermination)¦Deteriorated | Animal | Other | Pothead(Riser Termination) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Pothead(RiserTermination)¦Normal | Animal | Other | Pothead(Riser Termination) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Pothead(RiserTermination)¦Normal | Animal | Other | Pothead(Riser Termination) | Normal | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦PotheadRiserTermination¦Normal | Animal | Other | Pothead/Riser Termination | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦PTCCVT¦Burnedflashed | Animal | Other | PT/CCVT | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦PTCCVT¦Burnedflashed | Animal | Other | PT/CCVT | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0 | 0.5 | 0 | 0.5 | Animal¦Other¦Recloser¦Burnedflashed | Animal | Other | Recloser | Burned/flashed | FNLYEAR 2015: 2; FNLYEAR 2016: 2; FNLYEAR 2017: 1 | 5
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0.2 | 0.4 | Animal¦Other¦Recloser¦FailedFaulted | Animal | Other | Recloser | Failed/Faulted | FNLYEAR 2016: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 1 | 4
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Recloser¦Malfunctioning | Animal | Other | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Other¦Recloser¦Normal | Animal | Other | Recloser | Normal | FNLYEAR 2024: 3 | 3
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.72 | 0.72 | 0.85714 | 0.8 | 1.2 | 0.8 | Animal¦Other¦Recloser¦Normal | Animal | Other | Recloser | Normal | FNLYEAR 2016: 2; FNLYEAR 2020: 1; FNLYEAR 2022: 4; FNLYEAR 2023: 1 | 8
Animal (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.18 | 0.18 | 0.42857 | 0.3 | 0.4 | 0.3 | Animal¦Other¦Regulator¦Burnedflashed | Animal | Other | Regulator | Burned/flashed | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Secondary¦Burnedflashed | Animal | Other | Secondary | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Secondary¦FailedFaulted | Animal | Other | Secondary | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Secondary¦Normal | Animal | Other | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Sectionalizer¦Burnedflashed | Animal | Other | Sectionalizer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Sectionalizer¦FailedFaulted | Animal | Other | Sectionalizer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Sectionalizer¦Normal | Animal | Other | Sectionalizer | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Switch(OH)¦Broken | Animal | Other | Switch (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0 | 0.2 | Animal¦Other¦Switch(OH)¦Burnedflashed | Animal | Other | Switch (OH) | Burned/flashed | FNLYEAR 2018: 2 | 2
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Switch(OH)¦Normal | Animal | Other | Switch (OH) | Normal | FNLYEAR 2024: 2 | 2
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | Animal¦Other¦Switch(OH)¦Normal | Animal | Other | Switch (OH) | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Transformer(OH)¦ | Animal | Other | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Other¦Transformer(OH)¦Broken | Animal | Other | Transformer (OH) | Broken | FNLYEAR 2020: 1; FNLYEAR 2023: 2 | 3
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | Animal¦Other¦Transformer(OH)¦Burnedflashed | Animal | Other | Transformer (OH) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Transformer(OH)¦Contaminated | Animal | Other | Transformer (OH) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Transformer(OH)¦FailedFaulted | Animal | Other | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 1 | 0.8 | 0.8 | 0.8 | Animal¦Other¦Transformer(OH)¦FailedFaulted | Animal | Other | Transformer (OH) | Failed/Faulted | FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 2; FNLYEAR 2022: 2 | 8
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Transformer(OH)¦Normal | Animal | Other | Transformer (OH) | Normal | FNLYEAR 2024: 2 | 2
Animal (other) | None | 0% | 0 | 0 | High | 70% | 2.59 | 2.59 | 4.5714 | 3.7 | 4.8 | 3.7 | Animal¦Other¦Transformer(OH)¦Normal | Animal | Other | Transformer (OH) | Normal | 2 | 3 |  | 5 | 3 | 2 | 8 | 10 | 4 |  | 37
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Transformer(UG)¦Arcing | Animal | Other | Transformer (UG) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | Animal¦Other¦Transformer(UG)¦Burnedflashed | Animal | Other | Transformer (UG) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2017
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Other¦Transformer(UG)¦Normal | Animal | Other | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.7 | 0.4 | 0.7 | Animal¦Other¦Transformer(UG)¦Normal | Animal | Other | Transformer (UG) | Normal | FNLYEAR 2015: 1; FNLYEAR 2018: 4; FNLYEAR 2023: 2 | 7
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Other¦Transformer¦Broken | Animal | Other | Transformer | Broken | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Other¦Transformer¦Burnedflashed | Animal | Other | Transformer | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Animal (other) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 1 | 0.7 | 0.8 | 0.7 | Animal¦Other¦Transformer¦FailedFaulted | Animal | Other | Transformer | Failed/Faulted | FNLYEAR 2018: 3; FNLYEAR 2020: 1; FNLYEAR 2021: 3 | 7
Animal (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.2 | 0.3 | Animal¦Other¦TransformerPower¦Normal | Animal | Other | Transformer Power | Normal | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2021
Animal (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Other¦Woodpin¦Broken | Animal | Other | Woodpin | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦¦ | Animal | Squirrel | [12 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2020
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦¦Broken | Animal | Squirrel |  | Broken | [10 empty] | 3 | bar: FNLYEAR 2015 to FNLYEAR 2017
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦¦BurnedOpen | Animal | Squirrel |  | Burned Open | [10 empty] | 2 | bar: FNLYEAR 2015 to FNLYEAR 2016
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦¦FailedFaulted | Animal | Squirrel |  | Failed/Faulted | 11 | 22 | 5 | 9 | 2 | 3 | 7 | 2 |  |  | 61
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦¦Normal | Animal | Squirrel |  | Normal | FNLYEAR 2016: 1; FNLYEAR 2018: 2; FNLYEAR 2020: 1 | 4
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Bus¦Normal | Animal | Squirrel | Bus | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Squirrel¦Bus¦Normal | Animal | Squirrel | Bus | Normal | [10 empty] | 3 | bar: FNLYEAR 2020 to FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦Bushing¦Broken | Animal | Squirrel | Bushing | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Squirrel¦Bushing¦Burnedflashed | Animal | Squirrel | Bushing | Burned/flashed | FNLYEAR 2024: 3 | 3
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1.2857 | 0.9 | 1.2 | 0.9 | Animal¦Squirrel¦Bushing¦Burnedflashed | Animal | Squirrel | Bushing | Burned/flashed | FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 4 | 9
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.2 | 0.3 | Animal¦Squirrel¦Bushing¦FailedFaulted | Animal | Squirrel | Bushing | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 0.85714 | 0.9 | 0.8 | 0.9 | Animal¦Squirrel¦Bushing¦Normal | Animal | Squirrel | Bushing | Normal | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2019: 2; FNLYEAR 2020: 3; FNLYEAR 2022: 1 | 9
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Capacitor¦FailedFaulted | Animal | Squirrel | Capacitor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦ConductorOverhead¦ | Animal | Squirrel | Conductor, Overhead | [11 empty] | 1 | bar: FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦ConductorOverhead¦Arcing | Animal | Squirrel | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦ConductorOverhead¦Broken | Animal | Squirrel | Conductor, Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.57143 | 0.7 | 0.4 | 0.7 | Animal¦Squirrel¦ConductorOverhead¦Brokenwireonground | Animal | Squirrel | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2015: 2; FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 1 | 7
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0 | 0.2 | 0 | 0.2 | Animal¦Squirrel¦ConductorOverhead¦Burnedflashed | Animal | Squirrel | Conductor, Overhead | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2017
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦ConductorOverhead¦Deteriorated | Animal | Squirrel | Conductor, Overhead | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 3.15 | 3.15 | 5 | 3.5 | 7 | 3.5 | Animal¦Squirrel¦ConductorOverhead¦Normal | Animal | Squirrel | Conductor- Overhead | Normal | FNLYEAR 2024: 35 | 35
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 29.79 | 29.79 | 37.8571 | 33.1 | 38.8 | 33.1 | Animal¦Squirrel¦ConductorOverhead¦Normal | Animal | Squirrel | Conductor, Overhead | Normal | 22 | 30 | 14 | 45 | 26 | 46 | 61 | 61 | 26 |  | 331
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.42857 | 0.4 | 0.4 | 0.4 | Animal¦Squirrel¦ConductorOverhead¦Together | Animal | Squirrel | Conductor, Overhead | Together | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2019; FNLYEAR 2021; FNLYEAR 2023
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦ConductorUnderground¦Broken | Animal | Squirrel | Conductor, Underground | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦ConductorUnderground¦Burnedflashed | Animal | Squirrel | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.8 | 0.8 | 0.8 | Animal¦Squirrel¦ConductorUnderground¦Normal | Animal | Squirrel | Conductor, Underground | Normal | 1 |  | 1 | 2 |  | 1 | 1 | 1 | 1 |  | 8
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦ConnectororSplice(OH)¦Normal | Animal | Squirrel | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦ConnectororSplice(UG)¦Normal | Animal | Squirrel | Connector or Splice (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦CrossarmSteel¦Normal | Animal | Squirrel | Crossarm, Steel | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦CrossarmWood¦Broken | Animal | Squirrel | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦CrossarmWood¦Burnedflashed | Animal | Squirrel | Crossarm, Wood | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦CrossarmWood¦Normal | Animal | Squirrel | Crossarm, Wood | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦CutoutFusedDistribution¦FailedFaulted | Animal | Squirrel | Cutout, Fused, Distribution | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Squirrel¦Cutoutfuseholder¦Broken | Animal | Squirrel | Cutout- fuse holder | Broken | FNLYEAR 2024: 3 | 3
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 1.33 | 1.33 | 1.7143 | 1.9 | 1.8 | 1.9 | Animal¦Squirrel¦Cutoutfuseholder¦Broken | Animal | Squirrel | Cutout, fuse holder | Broken | 1 | 5 | 1 | 1 | 2 | 2 | 3 | 2 | 2 |  | 19
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 1.05 | 1.05 | 1.4286 | 1.5 | 1.8 | 1.5 | Animal¦Squirrel¦Cutoutfuseholder¦Burnedflashed | Animal | Squirrel | Cutout, fuse holder | Burned/flashed | 3 | 2 |  | 1 |  | 2 | 4 | 3 |  |  | 15
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 2.17 | 2.17 | 2 | 3.1 | 1.8 | 3.1 | Animal¦Squirrel¦Cutoutfuseholder¦FailedFaulted | Animal | Squirrel | Cutout, fuse holder | Failed/Faulted | 6 | 10 | 1 | 4 | 1 |  | 5 | 3 | 1 |  | 31
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | Animal¦Squirrel¦Cutoutfuseholder¦Normal | Animal | Squirrel | Cutout- fuse holder | Normal | FNLYEAR 2024: 5 | 5
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 5.11 | 5.11 | 7.2857 | 7.3 | 7.6 | 7.3 | Animal¦Squirrel¦Cutoutfuseholder¦Normal | Animal | Squirrel | Cutout, fuse holder | Normal | 10 | 5 | 7 | 7 | 6 | 9 | 15 | 9 | 5 |  | 73
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦FootingsTowerorPole¦Burnedflashed | Animal | Squirrel | Footings, Tower or Pole | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Fuse¦Broken | Animal | Squirrel | Fuse | Broken | FNLYEAR 2024: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.77 | 0.77 | 1.5714 | 1.1 | 2 | 1.1 | Animal¦Squirrel¦Fuse¦Broken | Animal | Squirrel | Fuse | Broken | FNLYEAR 2018: 1; FNLYEAR 2020: 5; FNLYEAR 2021: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 3 | 11
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.85714 | 0.6 | 1.2 | 0.6 | Animal¦Squirrel¦Fuse¦BurnedOpen | Animal | Squirrel | Fuse | Burned Open | FNLYEAR 2024: 6 | 6
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 4.48 | 4.48 | 8.7143 | 6.4 | 12.2 | 6.4 | Animal¦Squirrel¦Fuse¦BurnedOpen | Animal | Squirrel | Fuse | Burned Open | FNLYEAR 2017: 3; FNLYEAR 2020: 8; FNLYEAR 2021: 22; FNLYEAR 2022: 20; FNLYEAR 2023: 11 | 64
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 1.12 | 1.12 | 2.2857 | 1.6 | 3.2 | 1.6 | Animal¦Squirrel¦Fuse¦FailedFaulted | Animal | Squirrel | Fuse | Failed/Faulted | FNLYEAR 2024: 16 | 16
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 32.13 | 32.13 | 34.8571 | 45.9 | 23.4 | 45.9 | Animal¦Squirrel¦Fuse¦FailedFaulted | Animal | Squirrel | Fuse | Failed/Faulted | 73 | 64 | 78 | 85 | 42 | 29 | 26 | 34 | 28 |  | 459
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | Animal¦Squirrel¦Fuse¦Normal | Animal | Squirrel | Fuse | Normal | FNLYEAR 2024: 5 | 5
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 7.21 | 7.21 | 8.7143 | 10.3 | 9.4 | 10.3 | Animal¦Squirrel¦Fuse¦Normal | Animal | Squirrel | Fuse | Normal | 15 | 14 | 13 | 6 | 8 | 15 | 14 | 12 | 6 |  | 103
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Insulator¦Broken | Animal | Squirrel | Insulator | Broken | FNLYEAR 2022: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.42857 | 0.4 | 0.6 | 0.4 | Animal¦Squirrel¦Insulator¦Burnedflashed | Animal | Squirrel | Insulator | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2017; FNLYEAR 2020; FNLYEAR 2022 to FNLYEAR 2023
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Insulator¦FailedFaulted | Animal | Squirrel | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.42857 | 0.4 | 0.4 | 0.4 | Animal¦Squirrel¦Insulator¦Normal | Animal | Squirrel | Insulator | Normal | FNLYEAR 2015: 1; FNLYEAR 2018: 1; FNLYEAR 2020: 2 | 4
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦Jumper¦ | Animal | Squirrel | Jumper | [11 empty] | 1 | bar: FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Jumper¦Broken | Animal | Squirrel | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Jumper¦Burnedflashed | Animal | Squirrel | Jumper | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.14286 | 0.3 | 0 | 0.3 | Animal¦Squirrel¦Jumper¦BurnedOpen | Animal | Squirrel | Jumper | Burned Open | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2018
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0 | 0.4 | 0 | 0.4 | Animal¦Squirrel¦Jumper¦Normal | Animal | Squirrel | Jumper | Normal | FNLYEAR 2016: 4 | 4
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦LightningArrestor¦Broken | Animal | Squirrel | Lightning Arrestor | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.14286 | 0.3 | 0.2 | 0.3 | Animal¦Squirrel¦LightningArrestor¦Burnedflashed | Animal | Squirrel | Lightning Arrestor | Burned/flashed | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.72 | 0.72 | 0.85714 | 0.8 | 0.4 | 0.8 | Animal¦Squirrel¦LightningArrestor¦FailedFaulted | Animal | Squirrel | Lightning Arrestor | Failed/Faulted | 1 |  | 1 | 1 | 3 | 1 |  | 1 |  |  | 8
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 0.8 | 0.5 | Animal¦Squirrel¦LightningArrestor¦Normal | Animal | Squirrel | Lightning Arrestor | Normal | FNLYEAR 2018: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 2 | 5
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦Other¦Normal | Animal | Squirrel | Other | Normal | [10 empty] | 3 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦PoleWood¦Burnedflashed | Animal | Squirrel | Pole-Wood | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦PoleWood¦Normal | Animal | Squirrel | Pole-Wood | Normal | FNLYEAR 2024: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 1.61 | 1.61 | 2 | 2.3 | 2 | 2.3 | Animal¦Squirrel¦PoleWood¦Normal | Animal | Squirrel | Pole-Wood | Normal | 2 | 2 | 5 | 2 | 2 | 2 | 3 | 4 | 1 |  | 23
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Squirrel¦Pothead(RiserTermination)¦Broken | Animal | Squirrel | Pothead(Riser Termination) | Broken | FNLYEAR 2020: 2; FNLYEAR 2021: 1 | 3
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Pothead(RiserTermination)¦Burnedflashed | Animal | Squirrel | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.48 | 0.48 | 1.7143 | 1.2 | 1.8 | 1.2 | Animal¦Squirrel¦Pothead(RiserTermination)¦Burnedflashed | Animal | Squirrel | Pothead(Riser Termination) | Burned/flashed | FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 4; FNLYEAR 2022: 3; FNLYEAR 2023: 2 | 12
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Pothead(RiserTermination)¦FailedFaulted | Animal | Squirrel | Pothead(Riser Termination) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.63 | 0.63 | 1.2857 | 0.9 | 1.8 | 0.9 | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal | Animal | Squirrel | Pothead(Riser Termination) | Normal | FNLYEAR 2024: 9 | 9
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 5.53 | 5.53 | 9.5714 | 7.9 | 10.4 | 7.9 | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal | Animal | Squirrel | Pothead(Riser Termination) | Normal | 7 | 4 | 1 | 9 | 6 | 9 | 11 | 21 | 11 |  | 79
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦PotheadRiserTermination¦Burnedflashed | Animal | Squirrel | Pothead/Riser Termination | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦PotheadRiserTermination¦FailedFaulted | Animal | Squirrel | Pothead/Riser Termination | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦PTCCVT¦Normal | Animal | Squirrel | PT/CCVT | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Recloser¦Broken | Animal | Squirrel | Recloser | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Recloser¦Brokenwireonground | Animal | Squirrel | Recloser | Broken, wire on ground | FNLYEAR 2020: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Recloser¦Burnedflashed | Animal | Squirrel | Recloser | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.57143 | 0.5 | 0.6 | 0.5 | Animal¦Squirrel¦Recloser¦Burnedflashed | Animal | Squirrel | Recloser | Burned/flashed | [10 empty] | 5 | bar: FNLYEAR 2017; FNLYEAR 2019 to FNLYEAR 2021; FNLYEAR 2023
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦Recloser¦FailedFaulted | Animal | Squirrel | Recloser | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Recloser¦Normal | Animal | Squirrel | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.2 | 0.3 | Animal¦Squirrel¦Recloser¦Normal | Animal | Squirrel | Recloser | Normal | [10 empty] | 3 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Regulator¦Burnedflashed | Animal | Squirrel | Regulator | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Regulator¦Normal | Animal | Squirrel | Regulator | Normal | FNLYEAR 2023: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Riser¦Normal | Animal | Squirrel | Riser | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Secondary¦Broken | Animal | Squirrel | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Secondary¦Burnedflashed | Animal | Squirrel | Secondary | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Secondary¦BurnedOpen | Animal | Squirrel | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Secondary¦Normal | Animal | Squirrel | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Switch(OH)¦Normal | Animal | Squirrel | Switch (OH) | Normal | FNLYEAR 2024: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.99 | 0.99 | 1.5714 | 1.1 | 2.2 | 1.1 | Animal¦Squirrel¦Switch(OH)¦Normal | Animal | Squirrel | Switch (OH) | Normal | FNLYEAR 2020: 4; FNLYEAR 2021: 3; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 11
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦Switch(UG)¦Leaking | Animal | Squirrel | Switch (UG) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2016
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Switch(UG)¦Normal | Animal | Squirrel | Switch (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦Switch¦Normal | Animal | Squirrel | Switch | Normal | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Transformer(OH)¦ | Animal | Squirrel | Transformer (OH) |  | FNLYEAR 2024: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Transformer(OH)¦Arcing | Animal | Squirrel | Transformer (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Transformer(OH)¦Broken | Animal | Squirrel | Transformer (OH) | Broken | FNLYEAR 2024: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 1.26 | 1.26 | 2.4286 | 1.8 | 2.4 | 1.8 | Animal¦Squirrel¦Transformer(OH)¦Broken | Animal | Squirrel | Transformer (OH) | Broken |  | 1 |  | 2 | 3 | 6 | 3 | 3 |  |  | 18
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed | Animal | Squirrel | Transformer (OH) | Burned/flashed | FNLYEAR 2024: 5 | 5
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 2.45 | 2.45 | 4.4286 | 3.5 | 5.4 | 3.5 | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2 | 2 |  | 3 | 1 | 8 | 9 | 7 | 3 |  | 35
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted | Animal | Squirrel | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 5 | 5
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 5.39 | 5.39 | 9.8571 | 7.7 | 11 | 7.7 | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 4 | 1 | 3 | 5 | 9 | 8 | 21 | 16 | 10 |  | 77
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 1 | 0.7 | 1 | 0.7 | Animal¦Squirrel¦Transformer(OH)¦Leaking | Animal | Squirrel | Transformer (OH) | Leaking | FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 7
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.98 | 0.98 | 2 | 1.4 | 2.8 | 1.4 | Animal¦Squirrel¦Transformer(OH)¦Normal | Animal | Squirrel | Transformer (OH) | Normal | FNLYEAR 2024: 14 | 14
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 13.93 | 13.93 | 22 | 19.9 | 22.2 | 19.9 | Animal¦Squirrel¦Transformer(OH)¦Normal | Animal | Squirrel | Transformer (OH) | Normal | 18 | 12 | 15 | 20 | 23 | 24 | 49 | 27 | 11 |  | 199
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦Transformer(UG)¦Normal | Animal | Squirrel | Transformer (UG) | Normal | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0 | 0.4 | 0 | 0.4 | Animal¦Squirrel¦Transformer¦ | Animal | Squirrel | Transformer |  | FNLYEAR 2017: 4 | 4
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.57143 | 0.5 | 0.6 | 0.5 | Animal¦Squirrel¦Transformer¦Broken | Animal | Squirrel | Transformer | Broken | FNLYEAR 2016: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 5
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 0.71429 | 0.7 | 0.2 | 0.7 | Animal¦Squirrel¦Transformer¦Burnedflashed | Animal | Squirrel | Transformer | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 4; FNLYEAR 2022: 1 | 7
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | Animal¦Squirrel¦Transformer¦BurnedOpen | Animal | Squirrel | Transformer | Burned Open | FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 3
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Transformer¦Deteriorated | Animal | Squirrel | Transformer | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Animal¦Squirrel¦Transformer¦FailedFaulted | Animal | Squirrel | Transformer | Failed/Faulted | FNLYEAR 2024: 2 | 2
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 2.94 | 2.94 | 3.5714 | 4.2 | 3.4 | 4.2 | Animal¦Squirrel¦Transformer¦FailedFaulted | Animal | Squirrel | Transformer | Failed/Faulted | 11 | 4 | 2 | 7 | 1 | 4 | 7 | 3 | 3 |  | 42
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | Animal¦Squirrel¦Transformer¦Malfunctioning | Animal | Squirrel | Transformer | Malfunctioning | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Animal (Squirrel) | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 1 | 0.8 | 1.4 | 0.8 | Animal¦Squirrel¦Transformer¦Normal | Animal | Squirrel | Transformer | Normal | FNLYEAR 2015: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 8
Animal (Squirrel) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Animal¦Squirrel¦Transformer¦OnGround | Animal | Squirrel | Transformer | On Ground | [10 empty] | 1 | bar: FNLYEAR 2021
Animal (Squirrel) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | Animal¦Squirrel¦TransformerSTASVC¦FailedFaulted | Animal | Squirrel | Transformer, STA SVC | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Animal (Squirrel) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Animal¦Squirrel¦TransformerSTASVC¦Normal | Animal | Squirrel | Transformer- STA SVC | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦¦ | Company Initiated | Construction Activity/equip, company | [12 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦¦Normal | Company Initiated | Construction Activity/equip, company |  | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Broken | Company Initiated | Construction Activity/equip, company | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Deteriorated | Company Initiated | Construction Activity/equip, company | Anchor or Guy | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Normal | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Normal | Company Initiated | Construction Activity/equip, company | Anchor or Guy | Normal | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2020 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Bus¦Normal | Company Initiated | Construction Activity/equip, company | Bus | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Capacitor¦Broken | Company Initiated | Construction Activity/equip, company | Capacitor | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Arcing | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Broken | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Broken | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Broken | FNLYEAR 2020: 2; FNLYEAR 2021: 1 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Brokenwireonground | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Brokenwireonground | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Burnedflashed | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Contaminated | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Deteriorated | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Normal | FNLYEAR 2024: 16 | 16
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2 | 1 | 1 | 9 | 14 | 14 | 8 | 15 | 6 |  | 70
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦OnGround | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | On Ground | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Together | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Together | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Together |  | 1 | 1 | 3 | 3 |  | 1 | 3 | 2 |  | 14
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorUnderground¦Deteriorated | Company Initiated | Construction Activity/equip, company | Conductor, Underground | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorUnderground¦Normal | Company Initiated | Construction Activity/equip, company | Conductor, Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Broken | Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Brokenwireonground | Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Brokenwireonobject | Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Deteriorated | Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Normal | Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Broken | Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Broken | FNLYEAR 2019: 5; FNLYEAR 2020: 3; FNLYEAR 2021: 1 | 9
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Burnedflashed | Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Burned/flashed | FNLYEAR 2020: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Deteriorated | Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Normal | Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Normal | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Cutoutfuseholder¦FailedFaulted | Company Initiated | Construction Activity/equip, company | Cutout, fuse holder | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Cutoutfuseholder¦Normal | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Cutoutfuseholder¦Normal | Company Initiated | Construction Activity/equip, company | Cutout, fuse holder | Normal | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2020; FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Elbow¦Broken | Company Initiated | Construction Activity/equip, company | Elbow | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Elbow¦Normal | Company Initiated | Construction Activity/equip, company | Elbow | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Broken | Company Initiated | Construction Activity/equip, company | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦FailedFaulted | Company Initiated | Construction Activity/equip, company | Fuse | Failed/Faulted | [10 empty] | 4 | bar: FNLYEAR 2017; FNLYEAR 2019 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Normal | Company Initiated | Construction Activity/equip- company | Fuse | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Normal | Company Initiated | Construction Activity/equip, company | Fuse | Normal |  |  | 1 | 1 | 2 | 2 | 4 | 4 |  |  | 14
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Generator¦Broken | Company Initiated | Construction Activity/equip, company | Generator | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Generator¦Malfunctioning | Company Initiated | Construction Activity/equip, company | Generator | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Generator¦Normal | Company Initiated | Construction Activity/equip- company | Generator | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Broken | Company Initiated | Construction Activity/equip- company | Insulator | Broken | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Broken | Company Initiated | Construction Activity/equip, company | Insulator | Broken | FNLYEAR 2016: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 2 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Brokenwireonground | Company Initiated | Construction Activity/equip, company | Insulator | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Burnedflashed | Company Initiated | Construction Activity/equip, company | Insulator | Burned/flashed | FNLYEAR 2019: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦FailedFaulted | Company Initiated | Construction Activity/equip- company | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Arcing | Company Initiated | Construction Activity/equip, company | Jumper | Arcing | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Broken | Company Initiated | Construction Activity/equip, company | Jumper | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Burnedflashed | Company Initiated | Construction Activity/equip, company | Jumper | Burned/flashed | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Normal | Company Initiated | Construction Activity/equip, company | Jumper | Normal | FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 3 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦LightningArrestor¦FailedFaulted | Company Initiated | Construction Activity/equip- company | Lightning Arrestor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Broken | Company Initiated | Construction Activity/equip, company | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Malfunctioning | Company Initiated | Construction Activity/equip- company | Other | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Normal | Company Initiated | Construction Activity/equip- company | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Normal | Company Initiated | Construction Activity/equip, company | Other | Normal | FNLYEAR 2015: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 1; FNLYEAR 2023: 5 | 9
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Broken | Company Initiated | Construction Activity/equip, company | Pole-Wood | Broken | FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 1 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Burnedflashed | Company Initiated | Construction Activity/equip, company | Pole-Wood | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated | Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | FNLYEAR 2017: 1; FNLYEAR 2019: 11; FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 15
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Normal | Company Initiated | Construction Activity/equip- company | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Normal | Company Initiated | Construction Activity/equip, company | Pole-Wood | Normal |  |  |  | 1 | 1 | 2 | 1 | 1 | 2 |  | 8
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Recloser¦Malfunctioning | Company Initiated | Construction Activity/equip, company | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Recloser¦Normal | Company Initiated | Construction Activity/equip, company | Recloser | Normal | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2018 to FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Regulator¦Normal | Company Initiated | Construction Activity/equip- company | Regulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Secondary¦Broken | Company Initiated | Construction Activity/equip- company | Secondary | Broken | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Secondary¦Normal | Company Initiated | Construction Activity/equip- company | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Secondary¦Normal | Company Initiated | Construction Activity/equip, company | Secondary | Normal | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Serviceconductor¦Broken | Company Initiated | Construction Activity/equip, company | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Serviceconductor¦Brokenwireonobject | Company Initiated | Construction Activity/equip, company | Service conductor | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Switch(OH)¦Normal | Company Initiated | Construction Activity/equip, company | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦ | Company Initiated | Construction Activity/equip- company | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦ | Company Initiated | Construction Activity/equip, company | Transformer (OH) | [11 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Broken | Company Initiated | Construction Activity/equip, company | Transformer (OH) | Broken | FNLYEAR 2019: 2; FNLYEAR 2021: 1 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Deteriorated | Company Initiated | Construction Activity/equip, company | Transformer (OH) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦FailedFaulted | Company Initiated | Construction Activity/equip, company | Transformer (OH) | Failed/Faulted | FNLYEAR 2020: 2; FNLYEAR 2023: 1 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Leaking | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Normal | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Normal | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Normal | Company Initiated | Construction Activity/equip, company | Transformer (OH) | Normal |  |  | 2 | 2 | 1 | 8 | 2 |  | 1 |  | 16
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(UG)¦Broken | Company Initiated | Construction Activity/equip, company | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(UG)¦FailedFaulted | Company Initiated | Construction Activity/equip, company | Transformer (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(UG)¦Normal | Company Initiated | Construction Activity/equip, company | Transformer (UG) | Normal | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Broken | Company Initiated | Construction Activity/equip, company | Transformer | Broken | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Deteriorated | Company Initiated | Construction Activity/equip, company | Transformer | Deteriorated | FNLYEAR 2016: 1; FNLYEAR 2022: 2 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦FailedFaulted | Company Initiated | Construction Activity/equip- company | Transformer | Failed/Faulted | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Leaking | Company Initiated | Construction Activity/equip, company | Transformer | Leaking | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Malfunctioning | Company Initiated | Construction Activity/equip, company | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Normal | Company Initiated | Construction Activity/equip- company | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Normal | Company Initiated | Construction Activity/equip, company | Transformer | Normal | FNLYEAR 2021: 2; FNLYEAR 2022: 5; FNLYEAR 2023: 3 | 10
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ContactwithHighVoltagecompany¦¦FailedFaulted | Company Initiated | Contact with High Voltage, company |  | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ContactwithHighVoltagecompany¦ConductorOverhead¦Brokenwireonground | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ContactwithHighVoltagecompany¦ConductorOverhead¦Brokenwireonground | Company Initiated | Contact with High Voltage, company | Conductor, Overhead | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ContactwithHighVoltagecompany¦ConductorOverhead¦Normal | Company Initiated | Contact with High Voltage, company | Conductor, Overhead | Normal | [10 empty] | 3 | bar: FNLYEAR 2021 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ContactwithHighVoltagecompany¦Fuse¦FailedFaulted | Company Initiated | Contact with High Voltage, company | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ContactwithHighVoltagecompany¦Transformer(OH)¦FailedFaulted | Company Initiated | Contact with High Voltage, company | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ContactwithHighVoltagecompany¦Transformer¦Broken | Company Initiated | Contact with High Voltage, company | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦CircuitBreaker¦Normal | Company Initiated | Coordination failure | Circuit Breaker | Normal | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦CircuitBreaker¦Normal | Company Initiated | Coordination failure | Circuit Breaker | Normal | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Brokenwireonground | Company Initiated | Coordination failure | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Burnedflashed | Company Initiated | Coordination failure | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2016
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Normal | Company Initiated | Coordination failure | Conductor- Overhead | Normal | FNLYEAR 2024: 13 | 13
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Normal | Company Initiated | Coordination failure | Conductor, Overhead | Normal | FNLYEAR 2020: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 5; FNLYEAR 2023: 11 | 20
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦ConductorUnderground¦Normal | Company Initiated | Coordination failure | Conductor- Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦CustomerEquipment¦Normal | Company Initiated | Coordination failure | Customer Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Cutoutfuseholder¦Normal | Company Initiated | Coordination failure | Cutout, fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Fuse¦FailedFaulted | Company Initiated | Coordination failure | Fuse | Failed/Faulted | [10 empty] | 4 | bar: FNLYEAR 2018 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Fuse¦Normal | Company Initiated | Coordination failure | Fuse | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Fuse¦Normal | Company Initiated | Coordination failure | Fuse | Normal | FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 7
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Generator¦Normal | Company Initiated | Coordination failure | Generator | Normal | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Interrupter¦Malfunctioning | Company Initiated | Coordination failure | Interrupter | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Jumper¦Normal | Company Initiated | Coordination failure | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Other¦BurnedOpen | Company Initiated | Coordination failure | Other | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Other¦Malfunctioning | Company Initiated | Coordination failure | Other | Malfunctioning | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Other¦Normal | Company Initiated | Coordination failure | Other | Normal | FNLYEAR 2018: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 5
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦PoleWood¦Broken | Company Initiated | Coordination failure | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Recloser¦Malfunctioning | Company Initiated | Coordination failure | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Recloser¦Malfunctioning | Company Initiated | Coordination failure | Recloser | Malfunctioning | [10 empty] | 3 | bar: FNLYEAR 2021 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Recloser¦Normal | Company Initiated | Coordination failure | Recloser | Normal | FNLYEAR 2024: 28 | 28
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Recloser¦Normal | Company Initiated | Coordination failure | Recloser | Normal | FNLYEAR 2015: 1; FNLYEAR 2021: 5; FNLYEAR 2022: 5; FNLYEAR 2023: 22 | 33
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Relay¦Normal | Company Initiated | Coordination failure | Relay | Normal | [10 empty] | 3 | bar: FNLYEAR 2020; FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Serviceconductor¦Brokenwireonground | Company Initiated | Coordination failure | Service conductor | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Serviceconductor¦Normal | Company Initiated | Coordination failure | Service conductor | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Transformer¦BurnedOpen | Company Initiated | Coordination failure | Transformer | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Coordinationfailure¦Transformer¦FailedFaulted | Company Initiated | Coordination failure | Transformer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Digincompany¦ConductorUnderground¦Broken | Company Initiated | Dig in, company | Conductor, Underground | Broken | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Digincompany¦ConnectororSplice(UG)¦Broken | Company Initiated | Dig in, company | Connector or Splice (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Digincompany¦PoleWood¦Normal | Company Initiated | Dig in, company | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Digincompany¦Secondary¦Broken | Company Initiated | Dig in, company | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Digincompany¦Serviceconductor¦Broken | Company Initiated | Dig in, company | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦AnchororGuy¦Broken | Company Initiated | Improper Construction | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Arcing | Company Initiated | Improper Construction | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦BentorTwisted | Company Initiated | Improper Construction | Conductor, Overhead | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Broken | Company Initiated | Improper Construction | Conductor, Overhead | Broken | [10 empty] | 3 | bar: FNLYEAR 2020 to FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Brokenwireonground | Company Initiated | Improper Construction | Conductor, Overhead | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Burnedflashed | Company Initiated | Improper Construction | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Deteriorated | Company Initiated | Improper Construction | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Normal | Company Initiated | Improper Construction | Conductor- Overhead | Normal | FNLYEAR 2024: 4 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Normal | Company Initiated | Improper Construction | Conductor, Overhead | Normal | 1 |  | 1 | 7 |  | 5 | 1 | 1 | 3 |  | 19
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Together | Company Initiated | Improper Construction | Conductor, Overhead | Together | FNLYEAR 2019: 1; FNLYEAR 2021: 3; FNLYEAR 2023: 1 | 5
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorUnderground¦Broken | Company Initiated | Improper Construction | Conductor- Underground | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorUnderground¦Normal | Company Initiated | Improper Construction | Conductor- Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConductorUnderground¦Normal | Company Initiated | Improper Construction | Conductor, Underground | Normal | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2020; FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConnectororSplice(OH)¦Arcing | Company Initiated | Improper Construction | Connector or Splice (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConnectororSplice(OH)¦Broken | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConnectororSplice(OH)¦Broken | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦ConnectororSplice(OH)¦Normal | Company Initiated | Improper Construction | Connector or Splice (OH) | Normal | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦CrossarmWood¦Broken | Company Initiated | Improper Construction | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦CrossarmWood¦Normal | Company Initiated | Improper Construction | Crossarm, Wood | Normal | FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 2 | 7
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Cutoutfuseholder¦Broken | Company Initiated | Improper Construction | Cutout, fuse holder | Broken | FNLYEAR 2023: 4 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Cutoutfuseholder¦Normal | Company Initiated | Improper Construction | Cutout, fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Elbow¦Normal | Company Initiated | Improper Construction | Elbow | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Fuse¦BurnedOpen | Company Initiated | Improper Construction | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Fuse¦BurnedOpen | Company Initiated | Improper Construction | Fuse | Burned Open | FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Fuse¦FailedFaulted | Company Initiated | Improper Construction | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Fuse¦Normal | Company Initiated | Improper Construction | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Fuse¦Normal | Company Initiated | Improper Construction | Fuse | Normal | FNLYEAR 2017: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Insulator¦Normal | Company Initiated | Improper Construction | Insulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Interrupter¦Normal | Company Initiated | Improper Construction | Interrupter | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Jumper¦ | Company Initiated | Improper Construction | Jumper | [11 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Jumper¦Arcing | Company Initiated | Improper Construction | Jumper | Arcing | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Jumper¦Broken | Company Initiated | Improper Construction | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Jumper¦Normal | Company Initiated | Improper Construction | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Jumper¦Normal | Company Initiated | Improper Construction | Jumper | Normal | FNLYEAR 2016: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 7
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Other¦Broken | Company Initiated | Improper Construction | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Other¦FailedFaulted | Company Initiated | Improper Construction | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Other¦Malfunctioning | Company Initiated | Improper Construction | Other | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦PoleWood¦Broken | Company Initiated | Improper Construction | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦PoleWood¦Normal | Company Initiated | Improper Construction | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦PoleWood¦Normal | Company Initiated | Improper Construction | Pole-Wood | Normal | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2020 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Secondary¦BurnedOpen | Company Initiated | Improper Construction | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Secondary¦Normal | Company Initiated | Improper Construction | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Switch(OH)¦Arcing | Company Initiated | Improper Construction | Switch (OH) | Arcing | FNLYEAR 2019: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Switch(OH)¦Normal | Company Initiated | Improper Construction | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Switch(UG)¦Broken | Company Initiated | Improper Construction | Switch (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Transformer(OH)¦Broken | Company Initiated | Improper Construction | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Transformer(OH)¦FailedFaulted | Company Initiated | Improper Construction | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ImproperConstruction¦Transformer(UG)¦Normal | Company Initiated | Improper Construction | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Insulatorwashing¦Bus¦Contaminated | Company Initiated | Insulator washing | Bus | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Insulatorwashing¦PoleWood¦Contaminated | Company Initiated | Insulator washing | Pole-Wood | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦¦ | Company Initiated | Operating error |  |  | FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 1 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦CircuitBreaker¦Normal | Company Initiated | Operating error | Circuit Breaker | Normal |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 |  |  | 8
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦ConductorOverhead¦Normal | Company Initiated | Operating error | Conductor- Overhead | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦ConductorOverhead¦Normal | Company Initiated | Operating error | Conductor, Overhead | Normal | FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 3 | 5
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦ConnectororSplice(OH)¦Normal | Company Initiated | Operating error | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Cutoutfuseholder¦Normal | Company Initiated | Operating error | Cutout, fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Fuse¦ | Company Initiated | Operating error | Fuse | [11 empty] | 1 | bar: FNLYEAR 2017
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Fuse¦BurnedOpen | Company Initiated | Operating error | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Fuse¦FailedFaulted | Company Initiated | Operating error | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Fuse¦Normal | Company Initiated | Operating error | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Fuse¦Normal | Company Initiated | Operating error | Fuse | Normal | FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 5
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Generator¦FailedFaulted | Company Initiated | Operating error | Generator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Jumper¦Normal | Company Initiated | Operating error | Jumper | Normal | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Other¦Normal | Company Initiated | Operating error | Other | Normal | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦PoleWood¦Normal | Company Initiated | Operating error | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Recloser¦Normal | Company Initiated | Operating error | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Recloser¦Normal | Company Initiated | Operating error | Recloser | Normal |  | 1 | 1 |  |  | 1 | 1 | 2 | 1 |  | 7
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Relay¦Normal | Company Initiated | Operating error | Relay | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Switch(OH)¦Normal | Company Initiated | Operating error | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Switch(OH)¦Normal | Company Initiated | Operating error | Switch (OH) | Normal | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Switch(UG)¦Normal | Company Initiated | Operating error | Switch (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Switch(UG)¦Normal | Company Initiated | Operating error | Switch (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦Switch¦Normal | Company Initiated | Operating error | Switch | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Operatingerror¦TransformerPower¦Normal | Company Initiated | Operating error | Transformer Power | Normal | FNLYEAR 2015: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦¦ | Company Initiated | Other Circuits |  |  | FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2023: 2 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦CircuitBreaker¦Normal | Company Initiated | Other Circuits | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Arcing | Company Initiated | Other Circuits | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Deteriorated | Company Initiated | Other Circuits | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Normal | Company Initiated | Other Circuits | Conductor- Overhead | Normal | FNLYEAR 2024: 7 | 7
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Normal | Company Initiated | Other Circuits | Conductor, Overhead | Normal | 1 | 1 | 4 |  | 4 | 1 | 7 | 1 | 2 |  | 21
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Together | Company Initiated | Other Circuits | Conductor, Overhead | Together | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦CrossarmWood¦Broken | Company Initiated | Other Circuits | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Fuse¦Arcing | Company Initiated | Other Circuits | Fuse | Arcing | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Fuse¦Normal | Company Initiated | Other Circuits | Fuse | Normal | FNLYEAR 2019: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Generator¦Malfunctioning | Company Initiated | Other Circuits | Generator | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Insulator¦Broken | Company Initiated | Other Circuits | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Jumper¦Broken | Company Initiated | Other Circuits | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦LightningArrestor¦FailedFaulted | Company Initiated | Other Circuits | Lightning Arrestor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Other¦Broken | Company Initiated | Other Circuits | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Other¦Normal | Company Initiated | Other Circuits | Other | Normal | FNLYEAR 2024: 4 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Other¦Normal | Company Initiated | Other Circuits | Other | Normal | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 4 | 8
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦PoleWood¦Burnedflashed | Company Initiated | Other Circuits | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦PoleWood¦Deteriorated | Company Initiated | Other Circuits | Pole-Wood | Deteriorated | FNLYEAR 2016: 1; FNLYEAR 2022: 2 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦PoleWood¦Normal | Company Initiated | Other Circuits | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Recloser¦Normal | Company Initiated | Other Circuits | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Regulator¦Normal | Company Initiated | Other Circuits | Regulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Relay¦Normal | Company Initiated | Other Circuits | Relay | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Secondary¦Normal | Company Initiated | Other Circuits | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Switch(UG)¦Broken | Company Initiated | Other Circuits | Switch (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Transformer(OH)¦Normal | Company Initiated | Other Circuits | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Transformer(OH)¦Normal | Company Initiated | Other Circuits | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦OtherCircuits¦Transformer¦Normal | Company Initiated | Other Circuits | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦¦ | Company Initiated | Personnel- company |  |  | FNLYEAR 2024: 4 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦¦ | Company Initiated | Personnel, company |  |  | 2 | 1 | 2 | 3 | 1 | 1 | 1 | 4 | 3 |  | 18
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦¦Broken | Company Initiated | Personnel, company |  | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Capacitor¦Normal |  |  |  |  | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦CircuitBreaker¦Normal | Company Initiated | Personnel, company | Circuit Breaker | Normal | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦ | Company Initiated | Personnel, company | Conductor, Overhead | [11 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Annealed | Company Initiated | Personnel- company | Conductor- Overhead | Annealed | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Brokenwireonground | Company Initiated | Personnel, company | Conductor, Overhead | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Deteriorated | Company Initiated | Personnel, company | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Normal | Company Initiated | Personnel- company | Conductor- Overhead | Normal | FNLYEAR 2024: 82 | 82
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Normal | Company Initiated | Personnel, company | Conductor, Overhead | Normal | 1 | 3 | 3 |  | 2 | 2 | 1 | 14 | 54 |  | 80
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Together | Company Initiated | Personnel, company | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorUnderground¦Burnedflashed | Company Initiated | Personnel, company | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorUnderground¦Normal | Company Initiated | Personnel- company | Conductor- Underground | Normal | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConductorUnderground¦Normal | Company Initiated | Personnel, company | Conductor, Underground | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦ConnectororSplice(OH)¦Broken | Company Initiated | Personnel, company | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦CrossarmWood¦Broken | Company Initiated | Personnel- company | Crossarm- Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦CrossarmWood¦Broken | Company Initiated | Personnel, company | Crossarm, Wood | Broken | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦CrossarmWood¦Deteriorated | Company Initiated | Personnel, company | Crossarm, Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦CT¦Normal | Company Initiated | Personnel, company | CT | Normal | FNLYEAR 2022: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Cutoutfuseholder¦Normal | Company Initiated | Personnel, company | Cutout, fuse holder | Normal | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Elbow¦Normal | Company Initiated | Personnel- company | Elbow | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Elbow¦Normal | Company Initiated | Personnel, company | Elbow | Normal | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Fuse¦BurnedOpen | Company Initiated | Personnel, company | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Fuse¦Normal | Company Initiated | Personnel- company | Fuse | Normal | FNLYEAR 2024: 15 | 15
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Fuse¦Normal | Company Initiated | Personnel, company | Fuse | Normal | FNLYEAR 2016: 2; FNLYEAR 2021: 4; FNLYEAR 2022: 11; FNLYEAR 2023: 20 | 37
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Generator¦Broken | Company Initiated | Personnel, company | Generator | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Generator¦Malfunctioning | Company Initiated | Personnel, company | Generator | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Generator¦Normal | Company Initiated | Personnel, company | Generator | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Insulator¦Broken | Company Initiated | Personnel, company | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Insulator¦Normal | Company Initiated | Personnel, company | Insulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Jumper¦Broken | Company Initiated | Personnel, company | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Jumper¦Normal | Company Initiated | Personnel- company | Jumper | Normal | FNLYEAR 2024: 8 | 8
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Jumper¦Normal | Company Initiated | Personnel, company | Jumper | Normal | FNLYEAR 2015: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 5 | 8
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦LightningArrestor¦ | Company Initiated | Personnel, company | Lightning Arrestor | [11 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦LightningArrestor¦Burnedflashed | Company Initiated | Personnel, company | Lightning Arrestor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦MeteringEquipment¦ | Company Initiated | Personnel, company | Metering Equipment | [11 empty] | 1 | bar: FNLYEAR 2017
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Other¦Arcing | Company Initiated | Personnel, company | Other | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Other¦Broken | Company Initiated | Personnel, company | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Other¦Deteriorated | Company Initiated | Personnel, company | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2016
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Other¦Normal | Company Initiated | Personnel- company | Other | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Other¦Normal | Company Initiated | Personnel, company | Other | Normal | FNLYEAR 2016: 1; FNLYEAR 2018: 3; FNLYEAR 2023: 2 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦PoleWood¦Broken | Company Initiated | Personnel, company | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦PoleWood¦Deteriorated | Company Initiated | Personnel, company | Pole-Wood | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦PoleWood¦Normal | Company Initiated | Personnel, company | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Pothead(RiserTermination)¦Burnedflashed | Company Initiated | Personnel- company | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Recloser¦Malfunctioning | Company Initiated | Personnel- company | Recloser | Malfunctioning | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Recloser¦Malfunctioning | Company Initiated | Personnel, company | Recloser | Malfunctioning | FNLYEAR 2023: 4 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Recloser¦Normal | Company Initiated | Personnel- company | Recloser | Normal | FNLYEAR 2024: 28 | 28
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Recloser¦Normal | Company Initiated | Personnel, company | Recloser | Normal | FNLYEAR 2017: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 14; FNLYEAR 2023: 27 | 46
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Regulator¦Normal | Company Initiated | Personnel, company | Regulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Relay¦Malfunctioning | Company Initiated | Personnel, company | Relay | Malfunctioning | FNLYEAR 2020: 4 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Relay¦Normal | Company Initiated | Personnel, company | Relay | Normal | FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 4 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Secondary¦Brokenwireonground | Company Initiated | Personnel, company | Secondary | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Sectionalizer¦Normal | Company Initiated | Personnel, company | Sectionalizer | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Serviceconductor¦Broken | Company Initiated | Personnel, company | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Switch(OH)¦Normal | Company Initiated | Personnel- company | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Switch(OH)¦Normal | Company Initiated | Personnel, company | Switch (OH) | Normal | FNLYEAR 2022: 2; FNLYEAR 2023: 3 | 5
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Switch¦Normal | Company Initiated | Personnel, company | Switch | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦ | Company Initiated | Personnel, company | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Broken | Company Initiated | Personnel- company | Transformer (OH) | Broken | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Broken | Company Initiated | Personnel, company | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Burnedflashed | Company Initiated | Personnel, company | Transformer (OH) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Deteriorated | Company Initiated | Personnel- company | Transformer (OH) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦FailedFaulted | Company Initiated | Personnel, company | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Leaking | Company Initiated | Personnel, company | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2015
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Normal | Company Initiated | Personnel- company | Transformer (OH) | Normal | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Normal | Company Initiated | Personnel, company | Transformer (OH) | Normal | FNLYEAR 2021: 1; FNLYEAR 2022: 3; FNLYEAR 2023: 4 | 8
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer(UG)¦Normal | Company Initiated | Personnel- company | Transformer (UG) | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer¦Broken | Company Initiated | Personnel- company | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer¦Deteriorated | Company Initiated | Personnel, company | Transformer | Deteriorated | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer¦Malfunctioning | Company Initiated | Personnel- company | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer¦Normal | Company Initiated | Personnel, company | Transformer | Normal | FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Personnelcompany¦Transformer¦Together | Company Initiated | Personnel, company | Transformer | Together | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦¦ | Company Initiated | Planned- capital |  |  | FNLYEAR 2024: 1888 | 1888
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦ConductorOverhead¦Normal | Company Initiated | Planned- capital | Conductor- Overhead | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦ConnectororSplice(UG)¦Arcing | Company Initiated | Planned- capital | Connector or Splice (UG) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Elbow¦Normal | Company Initiated | Planned- capital | Elbow | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Fuse¦Normal | Company Initiated | Planned- capital | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Interrupter¦ | Company Initiated | Planned- capital | Interrupter | [11 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Other¦Normal | Company Initiated | Planned- capital | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦PoleWood¦Normal | Company Initiated | Planned- capital | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Transformer(OH)¦ | Company Initiated | Planned- capital | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Transformer(UG)¦Normal | Company Initiated | Planned- capital | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Transformer¦Broken | Company Initiated | Planned- capital | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcapital¦Transformer¦Normal | Company Initiated | Planned- capital | Transformer | Normal | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcustomer¦¦ | Company Initiated | Planned- customer |  |  | FNLYEAR 2024: 14 | 14
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcustomer¦Serviceconductor¦Normal | Company Initiated | Planned- customer | Service conductor | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcustomer¦Transformer(OH)¦ | Company Initiated | Planned- customer | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedcustomer¦Transformer¦Normal | Company Initiated | Planned- customer | Transformer | Normal | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦¦ | Company Initiated | Planned- maintenance |  |  | FNLYEAR 2024: 9386 | 9386
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦ConductorOverhead¦Brokenwireonobject | Company Initiated | Planned- maintenance | Conductor- Overhead | Broken- wire on object | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦ConductorUnderground¦Normal | Company Initiated | Planned- maintenance | Conductor- Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦Cutoutfuseholder¦Normal | Company Initiated | Planned- maintenance | Cutout- fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦Other¦Normal | Company Initiated | Planned- maintenance | Other | Normal | FNLYEAR 2024: 3 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦PoleWood¦Normal | Company Initiated | Planned- maintenance | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦Secondary¦Normal | Company Initiated | Planned- maintenance | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦Transformer(OH)¦ | Company Initiated | Planned- maintenance | Transformer (OH) |  | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦Transformer(UG)¦Normal | Company Initiated | Planned- maintenance | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦Transformer¦Deteriorated | Company Initiated | Planned- maintenance | Transformer | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦Plannedmaintenance¦Transformer¦Normal | Company Initiated | Planned- maintenance | Transformer | Normal | FNLYEAR 2024: 11 | 11
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦CircuitBreaker¦Normal | Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦CircuitBreaker¦Normal | Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | FNLYEAR 2019: 1; FNLYEAR 2021: 2 | 3
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Brokenwireonground | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Brokenwireonground | Company Initiated | Return Circuit Normal | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Deteriorated | Company Initiated | Return Circuit Normal | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Normal | Company Initiated | Return Circuit Normal | Conductor- Overhead | Normal | FNLYEAR 2024: 42 | 42
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Normal | Company Initiated | Return Circuit Normal | Conductor, Overhead | Normal |  |  | 2 | 6 | 8 | 9 | 4 | 3 | 33 |  | 65
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Together | Company Initiated | Return Circuit Normal | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Broken | Company Initiated | Return Circuit Normal | Conductor, Underground | Broken | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Deteriorated | Company Initiated | Return Circuit Normal | Conductor, Underground | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Normal | Company Initiated | Return Circuit Normal | Conductor- Underground | Normal | FNLYEAR 2024: 6 | 6
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Normal | Company Initiated | Return Circuit Normal | Conductor, Underground | Normal | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 7 |  | 19
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦ConnectororSplice(UG)¦Normal | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦CrossarmWood¦Broken | Company Initiated | Return Circuit Normal | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Cutoutfuseholder¦Broken | Company Initiated | Return Circuit Normal | Cutout, fuse holder | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Elbow¦Normal | Company Initiated | Return Circuit Normal | Elbow | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Fuse¦BurnedOpen | Company Initiated | Return Circuit Normal | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Fuse¦Normal | Company Initiated | Return Circuit Normal | Fuse | Normal | [10 empty] | 3 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Generator¦Normal | Company Initiated | Return Circuit Normal | Generator | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Generator¦Normal | Company Initiated | Return Circuit Normal | Generator | Normal | 1 |  | 1 | 1 | 1 |  | 2 | 3 | 1 |  | 10
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Jumper¦Broken | Company Initiated | Return Circuit Normal | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Jumper¦Normal | Company Initiated | Return Circuit Normal | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Jumper¦Normal | Company Initiated | Return Circuit Normal | Jumper | Normal | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Other¦Normal | Company Initiated | Return Circuit Normal | Other | Normal | FNLYEAR 2016: 2; FNLYEAR 2017: 2; FNLYEAR 2019: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 3 | 10
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Broken | Company Initiated | Return Circuit Normal | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Brokenwireonground | Company Initiated | Return Circuit Normal | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Burnedflashed | Company Initiated | Return Circuit Normal | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Burnedflashed | Company Initiated | Return Circuit Normal | Pole-Wood | Burned/flashed | FNLYEAR 2018: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Deteriorated | Company Initiated | Return Circuit Normal | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Normal | Company Initiated | Return Circuit Normal | Pole-Wood | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Normal | Company Initiated | Return Circuit Normal | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦PTCCVT¦Normal | Company Initiated | Return Circuit Normal | PT/CCVT | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Recloser¦Normal | Company Initiated | Return Circuit Normal | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Recloser¦Normal | Company Initiated | Return Circuit Normal | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Secondary¦Normal | Company Initiated | Return Circuit Normal | Secondary | Normal | FNLYEAR 2016: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Switch(OH)¦Broken | Company Initiated | Return Circuit Normal | Switch (OH) | Broken | FNLYEAR 2019: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Switch(OH)¦Normal | Company Initiated | Return Circuit Normal | Switch (OH) | Normal | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2023: 2 | 4
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Switch(UG)¦Normal | Company Initiated | Return Circuit Normal | Switch (UG) | Normal | FNLYEAR 2023: 2 | 2
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Transformer(OH)¦FailedFaulted | Company Initiated | Return Circuit Normal | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Transformer(OH)¦Normal | Company Initiated | Return Circuit Normal | Transformer (OH) | Normal | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Transformer(UG)¦Normal | Company Initiated | Return Circuit Normal | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Transformer(UG)¦Normal | Company Initiated | Return Circuit Normal | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Transformer¦Broken | Company Initiated | Return Circuit Normal | Transformer | Broken | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Company Initiated | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | CompanyInitiated¦ReturnCircuitNormal¦Transformer¦Normal | Company Initiated | Return Circuit Normal | Transformer | Normal | FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 4
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Brokenwireonground | Environmental/External | Earthquake | Conductor- Overhead | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Brokenwireonground | Environmental/External | Earthquake | Conductor, Overhead | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Normal | Environmental/External | Earthquake | Conductor- Overhead | Normal | FNLYEAR 2024: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 1 | 0.5 | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Normal | Environmental/External | Earthquake | Conductor, Overhead | Normal | FNLYEAR 2022: 5 | 5
Primary Conductor - Line Slap | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Together | Environmental/External | Earthquake | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Earthquake¦Fuse¦FailedFaulted | Environmental/External | Earthquake | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Earthquake¦Fuse¦Normal | Environmental/External | Earthquake | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Earthquake¦Other¦Normal | Environmental/External | Earthquake | Other | Normal | FNLYEAR 2022: 2 | 2
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Earthquake¦PoleWood¦Burnedflashed | Environmental/External | Earthquake | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Earthquake¦PoleWood¦Deteriorated | Environmental/External | Earthquake | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Earthquake¦Transformer¦ | Environmental/External | Earthquake | Transformer | [11 empty] | 1 | bar: FNLYEAR 2018
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦AnchororGuy¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Anchor or Guy | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (DPD) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦CircuitBreaker¦Normal | Environmental/External | Fire, Forest/Grass | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦BentorTwisted | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2020
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Broken | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken | FNLYEAR 2017: 5; FNLYEAR 2020: 2; FNLYEAR 2021: 2 | 9
Primary Conductor - Wire Down | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2 | 4 | 27 | 5 | 2 | 13 | 2 |  |  |  | 55
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 16 |  | 18 | 6 |  | 159 | 1 | 2 |  |  | 202
Primary Conductor - Line Slap | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Contaminated | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Contaminated | FNLYEAR 2017: 4; FNLYEAR 2020: 1 | 5
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Deteriorated | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Deteriorated | FNLYEAR 2020: 14 | 14
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Normal | FNLYEAR 2024: 14 | 14
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 17 | 14 | 30 | 39 | 4 | 198 | 18 | 11 | 2 |  | 333
Primary Conductor - Wire Down | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦OnGround | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | On Ground | [10 empty] | 4 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2020
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Broken | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Broken | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2017: 3; FNLYEAR 2018: 7; FNLYEAR 2020: 2 | 13
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Normal | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Normal | FNLYEAR 2018: 2; FNLYEAR 2020: 3; FNLYEAR 2021: 1 | 6
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦ConnectororSplice(OH)¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Connector or Splice (OH) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Broken | Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Broken | [10 empty] | 5 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2022
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Brokenwireonground | Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Broken, wire on ground | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2021
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Burned/flashed | FNLYEAR 2015: 3; FNLYEAR 2017: 4; FNLYEAR 2018: 2; FNLYEAR 2020: 1 | 10
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦Broken | Environmental/External | Fire, Forest/Grass | Customer Equipment | Broken | FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1 | 4
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Customer Equipment | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2017: 12; FNLYEAR 2020: 13 | 26
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦BurnedOpen | Environmental/External | Fire, Forest/Grass | Customer Equipment | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Cutoutfuseholder¦Broken | Environmental/External | Fire, Forest/Grass | Cutout, fuse holder | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Cutoutfuseholder¦Normal | Environmental/External | Fire, Forest/Grass | Cutout, fuse holder | Normal | FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 3 | 6
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Elbow¦FailedFaulted | Environmental/External | Fire, Forest/Grass | Elbow | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦FootingsTowerorPole¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Footings, Tower or Pole | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦FootingsTowerorPole¦Normal | Environmental/External | Fire, Forest/Grass | Footings, Tower or Pole | Normal | FNLYEAR 2021: 2 | 2
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Fuse¦BurnedOpen | Environmental/External | Fire, Forest/Grass | Fuse | Burned Open | FNLYEAR 2020: 3 | 3
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Fuse¦FailedFaulted | Environmental/External | Fire, Forest/Grass | Fuse | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2017: 4; FNLYEAR 2019: 1 | 7
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal | Environmental/External | Fire, Forest/Grass | Fuse | Normal | 5 | 3 | 2 | 1 | 4 | 9 | 3 |  |  |  | 27
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Insulator¦Broken | Environmental/External | Fire- Forest/Grass | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Insulator¦Broken | Environmental/External | Fire, Forest/Grass | Insulator | Broken | FNLYEAR 2020: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Insulator¦Normal | Environmental/External | Fire, Forest/Grass | Insulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Jumper¦Broken | Environmental/External | Fire, Forest/Grass | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Jumper¦Normal | Environmental/External | Fire, Forest/Grass | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦MeteringEquipment¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Metering Equipment | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Wire Down | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Other¦Brokenwireonground | Environmental/External | Fire, Forest/Grass | Other | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Other¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Other | Burned/flashed | FNLYEAR 2015: 4; FNLYEAR 2017: 2; FNLYEAR 2020: 10; FNLYEAR 2022: 1 | 17
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Other¦BurnedOpen | Environmental/External | Fire, Forest/Grass | Other | Burned Open | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Other¦Deteriorated | Environmental/External | Fire, Forest/Grass | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Other¦Normal | Environmental/External | Fire, Forest/Grass | Other | Normal |  | 2 | 1 | 2 | 1 | 2 |  | 1 |  |  | 9
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleTowersteel¦Broken | Environmental/External | Fire, Forest/Grass | Pole - Tower, steel | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleTowersteel¦Brokenwireonground | Environmental/External | Fire, Forest/Grass | Pole - Tower, steel | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Broken | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken | FNLYEAR 2015: 2; FNLYEAR 2016: 1; FNLYEAR 2017: 19; FNLYEAR 2018: 2; FNLYEAR 2020: 5 | 29
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 8 | 2 | 58 | 8 | 1 | 14 | 4 | 2 |  |  | 97
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonobject | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed | Environmental/External | Fire- Forest/Grass | Pole-Wood | Burned/flashed | FNLYEAR 2024: 9 | 9
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 125 | 10 | 102 | 432 | 10 | 96 | 22 | 8 | 2 |  | 807
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Deteriorated | Environmental/External | Fire, Forest/Grass | Pole-Wood | Deteriorated | FNLYEAR 2020: 2; FNLYEAR 2021: 2 | 4
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal | Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | 2 |  | 2 | 12 | 4 | 2 | 1 |  | 2 |  | 25
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦PoleWood¦OnGround | Environmental/External | Fire, Forest/Grass | Pole-Wood | On Ground | FNLYEAR 2016: 1; FNLYEAR 2017: 2; FNLYEAR 2018: 2; FNLYEAR 2020: 1 | 6
Equipment (DPD) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Pothead(RiserTermination)¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Equipment (DPD) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Recloser¦Broken | Environmental/External | Fire, Forest/Grass | Recloser | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (DPD) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Recloser¦Normal | Environmental/External | Fire, Forest/Grass | Recloser | Normal | FNLYEAR 2015: 2; FNLYEAR 2016: 1 | 3
Equipment (Voltage Control) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Regulator¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Regulator | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Voltage Control) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Regulator¦FailedFaulted | Environmental/External | Fire, Forest/Grass | Regulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Secondary¦Arcing | Environmental/External | Fire, Forest/Grass | Secondary | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Secondary¦Broken | Environmental/External | Fire, Forest/Grass | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Secondary¦Brokenwireonground | Environmental/External | Fire, Forest/Grass | Secondary | Broken, wire on ground | FNLYEAR 2017: 2; FNLYEAR 2018: 1 | 3
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Secondary¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Secondary | Burned/flashed | 4 | 1 | 6 | 4 |  | 1 |  | 2 |  |  | 18
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Secondary¦BurnedOpen | Environmental/External | Fire, Forest/Grass | Secondary | Burned Open | FNLYEAR 2015: 3; FNLYEAR 2016: 1; FNLYEAR 2017: 2 | 6
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Secondary¦Together | Environmental/External | Fire, Forest/Grass | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2018
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦Broken | Environmental/External | Fire, Forest/Grass | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Service conductor | Burned/flashed | [10 empty] | 5 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2020 to FNLYEAR 2022
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦BurnedOpen | Environmental/External | Fire, Forest/Grass | Service conductor | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2021
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦OnGround | Environmental/External | Fire, Forest/Grass | Service conductor | On Ground | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Switch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Switch(OH)¦Normal | Environmental/External | Fire, Forest/Grass | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Switch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Switch(UG)¦Normal | Environmental/External | Fire, Forest/Grass | Switch (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Switch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Switch¦Normal | Environmental/External | Fire, Forest/Grass | Switch | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2020
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦ | Environmental/External | Fire, Forest/Grass | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Broken | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Broken | FNLYEAR 2017: 4 | 4
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Burned/flashed | 2 | 9 | 12 | 7 | 1 | 3 | 1 |  |  |  | 35
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Deteriorated | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦FailedFaulted | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Normal | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Normal | FNLYEAR 2015: 1; FNLYEAR 2017: 4; FNLYEAR 2018: 1; FNLYEAR 2020: 11 | 17
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦Broken | Environmental/External | Fire, Forest/Grass | Transformer (UG) | Broken | FNLYEAR 2020: 3 | 3
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Transformer (UG) | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2017: 6; FNLYEAR 2018: 3; FNLYEAR 2020: 1 | 11
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦FailedFaulted | Environmental/External | Fire, Forest/Grass | Transformer (UG) | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦Normal | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer¦Broken | Environmental/External | Fire, Forest/Grass | Transformer | Broken | FNLYEAR 2017: 2 | 2
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer¦Brokenwireonground | Environmental/External | Fire- Forest/Grass | Transformer | Broken- wire on ground | FNLYEAR 2024: 2 | 2
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer¦Burnedflashed | Environmental/External | Fire- Forest/Grass | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer¦Burnedflashed | Environmental/External | Fire, Forest/Grass | Transformer | Burned/flashed | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 2 | 5
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer¦BurnedOpen | Environmental/External | Fire, Forest/Grass | Transformer | Burned Open | FNLYEAR 2020: 2 | 2
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer¦FailedFaulted | Environmental/External | Fire, Forest/Grass | Transformer | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 1 | 6
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal | Environmental/External | Fire, Forest/Grass | Transformer | Normal | FNLYEAR 2020: 39 | 39
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦AnchororGuy¦Broken | Environmental/External | Flood/Erosion | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦AnchororGuy¦Deteriorated | Environmental/External | Flood/Erosion | Anchor or Guy | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Arcing | Environmental/External | Flood/Erosion | Conductor, Overhead | Arcing | FNLYEAR 2017: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Broken | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1 | 4 | 0.8 | 4 | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | 1 | 3 | 29 |  | 3 |  | 1 | 1 | 2 |  | 40
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonobject | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 2.3 | 0.6 | 2.3 | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal | Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | FNLYEAR 2016: 2; FNLYEAR 2017: 17; FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 2 | 23
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.4 | 0 | 0.4 | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦OnGround | Environmental/External | Flood/Erosion | Conductor, Overhead | On Ground | FNLYEAR 2017: 3; FNLYEAR 2019: 1 | 4
Primary Conductor - Line Slap | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.3 | 0 | 0.3 | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Together | Environmental/External | Flood/Erosion | Conductor, Overhead | Together | FNLYEAR 2016: 1; FNLYEAR 2017: 2 | 3
Primary Conductor - Line Slap | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦FloodErosion¦ConductorUnderground¦Contaminated | Environmental/External | Flood/Erosion | Conductor, Underground | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2023
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦FloodErosion¦ConductorUnderground¦Normal | Environmental/External | Flood/Erosion | Conductor, Underground | Normal | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦FloodErosion¦CrossarmWood¦Broken | Environmental/External | Flood/Erosion | Crossarm, Wood | Broken | FNLYEAR 2016: 2 | 2
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦FloodErosion¦CrossarmWood¦Brokenwireonground | Environmental/External | Flood/Erosion | Crossarm, Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦CrossarmWood¦Deteriorated | Environmental/External | Flood/Erosion | Crossarm, Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦CustomerEquipment¦Normal | Environmental/External | Flood/Erosion | Customer Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦Cutoutfuseholder¦FailedFaulted | Environmental/External | Flood/Erosion | Cutout, fuse holder | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦Fuse¦FailedFaulted | Environmental/External | Flood/Erosion | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦Fuse¦Normal | Environmental/External | Flood/Erosion | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FloodErosion¦Other¦Deteriorated | Environmental/External | Flood/Erosion | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FloodErosion¦Other¦Normal | Environmental/External | Flood/Erosion | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FloodErosion¦Other¦Normal | Environmental/External | Flood/Erosion | Other | Normal | FNLYEAR 2017: 2 | 2
Primary Conductor - Wire Down | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FloodErosion¦Other¦OnGround | Environmental/External | Flood/Erosion | Other | On Ground | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦PoleTowersteel¦Deteriorated | Environmental/External | Flood/Erosion | Pole - Tower, steel | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 2 | 1.2 | 2 | EnvironmentalExternal¦FloodErosion¦PoleWood¦Broken | Environmental/External | Flood/Erosion | Pole-Wood | Broken | 2 | 4 | 6 | 1 | 1 |  |  | 2 | 4 |  | 20
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 2.5 | 1.2 | 2.5 | EnvironmentalExternal¦FloodErosion¦PoleWood¦Brokenwireonground | Environmental/External | Flood/Erosion | Pole-Wood | Broken, wire on ground |  | 1 | 13 | 1 | 4 |  | 1 | 3 | 2 |  | 25
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 1 | 0.8 | 1 | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | FNLYEAR 2016: 2; FNLYEAR 2017: 2; FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2023: 3 | 10
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦FloodErosion¦PoleWood¦Normal | Environmental/External | Flood/Erosion | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1 | 1.5 | 1 | 1.5 | EnvironmentalExternal¦FloodErosion¦PoleWood¦Normal | Environmental/External | Flood/Erosion | Pole-Wood | Normal | FNLYEAR 2016: 3; FNLYEAR 2017: 5; FNLYEAR 2019: 2; FNLYEAR 2021: 1; FNLYEAR 2023: 4 | 15
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦FloodErosion¦PoleWood¦OnGround | Environmental/External | Flood/Erosion | Pole-Wood | On Ground | FNLYEAR 2017: 2 | 2
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦Switch(UG)¦Normal | Environmental/External | Flood/Erosion | Switch (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦FloodErosion¦Transformer(OH)¦ | Environmental/External | Flood/Erosion | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦FloodErosion¦Transformer(OH)¦Broken | Environmental/External | Flood/Erosion | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦FloodErosion¦Transformer(OH)¦Normal | Environmental/External | Flood/Erosion | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦FloodErosion¦Transformer(UG)¦Deteriorated | Environmental/External | Flood/Erosion | Transformer (UG) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦FloodErosion¦Transformer(UG)¦Normal | Environmental/External | Flood/Erosion | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | EnvironmentalExternal¦FloodErosion¦Transformer¦Broken | Environmental/External | Flood/Erosion | Transformer | Broken | FNLYEAR 2017: 1; FNLYEAR 2023: 2 | 3
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦FloodErosion¦Transformer¦FailedFaulted | Environmental/External | Flood/Erosion | Transformer | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦¦FailedFaulted | Environmental/External | Ice or snow |  | Failed/Faulted | FNLYEAR 2017: 1; FNLYEAR 2021: 2 | 3
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦AnchororGuy¦Broken | Environmental/External | Ice or snow | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦CircuitBreaker¦Normal | Environmental/External | Ice or snow | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Arcing | Environmental/External | Ice or snow | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2019
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.6 | 0.4 | 0.6 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦BentorTwisted | Environmental/External | Ice or snow | Conductor, Overhead | Bent or Twisted | FNLYEAR 2015: 2; FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2021: 2 | 6
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.3 | 1.6 | 1.3 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Broken | Environmental/External | Ice or snow | Conductor, Overhead | Broken |  | 1 | 1 | 1 | 2 | 1 | 7 |  |  |  | 13
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 1 | 0.5 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground | Environmental/External | Ice or snow | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 5 | 5
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 16.2857 | 12.7 | 17.2 | 12.7 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 4 | 4 | 5 | 3 | 25 | 9 | 61 | 7 | 9 |  | 127
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Burnedflashed | Environmental/External | Ice or snow | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2016
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Deteriorated | Environmental/External | Ice or snow | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2023
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal | Environmental/External | Ice or snow | Conductor- Overhead | Normal | FNLYEAR 2024: 4 | 4
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 7 | 5.3 | 6.2 | 5.3 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal | Environmental/External | Ice or snow | Conductor, Overhead | Normal |  | 1 | 3 | 2 | 16 | 3 | 12 | 9 | 7 |  | 53
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦OnGround | Environmental/External | Ice or snow | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2022
Primary Conductor - Line Slap | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Together | Environmental/External | Ice or snow | Conductor- Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Line Slap | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 1.2 | 1.2 | 1.2 | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Together | Environmental/External | Ice or snow | Conductor, Overhead | Together |  | 2 | 2 | 1 | 1 | 2 | 4 |  |  |  | 12
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦ConnectororSplice(OH)¦Broken | Environmental/External | Ice or snow | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Iceorsnow¦ConnectororSplice(OH)¦Broken | Environmental/External | Ice or snow | Connector or Splice (OH) | Broken | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0.2 | 0.4 | EnvironmentalExternal¦Iceorsnow¦ConnectororSplice(OH)¦Brokenwireonground | Environmental/External | Ice or snow | Connector or Splice (OH) | Broken, wire on ground | [10 empty] | 4 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2021
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.1429 | 1.7 | 1.6 | 1.7 | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Broken | Environmental/External | Ice or snow | Crossarm, Wood | Broken | 2 |  |  |  | 7 | 1 | 1 | 2 | 4 |  | 17
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.7 | 0.8 | 0.7 | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Brokenwireonground | Environmental/External | Ice or snow | Crossarm, Wood | Broken, wire on ground | FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2023: 1 | 7
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Brokenwireonobject | Environmental/External | Ice or snow | Crossarm, Wood | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Cutoutfuseholder¦Arcing | Environmental/External | Ice or snow | Cutout, fuse holder | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | EnvironmentalExternal¦Iceorsnow¦Cutoutfuseholder¦Broken | Environmental/External | Ice or snow | Cutout, fuse holder | Broken | FNLYEAR 2021: 2; FNLYEAR 2023: 1 | 3
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Fuse¦Broken | Environmental/External | Ice or snow | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Fuse¦Broken | Environmental/External | Ice or snow | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Fuse¦BurnedOpen | Environmental/External | Ice or snow | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.7143 | 1.2 | 2.4 | 1.2 | EnvironmentalExternal¦Iceorsnow¦Fuse¦BurnedOpen | Environmental/External | Ice or snow | Fuse | Burned Open | FNLYEAR 2021: 10; FNLYEAR 2022: 2 | 12
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.6 | 0.4 | 0.6 | EnvironmentalExternal¦Iceorsnow¦Fuse¦FailedFaulted | Environmental/External | Ice or snow | Fuse | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2023: 2 | 6
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Iceorsnow¦Fuse¦Normal | Environmental/External | Ice or snow | Fuse | Normal | FNLYEAR 2024: 2 | 2
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 3.2857 | 2.3 | 4.4 | 2.3 | EnvironmentalExternal¦Iceorsnow¦Fuse¦Normal | Environmental/External | Ice or snow | Fuse | Normal | FNLYEAR 2019: 1; FNLYEAR 2021: 8; FNLYEAR 2022: 6; FNLYEAR 2023: 8 | 23
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.6 | 0.6 | 0.6 | EnvironmentalExternal¦Iceorsnow¦Insulator¦Broken | Environmental/External | Ice or snow | Insulator | Broken | FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 6
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Insulator¦Brokenwireonground | Environmental/External | Ice or snow | Insulator | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Insulator¦Brokenwireonobject | Environmental/External | Ice or snow | Insulator | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2018
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Iceorsnow¦Jumper¦Broken | Environmental/External | Ice or snow | Jumper | Broken | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦LightningArrestor¦FailedFaulted | Environmental/External | Ice or snow | Lightning Arrestor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Other¦Annealed | Environmental/External | Ice or snow | Other | Annealed | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦Other¦Broken | Environmental/External | Ice or snow | Other | Broken | FNLYEAR 2024: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦Other¦Broken | Environmental/External | Ice or snow | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Broken | Environmental/External | Ice or snow | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.2 | 1.4 | 1.2 | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Broken | Environmental/External | Ice or snow | Pole-Wood | Broken | 1 |  |  | 1 | 3 | 1 | 4 | 2 |  |  | 12
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 4.7143 | 3.4 | 4.8 | 3.4 | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground | Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | 1 |  |  | 1 | 8 | 3 | 17 | 2 | 2 |  | 34
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Normal | Environmental/External | Ice or snow | Pole-Wood | Normal | FNLYEAR 2023: 2 | 2
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | EnvironmentalExternal¦Iceorsnow¦Recloser¦Normal | Environmental/External | Ice or snow | Recloser | Normal | FNLYEAR 2016: 1; FNLYEAR 2021: 2 | 3
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EnvironmentalExternal¦Iceorsnow¦Secondary¦Broken | Environmental/External | Ice or snow | Secondary | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.4 | 0.3 | EnvironmentalExternal¦Iceorsnow¦Secondary¦Brokenwireonground | Environmental/External | Ice or snow | Secondary | Broken, wire on ground | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2021
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦BentorTwisted | Environmental/External | Ice or snow | Service conductor | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2021
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦Broken | Environmental/External | Ice or snow | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦Broken | Environmental/External | Ice or snow | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.2 | 0.4 | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦Brokenwireonground | Environmental/External | Ice or snow | Service conductor | Broken, wire on ground | FNLYEAR 2019: 3; FNLYEAR 2022: 1 | 4
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Switch(OH)¦Normal | Environmental/External | Ice or snow | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Broken | Environmental/External | Ice or snow | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Broken | Environmental/External | Ice or snow | Transformer (OH) | Broken | [10 empty] | 3 | bar: FNLYEAR 2020 to FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Brokenwireonground | Environmental/External | Ice or snow | Transformer (OH) | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦FailedFaulted | Environmental/External | Ice or snow | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Leaking | Environmental/External | Ice or snow | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Normal | Environmental/External | Ice or snow | Transformer (OH) | Normal | FNLYEAR 2023: 4 | 4
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Iceorsnow¦Transformer¦Arcing | Environmental/External | Ice or snow | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.6 | 1 | 0.6 | EnvironmentalExternal¦Iceorsnow¦Transformer¦Broken | Environmental/External | Ice or snow | Transformer | Broken | FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Iceorsnow¦Transformer¦Brokenwireonground | Environmental/External | Ice or snow | Transformer | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Transformer¦Burnedflashed | Environmental/External | Ice or snow | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Transformer¦Deteriorated | Environmental/External | Ice or snow | Transformer | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.7143 | 1.2 | 2 | 1.2 | EnvironmentalExternal¦Iceorsnow¦Transformer¦FailedFaulted | Environmental/External | Ice or snow | Transformer | Failed/Faulted | FNLYEAR 2019: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 5; FNLYEAR 2023: 4 | 12
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Iceorsnow¦Transformer¦Normal | Environmental/External | Ice or snow | Transformer | Normal | FNLYEAR 2024: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Iceorsnow¦Transformer¦Normal | Environmental/External | Ice or snow | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦¦ | Environmental/External | Lightning | [12 empty] | 3 | bar: FNLYEAR 2015 to FNLYEAR 2017
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦¦Broken | Environmental/External | Lightning |  | Broken | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2018
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦¦FailedFaulted | Environmental/External | Lightning |  | Failed/Faulted | FNLYEAR 2015: 17; FNLYEAR 2016: 9; FNLYEAR 2017: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 1 | 29
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦¦Normal | Environmental/External | Lightning |  | Normal | [10 empty] | 2 | bar: FNLYEAR 2015 to FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Bushing¦Broken | Environmental/External | Lightning | Bushing | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦Bushing¦FailedFaulted | Environmental/External | Lightning | Bushing | Failed/Faulted | FNLYEAR 2019: 2 | 2
Equipment (Capacitor) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Capacitor¦Broken | Environmental/External | Lightning | Capacitor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Capacitor) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Capacitor¦Burnedflashed | Environmental/External | Lightning | Capacitor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Capacitor) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EnvironmentalExternal¦Lightning¦Capacitor¦Burnedflashed | Environmental/External | Lightning | Capacitor | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2022
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Burnedflashed | Environmental/External | Lightning | Circuit Breaker | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Malfunctioning | Environmental/External | Lightning | Circuit Breaker | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0 | 0.3 | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Normal | Environmental/External | Lightning | Circuit Breaker | Normal | FNLYEAR 2015: 1; FNLYEAR 2019: 2 | 3
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 2.3 | 1.6 | 2.3 | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Brokenwireonground | Environmental/External | Lightning | Conductor, Overhead | Broken, wire on ground | 6 | 4 | 2 | 2 | 1 | 6 | 1 |  | 1 |  | 23
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Burnedflashed | Environmental/External | Lightning | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.7143 | 1.2 | 2.4 | 1.2 | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal | Environmental/External | Lightning | Conductor- Overhead | Normal | FNLYEAR 2024: 12 | 12
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 7.8571 | 8.6 | 6.6 | 8.6 | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal | Environmental/External | Lightning | Conductor, Overhead | Normal | 17 | 9 | 5 | 4 | 18 | 5 | 8 | 6 | 14 |  | 86
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦ConductorOverhead¦OnGround | Environmental/External | Lightning | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Line Slap | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Together | Environmental/External | Lightning | Conductor, Overhead | Together | FNLYEAR 2015: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦ConductorUnderground¦Burnedflashed | Environmental/External | Lightning | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦ConductorUnderground¦Normal | Environmental/External | Lightning | Conductor, Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | EnvironmentalExternal¦Lightning¦ConnectororSplice(OH)¦Brokenwireonground | Environmental/External | Lightning | Connector or Splice (OH) | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦ConnectororSplice(OH)¦Normal | Environmental/External | Lightning | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦ConnectororSplice(UG)¦FailedFaulted | Environmental/External | Lightning | Connector or Splice (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦CrossarmSteel¦Normal | Environmental/External | Lightning | Crossarm, Steel | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦CrossarmWood¦Broken | Environmental/External | Lightning | Crossarm, Wood | Broken | FNLYEAR 2019: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦CT¦Burnedflashed | Environmental/External | Lightning | CT | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦CustomerEquipment¦FailedFaulted | Environmental/External | Lightning | Customer Equipment | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Arcing | Environmental/External | Lightning | Cutout, fuse holder | Arcing | FNLYEAR 2018: 2 | 2
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.3 | 0 | 0.3 | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Broken | Environmental/External | Lightning | Cutout, fuse holder | Broken | FNLYEAR 2016: 1; FNLYEAR 2017: 2 | 3
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Burnedflashed | Environmental/External | Lightning | Cutout, fuse holder | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.9 | 0 | 0.9 | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦FailedFaulted | Environmental/External | Lightning | Cutout, fuse holder | Failed/Faulted | FNLYEAR 2015: 4; FNLYEAR 2016: 3; FNLYEAR 2017: 1; FNLYEAR 2019: 1 | 9
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Normal | Environmental/External | Lightning | Cutout, fuse holder | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Elbow¦FailedFaulted | Environmental/External | Lightning | Elbow | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Fuse¦Arcing | Environmental/External | Lightning | Fuse | Arcing | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Fuse¦BurnedOpen | Environmental/External | Lightning | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1 | 0.7 | 1.4 | 0.7 | EnvironmentalExternal¦Lightning¦Fuse¦BurnedOpen | Environmental/External | Lightning | Fuse | Burned Open | FNLYEAR 2020: 1; FNLYEAR 2023: 6 | 7
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted | Environmental/External | Lightning | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 4.5714 | 13.4 | 2 | 13.4 | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted | Environmental/External | Lightning | Fuse | Failed/Faulted | 75 | 16 | 11 | 6 | 16 | 2 |  | 3 | 5 |  | 134
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.3 | 0 | 0.3 | EnvironmentalExternal¦Lightning¦Fuse¦Normal | Environmental/External | Lightning | Fuse | Normal | [10 empty] | 3 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.3 | 0.2 | 0.3 | EnvironmentalExternal¦Lightning¦Insulator¦Broken | Environmental/External | Lightning | Insulator | Broken | FNLYEAR 2016: 2; FNLYEAR 2022: 1 | 3
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Insulator¦Brokenwireonground | Environmental/External | Lightning | Insulator | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 0.9 | 1.2 | 0.9 | EnvironmentalExternal¦Lightning¦Insulator¦Burnedflashed | Environmental/External | Lightning | Insulator | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 2; FNLYEAR 2021: 3; FNLYEAR 2022: 1 | 9
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | EnvironmentalExternal¦Lightning¦Insulator¦FailedFaulted | Environmental/External | Lightning | Insulator | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Jumper¦Brokenwireonobject | Environmental/External | Lightning | Jumper | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.2 | 0.3 | EnvironmentalExternal¦Lightning¦Jumper¦BurnedOpen | Environmental/External | Lightning | Jumper | Burned Open | FNLYEAR 2019: 2; FNLYEAR 2023: 1 | 3
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.3 | 0.2 | 0.3 | EnvironmentalExternal¦Lightning¦LightningArrestor¦Broken | Environmental/External | Lightning | Lightning Arrestor | Broken | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦LightningArrestor¦Burnedflashed | Environmental/External | Lightning | Lightning Arrestor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦LightningArrestor¦Burnedflashed | Environmental/External | Lightning | Lightning Arrestor | Burned/flashed | FNLYEAR 2016: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 0.85714 | 0.9 | 0.2 | 0.9 | EnvironmentalExternal¦Lightning¦LightningArrestor¦FailedFaulted | Environmental/External | Lightning | Lightning Arrestor | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2017: 2; FNLYEAR 2018: 2; FNLYEAR 2019: 3; FNLYEAR 2020: 1 | 9
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦Other¦Broken | Environmental/External | Lightning | Other | Broken | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 4 | 6
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦Other¦FailedFaulted | Environmental/External | Lightning | Other | Failed/Faulted | FNLYEAR 2015: 10; FNLYEAR 2016: 7; FNLYEAR 2017: 4; FNLYEAR 2020: 1; FNLYEAR 2023: 1 | 23
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦Other¦Malfunctioning | Environmental/External | Lightning | Other | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦Other¦Normal | Environmental/External | Lightning | Other | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | EnvironmentalExternal¦Lightning¦PoleWood¦Broken | Environmental/External | Lightning | Pole-Wood | Broken | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2020; FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦PoleWood¦Brokenwireonground | Environmental/External | Lightning | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | EnvironmentalExternal¦Lightning¦PoleWood¦Burnedflashed | Environmental/External | Lightning | Pole-Wood | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2020: 2 | 3
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦PoleWood¦Deteriorated | Environmental/External | Lightning | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Pothead(RiserTermination)¦Burnedflashed | Environmental/External | Lightning | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | EnvironmentalExternal¦Lightning¦Pothead(RiserTermination)¦FailedFaulted | Environmental/External | Lightning | Pothead(Riser Termination) | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Pothead(RiserTermination)¦Normal | Environmental/External | Lightning | Pothead(Riser Termination) | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦PTCCVT¦Burnedflashed | Environmental/External | Lightning | PT/CCVT | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦PTCCVT¦FailedFaulted | Environmental/External | Lightning | PT/CCVT | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Recloser¦Burnedflashed | Environmental/External | Lightning | Recloser | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Recloser¦FailedFaulted | Environmental/External | Lightning | Recloser | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Lightning¦Recloser¦Normal | Environmental/External | Lightning | Recloser | Normal | FNLYEAR 2023: 2 | 2
Equipment (Voltage Control) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Regulator¦Brokenwireonground | Environmental/External | Lightning | Regulator | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2016
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Secondary¦Brokenwireonground | Environmental/External | Lightning | Secondary | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Secondary¦Burnedflashed | Environmental/External | Lightning | Secondary | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦Serviceconductor¦Brokenwireonground | Environmental/External | Lightning | Service conductor | Broken, wire on ground | FNLYEAR 2016: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦StreetLightEquipment¦FailedFaulted | Environmental/External | Lightning | Street Light Equipment | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Switch(OH)¦FailedFaulted | Environmental/External | Lightning | Switch (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Switch(OH)¦Normal | Environmental/External | Lightning | Switch (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Switch¦Broken | Environmental/External | Lightning | Switch | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Switch¦Normal | Environmental/External | Lightning | Switch | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦ | Environmental/External | Lightning | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 1 | 0.5 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken | Environmental/External | Lightning | Transformer (OH) | Broken | FNLYEAR 2024: 5 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.4286 | 3.6 | 2.6 | 3.6 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken | Environmental/External | Lightning | Transformer (OH) | Broken | 4 | 10 | 5 | 2 | 2 | 7 |  | 1 | 5 |  | 36
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.6 | 0 | 0.6 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Brokenwireonground | Environmental/External | Lightning | Transformer (OH) | Broken, wire on ground | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 3 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.8571 | 1.3 | 2.6 | 1.3 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | FNLYEAR 2024: 13 | 13
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 7 | 6.2 | 9 | 6.2 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 5 | 7 | 1 | 3 | 1 | 16 | 8 | 8 | 13 |  | 62
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.9 | 0 | 0.9 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Deteriorated | Environmental/External | Lightning | Transformer (OH) | Deteriorated | FNLYEAR 2015: 9 | 9
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 4.4286 | 3.1 | 6.2 | 3.1 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 31 | 31
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 44.5714 | 50.7 | 45 | 50.7 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 119 | 34 | 42 | 25 | 62 | 55 | 43 | 53 | 74 |  | 507
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 1.4 | 0.4 | 1.4 | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal | Environmental/External | Lightning | Transformer (OH) | Normal | 8 | 1 | 2 |  | 1 | 1 |  |  | 1 |  | 14
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.3 | 0.2 | 0.3 | EnvironmentalExternal¦Lightning¦Transformer(UG)¦Burnedflashed | Environmental/External | Lightning | Transformer (UG) | Burned/flashed | FNLYEAR 2015: 2; FNLYEAR 2020: 1 | 3
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer(UG)¦Deteriorated | Environmental/External | Lightning | Transformer (UG) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.8 | 0.4 | 0.8 | EnvironmentalExternal¦Lightning¦Transformer(UG)¦FailedFaulted | Environmental/External | Lightning | Transformer (UG) | Failed/Faulted | FNLYEAR 2015: 4; FNLYEAR 2016: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 1 | 8
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Lightning¦Transformer¦ | Environmental/External | Lightning | Transformer | [11 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer¦Arcing | Environmental/External | Lightning | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer¦Broken | Environmental/External | Lightning | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 1.2 | 0.4 | 1.2 | EnvironmentalExternal¦Lightning¦Transformer¦Broken | Environmental/External | Lightning | Transformer | Broken | FNLYEAR 2015: 3; FNLYEAR 2016: 4; FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2023: 2 | 12
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer¦Brokenwireonground | Environmental/External | Lightning | Transformer | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | EnvironmentalExternal¦Lightning¦Transformer¦Burnedflashed | Environmental/External | Lightning | Transformer | Burned/flashed | FNLYEAR 2024: 4 | 4
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 1.8 | 0.8 | 1.8 | EnvironmentalExternal¦Lightning¦Transformer¦Burnedflashed | Environmental/External | Lightning | Transformer | Burned/flashed | 6 | 6 |  |  | 2 | 1 | 2 |  | 1 |  | 18
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer¦Contaminated | Environmental/External | Lightning | Transformer | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Lightning¦Transformer¦Deteriorated | Environmental/External | Lightning | Transformer | Deteriorated | FNLYEAR 2015: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.1 | 2.2 | 1.1 | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted | Environmental/External | Lightning | Transformer | Failed/Faulted | FNLYEAR 2024: 11 | 11
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 49.7143 | 66.5 | 29 | 66.5 | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted | Environmental/External | Lightning | Transformer | Failed/Faulted | 137 | 71 | 109 | 46 | 157 | 79 | 22 | 3 | 41 |  | 665
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Lightning¦Transformer¦Leaking | Environmental/External | Lightning | Transformer | Leaking | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer¦Malfunctioning | Environmental/External | Lightning | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | EnvironmentalExternal¦Lightning¦Transformer¦Malfunctioning | Environmental/External | Lightning | Transformer | Malfunctioning | FNLYEAR 2021: 1; FNLYEAR 2023: 3 | 4
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Lightning¦Transformer¦Normal | Environmental/External | Lightning | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | EnvironmentalExternal¦Water¦ConductorOverhead¦Brokenwireonground | Environmental/External | Water | Conductor, Overhead | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Primary Conductor - Wire Down | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦ConductorOverhead¦OnGround | Environmental/External | Water | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦ConductorUnderground¦Deteriorated | Environmental/External | Water | Conductor, Underground | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦ConnectororSplice(UG)¦Normal | Environmental/External | Water | Connector or Splice (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦CrossarmWood¦Broken | Environmental/External | Water | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦CrossarmWood¦Burnedflashed | Environmental/External | Water | Crossarm, Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EnvironmentalExternal¦Water¦Fuse¦FailedFaulted | Environmental/External | Water | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Other¦Normal | Environmental/External | Water | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Water¦PoleWood¦Broken | Environmental/External | Water | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.4 | 0.2 | 0.4 | EnvironmentalExternal¦Water¦PoleWood¦Brokenwireonground | Environmental/External | Water | Pole-Wood | Broken, wire on ground | FNLYEAR 2017: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 1 | 4
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Water¦PoleWood¦Normal | Environmental/External | Water | Pole-Wood | Normal | FNLYEAR 2024: 2 | 2
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | EnvironmentalExternal¦Water¦PoleWood¦Normal | Environmental/External | Water | Pole-Wood | Normal | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Water¦PoleWood¦OnGround | Environmental/External | Water | Pole-Wood | On Ground | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Recloser¦Leaking | Environmental/External | Water | Recloser | Leaking | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EnvironmentalExternal¦Water¦Recloser¦Malfunctioning | Environmental/External | Water | Recloser | Malfunctioning | FNLYEAR 2024: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Transformer(UG)¦Contaminated | Environmental/External | Water | Transformer (UG) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Transformer(UG)¦Normal | Environmental/External | Water | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Transformer(UG)¦Normal | Environmental/External | Water | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Water¦Transformer¦Arcing | Environmental/External | Water | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 1.1429 | 0.8 | 1.6 | 0.8 | EnvironmentalExternal¦Water¦Transformer¦Broken | Environmental/External | Water | Transformer | Broken | FNLYEAR 2021: 4; FNLYEAR 2022: 1; FNLYEAR 2023: 3 | 8
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Transformer¦Brokenwireonground | Environmental/External | Water | Transformer | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EnvironmentalExternal¦Water¦Transformer¦Brokenwireonobject | Environmental/External | Water | Transformer | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Transformer¦BurnedOpen | Environmental/External | Water | Transformer | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 1 | 0.5 | EnvironmentalExternal¦Water¦Transformer¦FailedFaulted | Environmental/External | Water | Transformer | Failed/Faulted | FNLYEAR 2024: 5 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 1 | 0.5 | EnvironmentalExternal¦Water¦Transformer¦FailedFaulted | Environmental/External | Water | Transformer | Failed/Faulted | FNLYEAR 2021: 1; FNLYEAR 2022: 3; FNLYEAR 2023: 1 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EnvironmentalExternal¦Water¦Transformer¦Normal | Environmental/External | Water | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦¦Broken | Equipment Failure/Involved | Electrical Overload |  | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦¦FailedFaulted | Equipment Failure/Involved | Electrical Overload |  | Failed/Faulted | FNLYEAR 2015: 4; FNLYEAR 2016: 2; FNLYEAR 2018: 3; FNLYEAR 2019: 3 | 12
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦¦Normal | Equipment Failure/Involved | Electrical Overload |  | Normal | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Bushing¦Broken | Equipment Failure/Involved | Electrical Overload | Bushing | Broken | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2021
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Capacitor¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Capacitor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (DPD) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦ElectricalOverload¦CircuitBreaker¦Normal | Equipment Failure/Involved | Electrical Overload | Circuit Breaker | Normal | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2022
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Annealed | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Annealed | [10 empty] | 1 | bar: FNLYEAR 2018
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Arcing | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Broken | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Broken | FNLYEAR 2017: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 1 | 4
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Brokenwireonground | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.28571 | 0.5 | 0.2 | 0.5 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Brokenwireonground | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2017: 3; FNLYEAR 2018: 1; FNLYEAR 2021: 1 | 5
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.6 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Burned/flashed | FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 4
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Normal | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Normal | FNLYEAR 2024: 6 | 6
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.57143 | 0.6 | 0.6 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Normal | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Normal | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 6
Primary Conductor - Line Slap | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Together | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Arcing | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Brokenwireonground | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.28571 | 0.3 | 0 | 0.3 | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned Open | FNLYEAR 2016: 1; FNLYEAR 2019: 2 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Deteriorated | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Deteriorated | FNLYEAR 2020: 1; FNLYEAR 2022: 2 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(UG)¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(UG)¦Normal | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.63 | 0.63 | 0.71429 | 0.7 | 0.4 | 0.7 | EquipmentFailureInvolved¦ElectricalOverload¦CrossarmWood¦Broken | Equipment Failure/Involved | Electrical Overload | Crossarm, Wood | Broken | FNLYEAR 2015: 2; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 1 | 7
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦CrossarmWood¦Deteriorated | Equipment Failure/Involved | Electrical Overload | Crossarm- Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦CrossarmWood¦Normal | Equipment Failure/Involved | Electrical Overload | Crossarm, Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦CustomerEquipment¦Malfunctioning | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.42857 | 0.6 | 0.4 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦Broken | Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Broken | FNLYEAR 2015: 2; FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 6
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.28571 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2019; FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦Broken | Equipment Failure/Involved | Electrical Overload | Fuse | Broken | FNLYEAR 2021: 3; FNLYEAR 2022: 1 | 4
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | FNLYEAR 2024: 2 | 2
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 1.53 | 1.53 | 2.2857 | 1.7 | 3 | 1.7 | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open |  |  | 1 |  | 1 | 4 | 5 | 3 | 3 |  | 17
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Fuse | Failed/Faulted | FNLYEAR 2024: 4 | 4
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 2.79 | 2.79 | 2.4286 | 3.1 | 2 | 3.1 | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Fuse | Failed/Faulted | 2 | 1 | 11 | 4 | 3 | 2 | 4 | 2 | 2 |  | 31
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦Normal | Equipment Failure/Involved | Electrical Overload | Fuse | Normal | FNLYEAR 2024: 2 | 2
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦Normal | Equipment Failure/Involved | Electrical Overload | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Generator¦Normal | Equipment Failure/Involved | Electrical Overload | Generator | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Arcing | Equipment Failure/Involved | Electrical Overload | Insulator | Arcing | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.71429 | 0.6 | 0.8 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Broken | Equipment Failure/Involved | Electrical Overload | Insulator | Broken | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2022: 3; FNLYEAR 2023: 1 | 6
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Insulator | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Insulator | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Interrupter¦Normal | Equipment Failure/Involved | Electrical Overload | Interrupter | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦Arcing | Equipment Failure/Involved | Electrical Overload | Jumper | Arcing | [10 empty] | 1 | bar: FNLYEAR 2019
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦BentorTwisted | Equipment Failure/Involved | Electrical Overload | Jumper | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦Broken | Equipment Failure/Involved | Electrical Overload | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Jumper | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.14286 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Jumper | Burned Open | FNLYEAR 2015: 2; FNLYEAR 2016: 1; FNLYEAR 2021: 1 | 4
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦Deteriorated | Equipment Failure/Involved | Electrical Overload | Jumper | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦LightningArrestor¦Broken | Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Broken | FNLYEAR 2021: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦ElectricalOverload¦LightningArrestor¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Burned/flashed | FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 3
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦Other¦Broken | Equipment Failure/Involved | Electrical Overload | Other | Broken | [10 empty] | 2 | bar: FNLYEAR 2015 to FNLYEAR 2016
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦Other¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Other | Failed/Faulted | FNLYEAR 2015: 5; FNLYEAR 2016: 2; FNLYEAR 2017: 2; FNLYEAR 2018: 5; FNLYEAR 2019: 1 | 15
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦Other¦Malfunctioning | Equipment Failure/Involved | Electrical Overload | Other | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦ElectricalOverload¦Other¦Normal | Equipment Failure/Involved | Electrical Overload | Other | Normal | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1 | 5
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦PoleWood¦Broken | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.42857 | 0.6 | 0.4 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦PoleWood¦Broken | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Broken | [10 empty] | 6 | bar: FNLYEAR 2015 to FNLYEAR 2017; FNLYEAR 2019 to FNLYEAR 2021
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 0.6 | 0.5 | EquipmentFailureInvolved¦ElectricalOverload¦PoleWood¦Deteriorated | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Deteriorated | FNLYEAR 2019: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 5
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Pothead(RiserTermination)¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (DPD) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦Recloser¦Normal | Equipment Failure/Involved | Electrical Overload | Recloser | Normal | FNLYEAR 2024: 4 | 4
Equipment (DPD) | None | 0% | 0 | 0 | Very High | 90% | 1.53 | 1.53 | 2 | 1.7 | 2.4 | 1.7 | EquipmentFailureInvolved¦ElectricalOverload¦Recloser¦Normal | Equipment Failure/Involved | Electrical Overload | Recloser | Normal |  | 1 | 2 | 1 | 1 | 1 | 2 | 6 | 3 |  | 17
Equipment (Voltage Control) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Regulator¦Malfunctioning | Equipment Failure/Involved | Electrical Overload | Regulator | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Arcing | Equipment Failure/Involved | Electrical Overload | Secondary | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Broken | Equipment Failure/Involved | Electrical Overload | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Broken | Equipment Failure/Involved | Electrical Overload | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Secondary | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Secondary | Burned Open | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Deteriorated | Equipment Failure/Involved | Electrical Overload | Secondary | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2016
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0 | 0.4 | 0 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦Serviceconductor¦Arcing | Equipment Failure/Involved | Electrical Overload | Service conductor | Arcing | FNLYEAR 2015: 2; FNLYEAR 2016: 2 | 4
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Serviceconductor¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Service conductor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Switch(OH)¦Arcing | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Switch¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Switch | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦ | Equipment Failure/Involved | Electrical Overload | Transformer (OH) |  | FNLYEAR 2021: 5; FNLYEAR 2022: 1 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Arcing | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Arcing | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Broken | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.05 | 1.05 | 1.1429 | 1.5 | 1 | 1.5 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Broken | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | 1 | 2 | 4 | 3 |  | 1 | 2 | 2 |  |  | 15
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.57143 | 0.5 | 0.8 | 0.5 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.71429 | 0.6 | 1 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Deteriorated | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Deteriorated | FNLYEAR 2016: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 3; FNLYEAR 2022: 1 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 5 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 7.56 | 7.56 | 11.2857 | 10.8 | 13 | 10.8 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 13 | 9 | 7 | 5 | 9 | 17 | 31 | 9 | 8 |  | 108
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Leaking | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 0.42857 | 0.8 | 0.6 | 0.8 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Leaking | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Leaking | FNLYEAR 2015: 3; FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 8
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.77 | 0.77 | 1 | 1.1 | 0.8 | 1.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Normal | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | 2 | 1 | 1 | 3 |  |  | 1 | 3 |  |  | 11
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦Broken | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Broken | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2021
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2020; FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦Normal | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦Normal | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Normal | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.14286 | 0.4 | 0 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦ | Equipment Failure/Involved | Electrical Overload | Transformer |  | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2018: 1 | 4
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Annealed | Equipment Failure/Involved | Electrical Overload | Transformer | Annealed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.28571 | 0.5 | 0.2 | 0.5 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Arcing | Equipment Failure/Involved | Electrical Overload | Transformer | Arcing | FNLYEAR 2016: 2; FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2021: 1 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | FNLYEAR 2024: 5 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 2.1 | 2.1 | 3.7143 | 3 | 4.4 | 3 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | 2 | 1 | 1 | 2 | 2 |  | 10 | 8 | 4 |  | 30
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Brokenwireonground | Equipment Failure/Involved | Electrical Overload | Transformer | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Brokenwireonground | Equipment Failure/Involved | Electrical Overload | Transformer | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 0.85714 | 0.8 | 1.2 | 0.8 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Burnedflashed | Equipment Failure/Involved | Electrical Overload | Transformer | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2022: 5; FNLYEAR 2023: 1 | 8
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦BurnedOpen | Equipment Failure/Involved | Electrical Overload | Transformer | Burned Open | FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 4
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.98 | 0.98 | 1.1429 | 1.4 | 1.4 | 1.4 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Deteriorated | Equipment Failure/Involved | Electrical Overload | Transformer | Deteriorated | 2 | 2 | 2 | 1 |  | 1 | 1 | 3 | 2 |  | 14
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.91 | 0.91 | 1.8571 | 1.3 | 2.6 | 1.3 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | FNLYEAR 2024: 13 | 13
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 16.66 | 16.66 | 18.4286 | 23.8 | 14.8 | 23.8 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 36 | 43 | 30 | 26 | 29 | 19 | 17 | 16 | 22 |  | 238
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.12 | 1.12 | 1.1429 | 1.6 | 1.4 | 1.6 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Leaking | Equipment Failure/Involved | Electrical Overload | Transformer | Leaking | 1 | 1 | 6 | 1 |  | 1 |  | 4 | 2 |  | 16
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Malfunctioning | Equipment Failure/Involved | Electrical Overload | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.91 | 0.91 | 1.4286 | 1.3 | 1.8 | 1.3 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Malfunctioning | Equipment Failure/Involved | Electrical Overload | Transformer | Malfunctioning | 2 |  | 1 |  | 1 | 1 | 6 | 1 | 1 |  | 13
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Normal | Equipment Failure/Involved | Electrical Overload | Transformer | Normal | FNLYEAR 2021: 3; FNLYEAR 2022: 3 | 6
Equipment (Support Structure) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦AnchororGuy¦Deteriorated | Equipment Failure/Involved | Fire, pole | Anchor or Guy | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Firepole¦Capacitor¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Capacitor | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Arcing | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Broken | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Brokenwireonground | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Burnedflashed | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Normal | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.71429 | 0.6 | 0.6 | 0.6 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Normal | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Normal | FNLYEAR 2015: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 6
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦OnGround | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConductorUnderground¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦ConnectororSplice(OH)¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Connector or Splice (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦CrossarmSteel¦Burnedflashed | Equipment Failure/Involved | Fire- pole | Crossarm- Steel | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦CrossarmSteel¦Deteriorated | Equipment Failure/Involved | Fire, pole | Crossarm, Steel | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Broken | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Broken | FNLYEAR 2024: 2 | 2
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Broken | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Broken | FNLYEAR 2020: 2; FNLYEAR 2021: 2; FNLYEAR 2022: 2 | 6
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Brokenwireonground | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Burnedflashed | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 1.33 | 1.33 | 1.4286 | 1.9 | 1.6 | 1.9 | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Burned/flashed | 3 | 3 | 3 |  | 2 | 4 | 1 | 1 | 2 |  | 19
Equipment (Fuse) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦Cutoutfuseholder¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Cutout, fuse holder | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦FootingsTowerorPole¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Footings, Tower or Pole | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Firepole¦Fuse¦Broken | Equipment Failure/Involved | Fire, pole | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦Fuse¦BurnedOpen | Equipment Failure/Involved | Fire, pole | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.28571 | 0.6 | 0.4 | 0.6 | EquipmentFailureInvolved¦Firepole¦Insulator¦Broken | Equipment Failure/Involved | Fire, pole | Insulator | Broken | FNLYEAR 2017: 4; FNLYEAR 2020: 1; FNLYEAR 2023: 1 | 6
Equipment (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.24 | 0.24 | 0.42857 | 0.4 | 0.6 | 0.4 | EquipmentFailureInvolved¦Firepole¦Insulator¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Insulator | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2017; FNLYEAR 2021 to FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦Insulator¦FailedFaulted | Equipment Failure/Involved | Fire- pole | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦Insulator¦FailedFaulted | Equipment Failure/Involved | Fire, pole | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2022
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦Jumper¦Broken | Equipment Failure/Involved | Fire- pole | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦Jumper¦BurnedOpen | Equipment Failure/Involved | Fire, pole | Jumper | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦Jumper¦Deteriorated | Equipment Failure/Involved | Fire, pole | Jumper | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Firepole¦Other¦Broken | Equipment Failure/Involved | Fire, pole | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Firepole¦PoleTowersteel¦Normal | Equipment Failure/Involved | Fire, pole | Pole - Tower, steel | Normal | FNLYEAR 2021: 2 | 2
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken | Equipment Failure/Involved | Fire- pole | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 2.52 | 2.52 | 2 | 2.8 | 2.6 | 2.8 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | 2 | 3 | 9 |  | 1 | 1 | 9 | 2 | 1 |  | 28
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 0.85714 | 1.1 | 0.6 | 1.1 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Brokenwireonground | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken, wire on ground | 1 | 1 | 3 | 1 | 2 | 1 | 1 | 1 |  |  | 11
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Brokenwireonobject | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium High | 60% | 0.42 | 0.42 | 1 | 0.7 | 1.4 | 0.7 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed | Equipment Failure/Involved | Fire- pole | Pole-Wood | Burned/flashed | FNLYEAR 2024: 7 | 7
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium High | 60% | 6.3 | 6.3 | 8.2857 | 10.5 | 6.8 | 10.5 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 15 | 13 | 19 | 14 | 10 | 10 | 13 | 7 | 4 |  | 105
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 0.6 | 0.5 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Deteriorated | Equipment Failure/Involved | Fire, pole | Pole-Wood | Deteriorated | FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2021: 2; FNLYEAR 2023: 1 | 5
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦PoleWood¦Normal | Equipment Failure/Involved | Fire, pole | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦PoleWood¦OnGround | Equipment Failure/Involved | Fire, pole | Pole-Wood | On Ground | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦Pothead(RiserTermination)¦FailedFaulted | Equipment Failure/Involved | Fire, pole | Pothead(Riser Termination) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦Recloser¦Normal | Equipment Failure/Involved | Fire, pole | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Firepole¦Secondary¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Secondary | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦Serviceconductor¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Service conductor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦StreetLightEquipment¦Burnedflashed | Equipment Failure/Involved | Fire- pole | Street Light Equipment | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Firepole¦Transformer(OH)¦Burnedflashed | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0 | 0.3 | 0 | 0.3 | EquipmentFailureInvolved¦Firepole¦Transformer(OH)¦Burnedflashed | Equipment Failure/Involved | Fire, pole | Transformer (OH) | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2017: 2 | 3
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Firepole¦Transformer(OH)¦FailedFaulted | Equipment Failure/Involved | Fire, pole | Transformer (OH) | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Firepole¦Transformer(UG)¦Broken | Equipment Failure/Involved | Fire, pole | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦Firepole¦Transformer¦FailedFaulted | Equipment Failure/Involved | Fire, pole | Transformer | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2022
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Iceorsnow¦ConductorOverhead¦Brokenwireonobject | Equipment Failure/Involved | Ice or snow | Conductor, Overhead | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Iceorsnow¦ConductorOverhead¦Normal | Equipment Failure/Involved | Ice or snow | Conductor, Overhead | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Lightning¦ConnectororSplice(OH)¦Broken | Equipment Failure/Involved | Lightning | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Lightning¦CutoutFusedDistribution¦FailedFaulted | Equipment Failure/Involved | Lightning | Cutout, Fused, Distribution | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Lightning¦Cutoutfuseholder¦FailedFaulted | Equipment Failure/Involved | Lightning | Cutout, fuse holder | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Lightning¦Fuse¦Arcing | Equipment Failure/Involved | Lightning | Fuse | Arcing | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Lightning¦Fuse¦FailedFaulted | Equipment Failure/Involved | Lightning | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Lightning¦LightningArrestor¦FailedFaulted | Equipment Failure/Involved | Lightning | Lightning Arrestor | Failed/Faulted | FNLYEAR 2015: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Lightning¦Other¦BentorTwisted | Equipment Failure/Involved | Lightning | Other | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Lightning¦Other¦FailedFaulted | Equipment Failure/Involved | Lightning | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Lightning¦Other¦Malfunctioning | Equipment Failure/Involved | Lightning | Other | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0 | 0.5 | 0 | 0.5 | EquipmentFailureInvolved¦Lightning¦Transformer¦Broken | Equipment Failure/Involved | Lightning | Transformer | Broken | FNLYEAR 2015: 5 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0 | 0.6 | 0 | 0.6 | EquipmentFailureInvolved¦Lightning¦Transformer¦Burnedflashed | Equipment Failure/Involved | Lightning | Transformer | Burned/flashed | FNLYEAR 2015: 6 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.96 | 1.96 | 0 | 2.8 | 0 | 2.8 | EquipmentFailureInvolved¦Lightning¦Transformer¦FailedFaulted | Equipment Failure/Involved | Lightning | Transformer | Failed/Faulted | FNLYEAR 2015: 28 | 28
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 0 | 0.7 | 0 | 0.7 | EquipmentFailureInvolved¦Lightning¦Transformer¦Malfunctioning | Equipment Failure/Involved | Lightning | Transformer | Malfunctioning | FNLYEAR 2015: 7 | 7
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦¦Broken | Equipment Failure/Involved | Other |  | Broken | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦¦FailedFaulted | Equipment Failure/Involved | Other |  | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2019
Primary Conductor - Other | N/A | 0% | 0 | 0 | Very High | 90% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦BentorTwisted | Equipment Failure/Involved | Other | Conductor, Overhead | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Broken | Equipment Failure/Involved | Other | Conductor, Overhead | Broken | FNLYEAR 2015: 5 | 5
Primary Conductor - Wire Down | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonground | Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2015: 23; FNLYEAR 2016: 1; FNLYEAR 2017: 2 | 26
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonobject | Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on object | FNLYEAR 2015: 2 | 2
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Burnedflashed | Equipment Failure/Involved | Other | Conductor, Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦BurnedOpen | Equipment Failure/Involved | Other | Conductor, Overhead | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Deteriorated | Equipment Failure/Involved | Other | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Malfunctioning | Equipment Failure/Involved | Other | Conductor, Overhead | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Normal | Equipment Failure/Involved | Other | Conductor, Overhead | Normal | FNLYEAR 2015: 2 | 2
Primary Conductor - Wire Down | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦OnGround | Equipment Failure/Involved | Other | Conductor, Overhead | On Ground | FNLYEAR 2015: 4 | 4
Primary Conductor - Line Slap | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Together | Equipment Failure/Involved | Other | Conductor, Overhead | Together | FNLYEAR 2015: 4 | 4
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorUnderground¦Broken | Equipment Failure/Involved | Other | Conductor, Underground | Broken | FNLYEAR 2015: 4 | 4
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConductorUnderground¦FailedFaulted | Equipment Failure/Involved | Other | Conductor, Underground | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Arcing | Equipment Failure/Involved | Other | Connector or Splice (OH) | Arcing | FNLYEAR 2015: 3; FNLYEAR 2018: 1; FNLYEAR 2019: 1 | 5
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Broken | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken | FNLYEAR 2015: 7; FNLYEAR 2017: 2 | 9
Primary Conductor - Wire Down | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Brokenwireonground | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken, wire on ground | FNLYEAR 2015: 8 | 8
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Burnedflashed | Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned/flashed | FNLYEAR 2015: 2 | 2
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦BurnedOpen | Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2016
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Deteriorated | Equipment Failure/Involved | Other | Connector or Splice (OH) | Deteriorated | FNLYEAR 2016: 3; FNLYEAR 2017: 1; FNLYEAR 2018: 1 | 5
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦ConnectororSplice(UG)¦FailedFaulted | Equipment Failure/Involved | Other | Connector or Splice (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CrossarmWood¦ | Equipment Failure/Involved | Other | Crossarm, Wood | [11 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CrossarmWood¦Broken | Equipment Failure/Involved | Other | Crossarm, Wood | Broken | FNLYEAR 2015: 15 | 15
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CrossarmWood¦Brokenwireonground | Equipment Failure/Involved | Other | Crossarm, Wood | Broken, wire on ground | FNLYEAR 2015: 3 | 3
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CrossarmWood¦Burnedflashed | Equipment Failure/Involved | Other | Crossarm, Wood | Burned/flashed | FNLYEAR 2015: 2 | 2
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CrossarmWood¦Deteriorated | Equipment Failure/Involved | Other | Crossarm, Wood | Deteriorated | FNLYEAR 2015: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CustomerEquipment¦Burnedflashed | Equipment Failure/Involved | Other | Customer Equipment | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CustomerEquipment¦Deteriorated | Equipment Failure/Involved | Other | Customer Equipment | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦CustomerEquipment¦Malfunctioning | Equipment Failure/Involved | Other | Customer Equipment | Malfunctioning | FNLYEAR 2015: 3; FNLYEAR 2016: 3; FNLYEAR 2017: 7; FNLYEAR 2018: 3; FNLYEAR 2019: 4 | 20
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Arcing | Equipment Failure/Involved | Other | Cutout, fuse holder | Arcing | FNLYEAR 2015: 2 | 2
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Broken | Equipment Failure/Involved | Other | Cutout, fuse holder | Broken | FNLYEAR 2015: 12; FNLYEAR 2017: 2 | 14
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Burnedflashed | Equipment Failure/Involved | Other | Cutout, fuse holder | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦FailedFaulted | Equipment Failure/Involved | Other | Cutout, fuse holder | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2017
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Elbow¦Malfunctioning | Equipment Failure/Involved | Other | Elbow | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Fuse¦Arcing | Equipment Failure/Involved | Other | Fuse | Arcing | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Fuse¦Broken | Equipment Failure/Involved | Other | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Fuse¦FailedFaulted | Equipment Failure/Involved | Other | Fuse | Failed/Faulted | FNLYEAR 2015: 4; FNLYEAR 2016: 1 | 5
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Insulator¦Broken | Equipment Failure/Involved | Other | Insulator | Broken | FNLYEAR 2015: 9 | 9
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Insulator¦Brokenwireonobject | Equipment Failure/Involved | Other | Insulator | Broken, wire on object | FNLYEAR 2015: 3 | 3
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Insulator¦Burnedflashed | Equipment Failure/Involved | Other | Insulator | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Insulator¦FailedFaulted | Equipment Failure/Involved | Other | Insulator | Failed/Faulted | FNLYEAR 2015: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Insulator¦Malfunctioning | Equipment Failure/Involved | Other | Insulator | Malfunctioning | FNLYEAR 2015: 2 | 2
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Jumper¦Arcing | Equipment Failure/Involved | Other | Jumper | Arcing | FNLYEAR 2015: 2 | 2
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Jumper¦Broken | Equipment Failure/Involved | Other | Jumper | Broken | FNLYEAR 2015: 7; FNLYEAR 2017: 1 | 8
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Jumper¦Burnedflashed | Equipment Failure/Involved | Other | Jumper | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Jumper¦BurnedOpen | Equipment Failure/Involved | Other | Jumper | Burned Open | FNLYEAR 2015: 12 | 12
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦LightningArrestor¦Broken | Equipment Failure/Involved | Other | Lightning Arrestor | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦LightningArrestor¦FailedFaulted | Equipment Failure/Involved | Other | Lightning Arrestor | Failed/Faulted | FNLYEAR 2015: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦MeteringEquipment¦Malfunctioning | Equipment Failure/Involved | Other | Metering Equipment | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Other¦Broken | Equipment Failure/Involved | Other | Other | Broken | FNLYEAR 2015: 6; FNLYEAR 2016: 1; FNLYEAR 2017: 1 | 8
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Other¦Burnedflashed | Equipment Failure/Involved | Other | Other | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Other¦Deteriorated | Equipment Failure/Involved | Other | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Other¦FailedFaulted | Equipment Failure/Involved | Other | Other | Failed/Faulted | FNLYEAR 2016: 4; FNLYEAR 2017: 2 | 6
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Other¦Leaking | Equipment Failure/Involved | Other | Other | Leaking | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Other¦Malfunctioning | Equipment Failure/Involved | Other | Other | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦PoleWood¦BentorTwisted | Equipment Failure/Involved | Other | Pole-Wood | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦PoleWood¦Broken | Equipment Failure/Involved | Other | Pole-Wood | Broken | FNLYEAR 2015: 16; FNLYEAR 2017: 1 | 17
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦PoleWood¦Brokenwireonground | Equipment Failure/Involved | Other | Pole-Wood | Broken, wire on ground | FNLYEAR 2015: 8 | 8
Equipment (Support Structure) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦PoleWood¦Burnedflashed | Equipment Failure/Involved | Other | Pole-Wood | Burned/flashed | FNLYEAR 2015: 3 | 3
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦PotheadRiserTermination¦Burnedflashed | Equipment Failure/Involved | Other | Pothead/Riser Termination | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Riser¦FailedFaulted | Equipment Failure/Involved | Other | Riser | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Secondary¦Broken | Equipment Failure/Involved | Other | Secondary | Broken | FNLYEAR 2015: 2 | 2
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Secondary¦Malfunctioning | Equipment Failure/Involved | Other | Secondary | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Serviceconductor¦Broken | Equipment Failure/Involved | Other | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Switch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Switch¦Malfunctioning | Equipment Failure/Involved | Other | Switch | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer(OH)¦Broken | Equipment Failure/Involved | Other | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦ | Equipment Failure/Involved | Other | Transformer | [11 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Arcing | Equipment Failure/Involved | Other | Transformer | Arcing | FNLYEAR 2015: 3 | 3
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Broken | Equipment Failure/Involved | Other | Transformer | Broken | FNLYEAR 2015: 12 | 12
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Burnedflashed | Equipment Failure/Involved | Other | Transformer | Burned/flashed | FNLYEAR 2015: 7 | 7
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦BurnedOpen | Equipment Failure/Involved | Other | Transformer | Burned Open | FNLYEAR 2015: 2 | 2
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Contaminated | Equipment Failure/Involved | Other | Transformer | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Deteriorated | Equipment Failure/Involved | Other | Transformer | Deteriorated | FNLYEAR 2015: 15; FNLYEAR 2016: 1 | 16
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | FNLYEAR 2015: 64; FNLYEAR 2016: 7; FNLYEAR 2017: 5; FNLYEAR 2018: 1 | 77
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Leaking | Equipment Failure/Involved | Other | Transformer | Leaking | FNLYEAR 2015: 6 | 6
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning | Equipment Failure/Involved | Other | Transformer | Malfunctioning | FNLYEAR 2015: 62 | 62
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Transformer¦Normal | Equipment Failure/Involved | Other | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Other¦Woodpin¦Broken | Equipment Failure/Involved | Other | Woodpin | Broken | FNLYEAR 2015: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦¦Arcing | Equipment Failure/Involved | Overhead |  | Arcing | FNLYEAR 2017: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦¦Broken | Equipment Failure/Involved | Overhead |  | Broken | 7 | 12 | 11 | 9 | 8 | 5 | 10 |  |  |  | 62
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦¦BurnedOpen | Equipment Failure/Involved | Overhead |  | Burned Open | 2 | 2 | 1 | 1 | 1 |  | 3 | 2 |  |  | 12
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 11 | 27 | 16 | 7 | 11 | 5 | 11 | 3 |  |  | 91
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦¦Normal | Equipment Failure/Involved | Overhead |  | Normal | 1 | 5 | 3 |  | 3 |  | 1 | 1 |  |  | 14
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦BentorTwisted | Equipment Failure/Involved | Overhead | Anchor or Guy | Bent or Twisted | [10 empty] | 2 | bar: FNLYEAR 2018 to FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | FNLYEAR 2024: 4 | 4
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 4.77 | 4.77 | 6.1429 | 5.3 | 5.6 | 5.3 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2 | 1 | 7 | 4 | 11 | 6 | 7 | 7 | 8 |  | 53
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Brokenwireonground | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0 | 0.3 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken, wire on object | FNLYEAR 2018: 1; FNLYEAR 2019: 2 | 3
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Burnedflashed | Equipment Failure/Involved | Overhead | Anchor or Guy | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2023
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Deteriorated | Equipment Failure/Involved | Overhead | Anchor or Guy | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 0.8 | 0.5 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Deteriorated | Equipment Failure/Involved | Overhead | Anchor or Guy | Deteriorated | FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 5
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.42857 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Normal | Equipment Failure/Involved | Overhead | Anchor or Guy | Normal | [10 empty] | 4 | bar: FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2021 to FNLYEAR 2022
Equipment (Voltage Control) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Overhead¦Booster¦Arcing | Equipment Failure/Involved | Overhead | Booster | Arcing | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2022: 2 | 4
Equipment (Voltage Control) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.28571 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦Overhead¦Booster¦Burnedflashed | Equipment Failure/Involved | Overhead | Booster | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2022
Equipment (Voltage Control) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 0.6 | 0.6 | EquipmentFailureInvolved¦Overhead¦Booster¦FailedFaulted | Equipment Failure/Involved | Overhead | Booster | Failed/Faulted | FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2023: 2 | 6
Equipment (Voltage Control) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Booster¦Leaking | Equipment Failure/Involved | Overhead | Booster | Leaking | FNLYEAR 2024: 2 | 2
Equipment (Voltage Control) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Booster¦Malfunctioning | Equipment Failure/Involved | Overhead | Booster | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Voltage Control) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.28571 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦Overhead¦Booster¦Malfunctioning | Equipment Failure/Involved | Overhead | Booster | Malfunctioning | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2020; FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Bus¦Annealed | Equipment Failure/Involved | Overhead | Bus | Annealed | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Bus¦BurnedOpen | Equipment Failure/Involved | Overhead | Bus | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Bus¦FailedFaulted | Equipment Failure/Involved | Overhead | Bus | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Bus¦Normal | Equipment Failure/Involved | Overhead | Bus | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Bushing¦Arcing | Equipment Failure/Involved | Overhead | Bushing | Arcing | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.4 | 0.4 | 1.4286 | 1 | 2 | 1 | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken | Equipment Failure/Involved | Overhead | Bushing | Broken | FNLYEAR 2024: 10 | 10
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 2 | 2 | 6 | 5 | 5.4 | 5 | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken | Equipment Failure/Involved | Overhead | Bushing | Broken | 2 | 4 | 2 | 6 | 9 | 5 | 5 | 11 | 6 |  | 50
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Bushing¦Burnedflashed | Equipment Failure/Involved | Overhead | Bushing | Burned/flashed | FNLYEAR 2024: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 0.8 | 0.5 | EquipmentFailureInvolved¦Overhead¦Bushing¦Burnedflashed | Equipment Failure/Involved | Overhead | Bushing | Burned/flashed | FNLYEAR 2018: 1; FNLYEAR 2020: 2; FNLYEAR 2022: 2 | 5
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Bushing¦BurnedOpen | Equipment Failure/Involved | Overhead | Bushing | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Bushing¦Deteriorated | Equipment Failure/Involved | Overhead | Bushing | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Bushing¦Deteriorated | Equipment Failure/Involved | Overhead | Bushing | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Bushing¦FailedFaulted | Equipment Failure/Involved | Overhead | Bushing | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.4 | 0.4 | 0.42857 | 1 | 0.4 | 1 | EquipmentFailureInvolved¦Overhead¦Bushing¦FailedFaulted | Equipment Failure/Involved | Overhead | Bushing | Failed/Faulted | FNLYEAR 2016: 4; FNLYEAR 2017: 3; FNLYEAR 2018: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 10
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Bushing¦Leaking | Equipment Failure/Involved | Overhead | Bushing | Leaking | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Capacitor¦Arcing | Equipment Failure/Involved | Overhead | Capacitor | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Capacitor¦Broken | Equipment Failure/Involved | Overhead | Capacitor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Capacitor¦Broken | Equipment Failure/Involved | Overhead | Capacitor | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Capacitor¦Burnedflashed | Equipment Failure/Involved | Overhead | Capacitor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.57143 | 0.5 | 0.2 | 0.5 | EquipmentFailureInvolved¦Overhead¦Capacitor¦Burnedflashed | Equipment Failure/Involved | Overhead | Capacitor | Burned/flashed | FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 1 | 5
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Overhead¦Capacitor¦FailedFaulted | Equipment Failure/Involved | Overhead | Capacitor | Failed/Faulted | FNLYEAR 2024: 5 | 5
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1.4286 | 1.3 | 1.4 | 1.3 | EquipmentFailureInvolved¦Overhead¦Capacitor¦FailedFaulted | Equipment Failure/Involved | Overhead | Capacitor | Failed/Faulted |  |  | 3 | 2 | 1 |  | 3 | 2 | 2 |  | 13
Equipment (Capacitor) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Capacitor¦Normal | Equipment Failure/Involved | Overhead | Capacitor | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed | Equipment Failure/Involved | Overhead | Conductor- Overhead | Annealed | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 2.25 | 2.25 | 2.7143 | 2.5 | 2.2 | 2.5 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed | Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | 3 | 1 | 2 | 1 | 7 | 2 | 3 | 5 | 1 |  | 25
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing | Equipment Failure/Involved | Overhead | Conductor- Overhead | Arcing | FNLYEAR 2024: 3 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 2.25 | 2.25 | 2.4286 | 2.5 | 2.2 | 2.5 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2 | 2 | 4 |  | 6 | 2 | 2 | 3 | 4 |  | 25
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted | Equipment Failure/Involved | Overhead | Conductor- Overhead | Bent or Twisted | FNLYEAR 2024: 6 | 6
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 4.5 | 4.5 | 5.7143 | 5 | 6 | 5 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 4 | 1 | 5 | 3 | 7 | 3 | 11 | 6 | 10 |  | 50
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 2.25 | 2.25 | 3.5714 | 2.5 | 5 | 2.5 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken | FNLYEAR 2024: 25 | 25
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 26.1 | 26.1 | 29.4286 | 29 | 27.6 | 29 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 5 | 32 | 47 | 22 | 46 | 29 | 42 | 26 | 41 |  | 290
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 1.96 | 1.96 | 7 | 4.9 | 9.8 | 4.9 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 49 | 49
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 41.88 | 41.88 | 94 | 104.7 | 83.6 | 104.7 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 49 | 91 | 249 | 83 | 157 | 64 | 203 | 85 | 66 |  | 1047
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken- wire on object | FNLYEAR 2024: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 1.24 | 1.24 | 3 | 3.1 | 2.2 | 3.1 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on object | 3 | 1 | 6 | 3 | 7 | 3 | 2 | 1 | 5 |  | 31
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed | Equipment Failure/Involved | Overhead | Conductor- Overhead | Burned/flashed | FNLYEAR 2024: 6 | 6
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 2.7 | 2.7 | 2.7143 | 3 | 2.6 | 3 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed | Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | 4 | 1 | 6 | 4 | 2 | 3 | 2 | 3 | 5 |  | 30
Primary Conductor - Line Slap | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.28571 | 0.3 | 0 | 0.3 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Contaminated | Equipment Failure/Involved | Overhead | Conductor, Overhead | Contaminated | FNLYEAR 2016: 1; FNLYEAR 2018: 2 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 3.24 | 3.24 | 5.1429 | 3.6 | 7.2 | 3.6 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated | Equipment Failure/Involved | Overhead | Conductor- Overhead | Deteriorated | FNLYEAR 2024: 36 | 36
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 16.47 | 16.47 | 23.7143 | 18.3 | 24.8 | 18.3 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 6 | 7 | 4 | 8 | 34 | 19 | 30 | 39 | 36 |  | 183
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦FailedFaulted | Equipment Failure/Involved | Overhead | Conductor, Overhead | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 2.7 | 2.7 | 4.2857 | 3 | 6 | 3 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal | Equipment Failure/Involved | Overhead | Conductor- Overhead | Normal | FNLYEAR 2024: 30 | 30
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 17.82 | 17.82 | 21.4286 | 19.8 | 20 | 19.8 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 10 | 16 | 22 | 11 | 39 | 11 | 33 | 22 | 34 |  | 198
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround | Equipment Failure/Involved | Overhead | Conductor- Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 1.96 | 1.96 | 4.8571 | 4.9 | 4.8 | 4.9 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 1 | 5 | 9 | 1 | 9 | 1 | 17 | 6 |  |  | 49
Primary Conductor - Line Slap | None | 0% | 0 | 0 | Very High | 90% | 3.15 | 3.15 | 5 | 3.5 | 7 | 3.5 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together | Equipment Failure/Involved | Overhead | Conductor- Overhead | Together | FNLYEAR 2024: 35 | 35
Primary Conductor - Line Slap | None | 0% | 0 | 0 | Very High | 90% | 26.19 | 26.19 | 30.4286 | 29.1 | 27 | 29.1 | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 12 | 26 | 40 | 25 | 53 | 33 | 43 | 32 | 27 |  | 291
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConductorUnderground¦Burnedflashed | Equipment Failure/Involved | Overhead | Conductor, Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConnectorBolted¦Annealed | Equipment Failure/Involved | Overhead | Connector- Bolted | Annealed | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.63 | 0.63 | 1 | 0.7 | 1.4 | 0.7 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | FNLYEAR 2024: 7 | 7
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 5.76 | 5.76 | 6.8571 | 6.4 | 6.2 | 6.4 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 3 | 5 | 8 | 9 | 8 | 5 | 13 | 7 | 6 |  | 64
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 2.16 | 2.16 | 3.4286 | 2.4 | 4.8 | 2.4 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | FNLYEAR 2024: 24 | 24
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 27.45 | 27.45 | 34.4286 | 30.5 | 33 | 30.5 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 9 | 15 | 40 | 26 | 50 | 29 | 43 | 53 | 40 |  | 305
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Very High | 90% | 1.44 | 1.44 | 2.2857 | 1.6 | 3.2 | 1.6 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken- wire on ground | FNLYEAR 2024: 16 | 16
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Very High | 90% | 21.87 | 21.87 | 22.5714 | 24.3 | 19.4 | 24.3 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 11 | 33 | 41 | 26 | 35 | 22 | 36 | 23 | 16 |  | 243
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.99 | 0.99 | 0.85714 | 1.1 | 0.4 | 1.1 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on object | 1 | 2 | 2 | 2 | 2 | 1 | 1 |  |  |  | 11
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Burnedflashed | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | FNLYEAR 2024: 3 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 3.42 | 3.42 | 3 | 3.8 | 3.6 | 3.8 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Burnedflashed | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | 2 | 4 | 11 | 1 | 2 | 3 | 7 | 6 | 2 |  | 38
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 1.2857 | 0.9 | 1.8 | 0.9 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | FNLYEAR 2024: 9 | 9
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 7.2 | 7.2 | 7 | 8 | 6.6 | 8 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 6 | 12 | 13 | 10 | 6 | 3 | 8 | 11 | 11 |  | 80
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Contaminated | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.9 | 0.9 | 1.1429 | 1 | 1.4 | 1 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Contaminated | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Contaminated |  | 1 | 1 |  | 1 | 1 | 2 | 4 |  |  | 10
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.72 | 0.72 | 1.1429 | 0.8 | 1.6 | 0.8 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | FNLYEAR 2024: 8 | 8
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 7.74 | 7.74 | 9.5714 | 8.6 | 10 | 8.6 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 3 | 7 | 9 | 8 | 9 | 10 | 12 | 15 | 13 |  | 86
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Normal | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Normal | FNLYEAR 2024: 3 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.63 | 0.63 | 0.71429 | 0.7 | 1 | 0.7 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Normal | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Normal | FNLYEAR 2017: 2; FNLYEAR 2021: 3; FNLYEAR 2023: 2 | 7
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(UG)¦Deteriorated | Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(UG)¦Normal | Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Broken | Equipment Failure/Involved | Overhead | Crossarm- Steel | Broken | FNLYEAR 2024: 4 | 4
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.9 | 0.9 | 1.2857 | 1 | 1.2 | 1 | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Broken | Equipment Failure/Involved | Overhead | Crossarm, Steel | Broken | FNLYEAR 2017: 1; FNLYEAR 2019: 3; FNLYEAR 2021: 4; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 10
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Crossarm, Steel | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Burnedflashed | Equipment Failure/Involved | Overhead | Crossarm, Steel | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Deteriorated | Equipment Failure/Involved | Overhead | Crossarm, Steel | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2020 to FNLYEAR 2021
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 9.99 | 9.99 | 15.8571 | 11.1 | 22.2 | 11.1 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken | FNLYEAR 2024: 111 | 111
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 112.5 | 112.5 | 138.5714 | 125 | 117 | 125 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 60 | 98 | 122 | 129 | 256 | 138 | 190 | 107 | 150 |  | 1250
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 3.32 | 3.32 | 8.1429 | 8.3 | 7.2 | 8.3 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2 | 3 | 21 | 6 | 15 | 10 | 14 | 9 | 3 |  | 83
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken- wire on object | FNLYEAR 2024: 2 | 2
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.68 | 0.68 | 1.5714 | 1.7 | 0.8 | 1.7 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on object |  | 2 | 4 | 2 | 5 | 2 | 1 |  | 1 |  | 17
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed | Equipment Failure/Involved | Overhead | Crossarm- Wood | Burned/flashed | FNLYEAR 2024: 4 | 4
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 4.77 | 4.77 | 5.2857 | 5.3 | 4.8 | 5.3 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 4 | 6 | 6 | 4 | 9 | 5 | 7 | 6 | 6 |  | 53
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 2.97 | 2.97 | 4.7143 | 3.3 | 6.6 | 3.3 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated | Equipment Failure/Involved | Overhead | Crossarm- Wood | Deteriorated | FNLYEAR 2024: 33 | 33
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 15.03 | 15.03 | 18.8571 | 16.7 | 19 | 16.7 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 10 | 13 | 12 | 12 | 25 | 21 | 26 | 23 | 25 |  | 167
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦FailedFaulted | Equipment Failure/Involved | Overhead | Crossarm, Wood | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Normal | Equipment Failure/Involved | Overhead | Crossarm- Wood | Normal | FNLYEAR 2024: 2 | 2
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.72 | 0.72 | 1.1429 | 0.8 | 1.4 | 0.8 | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Normal | Equipment Failure/Involved | Overhead | Crossarm, Wood | Normal | FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1; FNLYEAR 2023: 3 | 8
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦CT¦Deteriorated | Equipment Failure/Involved | Overhead | CT | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦CT¦FailedFaulted | Equipment Failure/Involved | Overhead | CT | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Arcing | Equipment Failure/Involved | Overhead | Customer Equipment | Arcing | FNLYEAR 2018: 2; FNLYEAR 2022: 1 | 3
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Broken | Equipment Failure/Involved | Overhead | Customer Equipment | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Broken | Equipment Failure/Involved | Overhead | Customer Equipment | Broken | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2022 to FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Burnedflashed | Equipment Failure/Involved | Overhead | Customer Equipment | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Deteriorated | Equipment Failure/Involved | Overhead | Customer Equipment | Deteriorated | FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 3
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦FailedFaulted | Equipment Failure/Involved | Overhead | Customer Equipment | Failed/Faulted | FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 4
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Normal | Equipment Failure/Involved | Overhead | Customer Equipment | Normal | FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 3
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Together | Equipment Failure/Involved | Overhead | Customer Equipment | Together | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Arcing | FNLYEAR 2024: 6 | 6
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 2.07 | 2.07 | 2.7143 | 2.3 | 2.4 | 2.3 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing |  | 4 |  | 3 | 4 | 3 | 3 | 4 | 2 |  | 23
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 2.94 | 2.94 | 6 | 4.2 | 8.4 | 4.2 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Broken | FNLYEAR 2024: 42 | 42
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 31.78 | 31.78 | 45.5714 | 45.4 | 40.8 | 45.4 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 22 | 45 | 68 | 41 | 74 | 60 | 49 | 56 | 39 |  | 454
Equipment (Fuse) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Brokenwireonground | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Burned/flashed | FNLYEAR 2024: 4 | 4
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 3.92 | 3.92 | 5.4286 | 5.6 | 4.8 | 5.6 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | 4 | 7 | 7 | 4 | 10 | 4 | 7 | 8 | 5 |  | 56
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦BurnedOpen | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Failed/Faulted | FNLYEAR 2024: 5 | 5
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 6.84 | 6.84 | 9 | 7.6 | 7.4 | 7.6 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 3 | 3 | 7 | 8 | 18 | 9 | 8 | 10 | 10 |  | 76
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Malfunctioning | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.7 | 0.7 | 1.4286 | 1 | 2 | 1 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Normal | FNLYEAR 2024: 10 | 10
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 2.31 | 2.31 | 3.2857 | 3.3 | 3.4 | 3.3 | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 3 | 5 | 2 | 4 | 2 | 1 | 5 | 2 | 9 |  | 33
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Overhead¦FootingsTowerorPole¦Broken | Equipment Failure/Involved | Overhead | Footings, Tower or Pole | Broken | [10 empty] | 2 | bar: FNLYEAR 2018 to FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦FootingsTowerorPole¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Footings, Tower or Pole | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦FootingsTowerorPole¦Normal | Equipment Failure/Involved | Overhead | Footings, Tower or Pole | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Fuse) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Fuse¦ | Equipment Failure/Involved | Overhead | Fuse | [11 empty] | 1 | bar: FNLYEAR 2021
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Fuse¦Arcing | Equipment Failure/Involved | Overhead | Fuse | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 1.35 | 1.35 | 1.7143 | 1.5 | 2.4 | 1.5 | EquipmentFailureInvolved¦Overhead¦Fuse¦Arcing | Equipment Failure/Involved | Overhead | Fuse | Arcing | 1 | 2 |  |  |  | 1 | 4 | 3 | 4 |  | 15
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 3.96 | 3.96 | 6.2857 | 4.4 | 8.8 | 4.4 | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken | Equipment Failure/Involved | Overhead | Fuse | Broken | FNLYEAR 2024: 44 | 44
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 20.61 | 20.61 | 27.1429 | 22.9 | 33.6 | 22.9 | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken | Equipment Failure/Involved | Overhead | Fuse | Broken | 5 | 13 | 21 | 9 | 13 | 24 | 44 | 55 | 45 |  | 229
Equipment (Fuse) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Fuse¦Brokenwireonground | Equipment Failure/Involved | Overhead | Fuse | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 1.17 | 1.17 | 1.8571 | 1.3 | 2.6 | 1.3 | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen | Equipment Failure/Involved | Overhead | Fuse | Burned Open | FNLYEAR 2024: 13 | 13
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 7.38 | 7.38 | 10.4286 | 8.2 | 14 | 8.2 | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2 | 2 | 5 | 1 | 2 | 4 | 13 | 38 | 15 |  | 82
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 3.78 | 3.78 | 6 | 4.2 | 8.4 | 4.2 | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | FNLYEAR 2024: 42 | 42
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 25.29 | 25.29 | 29.1429 | 28.1 | 29.4 | 28.1 | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 14 | 18 | 45 | 21 | 36 | 13 | 26 | 45 | 63 |  | 281
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Fuse¦Malfunctioning | Equipment Failure/Involved | Overhead | Fuse | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.99 | 0.99 | 1.5714 | 1.1 | 2.2 | 1.1 | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal | Equipment Failure/Involved | Overhead | Fuse | Normal | FNLYEAR 2024: 11 | 11
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 6.93 | 6.93 | 9.2857 | 7.7 | 10.2 | 7.7 | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal | Equipment Failure/Involved | Overhead | Fuse | Normal | 1 | 6 | 5 | 7 | 7 | 6 | 14 | 13 | 18 |  | 77
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Generator¦Malfunctioning | Equipment Failure/Involved | Overhead | Generator | Malfunctioning | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Generator¦Normal | Equipment Failure/Involved | Overhead | Generator | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦Insulator¦Arcing | Equipment Failure/Involved | Overhead | Insulator | Arcing | FNLYEAR 2024: 3 | 3
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 1.89 | 1.89 | 1.5714 | 2.1 | 1.4 | 2.1 | EquipmentFailureInvolved¦Overhead¦Insulator¦Arcing | Equipment Failure/Involved | Overhead | Insulator | Arcing | 4 | 3 | 3 | 2 | 2 | 1 | 3 | 1 | 2 |  | 21
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 5.67 | 5.67 | 9 | 6.3 | 12.6 | 6.3 | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken | Equipment Failure/Involved | Overhead | Insulator | Broken | FNLYEAR 2024: 63 | 63
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 59.94 | 59.94 | 73.1429 | 66.6 | 66.4 | 66.6 | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken | Equipment Failure/Involved | Overhead | Insulator | Broken | 18 | 57 | 79 | 62 | 118 | 66 | 94 | 81 | 91 |  | 666
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonground | Equipment Failure/Involved | Overhead | Insulator | Broken- wire on ground | FNLYEAR 2024: 4 | 4
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 1.6 | 1.6 | 3.7143 | 4 | 3.8 | 4 | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonground | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on ground | 3 | 4 | 7 | 2 | 5 | 5 | 7 | 7 |  |  | 40
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Insulator | Broken- wire on object | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 1.6 | 1.6 | 3.1429 | 4 | 2.4 | 4 | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 3 | 2 | 13 | 9 | 1 | 5 | 4 | 3 |  |  | 40
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.63 | 0.63 | 1 | 0.7 | 1.4 | 0.7 | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | FNLYEAR 2024: 7 | 7
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 4.95 | 4.95 | 5.8571 | 5.5 | 6.8 | 5.5 | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2 | 6 | 6 | 2 | 5 | 9 | 10 | 10 | 5 |  | 55
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted | Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | FNLYEAR 2024: 4 | 4
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 3.78 | 3.78 | 4.5714 | 4.2 | 4.2 | 4.2 | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted | Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | 1 | 5 | 4 | 5 | 6 | 1 | 6 | 6 | 8 |  | 42
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 1.26 | 1.26 | 0.85714 | 1.4 | 0.6 | 1.4 | EquipmentFailureInvolved¦Overhead¦Insulator¦Normal | Equipment Failure/Involved | Overhead | Insulator | Normal | 1 | 1 | 6 | 2 | 1 |  |  | 1 | 2 |  | 14
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Jumper¦ | Equipment Failure/Involved | Overhead | Jumper | [11 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Jumper¦ | Equipment Failure/Involved | Overhead | Jumper | [11 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing | Equipment Failure/Involved | Overhead | Jumper | Arcing | FNLYEAR 2024: 3 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 2.38 | 2.38 | 3.4286 | 3.4 | 3.6 | 3.4 | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing | Equipment Failure/Involved | Overhead | Jumper | Arcing | 1 | 5 | 4 | 3 | 3 | 4 | 3 | 5 | 6 |  | 34
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Jumper¦BentorTwisted | Equipment Failure/Involved | Overhead | Jumper | Bent or Twisted | FNLYEAR 2024: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 1.19 | 1.19 | 1.7143 | 1.7 | 1 | 1.7 | EquipmentFailureInvolved¦Overhead¦Jumper¦BentorTwisted | Equipment Failure/Involved | Overhead | Jumper | Bent or Twisted |  | 4 | 1 | 2 | 5 |  | 1 |  | 4 |  | 17
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 1.47 | 1.47 | 3 | 2.1 | 4.2 | 2.1 | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken | Equipment Failure/Involved | Overhead | Jumper | Broken | FNLYEAR 2024: 21 | 21
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 12.04 | 12.04 | 18.1429 | 17.2 | 16.2 | 17.2 | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken | Equipment Failure/Involved | Overhead | Jumper | Broken | 5 | 17 | 23 | 11 | 35 | 10 | 29 | 18 | 24 |  | 172
Primary Conductor - Other | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Jumper¦Brokenwireonground | Equipment Failure/Involved | Overhead | Jumper | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | FNLYEAR 2024: 6 | 6
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 1.96 | 1.96 | 3 | 2.8 | 3.2 | 2.8 | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | 1 | 1 | 5 | 1 | 4 | 5 |  | 6 | 5 |  | 28
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 2.24 | 2.24 | 4.5714 | 3.2 | 6.4 | 3.2 | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen | Equipment Failure/Involved | Overhead | Jumper | Burned Open | FNLYEAR 2024: 32 | 32
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 28.84 | 28.84 | 38.8571 | 41.2 | 37.6 | 41.2 | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 26 | 32 | 82 | 29 | 55 | 52 | 60 | 39 | 37 |  | 412
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦Jumper¦Deteriorated | Equipment Failure/Involved | Overhead | Jumper | Deteriorated | FNLYEAR 2024: 3 | 3
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.57143 | 0.6 | 0.4 | 0.6 | EquipmentFailureInvolved¦Overhead¦Jumper¦Deteriorated | Equipment Failure/Involved | Overhead | Jumper | Deteriorated | FNLYEAR 2017: 2; FNLYEAR 2018: 2; FNLYEAR 2020: 1; FNLYEAR 2023: 1 | 6
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Jumper¦FailedFaulted | Equipment Failure/Involved | Overhead | Jumper | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Jumper¦Normal | Equipment Failure/Involved | Overhead | Jumper | Normal | FNLYEAR 2024: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 0.6 | 0.5 | EquipmentFailureInvolved¦Overhead¦Jumper¦Normal | Equipment Failure/Involved | Overhead | Jumper | Normal | [10 empty] | 5 | bar: FNLYEAR 2018 to FNLYEAR 2021; FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Arcing | Equipment Failure/Involved | Overhead | Lightning Arrestor | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.57143 | 0.6 | 0.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Arcing | Equipment Failure/Involved | Overhead | Lightning Arrestor | Arcing | FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2022: 1 | 6
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | FNLYEAR 2024: 6 | 6
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 5.4 | 5.4 | 7.5714 | 6 | 9.4 | 6 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | 3 | 1 | 3 | 2 | 4 | 8 | 12 | 17 | 10 |  | 60
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Brokenwireonground | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Burnedflashed | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | FNLYEAR 2024: 5 | 5
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 3.33 | 3.33 | 4.1429 | 3.7 | 5.6 | 3.7 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Burnedflashed | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | 2 | 5 | 1 | 1 |  | 2 | 8 | 11 | 7 |  | 37
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | FNLYEAR 2024: 6 | 6
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 12.78 | 12.78 | 15.4286 | 14.2 | 12 | 14.2 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 4 | 15 | 15 | 16 | 32 | 19 | 9 | 21 | 11 |  | 142
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 1.26 | 1.26 | 1.8571 | 1.4 | 2.6 | 1.4 | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Normal | Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | FNLYEAR 2016: 1; FNLYEAR 2021: 11; FNLYEAR 2022: 2 | 14
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦ | Equipment Failure/Involved | Overhead | Metering Equipment | [11 empty] | 1 | bar: FNLYEAR 2018
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Broken | Equipment Failure/Involved | Overhead | Metering Equipment | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Broken | Equipment Failure/Involved | Overhead | Metering Equipment | Broken | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Burnedflashed | Equipment Failure/Involved | Overhead | Metering Equipment | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2019: 2; FNLYEAR 2023: 1 | 4
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦FailedFaulted | Equipment Failure/Involved | Overhead | Metering Equipment | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦FailedFaulted | Equipment Failure/Involved | Overhead | Metering Equipment | Failed/Faulted | FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2023: 2 | 4
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.7 | 0.8 | 0.7 | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Malfunctioning | Equipment Failure/Involved | Overhead | Metering Equipment | Malfunctioning | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 3 | 7
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Arcing | Equipment Failure/Involved | Overhead | Other | Arcing | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Broken | Equipment Failure/Involved | Overhead | Other | Broken | FNLYEAR 2024: 19 | 19
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Broken | Equipment Failure/Involved | Overhead | Other | Broken | 7 | 14 | 25 | 13 | 11 | 37 | 20 | 16 | 30 |  | 173
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Other¦Brokenwireonground | Equipment Failure/Involved | Overhead | Other | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Other | Broken- wire on object | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Other | Broken, wire on object | FNLYEAR 2017: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 6
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Burnedflashed | Equipment Failure/Involved | Overhead | Other | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Burnedflashed | Equipment Failure/Involved | Overhead | Other | Burned/flashed | FNLYEAR 2015: 2; FNLYEAR 2016: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 5
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦BurnedOpen | Equipment Failure/Involved | Overhead | Other | Burned Open | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Deteriorated | Equipment Failure/Involved | Overhead | Other | Deteriorated | FNLYEAR 2024: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Deteriorated | Equipment Failure/Involved | Overhead | Other | Deteriorated |  |  |  | 1 | 1 | 2 | 1 | 1 | 2 |  | 8
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | FNLYEAR 2024: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 12 | 19 | 13 | 3 | 3 | 2 | 1 | 3 | 2 |  | 58
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Leaking | Equipment Failure/Involved | Overhead | Other | Leaking | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Leaking | Equipment Failure/Involved | Overhead | Other | Leaking | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Malfunctioning | Equipment Failure/Involved | Overhead | Other | Malfunctioning | FNLYEAR 2024: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Malfunctioning | Equipment Failure/Involved | Overhead | Other | Malfunctioning | 1 | 3 | 2 | 3 | 1 | 1 | 1 |  | 5 |  | 17
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Normal | Equipment Failure/Involved | Overhead | Other | Normal |  | 1 | 3 | 1 | 2 | 1 | 3 | 2 |  |  | 13
Primary Conductor - Line Slap | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Together | Equipment Failure/Involved | Overhead | Other | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Line Slap | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Other¦Together | Equipment Failure/Involved | Overhead | Other | Together | [10 empty] | 3 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Broken | Equipment Failure/Involved | Overhead | PGs, Kearneys | Broken | FNLYEAR 2018: 1; FNLYEAR 2021: 2 | 3
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.14286 | 0.4 | 0 | 0.4 | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Brokenwireonground | Equipment Failure/Involved | Overhead | PGs, Kearneys | Broken, wire on ground | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2019: 1 | 4
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Burnedflashed | Equipment Failure/Involved | Overhead | PGs, Kearneys | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦BurnedOpen | Equipment Failure/Involved | Overhead | PGs, Kearneys | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Deteriorated | Equipment Failure/Involved | Overhead | PGs- Kearneys | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Deteriorated | Equipment Failure/Involved | Overhead | PGs, Kearneys | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2023
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦BentorTwisted | Equipment Failure/Involved | Overhead | Pole - Tower, steel | Bent or Twisted | FNLYEAR 2019: 1; FNLYEAR 2021: 2 | 3
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.14286 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦Broken | Equipment Failure/Involved | Overhead | Pole - Tower, steel | Broken | FNLYEAR 2015: 1; FNLYEAR 2017: 2; FNLYEAR 2022: 1 | 4
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦Brokenwireonground | Equipment Failure/Involved | Overhead | Pole - Tower, steel | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦Deteriorated | Equipment Failure/Involved | Overhead | Pole - Tower, steel | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 12.74 | 12.74 | 26 | 18.2 | 36.4 | 18.2 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | FNLYEAR 2024: 182 | 182
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 89.32 | 89.32 | 148 | 127.6 | 143 | 127.6 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 28 | 63 | 149 | 97 | 224 | 143 | 193 | 170 | 209 |  | 1276
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground | Equipment Failure/Involved | Overhead | Pole-Wood | Broken- wire on ground | FNLYEAR 2024: 6 | 6
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 8.12 | 8.12 | 18.1429 | 20.3 | 13.6 | 20.3 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 6 | 18 | 52 | 15 | 44 | 12 | 27 | 17 | 12 |  | 203
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.57143 | 0.7 | 0.4 | 0.7 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on object |  | 1 | 2 | 1 | 1 | 1 |  | 1 |  |  | 7
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | FNLYEAR 2024: 3 | 3
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 3.71 | 3.71 | 4.7143 | 5.3 | 4 | 5.3 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 8 | 3 | 9 | 8 | 5 | 7 | 8 | 2 | 3 |  | 53
Primary Conductor - Other | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Contaminated | Equipment Failure/Involved | Overhead | Pole-Wood | Contaminated | [10 empty] | 4 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2021 to FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 11.34 | 11.34 | 23.1429 | 16.2 | 32.4 | 16.2 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | FNLYEAR 2024: 162 | 162
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 40.32 | 40.32 | 77.7143 | 57.6 | 86.8 | 57.6 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 5 | 14 | 13 | 19 | 91 | 46 | 101 | 146 | 141 |  | 576
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦PoleWood¦FailedFaulted | Equipment Failure/Involved | Overhead | Pole-Wood | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Normal | Equipment Failure/Involved | Overhead | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 2.38 | 2.38 | 4.2857 | 3.4 | 4.8 | 3.4 | EquipmentFailureInvolved¦Overhead¦PoleWood¦Normal | Equipment Failure/Involved | Overhead | Pole-Wood | Normal | 2 | 1 | 1 | 1 | 5 | 1 | 6 | 6 | 11 |  | 34
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.48 | 0.48 | 1 | 1.2 | 0.4 | 1.2 | EquipmentFailureInvolved¦Overhead¦PoleWood¦OnGround | Equipment Failure/Involved | Overhead | Pole-Wood | On Ground |  | 1 | 4 | 1 | 4 |  | 1 | 1 |  |  | 12
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.28571 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Arcing | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Arcing | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2020 to FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Broken | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.77 | 0.77 | 1.4286 | 1.1 | 1.6 | 1.1 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Broken | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken |  |  | 1 | 1 | 1 |  | 3 | 1 | 4 |  | 11
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 1.19 | 1.19 | 2.1429 | 1.7 | 2.6 | 1.7 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Burnedflashed | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed |  | 1 | 1 | 1 | 1 | 4 | 2 | 5 | 2 |  | 17
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Deteriorated | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Deteriorated | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 1.89 | 1.89 | 2.8571 | 2.7 | 1.6 | 2.7 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦FailedFaulted | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Failed/Faulted |  | 2 | 5 | 6 | 6 | 4 | 2 | 2 |  |  | 27
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Leaking | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦PotheadRiserTermination¦Broken | Equipment Failure/Involved | Overhead | Pothead/Riser Termination | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦PotheadRiserTermination¦Burnedflashed | Equipment Failure/Involved | Overhead | Pothead/Riser Termination | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦PTCCVT¦Broken | Equipment Failure/Involved | Overhead | PT/CCVT | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.4 | 0.6 | 0.4 | EquipmentFailureInvolved¦Overhead¦PTCCVT¦Burnedflashed | Equipment Failure/Involved | Overhead | PT/CCVT | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 4
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦PTCCVT¦BurnedOpen | Equipment Failure/Involved | Overhead | PT/CCVT | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.6 | 0.4 | 0.6 | EquipmentFailureInvolved¦Overhead¦PTCCVT¦FailedFaulted | Equipment Failure/Involved | Overhead | PT/CCVT | Failed/Faulted | FNLYEAR 2016: 2; FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 6
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦PTCCVT¦Leaking | Equipment Failure/Involved | Overhead | PT/CCVT | Leaking | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (DPD) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Recloser¦Arcing | Equipment Failure/Involved | Overhead | Recloser | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (DPD) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Recloser¦Arcing | Equipment Failure/Involved | Overhead | Recloser | Arcing | FNLYEAR 2023: 3 | 3
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦Recloser¦Broken | Equipment Failure/Involved | Overhead | Recloser | Broken | FNLYEAR 2024: 3 | 3
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Overhead¦Recloser¦Broken | Equipment Failure/Involved | Overhead | Recloser | Broken | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2019; FNLYEAR 2022
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.14286 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Overhead¦Recloser¦Burnedflashed | Equipment Failure/Involved | Overhead | Recloser | Burned/flashed | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2017; FNLYEAR 2023
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Recloser¦FailedFaulted | Equipment Failure/Involved | Overhead | Recloser | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.56 | 0.56 | 2 | 1.4 | 2.4 | 1.4 | EquipmentFailureInvolved¦Overhead¦Recloser¦FailedFaulted | Equipment Failure/Involved | Overhead | Recloser | Failed/Faulted | FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2021: 4; FNLYEAR 2022: 4; FNLYEAR 2023: 4 | 14
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Recloser¦Leaking | Equipment Failure/Involved | Overhead | Recloser | Leaking | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.56 | 0.56 | 2 | 1.4 | 2.8 | 1.4 | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | FNLYEAR 2024: 14 | 14
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 3.36 | 3.36 | 11.2857 | 8.4 | 14 | 8.4 | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning |  | 3 | 2 | 1 | 8 | 3 | 24 | 22 | 21 |  | 84
Equipment (DPD) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Recloser¦Normal | Equipment Failure/Involved | Overhead | Recloser | Normal | FNLYEAR 2024: 2 | 2
Equipment (DPD) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.14286 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Overhead¦Recloser¦Normal | Equipment Failure/Involved | Overhead | Recloser | Normal | FNLYEAR 2017: 2; FNLYEAR 2021: 1 | 3
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Regulator¦Arcing | Equipment Failure/Involved | Overhead | Regulator | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.42857 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Overhead¦Regulator¦Arcing | Equipment Failure/Involved | Overhead | Regulator | Arcing | [10 empty] | 4 | bar: FNLYEAR 2017; FNLYEAR 2019; FNLYEAR 2021 to FNLYEAR 2022
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Regulator¦Broken | Equipment Failure/Involved | Overhead | Regulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.71429 | 0.6 | 0.8 | 0.6 | EquipmentFailureInvolved¦Overhead¦Regulator¦Broken | Equipment Failure/Involved | Overhead | Regulator | Broken | FNLYEAR 2015: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 6
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.32 | 0.32 | 0.85714 | 0.8 | 1.2 | 0.8 | EquipmentFailureInvolved¦Overhead¦Regulator¦Burnedflashed | Equipment Failure/Involved | Overhead | Regulator | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2021: 4; FNLYEAR 2023: 2 | 8
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦Regulator¦FailedFaulted | Equipment Failure/Involved | Overhead | Regulator | Failed/Faulted | FNLYEAR 2024: 3 | 3
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.64 | 0.64 | 1.4286 | 1.6 | 1.2 | 1.6 | EquipmentFailureInvolved¦Overhead¦Regulator¦FailedFaulted | Equipment Failure/Involved | Overhead | Regulator | Failed/Faulted | 1 | 3 | 2 | 3 | 1 | 1 |  | 3 | 2 |  | 16
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Regulator¦Leaking | Equipment Failure/Involved | Overhead | Regulator | Leaking | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2022
Equipment (Voltage Control) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 0.8 | 1.6 | 0.8 | EquipmentFailureInvolved¦Overhead¦Regulator¦Malfunctioning | Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | FNLYEAR 2024: 8 | 8
Equipment (Voltage Control) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.8571 | 2.6 | 2.8 | 2.6 | EquipmentFailureInvolved¦Overhead¦Regulator¦Malfunctioning | Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | 2 | 1 | 3 | 2 | 4 | 3 | 4 | 3 | 4 |  | 26
Equipment (Voltage Control) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Regulator¦Normal | Equipment Failure/Involved | Overhead | Regulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Voltage Control) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦RegulatorLTCsubstation¦FailedFaulted | Equipment Failure/Involved | Overhead | Regulator, LTC substation | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Relay¦Malfunctioning | Equipment Failure/Involved | Overhead | Relay | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Secondary¦ | Equipment Failure/Involved | Overhead | Secondary | [11 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Secondary¦Arcing | Equipment Failure/Involved | Overhead | Secondary | Arcing | FNLYEAR 2024: 2 | 2
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.98 | 0.98 | 1.5714 | 1.4 | 1 | 1.4 | EquipmentFailureInvolved¦Overhead¦Secondary¦Arcing | Equipment Failure/Involved | Overhead | Secondary | Arcing |  | 1 | 2 | 2 | 4 | 2 | 2 |  | 1 |  | 14
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Secondary¦BentorTwisted | Equipment Failure/Involved | Overhead | Secondary | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 1.1429 | 0.8 | 0.8 | 0.8 | EquipmentFailureInvolved¦Overhead¦Secondary¦BentorTwisted | Equipment Failure/Involved | Overhead | Secondary | Bent or Twisted | FNLYEAR 2018: 1; FNLYEAR 2019: 3; FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 8
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 1.28 | 1.28 | 4.5714 | 3.2 | 6.4 | 3.2 | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken | Equipment Failure/Involved | Overhead | Secondary | Broken | FNLYEAR 2024: 32 | 32
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 9.72 | 9.72 | 28.2857 | 24.3 | 29.6 | 24.3 | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken | Equipment Failure/Involved | Overhead | Secondary | Broken | 7 | 19 | 19 | 22 | 28 | 16 | 32 | 52 | 48 |  | 243
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground | Equipment Failure/Involved | Overhead | Secondary | Broken- wire on ground | FNLYEAR 2024: 4 | 4
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 2.36 | 2.36 | 5.1429 | 5.9 | 5 | 5.9 | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 5 | 7 | 11 | 3 | 8 | 6 | 9 | 7 | 3 |  | 59
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2015
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦Secondary¦Burnedflashed | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | FNLYEAR 2024: 4 | 4
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 1.68 | 1.68 | 1.5714 | 2.4 | 1.2 | 2.4 | EquipmentFailureInvolved¦Overhead¦Secondary¦Burnedflashed | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | 3 | 5 | 5 | 1 | 4 | 1 | 3 | 1 | 1 |  | 24
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen | Equipment Failure/Involved | Overhead | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.88 | 0.88 | 2 | 2.2 | 2.4 | 2.2 | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen | Equipment Failure/Involved | Overhead | Secondary | Burned Open | 2 | 2 | 4 | 2 |  | 2 | 6 | 3 | 1 |  | 22
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Secondary¦Contaminated | Equipment Failure/Involved | Overhead | Secondary | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Secondary¦Contaminated | Equipment Failure/Involved | Overhead | Secondary | Contaminated | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2021
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 1.75 | 1.75 | 3.5714 | 2.5 | 5 | 2.5 | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | FNLYEAR 2024: 25 | 25
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 4.76 | 4.76 | 7.8571 | 6.8 | 9.2 | 6.8 | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 4 | 4 | 5 | 4 | 5 | 7 | 12 | 10 | 17 |  | 68
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Secondary¦FailedFaulted | Equipment Failure/Involved | Overhead | Secondary | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2022
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.56 | 0.56 | 1.1429 | 0.8 | 1.6 | 0.8 | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal | Equipment Failure/Involved | Overhead | Secondary | Normal | FNLYEAR 2024: 8 | 8
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 2.03 | 2.03 | 3.7143 | 2.9 | 4.4 | 2.9 | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal | Equipment Failure/Involved | Overhead | Secondary | Normal | 2 |  | 1 | 3 | 1 | 1 | 5 | 13 | 3 |  | 29
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.28571 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦Overhead¦Secondary¦OnGround | Equipment Failure/Involved | Overhead | Secondary | On Ground | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2018; FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Secondary¦Together | Equipment Failure/Involved | Overhead | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 1.26 | 1.26 | 2.1429 | 1.8 | 2 | 1.8 | EquipmentFailureInvolved¦Overhead¦Secondary¦Together | Equipment Failure/Involved | Overhead | Secondary | Together | 1 | 1 | 1 | 3 | 2 | 3 | 5 | 2 |  |  | 18
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Broken | Equipment Failure/Involved | Overhead | Sectionalizer | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Burnedflashed | Equipment Failure/Involved | Overhead | Sectionalizer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Malfunctioning | Equipment Failure/Involved | Overhead | Sectionalizer | Malfunctioning | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Annealed | Equipment Failure/Involved | Overhead | Service conductor | Annealed | [10 empty] | 1 | bar: FNLYEAR 2019
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.57143 | 0.5 | 0.6 | 0.5 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Arcing | Equipment Failure/Involved | Overhead | Service conductor | Arcing | FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 5
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦BentorTwisted | Equipment Failure/Involved | Overhead | Service conductor | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦BentorTwisted | Equipment Failure/Involved | Overhead | Service conductor | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2019
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken | Equipment Failure/Involved | Overhead | Service conductor | Broken | FNLYEAR 2024: 5 | 5
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 1.8 | 1.8 | 5.7143 | 4.5 | 6.2 | 4.5 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken | Equipment Failure/Involved | Overhead | Service conductor | Broken |  |  | 5 | 3 | 6 | 5 | 14 | 5 | 7 |  | 45
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.6 | 0.6 | 1.4286 | 1.5 | 1.2 | 1.5 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonground | Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on ground |  | 1 | 4 | 2 | 2 |  | 4 |  | 2 |  | 15
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on object | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2020
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.57143 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Burnedflashed | Equipment Failure/Involved | Overhead | Service conductor | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2021; FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.32 | 0.32 | 1 | 0.8 | 1.2 | 0.8 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦BurnedOpen | Equipment Failure/Involved | Overhead | Service conductor | Burned Open |  |  | 1 | 1 |  | 2 | 2 | 1 | 1 |  | 8
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Contaminated | Equipment Failure/Involved | Overhead | Service conductor | Contaminated | FNLYEAR 2024: 2 | 2
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Deteriorated | Equipment Failure/Involved | Overhead | Service conductor | Deteriorated | FNLYEAR 2024: 5 | 5
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 1.4 | 1.4 | 2.7143 | 2 | 3.2 | 2 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Deteriorated | Equipment Failure/Involved | Overhead | Service conductor | Deteriorated |  |  | 1 | 1 | 2 | 1 | 5 | 3 | 7 |  | 20
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦FailedFaulted | Equipment Failure/Involved | Overhead | Service conductor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦FailedFaulted | Equipment Failure/Involved | Overhead | Service conductor | Failed/Faulted | FNLYEAR 2023: 2 | 2
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 0.85714 | 0.7 | 0.6 | 0.7 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Normal | Equipment Failure/Involved | Overhead | Service conductor | Normal | FNLYEAR 2016: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 7
Secondary Conductor | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦OnGround | Equipment Failure/Involved | Overhead | Service conductor | On Ground | FNLYEAR 2021: 2 | 2
Secondary Conductor | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Together | Equipment Failure/Involved | Overhead | Service conductor | Together | FNLYEAR 2023: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Stepdown¦Arcing | Equipment Failure/Involved | Overhead | Stepdown | Arcing | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Stepdown¦Broken | Equipment Failure/Involved | Overhead | Stepdown | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Overhead¦Stepdown¦Burnedflashed | Equipment Failure/Involved | Overhead | Stepdown | Burned/flashed | [10 empty] | 3 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Stepdown¦Deteriorated | Equipment Failure/Involved | Overhead | Stepdown | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.7 | 0.2 | 0.7 | EquipmentFailureInvolved¦Overhead¦Stepdown¦FailedFaulted | Equipment Failure/Involved | Overhead | Stepdown | Failed/Faulted | FNLYEAR 2016: 2; FNLYEAR 2018: 3; FNLYEAR 2019: 1; FNLYEAR 2020: 1 | 7
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Stepdown¦Normal | Equipment Failure/Involved | Overhead | Stepdown | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦StreetLightEquipment¦Broken | Equipment Failure/Involved | Overhead | Street Light Equipment | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦StreetLightEquipment¦Broken | Equipment Failure/Involved | Overhead | Street Light Equipment | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦StreetLightEquipment¦Malfunctioning | Equipment Failure/Involved | Overhead | Street Light Equipment | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦StreetLightEquipment¦OnGround | Equipment Failure/Involved | Overhead | Street Light Equipment | On Ground | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Arcing | Equipment Failure/Involved | Overhead | Switch (OH) | Arcing | FNLYEAR 2024: 2 | 2
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Arcing | Equipment Failure/Involved | Overhead | Switch (OH) | Arcing | FNLYEAR 2018: 3; FNLYEAR 2022: 1 | 4
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Broken | Equipment Failure/Involved | Overhead | Switch (OH) | Broken | FNLYEAR 2024: 5 | 5
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 1.71 | 1.71 | 2.1429 | 1.9 | 2.4 | 1.9 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Broken | Equipment Failure/Involved | Overhead | Switch (OH) | Broken |  | 2 | 2 | 3 |  | 4 | 3 |  | 5 |  | 19
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Burnedflashed | Equipment Failure/Involved | Overhead | Switch (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.28571 | 0.6 | 0.4 | 0.6 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Burnedflashed | Equipment Failure/Involved | Overhead | Switch (OH) | Burned/flashed | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2017: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 6
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦FailedFaulted | Equipment Failure/Involved | Overhead | Switch (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦FailedFaulted | Equipment Failure/Involved | Overhead | Switch (OH) | Failed/Faulted | FNLYEAR 2021: 3; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 5
Equipment (Switch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Leaking | Equipment Failure/Involved | Overhead | Switch (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Normal | Equipment Failure/Involved | Overhead | Switch (OH) | Normal | FNLYEAR 2024: 2 | 2
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.42857 | 0.4 | 0.6 | 0.4 | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Normal | Equipment Failure/Involved | Overhead | Switch (OH) | Normal | [10 empty] | 4 | bar: FNLYEAR 2017; FNLYEAR 2021 to FNLYEAR 2023
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Switch¦Arcing | Equipment Failure/Involved | Overhead | Switch | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Switch¦Broken | Equipment Failure/Involved | Overhead | Switch | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Switch¦Broken | Equipment Failure/Involved | Overhead | Switch | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Overhead¦Switch¦FailedFaulted | Equipment Failure/Involved | Overhead | Switch | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2019
Equipment (Switch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Switch¦Normal | Equipment Failure/Involved | Overhead | Switch | Normal | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦ | Equipment Failure/Involved | Overhead | Transformer (OH) |  | FNLYEAR 2024: 3 | 3
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦ | Equipment Failure/Involved | Overhead | Transformer (OH) |  | FNLYEAR 2016: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 4; FNLYEAR 2023: 3 | 9
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | FNLYEAR 2024: 3 | 3
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 2.24 | 2.24 | 3.7143 | 3.2 | 3.8 | 3.2 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | 1 | 3 | 2 | 1 | 6 | 2 | 7 | 5 | 5 |  | 32
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 5.04 | 5.04 | 10.2857 | 7.2 | 14.4 | 7.2 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | FNLYEAR 2024: 72 | 72
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 51.59 | 51.59 | 78 | 73.7 | 81.2 | 73.7 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 43 | 60 | 88 | 53 | 87 | 74 | 150 | 120 | 62 |  | 737
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Brokenwireonground | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.71429 | 0.7 | 0.8 | 0.7 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Brokenwireonground | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken, wire on ground |  | 2 |  | 1 |  | 1 | 1 | 1 | 1 |  | 7
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.49 | 0.49 | 1 | 0.7 | 1.4 | 0.7 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | FNLYEAR 2024: 7 | 7
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 5.74 | 5.74 | 9.2857 | 8.2 | 11.2 | 8.2 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 8 | 4 | 5 | 1 | 8 | 10 | 16 | 16 | 14 |  | 82
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.12 | 1.12 | 2.2857 | 1.6 | 3.2 | 1.6 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | FNLYEAR 2024: 16 | 16
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 11.69 | 11.69 | 16.1429 | 16.7 | 17 | 16.7 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 25 | 18 | 11 | 5 | 23 | 23 | 25 | 25 | 12 |  | 167
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 17.85 | 17.85 | 36.4286 | 25.5 | 51 | 25.5 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 255 | 255
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 155.89 | 155.89 | 262.7143 | 222.7 | 309.2 | 222.7 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 95 | 139 | 154 | 116 | 177 | 288 | 527 | 414 | 317 |  | 2227
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 3.99 | 3.99 | 8.1429 | 5.7 | 11.4 | 5.7 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | FNLYEAR 2024: 57 | 57
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 23.66 | 23.66 | 39.2857 | 33.8 | 46.8 | 33.8 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 25 | 14 | 24 | 20 | 21 | 51 | 74 | 72 | 37 |  | 338
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.98 | 0.98 | 2 | 1.4 | 2.8 | 1.4 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | FNLYEAR 2024: 14 | 14
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 7.63 | 7.63 | 11.8571 | 10.9 | 13.2 | 10.9 | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 9 | 6 | 11 | 7 | 10 | 13 | 26 | 17 | 10 |  | 109
Equipment (Transformer) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Overhead¦Transformer¦ | Equipment Failure/Involved | Overhead | Transformer |  | 1 | 5 | 3 | 1 | 4 | 1 |  |  |  |  | 15
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦Transformer¦Arcing | Equipment Failure/Involved | Overhead | Transformer | Arcing | FNLYEAR 2024: 6 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.68 | 1.68 | 2.4286 | 2.4 | 1.6 | 2.4 | EquipmentFailureInvolved¦Overhead¦Transformer¦Arcing | Equipment Failure/Involved | Overhead | Transformer | Arcing | 2 | 3 | 2 | 4 | 5 | 3 | 1 | 4 |  |  | 24
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Transformer¦BentorTwisted | Equipment Failure/Involved | Overhead | Transformer | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Overhead¦Transformer¦BentorTwisted | Equipment Failure/Involved | Overhead | Transformer | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.98 | 0.98 | 2 | 1.4 | 2.8 | 1.4 | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken | Equipment Failure/Involved | Overhead | Transformer | Broken | FNLYEAR 2024: 14 | 14
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 15.54 | 15.54 | 24.2857 | 22.2 | 24 | 22.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken | Equipment Failure/Involved | Overhead | Transformer | Broken | 9 | 12 | 31 | 15 | 35 | 27 | 44 | 29 | 20 |  | 222
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground | Equipment Failure/Involved | Overhead | Transformer | Broken- wire on ground | FNLYEAR 2024: 4 | 4
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 1.36 | 1.36 | 3.5714 | 3.4 | 3.6 | 3.4 | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground | Equipment Failure/Involved | Overhead | Transformer | Broken, wire on ground |  | 4 | 5 | 2 | 5 | 3 | 5 | 4 | 6 |  | 34
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Transformer | Broken, wire on object | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | FNLYEAR 2024: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 4.34 | 4.34 | 4.7143 | 6.2 | 2.8 | 6.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 11 | 10 | 8 | 4 | 15 | 2 | 5 | 5 | 2 |  | 62
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Transformer¦BurnedOpen | Equipment Failure/Involved | Overhead | Transformer | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.26 | 1.26 | 1.8571 | 1.8 | 2.2 | 1.8 | EquipmentFailureInvolved¦Overhead¦Transformer¦BurnedOpen | Equipment Failure/Involved | Overhead | Transformer | Burned Open | 2 | 1 | 2 | 1 | 1 | 2 | 6 | 2 | 1 |  | 18
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Transformer¦Contaminated | Equipment Failure/Involved | Overhead | Transformer | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.28571 | 0.4 | 0 | 0.4 | EquipmentFailureInvolved¦Overhead¦Transformer¦Contaminated | Equipment Failure/Involved | Overhead | Transformer | Contaminated | FNLYEAR 2017: 2; FNLYEAR 2018: 2 | 4
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | FNLYEAR 2024: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 6.93 | 6.93 | 5.7143 | 9.9 | 3.2 | 9.9 | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 16 | 20 | 23 | 11 | 13 | 6 | 7 | 2 | 1 |  | 99
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 3.57 | 3.57 | 7.2857 | 5.1 | 10.2 | 5.1 | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | FNLYEAR 2024: 51 | 51
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 160.86 | 160.86 | 188 | 229.8 | 115 | 229.8 | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 192 | 309 | 481 | 293 | 448 | 320 | 106 | 65 | 84 |  | 2298
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking | Equipment Failure/Involved | Overhead | Transformer | Leaking | FNLYEAR 2024: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 5.11 | 5.11 | 6.5714 | 7.3 | 4.2 | 7.3 | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking | Equipment Failure/Involved | Overhead | Transformer | Leaking | 4 | 8 | 15 | 9 | 16 | 8 | 5 | 3 | 5 |  | 73
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.82 | 1.82 | 3.4286 | 2.6 | 3.8 | 2.6 | EquipmentFailureInvolved¦Overhead¦Transformer¦Malfunctioning | Equipment Failure/Involved | Overhead | Transformer | Malfunctioning | 1 |  | 1 | 3 | 2 | 5 | 7 | 4 | 3 |  | 26
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.85714 | 0.6 | 1.2 | 0.6 | EquipmentFailureInvolved¦Overhead¦Transformer¦Normal | Equipment Failure/Involved | Overhead | Transformer | Normal | FNLYEAR 2024: 6 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 1.4 | 1.4 | 2.7143 | 2 | 3.6 | 2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Normal | Equipment Failure/Involved | Overhead | Transformer | Normal |  |  | 1 |  | 1 | 4 | 6 | 6 | 2 |  | 20
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Transformer¦OnGround | Equipment Failure/Involved | Overhead | Transformer | On Ground | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦OnGround | Equipment Failure/Involved | Overhead | Transformer | On Ground | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Transformer¦Together | Equipment Failure/Involved | Overhead | Transformer | Together | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken | Equipment Failure/Involved | Overhead | Woodpin | Broken | FNLYEAR 2024: 4 | 4
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 6.21 | 6.21 | 8.2857 | 6.9 | 5.2 | 6.9 | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2 | 3 | 6 | 5 | 27 | 3 | 6 | 8 | 9 |  | 69
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Overhead¦Woodpin¦Brokenwireonground | Equipment Failure/Involved | Overhead | Woodpin | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Overhead¦Woodpin¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Woodpin | Broken- wire on object | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.14286 | 0.4 | 0 | 0.4 | EquipmentFailureInvolved¦Overhead¦Woodpin¦Brokenwireonobject | Equipment Failure/Involved | Overhead | Woodpin | Broken, wire on object | FNLYEAR 2016: 1; FNLYEAR 2017: 2; FNLYEAR 2019: 1 | 4
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Overhead¦Woodpin¦Normal | Equipment Failure/Involved | Overhead | Woodpin | Normal | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Equipment (Support Structure) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Rockmudslide¦PoleWood¦Brokenwireonground | Equipment Failure/Involved | Rock/mud slide | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Substation¦Bus¦Normal | Equipment Failure/Involved | Substation | Bus | Normal | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦Bushing¦Burnedflashed | Equipment Failure/Involved | Substation | Bushing | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦Bushing¦Deteriorated | Equipment Failure/Involved | Substation | Bushing | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Substation¦Bushing¦FailedFaulted | Equipment Failure/Involved | Substation | Bushing | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2015 to FNLYEAR 2016
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Broken | Equipment Failure/Involved | Substation | Circuit Breaker | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.5 | 0.6 | 0.5 | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦FailedFaulted | Equipment Failure/Involved | Substation | Circuit Breaker | Failed/Faulted | FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2022: 3 | 5
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Malfunctioning | Equipment Failure/Involved | Substation | Circuit Breaker | Malfunctioning | FNLYEAR 2024: 2 | 2
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.4286 | 1.1 | 1.2 | 1.1 | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Malfunctioning | Equipment Failure/Involved | Substation | Circuit Breaker | Malfunctioning | FNLYEAR 2015: 1; FNLYEAR 2019: 4; FNLYEAR 2020: 1; FNLYEAR 2021: 5 | 11
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Normal | Equipment Failure/Involved | Substation | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦ConductorUnderground¦Broken | Equipment Failure/Involved | Substation | Conductor, Underground | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Substation¦ControlCircuitWiring¦Broken | Equipment Failure/Involved | Substation | Control Circuit/Wiring | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Substation¦CT¦Broken | Equipment Failure/Involved | Substation | CT | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Substation¦Generator¦Burnedflashed | Equipment Failure/Involved | Substation | Generator | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Substation¦Generator¦FailedFaulted | Equipment Failure/Involved | Substation | Generator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Substation¦Generator¦Malfunctioning | Equipment Failure/Involved | Substation | Generator | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦Substation¦Generator¦Malfunctioning | Equipment Failure/Involved | Substation | Generator | Malfunctioning | FNLYEAR 2016: 1; FNLYEAR 2022: 2 | 3
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Substation¦Insulator¦Broken | Equipment Failure/Involved | Substation | Insulator | Broken | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦Insulator¦FailedFaulted | Equipment Failure/Involved | Substation | Insulator | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Substation¦LightningArrestor¦FailedFaulted | Equipment Failure/Involved | Substation | Lightning Arrestor | Failed/Faulted | FNLYEAR 2022: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦Arcing | Equipment Failure/Involved | Substation | Other | Arcing | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦BentorTwisted | Equipment Failure/Involved | Substation | Other | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦Broken | Equipment Failure/Involved | Substation | Other | Broken | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2019; FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦Burnedflashed | Equipment Failure/Involved | Substation | Other | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦FailedFaulted | Equipment Failure/Involved | Substation | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦FailedFaulted | Equipment Failure/Involved | Substation | Other | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2022
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦Leaking | Equipment Failure/Involved | Substation | Other | Leaking | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦Malfunctioning | Equipment Failure/Involved | Substation | Other | Malfunctioning | [10 empty] | 3 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦Other¦Normal | Equipment Failure/Involved | Substation | Other | Normal | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Substation¦PTCCVT¦Burnedflashed | Equipment Failure/Involved | Substation | PT/CCVT | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Substation¦PTCCVT¦FailedFaulted | Equipment Failure/Involved | Substation | PT/CCVT | Failed/Faulted | FNLYEAR 2019: 2 | 2
Equipment (Voltage Control) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0 | 0.3 | EquipmentFailureInvolved¦Substation¦RegulatorLTCsubstation¦FailedFaulted | Equipment Failure/Involved | Substation | Regulator, LTC substation | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2018 to FNLYEAR 2019
Equipment (Voltage Control) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Substation¦RegulatorLTCsubstation¦Malfunctioning | Equipment Failure/Involved | Substation | Regulator- LTC substation | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦Relay¦FailedFaulted | Equipment Failure/Involved | Substation | Relay | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.8 | 0.4 | 0.8 | EquipmentFailureInvolved¦Substation¦Relay¦Malfunctioning | Equipment Failure/Involved | Substation | Relay | Malfunctioning | FNLYEAR 2016: 2; FNLYEAR 2018: 3; FNLYEAR 2019: 1; FNLYEAR 2023: 2 | 8
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Substation¦Relay¦Normal | Equipment Failure/Involved | Substation | Relay | Normal | [10 empty] | 3 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2022
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦Secondary¦Broken | Equipment Failure/Involved | Substation | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.4 | 0 | 0.4 | EquipmentFailureInvolved¦Substation¦Switch¦Broken | Equipment Failure/Involved | Substation | Switch | Broken | FNLYEAR 2015: 1; FNLYEAR 2017: 3 | 4
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.4 | 0.3 | EquipmentFailureInvolved¦Substation¦Switch¦FailedFaulted | Equipment Failure/Involved | Substation | Switch | Failed/Faulted | FNLYEAR 2017: 1; FNLYEAR 2020: 2 | 3
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦Transformer¦Broken | Equipment Failure/Involved | Substation | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Substation¦Transformer¦FailedFaulted | Equipment Failure/Involved | Substation | Transformer | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2015; FNLYEAR 2017; FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Substation¦TransformerPower¦Burnedflashed | Equipment Failure/Involved | Substation | Transformer Power | Burned/flashed | FNLYEAR 2016: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Substation¦TransformerPower¦FailedFaulted | Equipment Failure/Involved | Substation | Transformer Power | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Substation¦TransformerPower¦Malfunctioning | Equipment Failure/Involved | Substation | Transformer Power | Malfunctioning | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2018
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦¦Malfunctioning | Equipment Failure/Involved | Underground |  | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Bus¦Burnedflashed | Equipment Failure/Involved | Underground | Bus | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Bus¦Contaminated | Equipment Failure/Involved | Underground | Bus | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Bus¦Deteriorated | Equipment Failure/Involved | Underground | Bus | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.2 | 0 | 0.2 | EquipmentFailureInvolved¦Underground¦Bus¦FailedFaulted | Equipment Failure/Involved | Underground | Bus | Failed/Faulted | FNLYEAR 2015: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Bushing¦Arcing | Equipment Failure/Involved | Underground | Bushing | Arcing | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.4 | 0.6 | 0.4 | EquipmentFailureInvolved¦Underground¦Bushing¦Broken | Equipment Failure/Involved | Underground | Bushing | Broken | FNLYEAR 2016: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1 | 4
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Underground¦Bushing¦Burnedflashed | Equipment Failure/Involved | Underground | Bushing | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2018; FNLYEAR 2021; FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Bushing¦FailedFaulted | Equipment Failure/Involved | Underground | Bushing | Failed/Faulted | FNLYEAR 2024: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦Broken | Equipment Failure/Involved | Underground | Cable Termination(live front) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦Burnedflashed | Equipment Failure/Involved | Underground | Cable Termination(live front) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦Contaminated | Equipment Failure/Involved | Underground | Cable Termination(live front) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦FailedFaulted | Equipment Failure/Involved | Underground | Cable Termination(live front) | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦CableTermination(livefront¦Broken | Equipment Failure/Involved | Underground | Cable Termination(live front | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.2857 | 1.6 | 3.2 | 1.6 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken | Equipment Failure/Involved | Underground | Conductor- Underground | Broken | FNLYEAR 2024: 16 | 16
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 21.4286 | 20.7 | 18.2 | 20.7 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 10 | 19 | 28 | 32 | 27 | 20 | 28 | 23 | 20 |  | 207
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.1 | 2.2 | 1.1 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed | Equipment Failure/Involved | Underground | Conductor- Underground | Burned/flashed | FNLYEAR 2024: 11 | 11
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 8.5714 | 9.6 | 7.6 | 9.6 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 12 | 12 | 12 | 11 | 11 | 9 | 10 | 12 | 7 |  | 96
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated | Equipment Failure/Involved | Underground | Conductor- Underground | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 6.2857 | 6.2 | 6.2 | 6.2 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 7 | 3 | 8 | 7 | 6 | 9 | 4 | 10 | 8 |  | 62
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦FailedFaulted | Equipment Failure/Involved | Underground | Conductor, Underground | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Normal | Equipment Failure/Involved | Underground | Conductor- Underground | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.7 | 1 | 0.7 | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Normal | Equipment Failure/Involved | Underground | Conductor, Underground | Normal | FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2021: 4; FNLYEAR 2023: 1 | 7
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(OH)¦Arcing | Equipment Failure/Involved | Underground | Connector or Splice (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(OH)¦Burnedflashed | Equipment Failure/Involved | Underground | Connector or Splice (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Broken | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Broken | FNLYEAR 2024: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.9 | 0.6 | 0.9 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Broken | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Broken | 1 | 1 | 2 | 2 |  |  | 1 | 1 | 1 |  | 9
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Burnedflashed | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Burned/flashed | FNLYEAR 2024: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.4286 | 1.1 | 1.8 | 1.1 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Burnedflashed | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Burned/flashed |  |  | 1 |  | 1 | 2 | 2 | 2 | 3 |  | 11
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Contaminated | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2017
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Deteriorated | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.6 | 0.2 | 0.6 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Deteriorated | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Deteriorated | FNLYEAR 2015: 3; FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2022: 1 | 6
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦FailedFaulted | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Failed/Faulted | FNLYEAR 2024: 4 | 4
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 3.2857 | 4 | 1.2 | 4 | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦FailedFaulted | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Failed/Faulted | 3 | 8 | 6 | 7 | 10 | 1 | 2 |  | 3 |  | 40
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦Burnedflashed | Equipment Failure/Involved | Underground | Customer Equipment | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦FailedFaulted | Equipment Failure/Involved | Underground | Customer Equipment | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦Malfunctioning | Equipment Failure/Involved | Underground | Customer Equipment | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦Normal | Equipment Failure/Involved | Underground | Customer Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 0.9 | 1.4 | 0.9 | EquipmentFailureInvolved¦Underground¦Elbow¦Broken | Equipment Failure/Involved | Underground | Elbow | Broken |  |  | 1 |  | 1 | 1 | 2 | 2 | 2 |  | 9
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Elbow¦Burnedflashed | Equipment Failure/Involved | Underground | Elbow | Burned/flashed | FNLYEAR 2024: 2 | 2
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.2857 | 2.4 | 2.6 | 2.4 | EquipmentFailureInvolved¦Underground¦Elbow¦Burnedflashed | Equipment Failure/Involved | Underground | Elbow | Burned/flashed | 1 | 3 | 4 | 1 | 2 | 2 | 2 | 5 | 4 |  | 24
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Underground¦Elbow¦Deteriorated | Equipment Failure/Involved | Underground | Elbow | Deteriorated | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2020
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.5 | 1 | 0.5 | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | FNLYEAR 2024: 5 | 5
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 3.4286 | 3.9 | 2.6 | 3.9 | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | 3 | 5 | 7 | 4 | 7 | 3 | 2 | 2 | 6 |  | 39
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Elbow¦Normal | Equipment Failure/Involved | Underground | Elbow | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.3 | 0.2 | 0.3 | EquipmentFailureInvolved¦Underground¦Elbow¦Normal | Equipment Failure/Involved | Underground | Elbow | Normal | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2019; FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Fuse¦Arcing | Equipment Failure/Involved | Underground | Fuse | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Underground¦Fuse¦Broken | Equipment Failure/Involved | Underground | Fuse | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Fuse¦BurnedOpen | Equipment Failure/Involved | Underground | Fuse | Burned Open | FNLYEAR 2024: 2 | 2
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Fuse¦BurnedOpen | Equipment Failure/Involved | Underground | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Fuse¦FailedFaulted | Equipment Failure/Involved | Underground | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Fuse) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.5 | 0.2 | 0.5 | EquipmentFailureInvolved¦Underground¦Fuse¦FailedFaulted | Equipment Failure/Involved | Underground | Fuse | Failed/Faulted | FNLYEAR 2017: 1; FNLYEAR 2019: 3; FNLYEAR 2022: 1 | 5
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦MeteringEquipment¦Broken | Equipment Failure/Involved | Underground | Metering Equipment | Broken | FNLYEAR 2021: 2 | 2
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦Broken | Equipment Failure/Involved | Underground | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦Broken | Equipment Failure/Involved | Underground | Other | Broken | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2022 to FNLYEAR 2023
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦Burnedflashed | Equipment Failure/Involved | Underground | Other | Burned/flashed | FNLYEAR 2016: 2 | 2
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Other¦Contaminated | Equipment Failure/Involved | Underground | Other | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Other¦Deteriorated | Equipment Failure/Involved | Underground | Other | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦FailedFaulted | Equipment Failure/Involved | Underground | Other | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2021 to FNLYEAR 2022
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦Leaking | Equipment Failure/Involved | Underground | Other | Leaking | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦Malfunctioning | Equipment Failure/Involved | Underground | Other | Malfunctioning | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦Normal | Equipment Failure/Involved | Underground | Other | Normal | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Primary Conductor - Line Slap | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | EquipmentFailureInvolved¦Underground¦Other¦Together | Equipment Failure/Involved | Underground | Other | Together | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦PotheadRiserTermination¦Broken | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦PotheadRiserTermination¦Broken | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦PotheadRiserTermination¦FailedFaulted | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Recloser¦Burnedflashed | Equipment Failure/Involved | Underground | Recloser | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Secondary¦Arcing | Equipment Failure/Involved | Underground | Secondary | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.2 | 0.2 | 0.2 | EquipmentFailureInvolved¦Underground¦Secondary¦Arcing | Equipment Failure/Involved | Underground | Secondary | Arcing | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.1 | 2.2 | 1.1 | EquipmentFailureInvolved¦Underground¦Secondary¦Broken | Equipment Failure/Involved | Underground | Secondary | Broken | FNLYEAR 2024: 11 | 11
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 5.5714 | 4.4 | 5.6 | 4.4 | EquipmentFailureInvolved¦Underground¦Secondary¦Broken | Equipment Failure/Involved | Underground | Secondary | Broken | 1 | 2 | 2 | 5 | 6 | 4 | 5 | 10 | 9 |  | 44
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.4286 | 1.3 | 1.6 | 1.3 | EquipmentFailureInvolved¦Underground¦Secondary¦Burnedflashed | Equipment Failure/Involved | Underground | Secondary | Burned/flashed | 1 | 1 | 1 |  | 2 | 2 | 2 | 2 | 2 |  | 13
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Secondary¦BurnedOpen | Equipment Failure/Involved | Underground | Secondary | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.9 | 0.6 | 0.9 | EquipmentFailureInvolved¦Underground¦Secondary¦BurnedOpen | Equipment Failure/Involved | Underground | Secondary | Burned Open |  | 2 | 1 | 2 | 1 |  | 2 | 1 |  |  | 9
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Secondary¦Contaminated | Equipment Failure/Involved | Underground | Secondary | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2017
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | EquipmentFailureInvolved¦Underground¦Secondary¦Deteriorated | Equipment Failure/Involved | Underground | Secondary | Deteriorated | FNLYEAR 2024: 4 | 4
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2 | 2.4 | 2 | 2.4 | EquipmentFailureInvolved¦Underground¦Secondary¦Deteriorated | Equipment Failure/Involved | Underground | Secondary | Deteriorated | 2 | 3 | 5 | 4 |  | 1 | 1 | 5 | 3 |  | 24
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦Underground¦Secondary¦Normal | Equipment Failure/Involved | Underground | Secondary | Normal | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019; FNLYEAR 2023
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Secondary¦Together | Equipment Failure/Involved | Underground | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2021
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Arcing | Equipment Failure/Involved | Underground | Service conductor | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Broken | Equipment Failure/Involved | Underground | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1 | 0.7 | 1.2 | 0.7 | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Broken | Equipment Failure/Involved | Underground | Service conductor | Broken | FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 7
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Serviceconductor¦BurnedOpen | Equipment Failure/Involved | Underground | Service conductor | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.7 | 0.8 | 0.7 | EquipmentFailureInvolved¦Underground¦Serviceconductor¦BurnedOpen | Equipment Failure/Involved | Underground | Service conductor | Burned Open |  |  | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 7
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Deteriorated | Equipment Failure/Involved | Underground | Service conductor | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Secondary Conductor | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Deteriorated | Equipment Failure/Involved | Underground | Service conductor | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Primary Conductor - Other | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Splicebox¦FailedFaulted | Equipment Failure/Involved | Underground | Splice box | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Stepdown¦Broken | Equipment Failure/Involved | Underground | Stepdown | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.4 | 0.4 | 0.4 | EquipmentFailureInvolved¦Underground¦Stepdown¦FailedFaulted | Equipment Failure/Involved | Underground | Stepdown | Failed/Faulted | FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2020: 2 | 4
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Broken | Equipment Failure/Involved | Underground | Switch (UG) | Broken | FNLYEAR 2024: 2 | 2
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.7 | 0.6 | 0.7 | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Broken | Equipment Failure/Involved | Underground | Switch (UG) | Broken | FNLYEAR 2016: 1; FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 7
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Burnedflashed | Equipment Failure/Involved | Underground | Switch (UG) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Switch(UG)¦FailedFaulted | Equipment Failure/Involved | Underground | Switch (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.6 | 0.8 | 0.6 | EquipmentFailureInvolved¦Underground¦Switch(UG)¦FailedFaulted | Equipment Failure/Involved | Underground | Switch (UG) | Failed/Faulted | FNLYEAR 2018: 2; FNLYEAR 2021: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 6
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Leaking | Equipment Failure/Involved | Underground | Switch (UG) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Switch¦Arcing | Equipment Failure/Involved | Underground | Switch | Arcing | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Switch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Switch¦Burnedflashed | Equipment Failure/Involved | Underground | Switch | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Transformer(OH)¦Burnedflashed | Equipment Failure/Involved | Underground | Transformer (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Transformer(OH)¦Deteriorated | Equipment Failure/Involved | Underground | Transformer (OH) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Transformer(OH)¦FailedFaulted | Equipment Failure/Involved | Underground | Transformer (OH) | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.5 | 0.4 | 0.5 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Arcing | Equipment Failure/Involved | Underground | Transformer (UG) | Arcing | FNLYEAR 2015: 2; FNLYEAR 2017: 1; FNLYEAR 2021: 1; FNLYEAR 2023: 1 | 5
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.1429 | 0.8 | 1.6 | 0.8 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | FNLYEAR 2024: 8 | 8
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 7 | 8.2 | 7.6 | 8.2 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 4 | 9 | 20 | 8 | 3 | 10 | 10 | 13 | 5 |  | 82
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.85714 | 0.7 | 1 | 0.7 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Burnedflashed | Equipment Failure/Involved | Underground | Transformer (UG) | Burned/flashed | FNLYEAR 2017: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 2; FNLYEAR 2022: 3 | 7
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Contaminated | Equipment Failure/Involved | Underground | Transformer (UG) | Contaminated | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Deteriorated | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | FNLYEAR 2024: 3 | 3
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.7143 | 2.6 | 3.6 | 2.6 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Deteriorated | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | 5 | 1 | 1 |  | 1 | 7 | 6 | 4 | 1 |  | 26
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 3.2857 | 2.3 | 4.6 | 2.3 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | FNLYEAR 2024: 23 | 23
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 21.1429 | 19 | 21.4 | 19 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 11 | 8 | 23 | 19 | 22 | 33 | 21 | 27 | 26 |  | 190
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.4286 | 1.7 | 3.4 | 1.7 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | FNLYEAR 2024: 17 | 17
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 11.4286 | 11 | 12.8 | 11 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 7 | 8 | 15 | 10 | 6 | 13 | 15 | 17 | 19 |  | 110
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Normal | Equipment Failure/Involved | Underground | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1 | 0.9 | 1 | 0.9 | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Normal | Equipment Failure/Involved | Underground | Transformer (UG) | Normal |  |  | 2 | 1 | 1 | 1 | 1 | 3 |  |  | 9
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | EquipmentFailureInvolved¦Underground¦Transformer¦Arcing | Equipment Failure/Involved | Underground | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | EquipmentFailureInvolved¦Underground¦Transformer¦Broken | Equipment Failure/Involved | Underground | Transformer | Broken | FNLYEAR 2024: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 1.5714 | 1.9 | 1.4 | 1.9 | EquipmentFailureInvolved¦Underground¦Transformer¦Broken | Equipment Failure/Involved | Underground | Transformer | Broken | 3 | 5 |  | 3 | 1 | 2 | 3 | 1 | 1 |  | 19
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.6 | 0.4 | EquipmentFailureInvolved¦Underground¦Transformer¦Burnedflashed | Equipment Failure/Involved | Underground | Transformer | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2019 to FNLYEAR 2021; FNLYEAR 2023
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Transformer¦BurnedOpen | Equipment Failure/Involved | Underground | Transformer | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.6 | 0 | 0.6 | EquipmentFailureInvolved¦Underground¦Transformer¦Deteriorated | Equipment Failure/Involved | Underground | Transformer | Deteriorated | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2017: 3; FNLYEAR 2018: 1 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.8571 | 5.1 | 1 | 5.1 | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 5 | 8 | 18 | 4 | 11 | 2 | 1 | 1 | 1 |  | 51
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.4 | 0.2 | 0.4 | EquipmentFailureInvolved¦Underground¦Transformer¦Leaking | Equipment Failure/Involved | Underground | Transformer | Leaking | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019 to FNLYEAR 2020
Equipment (Transformer) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | EquipmentFailureInvolved¦Underground¦Transformer¦Normal | Equipment Failure/Involved | Underground | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolfoundnothing¦¦ | Unknown Cause | Patrol - found nothing |  |  | FNLYEAR 2024: 1471 | 1471
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolfoundnothing¦¦ | Unknown Cause | Patrol - found nothing |  |  | 902 | 1282 | 1920 | 1477 | 2290 | 1763 | 2343 | 1735 | 1753 |  | 15465
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolfoundnothing¦¦Broken | Unknown Cause | Patrol - found nothing |  | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolfoundnothing¦¦BurnedOpen | Unknown Cause | Patrol - found nothing |  | Burned Open | FNLYEAR 2015: 1; FNLYEAR 2016: 3 | 4
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | FNLYEAR 2015: 20; FNLYEAR 2016: 23; FNLYEAR 2017: 10; FNLYEAR 2019: 2 | 55
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolfoundnothing¦¦Normal | Unknown Cause | Patrol - found nothing |  | Normal | FNLYEAR 2015: 2; FNLYEAR 2016: 2 | 4
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦ConductorOverhead¦BentorTwisted | Unknown Cause | Patrol - found nothing | Conductor, Overhead | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2016
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦ConductorOverhead¦Broken | Unknown Cause | Patrol - found nothing | Conductor, Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.14286 | 0.3 | 0.2 | 0.3 | UnknownCause¦Patrolfoundnothing¦ConductorOverhead¦Normal | Unknown Cause | Patrol - found nothing | Conductor, Overhead | Normal | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2022
Equipment (Support Structure) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦CrossarmWood¦Broken | Unknown Cause | Patrol - found nothing | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦Cutoutfuseholder¦FailedFaulted | Unknown Cause | Patrol - found nothing | Cutout, fuse holder | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | UnknownCause¦Patrolfoundnothing¦Fuse¦Broken | Unknown Cause | Patrol - found nothing | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | UnknownCause¦Patrolfoundnothing¦Fuse¦FailedFaulted | Unknown Cause | Patrol - found nothing | Fuse | Failed/Faulted | FNLYEAR 2024: 4 | 4
Equipment (Fuse) | None | 0% | 0 | 0 | Very High | 90% | 0.72 | 0.72 | 1.1429 | 0.8 | 1.6 | 0.8 | UnknownCause¦Patrolfoundnothing¦Fuse¦FailedFaulted | Unknown Cause | Patrol - found nothing | Fuse | Failed/Faulted | FNLYEAR 2022: 2; FNLYEAR 2023: 6 | 8
Equipment (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦Insulator¦Broken | Unknown Cause | Patrol - found nothing | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolfoundnothing¦Other¦Broken | Unknown Cause | Patrol - found nothing | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦PoleWood¦Burnedflashed | Unknown Cause | Patrol - found nothing | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Equipment (DPD) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦Recloser¦Malfunctioning | Unknown Cause | Patrol - found nothing | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (DPD) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | UnknownCause¦Patrolfoundnothing¦Recloser¦Normal | Unknown Cause | Patrol - found nothing | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (DPD) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦Sectionalizer¦Normal | Unknown Cause | Patrol - found nothing | Sectionalizer | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | UnknownCause¦Patrolfoundnothing¦Transformer(OH)¦FailedFaulted | Unknown Cause | Patrol - found nothing | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2022
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦Transformer¦Broken | Unknown Cause | Patrol - found nothing | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolfoundnothing¦Transformer¦Burnedflashed | Unknown Cause | Patrol - found nothing | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0 | 0.6 | 0 | 0.6 | UnknownCause¦Patrolfoundnothing¦Transformer¦FailedFaulted | Unknown Cause | Patrol - found nothing | Transformer | Failed/Faulted | FNLYEAR 2015: 4; FNLYEAR 2016: 2 | 6
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | UnknownCause¦Patrolfoundnothing¦Transformer¦Normal | Unknown Cause | Patrol - found nothing | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolnotconducted¦¦ | Unknown Cause | Patrol - not conducted |  |  | FNLYEAR 2024: 195 | 195
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolnotconducted¦¦ | Unknown Cause | Patrol - not conducted |  |  | 173 | 260 | 385 | 217 | 430 | 226 | 325 | 219 | 297 |  | 2532
Equipment (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | UnknownCause¦Patrolnotconducted¦¦FailedFaulted | Unknown Cause | Patrol - not conducted |  | Failed/Faulted | FNLYEAR 2015: 3; FNLYEAR 2016: 6 | 9
Equipment (DPD) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolnotconducted¦CircuitBreaker¦Malfunctioning | Unknown Cause | Patrol - not conducted | Circuit Breaker | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2018
Primary Conductor - Other | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | UnknownCause¦Patrolnotconducted¦ConductorOverhead¦Arcing | Unknown Cause | Patrol - not conducted | Conductor, Overhead | Arcing | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2022
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | UnknownCause¦Patrolnotconducted¦ConductorOverhead¦Brokenwireonground | Unknown Cause | Patrol - not conducted | Conductor, Overhead | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2022
Primary Conductor - Line Slap | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | UnknownCause¦Patrolnotconducted¦ConductorOverhead¦Together | Unknown Cause | Patrol - not conducted | Conductor, Overhead | Together | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2022
Equipment (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | UnknownCause¦Patrolnotconducted¦CustomerEquipment¦Malfunctioning | Unknown Cause | Patrol - not conducted | Customer Equipment | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2020
Equipment (Fuse) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolnotconducted¦Cutoutfuseholder¦Broken | Unknown Cause | Patrol - not conducted | Cutout, fuse holder | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Support Structure) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | UnknownCause¦Patrolnotconducted¦PoleWood¦Broken | Unknown Cause | Patrol - not conducted | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2016
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | UnknownCause¦Patrolnotconducted¦Transformer¦Broken | Unknown Cause | Patrol - not conducted | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0 | 0.2 | 0 | 0.2 | UnknownCause¦Patrolnotconducted¦Transformer¦FailedFaulted | Unknown Cause | Patrol - not conducted | Transformer | Failed/Faulted | FNLYEAR 2015: 2 | 2
Equipment (Transformer) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0 | 0.2 | 0 | 0.2 | UnknownCause¦Patrolnotconducted¦Transformer¦Malfunctioning | Unknown Cause | Patrol - not conducted | Transformer | Malfunctioning | FNLYEAR 2016: 2 | 2
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Othergroundvegetation¦AnchororGuy¦Normal | Vegetation | Other ground vegetation | Anchor or Guy | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Broken | Vegetation | Other ground vegetation | Conductor, Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Contaminated | Vegetation | Other ground vegetation | Conductor, Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.45 | 0.45 | 0.71429 | 0.5 | 1 | 0.5 | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal | Vegetation | Other ground vegetation | Conductor- Overhead | Normal | FNLYEAR 2024: 5 | 5
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 3.87 | 3.87 | 4.4286 | 4.3 | 3.4 | 4.3 | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2 | 3 | 7 | 6 | 8 | 1 | 4 | 9 | 3 |  | 43
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Together | Vegetation | Other ground vegetation | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Othergroundvegetation¦CrossarmWood¦Broken | Vegetation | Other ground vegetation | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Othergroundvegetation¦Cutoutfuseholder¦Normal | Vegetation | Other ground vegetation | Cutout, fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Fuse¦BurnedOpen | Vegetation | Other ground vegetation | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Othergroundvegetation¦Fuse¦FailedFaulted | Vegetation | Other ground vegetation | Fuse | Failed/Faulted | FNLYEAR 2024: 2 | 2
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.28571 | 0.3 | 0.2 | 0.3 | Vegetation¦Othergroundvegetation¦Fuse¦FailedFaulted | Vegetation | Other ground vegetation | Fuse | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2018; FNLYEAR 2022
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0 | 0.2 | Vegetation¦Othergroundvegetation¦Fuse¦Normal | Vegetation | Other ground vegetation | Fuse | Normal | [10 empty] | 2 | bar: FNLYEAR 2018 to FNLYEAR 2019
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Othergroundvegetation¦Insulator¦Arcing | Vegetation | Other ground vegetation | Insulator | Arcing | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Othergroundvegetation¦Other¦Normal | Vegetation | Other ground vegetation | Other | Normal | FNLYEAR 2024: 2 | 2
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Othergroundvegetation¦Other¦Normal | Vegetation | Other ground vegetation | Other | Normal | FNLYEAR 2015: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1 | 4
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Othergroundvegetation¦PoleWood¦Broken | Vegetation | Other ground vegetation | Pole-Wood | Broken | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.21 | 0.21 | 0.14286 | 0.3 | 0.2 | 0.3 | Vegetation¦Othergroundvegetation¦PoleWood¦Normal | Vegetation | Other ground vegetation | Pole-Wood | Normal | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2021
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Othergroundvegetation¦Pothead(RiserTermination)¦Burnedflashed | Vegetation | Other ground vegetation | Pothead(Riser Termination) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Secondary¦Burnedflashed | Vegetation | Other ground vegetation | Secondary | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Secondary¦Contaminated | Vegetation | Other ground vegetation | Secondary | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Transformer(OH)¦FailedFaulted | Vegetation | Other ground vegetation | Transformer (OH) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Transformer(UG)¦Broken | Vegetation | Other ground vegetation | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Transformer¦Arcing | Vegetation | Other ground vegetation | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Transformer¦Broken | Vegetation | Other ground vegetation | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Othergroundvegetation¦Transformer¦Brokenwireonground | Vegetation | Other ground vegetation | Transformer | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Othergroundvegetation¦Transformer¦Normal | Vegetation | Other ground vegetation | Transformer | Normal | FNLYEAR 2024: 2 | 2
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Othergroundvegetation¦Transformer¦Normal | Vegetation | Other ground vegetation | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebarkfellintoline¦¦FailedFaulted | Vegetation | Tree - bark fell into line |  | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebarkfellintoline¦AnchororGuy¦Broken | Vegetation | Tree - bark fell into line | Anchor or Guy | Broken | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2023
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebarkfellintoline¦Bus¦FailedFaulted | Vegetation | Tree - bark fell into line | Bus | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Arcing | Vegetation | Tree - bark fell into line | Conductor, Overhead | Arcing | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Broken | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.81 | 0.81 | 0.85714 | 0.9 | 0.6 | 0.9 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Broken | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken |  | 1 | 2 | 1 | 2 |  | 2 | 1 |  |  | 9
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.64 | 2.64 | 5.4286 | 6.6 | 4.6 | 6.6 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 8 | 9 | 11 | 5 | 10 | 6 | 9 | 4 | 4 |  | 66
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0 | 0.2 | 0 | 0.2 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonobject | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on object | FNLYEAR 2017: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Burnedflashed | Vegetation | Tree - bark fell into line | Conductor, Overhead | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Contaminated | Vegetation | Tree - bark fell into line | Conductor, Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Deteriorated | Vegetation | Tree - bark fell into line | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦FailedFaulted | Vegetation | Tree - bark fell into line | Conductor, Overhead | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 2.25 | 2.25 | 3.5714 | 2.5 | 5 | 2.5 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal | Vegetation | Tree - bark fell into line | Conductor- Overhead | Normal | FNLYEAR 2024: 25 | 25
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 20.25 | 20.25 | 22.4286 | 22.5 | 20 | 22.5 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 12 | 25 | 31 | 19 | 38 | 19 | 38 | 17 | 26 |  | 225
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦OnGround | Vegetation | Tree - bark fell into line | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 2.25 | 2.25 | 1.4286 | 2.5 | 1.2 | 2.5 | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Together | Vegetation | Tree - bark fell into line | Conductor, Overhead | Together | 4 | 1 | 10 | 1 | 3 | 1 | 1 | 2 | 2 |  | 25
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Arcing | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Arcing | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Broken | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Broken | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Burnedflashed | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Normal | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebarkfellintoline¦CrossarmWood¦Broken | Vegetation | Tree - bark fell into line | Crossarm, Wood | Broken | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebarkfellintoline¦CrossarmWood¦Brokenwireonground | Vegetation | Tree - bark fell into line | Crossarm, Wood | Broken, wire on ground | FNLYEAR 2021: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦CrossarmWood¦Burnedflashed | Vegetation | Tree - bark fell into line | Crossarm, Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦Broken | Vegetation | Tree - bark fell into line | Cutout, fuse holder | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦FailedFaulted | Vegetation | Tree - bark fell into line | Cutout, fuse holder | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦Normal | Vegetation | Tree - bark fell into line | Cutout, fuse holder | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treebarkfellintoline¦Fuse¦BurnedOpen | Vegetation | Tree - bark fell into line | Fuse | Burned Open | FNLYEAR 2020: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.36 | 0.36 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | FNLYEAR 2024: 4 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 3.15 | 3.15 | 2.1429 | 3.5 | 0.8 | 3.5 | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 5 | 9 | 6 | 5 | 6 | 2 |  | 2 |  |  | 35
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Fuse¦Normal | Vegetation | Tree - bark fell into line | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.54 | 0.54 | 0.57143 | 0.6 | 0.4 | 0.6 | Vegetation¦Treebarkfellintoline¦Fuse¦Normal | Vegetation | Tree - bark fell into line | Fuse | Normal | FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 2 | 6
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Insulator¦Broken | Vegetation | Tree - bark fell into line | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Insulator¦Normal | Vegetation | Tree - bark fell into line | Insulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.28 | 0.28 | 0.42857 | 0.4 | 0.6 | 0.4 | Vegetation¦Treebarkfellintoline¦PoleWood¦Broken | Vegetation | Tree - bark fell into line | Pole-Wood | Broken | FNLYEAR 2017: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.32 | 0.32 | 1 | 0.8 | 0.6 | 0.8 | Vegetation¦Treebarkfellintoline¦PoleWood¦Brokenwireonground | Vegetation | Tree - bark fell into line | Pole-Wood | Broken, wire on ground | FNLYEAR 2017: 1; FNLYEAR 2019: 4; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 8
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦PoleWood¦Normal | Vegetation | Tree - bark fell into line | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Pothead(RiserTermination)¦Normal | Vegetation | Tree - bark fell into line | Pothead(Riser Termination) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Recloser¦Normal | Vegetation | Tree - bark fell into line | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.42857 | 0.4 | 0.2 | 0.4 | Vegetation¦Treebarkfellintoline¦Secondary¦Broken | Vegetation | Tree - bark fell into line | Secondary | Broken | FNLYEAR 2016: 1; FNLYEAR 2019: 2; FNLYEAR 2020: 1 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treebarkfellintoline¦Secondary¦Brokenwireonground | Vegetation | Tree - bark fell into line | Secondary | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Secondary¦Brokenwireonobject | Vegetation | Tree - bark fell into line | Secondary | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Secondary¦OnGround | Vegetation | Tree - bark fell into line | Secondary | On Ground | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Secondary¦Together | Vegetation | Tree - bark fell into line | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Broken | Vegetation | Tree - bark fell into line | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Brokenwireonground | Vegetation | Tree - bark fell into line | Service conductor | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Normal | Vegetation | Tree - bark fell into line | Service conductor | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Together | Vegetation | Tree - bark fell into line | Service conductor | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.42857 | 0.5 | 0.4 | 0.5 | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Broken | Vegetation | Tree - bark fell into line | Transformer (OH) | Broken | FNLYEAR 2017: 2; FNLYEAR 2019: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Leaking | Vegetation | Tree - bark fell into line | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Leaking | Vegetation | Tree - bark fell into line | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.42 | 0.42 | 0.57143 | 0.6 | 0.6 | 0.6 | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Normal | Vegetation | Tree - bark fell into line | Transformer (OH) | Normal | FNLYEAR 2015: 1; FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 6
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Transformer¦Arcing | Vegetation | Tree - bark fell into line | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebarkfellintoline¦Transformer¦BentorTwisted | Vegetation | Tree - bark fell into line | Transformer | Bent or Twisted | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Transformer¦Broken | Vegetation | Tree - bark fell into line | Transformer | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.35 | 0.35 | 0.42857 | 0.5 | 0.2 | 0.5 | Vegetation¦Treebarkfellintoline¦Transformer¦Broken | Vegetation | Tree - bark fell into line | Transformer | Broken | FNLYEAR 2016: 2; FNLYEAR 2019: 2; FNLYEAR 2022: 1 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.4 | 0.3 | Vegetation¦Treebarkfellintoline¦Transformer¦Brokenwireonground | Vegetation | Tree - bark fell into line | Transformer | Broken, wire on ground | [10 empty] | 3 | bar: FNLYEAR 2019; FNLYEAR 2022 to FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebarkfellintoline¦Transformer¦Burnedflashed | Vegetation | Tree - bark fell into line | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebarkfellintoline¦Transformer¦FailedFaulted | Vegetation | Tree - bark fell into line | Transformer | Failed/Faulted | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebarkfellintoline¦Transformer¦FailedFaulted | Vegetation | Tree - bark fell into line | Transformer | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2020
Vegetation (Branch) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebarkfellintoline¦Transformer¦Normal | Vegetation | Tree - bark fell into line | Transformer | Normal | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦¦ | Vegetation | Tree - branch fell on line | [12 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦¦Broken | Vegetation | Tree - branch fell on line |  | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦¦BurnedOpen | Vegetation | Tree - branch fell on line |  | Burned Open | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2020
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦¦FailedFaulted | Vegetation | Tree - branch fell on line |  | Failed/Faulted | FNLYEAR 2016: 3; FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2019: 1; FNLYEAR 2021: 3 | 10
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebranchfellonline¦AnchororGuy¦Broken | Vegetation | Tree - branch fell on line | Anchor or Guy | Broken | [10 empty] | 2 | bar: FNLYEAR 2019 to FNLYEAR 2020
Vegetation (Branch) | None | 0% | 0 | 0 | Very High | 90% | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦AnchororGuy¦Normal | Vegetation | Tree - branch fell on line | Anchor or Guy | Normal | FNLYEAR 2021: 2; FNLYEAR 2023: 1 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Bushing¦Arcing | Vegetation | Tree - branch fell on line | Bushing | Arcing | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Bushing¦Broken | Vegetation | Tree - branch fell on line | Bushing | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.85714 | 0.7 | 0.8 | 0.7 | Vegetation¦Treebranchfellonline¦Bushing¦Broken | Vegetation | Tree - branch fell on line | Bushing | Broken | FNLYEAR 2015: 1; FNLYEAR 2019: 2; FNLYEAR 2022: 3; FNLYEAR 2023: 1 | 7
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Bushing¦Brokenwireonground | Vegetation | Tree - branch fell on line | Bushing | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0 | 0.2 | 0 | 0.2 | Vegetation¦Treebranchfellonline¦Bushing¦Normal | Vegetation | Tree - branch fell on line | Bushing | Normal | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Capacitor¦Brokenwireonground | Vegetation | Tree - branch fell on line | Capacitor | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Capacitor¦Normal | Vegetation | Tree - branch fell on line | Capacitor | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0 | 0.2 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Annealed | Vegetation | Tree - branch fell on line | Conductor, Overhead | Annealed | FNLYEAR 2019: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing | Vegetation | Tree - branch fell on line | Conductor- Overhead | Arcing | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.08 | 2.08 | 4.4286 | 5.2 | 4 | 5.2 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 5 | 5 | 11 | 5 | 6 | 4 | 7 | 5 | 4 |  | 52
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted | Vegetation | Tree - branch fell on line | Conductor- Overhead | Bent or Twisted | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.36 | 1.36 | 3.7143 | 3.4 | 3 | 3.4 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted | Vegetation | Tree - branch fell on line | Conductor, Overhead | Bent or Twisted | 2 | 2 | 4 | 2 | 9 | 3 | 5 | 4 | 3 |  | 34
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.32 | 0.32 | 1.1429 | 0.8 | 1.6 | 0.8 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken | FNLYEAR 2024: 8 | 8
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 3.44 | 3.44 | 8.5714 | 8.6 | 7 | 8.6 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 9 | 8 | 9 | 12 | 13 | 3 | 13 | 8 | 11 |  | 86
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 3.12 | 3.12 | 11.1429 | 7.8 | 15.6 | 7.8 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 78 | 78
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 54.8 | 54.8 | 123.4286 | 137 | 104.4 | 137 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 132 | 145 | 229 | 111 | 231 | 148 | 215 | 115 | 44 |  | 1370
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken- wire on object | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.24 | 1.24 | 1.7143 | 3.1 | 1.4 | 3.1 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 3 | 3 | 13 | 2 | 3 | 3 | 3 | 1 |  |  | 31
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Burnedflashed | Vegetation | Tree - branch fell on line | Conductor- Overhead | Burned/flashed | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.32 | 1.32 | 2.7143 | 3.3 | 1.8 | 3.3 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Burnedflashed | Vegetation | Tree - branch fell on line | Conductor, Overhead | Burned/flashed | 5 | 1 | 8 | 3 | 7 | 3 | 2 | 3 | 1 |  | 33
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.85714 | 0.6 | 1.2 | 0.6 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Contaminated | Vegetation | Tree - branch fell on line | Conductor- Overhead | Contaminated | FNLYEAR 2024: 6 | 6
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.84 | 0.84 | 1.8571 | 2.1 | 2.4 | 2.1 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Contaminated | Vegetation | Tree - branch fell on line | Conductor, Overhead | Contaminated |  | 2 | 6 |  | 1 | 3 | 2 | 2 | 5 |  | 21
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Deteriorated | Vegetation | Tree - branch fell on line | Conductor- Overhead | Deteriorated | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.68 | 0.68 | 2 | 1.7 | 2.2 | 1.7 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Deteriorated | Vegetation | Tree - branch fell on line | Conductor, Overhead | Deteriorated | 1 |  | 2 |  | 3 | 4 | 2 | 3 | 2 |  | 17
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦FailedFaulted | Vegetation | Tree - branch fell on line | Conductor, Overhead | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Malfunctioning | Vegetation | Tree - branch fell on line | Conductor, Overhead | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 14.36 | 14.36 | 51.2857 | 35.9 | 71.8 | 35.9 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal | Vegetation | Tree - branch fell on line | Conductor- Overhead | Normal | FNLYEAR 2024: 359 | 359
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 138.96 | 138.96 | 356 | 347.4 | 323.2 | 347.4 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 194 | 298 | 490 | 282 | 594 | 371 | 557 | 327 | 361 |  | 3474
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.16 | 2.16 | 3 | 5.4 | 2.6 | 5.4 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 12 | 8 | 13 | 2 | 6 | 2 | 8 | 3 |  |  | 54
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.68 | 0.68 | 2.4286 | 1.7 | 3.4 | 1.7 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together | Vegetation | Tree - branch fell on line | Conductor- Overhead | Together | FNLYEAR 2024: 17 | 17
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 13.44 | 13.44 | 32.4286 | 33.6 | 20.4 | 33.6 | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 18 | 28 | 63 | 44 | 81 | 33 | 38 | 15 | 16 |  | 336
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.28571 | 0.5 | 0.4 | 0.5 | Vegetation¦Treebranchfellonline¦ConductorUnderground¦Normal | Vegetation | Tree - branch fell on line | Conductor, Underground | Normal | FNLYEAR 2015: 2; FNLYEAR 2016: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 1 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Broken | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1.7143 | 1.3 | 0.8 | 1.3 | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Broken | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken |  |  | 1 | 2 | 6 | 1 | 2 |  | 1 |  | 13
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.56 | 0.56 | 1.5714 | 1.4 | 1.6 | 1.4 | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonground | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on ground |  | 1 | 2 |  | 3 | 3 | 1 | 2 | 2 |  | 14
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Burnedflashed | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Normal | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.57143 | 0.6 | 0.2 | 0.6 | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Normal | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Normal | FNLYEAR 2015: 1; FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 2; FNLYEAR 2022: 1 | 6
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦CrossarmSteel¦Brokenwireonground | Vegetation | Tree - branch fell on line | Crossarm, Steel | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken | FNLYEAR 2024: 4 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.92 | 2.92 | 7 | 7.3 | 5.2 | 7.3 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 6 | 4 | 14 | 3 | 20 | 9 | 9 | 7 | 1 |  | 73
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken- wire on ground | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.64 | 1.64 | 4.7143 | 4.1 | 4 | 4.1 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | 1 | 2 | 5 | 3 | 10 | 10 | 6 | 2 | 2 |  | 41
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken- wire on object | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.42857 | 0.6 | 0.2 | 0.6 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on object | FNLYEAR 2015: 1; FNLYEAR 2017: 2; FNLYEAR 2018: 2; FNLYEAR 2022: 1 | 6
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Burnedflashed | Vegetation | Tree - branch fell on line | Crossarm, Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦CrossarmWood¦Normal | Vegetation | Tree - branch fell on line | Crossarm, Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦CustomerEquipment¦Arcing | Vegetation | Tree - branch fell on line | Customer Equipment | Arcing | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦CustomerEquipment¦Broken | Vegetation | Tree - branch fell on line | Customer Equipment | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦CustomerEquipment¦Normal | Vegetation | Tree - branch fell on line | Customer Equipment | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦CutoutFusedDistribution¦FailedFaulted | Vegetation | Tree - branch fell on line | Cutout, Fused, Distribution | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Broken | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 0.85714 | 1.3 | 0.8 | 1.3 | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Broken | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Broken | 1 | 4 | 2 | 1 | 1 |  | 2 | 2 |  |  | 13
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Brokenwireonground | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Burnedflashed | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Burnedflashed | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.14286 | 0.5 | 0.2 | 0.5 | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦FailedFaulted | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2016: 2; FNLYEAR 2017: 1; FNLYEAR 2023: 1 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.4 | 0.4 | 1.1429 | 1 | 1.6 | 1 | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Normal | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Normal | FNLYEAR 2017: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 4 | 10
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Fuse¦Broken | Vegetation | Tree - branch fell on line | Fuse | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1 | 0.9 | 1 | 0.9 | Vegetation¦Treebranchfellonline¦Fuse¦Broken | Vegetation | Tree - branch fell on line | Fuse | Broken | 1 |  | 1 | 1 | 1 |  | 3 |  | 2 |  | 9
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦Fuse¦BurnedOpen | Vegetation | Tree - branch fell on line | Fuse | Burned Open | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.64 | 0.64 | 2.1429 | 1.6 | 3 | 1.6 | Vegetation¦Treebranchfellonline¦Fuse¦BurnedOpen | Vegetation | Tree - branch fell on line | Fuse | Burned Open | FNLYEAR 2017: 1; FNLYEAR 2020: 3; FNLYEAR 2021: 7; FNLYEAR 2022: 2; FNLYEAR 2023: 3 | 16
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 1 | 0.5 | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | FNLYEAR 2024: 5 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 16.64 | 16.64 | 27.1429 | 41.6 | 10 | 41.6 | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 41 | 63 | 122 | 58 | 82 | 35 | 2 | 8 | 5 |  | 416
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 1.5714 | 1.1 | 2.2 | 1.1 | Vegetation¦Treebranchfellonline¦Fuse¦Normal | Vegetation | Tree - branch fell on line | Fuse | Normal | FNLYEAR 2024: 11 | 11
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.6 | 2.6 | 5.1429 | 6.5 | 3.8 | 6.5 | Vegetation¦Treebranchfellonline¦Fuse¦Normal | Vegetation | Tree - branch fell on line | Fuse | Normal | 13 | 7 | 9 | 8 | 9 |  | 5 | 5 | 9 |  | 65
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Fuse¦OnGround | Vegetation | Tree - branch fell on line | Fuse | On Ground | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Insulator¦Broken | Vegetation | Tree - branch fell on line | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.04 | 1.04 | 2.5714 | 2.6 | 2.2 | 2.6 | Vegetation¦Treebranchfellonline¦Insulator¦Broken | Vegetation | Tree - branch fell on line | Insulator | Broken | 1 | 3 | 4 | 2 | 5 | 3 | 4 | 3 | 1 |  | 26
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.4 | 0.3 | Vegetation¦Treebranchfellonline¦Insulator¦Brokenwireonground | Vegetation | Tree - branch fell on line | Insulator | Broken, wire on ground | [10 empty] | 3 | bar: FNLYEAR 2019 to FNLYEAR 2020; FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Insulator¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Insulator | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.14286 | 0.3 | 0 | 0.3 | Vegetation¦Treebranchfellonline¦Insulator¦Burnedflashed | Vegetation | Tree - branch fell on line | Insulator | Burned/flashed | FNLYEAR 2017: 2; FNLYEAR 2019: 1 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium High | 60% | 0.12 | 0.12 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Insulator¦Normal | Vegetation | Tree - branch fell on line | Insulator | Normal | [10 empty] | 2 | bar: FNLYEAR 2021 to FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Jumper¦BentorTwisted | Vegetation | Tree - branch fell on line | Jumper | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Jumper¦Broken | Vegetation | Tree - branch fell on line | Jumper | Broken | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.6 | 0.6 | 1.5714 | 1.5 | 1.4 | 1.5 | Vegetation¦Treebranchfellonline¦Jumper¦Broken | Vegetation | Tree - branch fell on line | Jumper | Broken |  | 3 | 1 | 3 | 1 |  | 4 | 3 |  |  | 15
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Jumper¦Brokenwireonground | Vegetation | Tree - branch fell on line | Jumper | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Jumper¦BurnedOpen | Vegetation | Tree - branch fell on line | Jumper | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.42857 | 0.7 | 0.6 | 0.7 | Vegetation¦Treebranchfellonline¦Jumper¦BurnedOpen | Vegetation | Tree - branch fell on line | Jumper | Burned Open | 1 | 1 | 2 |  |  |  | 1 | 1 | 1 |  | 7
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Jumper¦Normal | Vegetation | Tree - branch fell on line | Jumper | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.42857 | 0.4 | 0.2 | 0.4 | Vegetation¦Treebranchfellonline¦Jumper¦Normal | Vegetation | Tree - branch fell on line | Jumper | Normal | FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2023: 1 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦LightningArrestor¦Broken | Vegetation | Tree - branch fell on line | Lightning Arrestor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦LightningArrestor¦Broken | Vegetation | Tree - branch fell on line | Lightning Arrestor | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0 | 0.2 | 0 | 0.2 | Vegetation¦Treebranchfellonline¦LightningArrestor¦Normal | Vegetation | Tree - branch fell on line | Lightning Arrestor | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2017
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦Other¦BentorTwisted | Vegetation | Tree - branch fell on line | Other | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦Other¦Broken | Vegetation | Tree - branch fell on line | Other | Broken | FNLYEAR 2016: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 1; FNLYEAR 2020: 3 | 7
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦Other¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Other | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦Other¦FailedFaulted | Vegetation | Tree - branch fell on line | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦Other¦Normal | Vegetation | Tree - branch fell on line | Other | Normal | FNLYEAR 2015: 1; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2023: 3 | 8
Vegetation (Branch) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treebranchfellonline¦Other¦OnGround | Vegetation | Tree - branch fell on line | Other | On Ground | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0 | 0.2 | Vegetation¦Treebranchfellonline¦PoleTowersteel¦Normal | Vegetation | Tree - branch fell on line | Pole - Tower, steel | Normal | FNLYEAR 2019: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦PoleWood¦Broken | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.2 | 2.2 | 5.4286 | 5.5 | 5.4 | 5.5 | Vegetation¦Treebranchfellonline¦PoleWood¦Broken | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 3 | 8 | 6 | 3 | 8 | 6 | 10 | 9 | 2 |  | 55
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground | Vegetation | Tree - branch fell on line | Pole-Wood | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.68 | 2.68 | 7.2857 | 6.7 | 6.4 | 6.7 | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 3 | 7 | 6 | 8 | 11 | 8 | 14 | 7 | 3 |  | 67
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on object | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦PoleWood¦Contaminated | Vegetation | Tree - branch fell on line | Pole-Wood | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦PoleWood¦Deteriorated | Vegetation | Tree - branch fell on line | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦PoleWood¦Normal | Vegetation | Tree - branch fell on line | Pole-Wood | Normal | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Pothead(RiserTermination)¦FailedFaulted | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Pothead(RiserTermination)¦Normal | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Normal | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Recloser¦Malfunctioning | Vegetation | Tree - branch fell on line | Recloser | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1.7143 | 1.3 | 1 | 1.3 | Vegetation¦Treebranchfellonline¦Recloser¦Normal | Vegetation | Tree - branch fell on line | Recloser | Normal |  |  | 1 | 2 | 5 | 1 |  | 1 | 3 |  | 13
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Secondary¦Annealed | Vegetation | Tree - branch fell on line | Secondary | Annealed | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.28571 | 0.4 | 0.4 | 0.4 | Vegetation¦Treebranchfellonline¦Secondary¦Arcing | Vegetation | Tree - branch fell on line | Secondary | Arcing | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2021; FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.71429 | 0.6 | 0.2 | 0.6 | Vegetation¦Treebranchfellonline¦Secondary¦BentorTwisted | Vegetation | Tree - branch fell on line | Secondary | Bent or Twisted | FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 2; FNLYEAR 2023: 1 | 6
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦Secondary¦Broken | Vegetation | Tree - branch fell on line | Secondary | Broken | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.28 | 1.28 | 3.2857 | 3.2 | 3 | 3.2 | Vegetation¦Treebranchfellonline¦Secondary¦Broken | Vegetation | Tree - branch fell on line | Secondary | Broken | 4 | 4 | 1 | 1 | 7 | 2 | 5 | 5 | 3 |  | 32
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground | Vegetation | Tree - branch fell on line | Secondary | Broken- wire on ground | FNLYEAR 2024: 4 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.52 | 1.52 | 3.7143 | 3.8 | 3 | 3.8 | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 1 | 4 | 7 | 4 | 7 | 5 | 3 | 3 | 4 |  | 38
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.28571 | 0.4 | 0.2 | 0.4 | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on object | FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2022: 1 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Secondary¦Deteriorated | Vegetation | Tree - branch fell on line | Secondary | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Secondary¦Normal | Vegetation | Tree - branch fell on line | Secondary | Normal | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.92 | 1.92 | 5.5714 | 4.8 | 5.8 | 4.8 | Vegetation¦Treebranchfellonline¦Secondary¦Normal | Vegetation | Tree - branch fell on line | Secondary | Normal | 4 | 3 | 2 | 2 | 8 | 3 | 8 | 10 | 8 |  | 48
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0 | 0.3 | 0 | 0.3 | Vegetation¦Treebranchfellonline¦Secondary¦OnGround | Vegetation | Tree - branch fell on line | Secondary | On Ground | FNLYEAR 2016: 1; FNLYEAR 2017: 2 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Secondary¦Together | Vegetation | Tree - branch fell on line | Secondary | Together | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 0.85714 | 1.1 | 1 | 1.1 | Vegetation¦Treebranchfellonline¦Secondary¦Together | Vegetation | Tree - branch fell on line | Secondary | Together | 1 | 2 | 2 |  | 1 | 1 | 2 | 1 | 1 |  | 11
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 1 | 0.5 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken | Vegetation | Tree - branch fell on line | Service conductor | Broken | FNLYEAR 2024: 5 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.44 | 1.44 | 4 | 3.6 | 3.8 | 3.6 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken | Vegetation | Tree - branch fell on line | Service conductor | Broken | 1 | 4 | 3 | 2 | 7 | 5 | 5 | 4 | 5 |  | 36
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1.2857 | 0.9 | 1.8 | 0.9 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground | Vegetation | Tree - branch fell on line | Service conductor | Broken- wire on ground | FNLYEAR 2024: 9 | 9
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 2.04 | 2.04 | 5.8571 | 5.1 | 5.6 | 5.1 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 1 | 3 | 6 | 6 | 7 | 9 | 6 | 6 | 7 |  | 51
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.42857 | 0.5 | 0.2 | 0.5 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on object | FNLYEAR 2017: 2; FNLYEAR 2019: 2; FNLYEAR 2021: 1 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Normal | Vegetation | Tree - branch fell on line | Service conductor | Normal | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1 | 0.9 | 1.2 | 0.9 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Normal | Vegetation | Tree - branch fell on line | Service conductor | Normal | FNLYEAR 2015: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 9
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Serviceconductor¦OnGround | Vegetation | Tree - branch fell on line | Service conductor | On Ground | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.14286 | 0.3 | 0.2 | 0.3 | Vegetation¦Treebranchfellonline¦Serviceconductor¦Together | Vegetation | Tree - branch fell on line | Service conductor | Together | FNLYEAR 2016: 2; FNLYEAR 2022: 1 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treebranchfellonline¦Switch(OH)¦Broken | Vegetation | Tree - branch fell on line | Switch (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treebranchfellonline¦Switch(OH)¦FailedFaulted | Vegetation | Tree - branch fell on line | Switch (OH) | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2019
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.42857 | 0.4 | 0.2 | 0.4 | Vegetation¦Treebranchfellonline¦Switch(OH)¦Normal | Vegetation | Tree - branch fell on line | Switch (OH) | Normal | FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 1 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦ | Vegetation | Tree - branch fell on line | Transformer (OH) |  | FNLYEAR 2021: 1; FNLYEAR 2023: 2 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1 | 1 | 2.8571 | 2.5 | 2.6 | 2.5 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken |  | 3 | 2 | 3 | 4 | 5 | 4 | 2 | 2 |  | 25
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Brokenwireonground | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken- wire on ground | FNLYEAR 2024: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.48 | 0.48 | 1.7143 | 1.2 | 2.4 | 1.2 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Brokenwireonground | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken, wire on ground | FNLYEAR 2020: 2; FNLYEAR 2021: 5; FNLYEAR 2022: 2; FNLYEAR 2023: 3 | 12
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Burnedflashed | Vegetation | Tree - branch fell on line | Transformer (OH) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Deteriorated | Vegetation | Tree - branch fell on line | Transformer (OH) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Deteriorated | Vegetation | Tree - branch fell on line | Transformer (OH) | Deteriorated | FNLYEAR 2023: 2 | 2
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦FailedFaulted | Vegetation | Tree - branch fell on line | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 4 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.08 | 1.08 | 2.7143 | 2.7 | 3.4 | 2.7 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦FailedFaulted | Vegetation | Tree - branch fell on line | Transformer (OH) | Failed/Faulted | 2 | 2 | 4 |  | 2 | 3 | 4 | 3 | 7 |  | 27
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Leaking | Vegetation | Tree - branch fell on line | Transformer (OH) | Leaking | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2020
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.8 | 1.8 | 5.8571 | 4.5 | 5.6 | 4.5 | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal |  | 1 | 3 | 2 | 11 | 7 | 14 | 4 | 3 |  | 45
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.28571 | 0.4 | 0 | 0.4 | Vegetation¦Treebranchfellonline¦Transformer¦ | Vegetation | Tree - branch fell on line | Transformer |  | FNLYEAR 2017: 2; FNLYEAR 2019: 2 | 4
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Transformer¦Arcing | Vegetation | Tree - branch fell on line | Transformer | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.2 | 0.3 | Vegetation¦Treebranchfellonline¦Transformer¦BentorTwisted | Vegetation | Tree - branch fell on line | Transformer | Bent or Twisted | FNLYEAR 2019: 2; FNLYEAR 2022: 1 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦Transformer¦Broken | Vegetation | Tree - branch fell on line | Transformer | Broken | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.32 | 1.32 | 3.8571 | 3.3 | 3.8 | 3.3 | Vegetation¦Treebranchfellonline¦Transformer¦Broken | Vegetation | Tree - branch fell on line | Transformer | Broken |  | 2 | 4 | 2 | 6 | 7 | 4 | 3 | 5 |  | 33
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 1 | 0.5 | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground | Vegetation | Tree - branch fell on line | Transformer | Broken- wire on ground | FNLYEAR 2024: 5 | 5
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.64 | 1.64 | 4.1429 | 4.1 | 3.4 | 4.1 | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 1 | 7 | 4 | 1 | 11 | 3 | 6 | 3 | 5 |  | 41
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonobject | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on object | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2018
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.6 | 0.4 | Vegetation¦Treebranchfellonline¦Transformer¦Burnedflashed | Vegetation | Tree - branch fell on line | Transformer | Burned/flashed | [10 empty] | 4 | bar: FNLYEAR 2019; FNLYEAR 2021 to FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer¦BurnedOpen | Vegetation | Tree - branch fell on line | Transformer | Burned Open | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2023
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer¦Deteriorated | Vegetation | Tree - branch fell on line | Transformer | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2021
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treebranchfellonline¦Transformer¦FailedFaulted | Vegetation | Tree - branch fell on line | Transformer | Failed/Faulted | FNLYEAR 2024: 3 | 3
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 1.24 | 1.24 | 3.1429 | 3.1 | 2 | 3.1 | Vegetation¦Treebranchfellonline¦Transformer¦FailedFaulted | Vegetation | Tree - branch fell on line | Transformer | Failed/Faulted | 3 | 2 | 4 | 6 | 6 | 3 | 2 | 3 | 2 |  | 31
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.4 | 0.4 | 0.71429 | 1 | 0.4 | 1 | Vegetation¦Treebranchfellonline¦Transformer¦Leaking | Vegetation | Tree - branch fell on line | Transformer | Leaking |  | 1 | 4 | 2 | 1 | 1 | 1 |  |  |  | 10
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treebranchfellonline¦Transformer¦Normal | Vegetation | Tree - branch fell on line | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.72 | 0.72 | 1.7143 | 1.8 | 2.2 | 1.8 | Vegetation¦Treebranchfellonline¦Transformer¦Normal | Vegetation | Tree - branch fell on line | Transformer | Normal | FNLYEAR 2017: 6; FNLYEAR 2019: 1; FNLYEAR 2020: 1; FNLYEAR 2021: 6; FNLYEAR 2023: 4 | 18
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treebranchfellonline¦Transformer¦OnGround | Vegetation | Tree - branch fell on line | Transformer | On Ground | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0.4 | 0.3 | Vegetation¦Treebranchfellonline¦Transformer¦Together | Vegetation | Tree - branch fell on line | Transformer | Together | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2021 to FNLYEAR 2022
Vegetation (Branch) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.14286 | 0.3 | 0.2 | 0.3 | Vegetation¦Treebranchfellonline¦Woodpin¦Broken | Vegetation | Tree - branch fell on line | Woodpin | Broken | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2020
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 0 | 0.9 | 0 | 0.9 | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2015: 9 | 9
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Together | Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0% | 0 | 0 | Medium High | 60% | 0.06 | 0.06 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treecutting3rdparty¦CrossarmWood¦Broken | Vegetation | Tree - cutting, 3rd party | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦AnchororGuy¦Broken | Vegetation | Tree - cutting, PG&E contractor | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦TreecuttingPG&Econtractor¦CircuitBreaker¦Normal | Vegetation | Tree - cutting, PG&E contractor | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Annealed | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Annealed | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Arcing | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Broken | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.2 | 0.3 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Broken | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken | FNLYEAR 2019: 2; FNLYEAR 2023: 1 | 3
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 2 | 2
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 1.44 | 1.44 | 2.7143 | 3.6 | 2.6 | 3.6 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 5 | 7 | 5 | 3 | 3 | 4 | 3 | 5 | 1 |  | 36
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Burnedflashed | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2019
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Contaminated | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1.8571 | 1.3 | 2.6 | 1.3 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Normal | FNLYEAR 2024: 13 | 13
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 4.52 | 4.52 | 13 | 11.3 | 11.8 | 11.3 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 5 | 7 | 10 | 12 | 20 | 12 | 17 | 12 | 18 |  | 113
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦OnGround | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | On Ground | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Together | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.42857 | 0.6 | 0.4 | 0.6 | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Together | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Together | FNLYEAR 2016: 2; FNLYEAR 2017: 1; FNLYEAR 2018: 1; FNLYEAR 2020: 2 | 6
Vegetation (other) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦ConnectororSplice(OH)¦Normal | Vegetation | Tree - cutting, PG&E contractor | Connector or Splice (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.14286 | 0.3 | 0.2 | 0.3 | Vegetation¦TreecuttingPG&Econtractor¦CrossarmWood¦Broken | Vegetation | Tree - cutting, PG&E contractor | Crossarm, Wood | Broken | [10 empty] | 3 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2020
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.4 | 0.3 | Vegetation¦TreecuttingPG&Econtractor¦CrossarmWood¦Brokenwireonground | Vegetation | Tree - cutting, PG&E contractor | Crossarm, Wood | Broken, wire on ground | FNLYEAR 2019: 1; FNLYEAR 2020: 2 | 3
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Fuse¦FailedFaulted | Vegetation | Tree - cutting- PG&E contractor | Fuse | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.57143 | 0.5 | 0 | 0.5 | Vegetation¦TreecuttingPG&Econtractor¦Fuse¦FailedFaulted | Vegetation | Tree - cutting, PG&E contractor | Fuse | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2018: 2; FNLYEAR 2019: 2 | 5
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Insulator¦Broken | Vegetation | Tree - cutting, PG&E contractor | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦TreecuttingPG&Econtractor¦Other¦Broken | Vegetation | Tree - cutting, PG&E contractor | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (other) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦TreecuttingPG&Econtractor¦Other¦Normal | Vegetation | Tree - cutting, PG&E contractor | Other | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2018
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.42857 | 0.7 | 0.2 | 0.7 | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Broken | Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken | 2 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 7
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Brokenwireonground | Vegetation | Tree - cutting- PG&E contractor | Pole-Wood | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.28571 | 0.4 | 0.2 | 0.4 | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Brokenwireonground | Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken, wire on ground | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019; FNLYEAR 2022
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Recloser¦Normal | Vegetation | Tree - cutting, PG&E contractor | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Secondary¦Broken | Vegetation | Tree - cutting, PG&E contractor | Secondary | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0% | 0 | 0 | High | 70% | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Secondary¦Normal | Vegetation | Tree - cutting, PG&E contractor | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Serviceconductor¦Broken | Vegetation | Tree - cutting- PG&E contractor | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Serviceconductor¦Broken | Vegetation | Tree - cutting, PG&E contractor | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Transformer(OH)¦Brokenwireonground | Vegetation | Tree - cutting, PG&E contractor | Transformer (OH) | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Transformer(OH)¦Normal | Vegetation | Tree - cutting, PG&E contractor | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Transformer¦Normal | Vegetation | Tree - cutting- PG&E contractor | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦TreecuttingPG&Econtractor¦Transformer¦Normal | Vegetation | Tree - cutting, PG&E contractor | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦¦ | Vegetation | Tree - fell into line | [12 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦¦BurnedOpen | Vegetation | Tree - fell into line |  | Burned Open | FNLYEAR 2016: 2 | 2
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦¦FailedFaulted | Vegetation | Tree - fell into line |  | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2017: 2 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Very High | 90% | 1.53 | 1.53 | 1.8571 | 1.7 | 1.4 | 1.7 | Vegetation¦Treefellintoline¦AnchororGuy¦Broken | Vegetation | Tree - fell into line | Anchor or Guy | Broken |  | 2 | 2 | 1 | 5 | 2 | 3 |  | 2 |  | 17
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦AnchororGuy¦Brokenwireonground | Vegetation | Tree - fell into line | Anchor or Guy | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.71429 | 0.6 | 0.8 | 0.6 | Vegetation¦Treefellintoline¦AnchororGuy¦Brokenwireonground | Vegetation | Tree - fell into line | Anchor or Guy | Broken, wire on ground | [10 empty] | 6 | bar: FNLYEAR 2017; FNLYEAR 2019 to FNLYEAR 2023
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦AnchororGuy¦Deteriorated | Vegetation | Tree - fell into line | Anchor or Guy | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (Trunk) | None | 0% | 0 | 0 | Very High | 90% | 0.18 | 0.18 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦AnchororGuy¦Normal | Vegetation | Tree - fell into line | Anchor or Guy | Normal | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Very High | 90% | 1.08 | 1.08 | 1.2857 | 1.2 | 1.6 | 1.2 | Vegetation¦Treefellintoline¦AnchororGuy¦Normal | Vegetation | Tree - fell into line | Anchor or Guy | Normal | 2 |  | 1 |  | 1 |  | 2 | 2 | 4 |  | 12
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.48 | 0.48 | 1 | 1.2 | 1 | 1.2 | Vegetation¦Treefellintoline¦Bushing¦Broken | Vegetation | Tree - fell into line | Bushing | Broken |  | 2 | 3 | 1 | 1 |  | 4 |  | 1 |  | 12
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Capacitor¦Brokenwireonground | Vegetation | Tree - fell into line | Capacitor | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.57143 | 0.6 | 0.8 | 0.6 | Vegetation¦Treefellintoline¦CircuitBreaker¦Normal | Vegetation | Tree - fell into line | Circuit Breaker | Normal | FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 1 | 6
Vegetation (Trunk) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦CommunicationEquipment¦Broken | Vegetation | Tree - fell into line | Communication Equipment | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Trunk) | None | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦ConductorOverhead¦ | Vegetation | Tree - fell into line | Conductor, Overhead | [11 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦Annealed | Vegetation | Tree - fell into line | Conductor, Overhead | Annealed | [10 empty] | 2 | bar: FNLYEAR 2020; FNLYEAR 2023
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing | Vegetation | Tree - fell into line | Conductor- Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 2.44 | 2.44 | 4.5714 | 6.1 | 3.2 | 6.1 | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 9 | 2 | 18 | 4 | 12 | 4 | 5 | 6 | 1 |  | 61
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted | Vegetation | Tree - fell into line | Conductor- Overhead | Bent or Twisted | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 4.72 | 4.72 | 10 | 11.8 | 9.8 | 11.8 | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 8 | 10 | 30 | 10 | 11 | 6 | 19 | 13 | 11 |  | 118
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.96 | 0.96 | 3.4286 | 2.4 | 4.8 | 2.4 | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken | Vegetation | Tree - fell into line | Conductor- Overhead | Broken | FNLYEAR 2024: 24 | 24
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 12.64 | 12.64 | 31 | 31.6 | 27.6 | 31.6 | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 21 | 23 | 55 | 28 | 51 | 23 | 51 | 29 | 35 |  | 316
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 14.36 | 14.36 | 51.2857 | 35.9 | 71.8 | 35.9 | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - fell into line | Conductor- Overhead | Broken- wire on ground | FNLYEAR 2024: 359 | 359
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 282.92 | 282.92 | 630.5714 | 707.3 | 510.8 | 707.3 | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 452 | 724 | 1483 | 433 | 1427 | 495 | 1153 | 482 | 424 |  | 7073
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject | Vegetation | Tree - fell into line | Conductor- Overhead | Broken- wire on object | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 3.92 | 3.92 | 6 | 9.8 | 3.2 | 9.8 | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 7 | 14 | 35 | 5 | 21 | 3 | 4 | 5 | 4 |  | 98
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed | Vegetation | Tree - fell into line | Conductor- Overhead | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 2.44 | 2.44 | 4.5714 | 6.1 | 4.2 | 6.1 | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed | Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | 4 | 5 | 20 | 7 | 4 | 5 | 5 | 6 | 5 |  | 61
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦Contaminated | Vegetation | Tree - fell into line | Conductor- Overhead | Contaminated | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.72 | 0.72 | 2 | 1.8 | 2 | 1.8 | Vegetation¦Treefellintoline¦ConductorOverhead¦Contaminated | Vegetation | Tree - fell into line | Conductor, Overhead | Contaminated | 2 | 2 |  | 2 | 2 | 3 | 3 | 3 | 1 |  | 18
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦Deteriorated | Vegetation | Tree - fell into line | Conductor- Overhead | Deteriorated | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1.4286 | 1.3 | 1.8 | 1.3 | Vegetation¦Treefellintoline¦ConductorOverhead¦Deteriorated | Vegetation | Tree - fell into line | Conductor, Overhead | Deteriorated |  |  | 3 |  | 1 | 2 | 3 | 2 | 2 |  | 13
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦FailedFaulted | Vegetation | Tree - fell into line | Conductor, Overhead | Failed/Faulted | [10 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 9.68 | 9.68 | 34.5714 | 24.2 | 48.4 | 24.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal | Vegetation | Tree - fell into line | Conductor- Overhead | Normal | FNLYEAR 2024: 242 | 242
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 123.24 | 123.24 | 314.1429 | 308.1 | 286.8 | 308.1 | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 159 | 282 | 441 | 188 | 577 | 277 | 450 | 296 | 411 |  | 3081
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround | Vegetation | Tree - fell into line | Conductor- Overhead | On Ground | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 11.28 | 11.28 | 18.4286 | 28.2 | 14.6 | 28.2 | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 46 | 38 | 69 | 19 | 37 | 7 | 43 | 11 | 12 |  | 282
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.68 | 0.68 | 2.4286 | 1.7 | 3.4 | 1.7 | Vegetation¦Treefellintoline¦ConductorOverhead¦Together | Vegetation | Tree - fell into line | Conductor- Overhead | Together | FNLYEAR 2024: 17 | 17
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 26.4 | 26.4 | 63 | 66 | 41 | 66 | Vegetation¦Treefellintoline¦ConductorOverhead¦Together | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 31 | 59 | 129 | 59 | 177 | 52 | 84 | 31 | 38 |  | 660
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treefellintoline¦ConductorUnderground¦Broken | Vegetation | Tree - fell into line | Conductor, Underground | Broken | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2021
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦ConductorUnderground¦Brokenwireonground | Vegetation | Tree - fell into line | Conductor, Underground | Broken, wire on ground | FNLYEAR 2015: 2; FNLYEAR 2018: 1 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦ConductorUnderground¦Burnedflashed | Vegetation | Tree - fell into line | Conductor- Underground | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.28571 | 0.6 | 0.4 | 0.6 | Vegetation¦Treefellintoline¦ConductorUnderground¦Normal | Vegetation | Tree - fell into line | Conductor, Underground | Normal | FNLYEAR 2015: 2; FNLYEAR 2017: 2; FNLYEAR 2021: 2 | 6
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Broken | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 0.71429 | 0.9 | 0.4 | 0.9 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Broken | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken | 2 |  | 2 | 1 | 2 | 1 |  | 1 |  |  | 9
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Primary Conductor - Wire Down | None | 0% | 0 | 0 | Medium | 40% | 1.44 | 1.44 | 2.7143 | 3.6 | 2.2 | 3.6 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 7 | 2 | 8 | 4 | 4 | 5 | 3 |  | 3 |  | 36
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonobject | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Trunk) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦BurnedOpen | Vegetation | Tree - fell into line | Connector or Splice (OH) | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Normal | Vegetation | Tree - fell into line | Connector or Splice (OH) | Normal | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1.2857 | 1.3 | 0.6 | 1.3 | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Normal | Vegetation | Tree - fell into line | Connector or Splice (OH) | Normal | 2 |  | 2 | 3 | 3 |  | 1 |  | 2 |  | 13
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.42857 | 0.6 | 0.2 | 0.6 | Vegetation¦Treefellintoline¦CrossarmSteel¦Broken | Vegetation | Tree - fell into line | Crossarm, Steel | Broken | FNLYEAR 2015: 1; FNLYEAR 2017: 2; FNLYEAR 2018: 2; FNLYEAR 2020: 1 | 6
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treefellintoline¦CrossarmSteel¦Brokenwireonground | Vegetation | Tree - fell into line | Crossarm, Steel | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2022
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1.2857 | 0.9 | 1.8 | 0.9 | Vegetation¦Treefellintoline¦CrossarmWood¦Broken | Vegetation | Tree - fell into line | Crossarm- Wood | Broken | FNLYEAR 2024: 9 | 9
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 9.92 | 9.92 | 26 | 24.8 | 22.2 | 24.8 | Vegetation¦Treefellintoline¦CrossarmWood¦Broken | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 21 | 15 | 30 | 12 | 59 | 35 | 44 | 18 | 14 |  | 248
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.56 | 0.56 | 2 | 1.4 | 2.8 | 1.4 | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground | Vegetation | Tree - fell into line | Crossarm- Wood | Broken- wire on ground | FNLYEAR 2024: 14 | 14
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 14 | 14 | 38.4286 | 35 | 31.6 | 35 | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 12 | 26 | 43 | 29 | 82 | 50 | 73 | 20 | 15 |  | 350
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1 | 1.3 | 0.8 | 1.3 | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonobject | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on object | 1 | 2 | 3 |  | 3 | 1 | 2 | 1 |  |  | 13
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦CrossarmWood¦Burnedflashed | Vegetation | Tree - fell into line | Crossarm, Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦CrossarmWood¦Normal | Vegetation | Tree - fell into line | Crossarm- Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.71429 | 0.6 | 1 | 0.6 | Vegetation¦Treefellintoline¦CustomerEquipment¦Broken | Vegetation | Tree - fell into line | Customer Equipment | Broken | FNLYEAR 2017: 1; FNLYEAR 2021: 4; FNLYEAR 2022: 1 | 6
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦CustomerEquipment¦OnGround | Vegetation | Tree - fell into line | Customer Equipment | On Ground | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Trunk) | None | 0% | 0 | 0 | High | 70% | 0.14 | 0.14 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken | Vegetation | Tree - fell into line | Cutout- fuse holder | Broken | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | High | 70% | 0.98 | 0.98 | 1.2857 | 1.4 | 1 | 1.4 | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken | Vegetation | Tree - fell into line | Cutout, fuse holder | Broken |  | 3 | 2 |  | 4 | 1 | 1 | 2 | 1 |  | 14
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Brokenwireonground | Vegetation | Tree - fell into line | Cutout, fuse holder | Broken, wire on ground | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2019
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Burnedflashed | Vegetation | Tree - fell into line | Cutout, fuse holder | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Cutoutfuseholder¦BurnedOpen | Vegetation | Tree - fell into line | Cutout, fuse holder | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.2 | 0.3 | Vegetation¦Treefellintoline¦Cutoutfuseholder¦FailedFaulted | Vegetation | Tree - fell into line | Cutout, fuse holder | Failed/Faulted | FNLYEAR 2019: 2; FNLYEAR 2020: 1 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.57143 | 0.5 | 0.8 | 0.5 | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Normal | Vegetation | Tree - fell into line | Cutout, fuse holder | Normal | FNLYEAR 2017: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 5
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Fuse¦Arcing | Vegetation | Tree - fell into line | Fuse | Arcing | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treefellintoline¦Fuse¦Broken | Vegetation | Tree - fell into line | Fuse | Broken | FNLYEAR 2024: 3 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.71429 | 0.6 | 1 | 0.6 | Vegetation¦Treefellintoline¦Fuse¦Broken | Vegetation | Tree - fell into line | Fuse | Broken | FNLYEAR 2017: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 3 | 6
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Fuse¦BurnedOpen | Vegetation | Tree - fell into line | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.52 | 0.52 | 1.8571 | 1.3 | 2.4 | 1.3 | Vegetation¦Treefellintoline¦Fuse¦BurnedOpen | Vegetation | Tree - fell into line | Fuse | Burned Open | FNLYEAR 2018: 1; FNLYEAR 2020: 2; FNLYEAR 2021: 3; FNLYEAR 2022: 3; FNLYEAR 2023: 4 | 13
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | FNLYEAR 2024: 3 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 7.72 | 7.72 | 11.7143 | 19.3 | 3.6 | 19.3 | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 16 | 34 | 61 | 27 | 37 | 13 | 1 | 2 | 2 |  | 193
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treefellintoline¦Fuse¦Normal | Vegetation | Tree - fell into line | Fuse | Normal | FNLYEAR 2024: 4 | 4
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 1.04 | 1.04 | 1.7143 | 2.6 | 1.4 | 2.6 | Vegetation¦Treefellintoline¦Fuse¦Normal | Vegetation | Tree - fell into line | Fuse | Normal | 4 | 5 | 5 | 3 | 2 |  | 2 | 2 | 3 |  | 26
Vegetation (Trunk) | None | 0% | 0 | 0 | Very High | 90% | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Insulator¦Broken | Vegetation | Tree - fell into line | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Very High | 90% | 4.77 | 4.77 | 4.5714 | 5.3 | 3.6 | 5.3 | Vegetation¦Treefellintoline¦Insulator¦Broken | Vegetation | Tree - fell into line | Insulator | Broken | 8 | 4 | 9 | 3 | 11 | 5 | 8 | 3 | 2 |  | 53
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.28571 | 0.4 | 0.2 | 0.4 | Vegetation¦Treefellintoline¦Insulator¦Brokenwireonground | Vegetation | Tree - fell into line | Insulator | Broken, wire on ground | FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2021: 1 | 4
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.28571 | 0.4 | 0 | 0.4 | Vegetation¦Treefellintoline¦Insulator¦Brokenwireonobject | Vegetation | Tree - fell into line | Insulator | Broken, wire on object | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2019
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Insulator¦Normal | Vegetation | Tree - fell into line | Insulator | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Jumper¦Broken | Vegetation | Tree - fell into line | Jumper | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.32 | 0.32 | 0.85714 | 0.8 | 1 | 0.8 | Vegetation¦Treefellintoline¦Jumper¦Broken | Vegetation | Tree - fell into line | Jumper | Broken | FNLYEAR 2015: 2; FNLYEAR 2019: 1; FNLYEAR 2021: 1; FNLYEAR 2022: 2; FNLYEAR 2023: 2 | 8
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Jumper¦Burnedflashed | Vegetation | Tree - fell into line | Jumper | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.28 | 0.28 | 0.57143 | 0.7 | 0.2 | 0.7 | Vegetation¦Treefellintoline¦Jumper¦BurnedOpen | Vegetation | Tree - fell into line | Jumper | Burned Open | 1 | 1 | 1 | 1 | 2 |  |  | 1 |  |  | 7
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treefellintoline¦Jumper¦Normal | Vegetation | Tree - fell into line | Jumper | Normal | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2023
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦LightningArrestor¦Brokenwireonground | Vegetation | Tree - fell into line | Lightning Arrestor | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦LightningArrestor¦Burnedflashed | Vegetation | Tree - fell into line | Lightning Arrestor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦LightningArrestor¦FailedFaulted | Vegetation | Tree - fell into line | Lightning Arrestor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦MeteringEquipment¦FailedFaulted | Vegetation | Tree - fell into line | Metering Equipment | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦Other¦Arcing | Vegetation | Tree - fell into line | Other | Arcing | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦Other¦Broken | Vegetation | Tree - fell into line | Other | Broken | 2 |  | 1 | 3 |  | 2 | 3 |  | 2 |  | 13
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦Other¦Brokenwireonground | Vegetation | Tree - fell into line | Other | Broken, wire on ground | [10 empty] | 4 | bar: FNLYEAR 2015; FNLYEAR 2019; FNLYEAR 2022 to FNLYEAR 2023
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦Other¦Normal | Vegetation | Tree - fell into line | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦Other¦Normal | Vegetation | Tree - fell into line | Other | Normal | FNLYEAR 2016: 1; FNLYEAR 2019: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 2 | 5
Vegetation (Trunk) | N/A | 0% | 0 | 0 | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treefellintoline¦Other¦Together | Vegetation | Tree - fell into line | Other | Together | [10 empty] | 1 | bar: FNLYEAR 2016
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0 | 0.2 | Vegetation¦Treefellintoline¦PoleTowersteel¦Burnedflashed | Vegetation | Tree - fell into line | Pole - Tower, steel | Burned/flashed | FNLYEAR 2019: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦PoleTowersteel¦Normal | Vegetation | Tree - fell into line | Pole - Tower, steel | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.76 | 0.76 | 2.7143 | 1.9 | 3.8 | 1.9 | Vegetation¦Treefellintoline¦PoleWood¦Broken | Vegetation | Tree - fell into line | Pole-Wood | Broken | FNLYEAR 2024: 19 | 19
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 17.72 | 17.72 | 41.1429 | 44.3 | 34.2 | 44.3 | Vegetation¦Treefellintoline¦PoleWood¦Broken | Vegetation | Tree - fell into line | Pole-Wood | Broken | 27 | 42 | 86 | 30 | 87 | 44 | 72 | 33 | 22 |  | 443
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 1.12 | 1.12 | 4 | 2.8 | 5.6 | 2.8 | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground | Vegetation | Tree - fell into line | Pole-Wood | Broken- wire on ground | FNLYEAR 2024: 28 | 28
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 42.8 | 42.8 | 102.4286 | 107 | 83.4 | 107 | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 58 | 84 | 211 | 48 | 252 | 103 | 203 | 64 | 47 |  | 1070
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.56 | 0.56 | 1.2857 | 1.4 | 0.8 | 1.4 | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonobject | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on object |  | 1 | 4 | 1 | 4 | 1 | 3 |  |  |  | 14
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦PoleWood¦Burnedflashed | Vegetation | Tree - fell into line | Pole-Wood | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.42857 | 0.5 | 0.6 | 0.5 | Vegetation¦Treefellintoline¦PoleWood¦Deteriorated | Vegetation | Tree - fell into line | Pole-Wood | Deteriorated | FNLYEAR 2017: 2; FNLYEAR 2023: 3 | 5
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦PoleWood¦Normal | Vegetation | Tree - fell into line | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.76 | 0.76 | 2.1429 | 1.9 | 2.2 | 1.9 | Vegetation¦Treefellintoline¦PoleWood¦Normal | Vegetation | Tree - fell into line | Pole-Wood | Normal |  | 1 | 3 | 1 | 3 | 4 | 4 | 1 | 2 |  | 19
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦PoleWood¦OnGround | Vegetation | Tree - fell into line | Pole-Wood | On Ground | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.14286 | 0.3 | 0.2 | 0.3 | Vegetation¦Treefellintoline¦PoleWood¦OnGround | Vegetation | Tree - fell into line | Pole-Wood | On Ground | FNLYEAR 2016: 2; FNLYEAR 2022: 1 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦PoleWood¦Together | Vegetation | Tree - fell into line | Pole-Wood | Together | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Recloser¦Arcing | Vegetation | Tree - fell into line | Recloser | Arcing | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Recloser¦Burnedflashed | Vegetation | Tree - fell into line | Recloser | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0 | 0.3 | Vegetation¦Treefellintoline¦Recloser¦Normal | Vegetation | Tree - fell into line | Recloser | Normal | FNLYEAR 2015: 1; FNLYEAR 2018: 2 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treefellintoline¦Secondary¦Arcing | Vegetation | Tree - fell into line | Secondary | Arcing | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2023
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 0.85714 | 1.1 | 0.4 | 1.1 | Vegetation¦Treefellintoline¦Secondary¦BentorTwisted | Vegetation | Tree - fell into line | Secondary | Bent or Twisted | 2 | 2 | 1 | 1 | 3 |  | 1 |  | 1 |  | 11
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.16 | 0.16 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treefellintoline¦Secondary¦Broken | Vegetation | Tree - fell into line | Secondary | Broken | FNLYEAR 2024: 4 | 4
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 3 | 3 | 8.2857 | 7.5 | 9.4 | 7.5 | Vegetation¦Treefellintoline¦Secondary¦Broken | Vegetation | Tree - fell into line | Secondary | Broken | 3 | 6 | 8 | 6 | 5 | 10 | 21 | 6 | 10 |  | 75
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.48 | 0.48 | 1.7143 | 1.2 | 2.4 | 1.2 | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground | Vegetation | Tree - fell into line | Secondary | Broken- wire on ground | FNLYEAR 2024: 12 | 12
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 5.04 | 5.04 | 11.7143 | 12.6 | 10.2 | 12.6 | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 15 | 14 | 15 | 9 | 22 | 8 | 15 | 14 | 14 |  | 126
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.24 | 0.24 | 0.57143 | 0.6 | 0.4 | 0.6 | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonobject | Vegetation | Tree - fell into line | Secondary | Broken, wire on object | [10 empty] | 6 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2018 to FNLYEAR 2020; FNLYEAR 2022
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦Secondary¦Burnedflashed | Vegetation | Tree - fell into line | Secondary | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.36 | 0.36 | 1.2857 | 0.9 | 1.8 | 0.9 | Vegetation¦Treefellintoline¦Secondary¦Normal | Vegetation | Tree - fell into line | Secondary | Normal | FNLYEAR 2024: 9 | 9
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 1.8 | 1.8 | 4.4286 | 4.5 | 4.4 | 4.5 | Vegetation¦Treefellintoline¦Secondary¦Normal | Vegetation | Tree - fell into line | Secondary | Normal | 2 | 7 | 5 | 4 | 5 | 7 | 4 | 9 | 2 |  | 45
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.57143 | 0.5 | 0.4 | 0.5 | Vegetation¦Treefellintoline¦Secondary¦OnGround | Vegetation | Tree - fell into line | Secondary | On Ground | FNLYEAR 2017: 1; FNLYEAR 2018: 2; FNLYEAR 2020: 1; FNLYEAR 2023: 1 | 5
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Secondary¦Together | Vegetation | Tree - fell into line | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.6 | 0.6 | 1.2857 | 1.5 | 1.6 | 1.5 | Vegetation¦Treefellintoline¦Secondary¦Together | Vegetation | Tree - fell into line | Secondary | Together | 3 | 1 | 2 |  | 1 | 1 | 5 | 2 |  |  | 15
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Sectionalizer¦Normal | Vegetation | Tree - fell into line | Sectionalizer | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦Serviceconductor¦BentorTwisted | Vegetation | Tree - fell into line | Service conductor | Bent or Twisted | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.42857 | 0.5 | 0.4 | 0.5 | Vegetation¦Treefellintoline¦Serviceconductor¦BentorTwisted | Vegetation | Tree - fell into line | Service conductor | Bent or Twisted | [10 empty] | 5 | bar: FNLYEAR 2015 to FNLYEAR 2016; FNLYEAR 2019; FNLYEAR 2021 to FNLYEAR 2022
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treefellintoline¦Serviceconductor¦Broken | Vegetation | Tree - fell into line | Service conductor | Broken | FNLYEAR 2024: 3 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 3.04 | 3.04 | 7.5714 | 7.6 | 6.6 | 7.6 | Vegetation¦Treefellintoline¦Serviceconductor¦Broken | Vegetation | Tree - fell into line | Service conductor | Broken | 2 | 13 | 8 | 8 | 12 | 10 | 9 | 7 | 7 |  | 76
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 1.5714 | 1.1 | 2.2 | 1.1 | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground | Vegetation | Tree - fell into line | Service conductor | Broken- wire on ground | FNLYEAR 2024: 11 | 11
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 5.64 | 5.64 | 14.7143 | 14.1 | 13.2 | 14.1 | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 3 | 17 | 18 | 11 | 26 | 7 | 26 | 18 | 15 |  | 141
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonobject | Vegetation | Tree - fell into line | Service conductor | Broken- wire on object | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.44 | 0.44 | 1.1429 | 1.1 | 1.2 | 1.1 | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonobject | Vegetation | Tree - fell into line | Service conductor | Broken, wire on object | 1 |  | 2 | 1 | 1 | 1 | 3 | 1 | 1 |  | 11
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Serviceconductor¦BurnedOpen | Vegetation | Tree - fell into line | Service conductor | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treefellintoline¦Serviceconductor¦Deteriorated | Vegetation | Tree - fell into line | Service conductor | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2019
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Serviceconductor¦FailedFaulted | Vegetation | Tree - fell into line | Service conductor | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦Serviceconductor¦Normal | Vegetation | Tree - fell into line | Service conductor | Normal | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.4 | 0.4 | 1.1429 | 1 | 1.2 | 1 | Vegetation¦Treefellintoline¦Serviceconductor¦Normal | Vegetation | Tree - fell into line | Service conductor | Normal | 1 | 1 |  | 2 |  |  | 3 | 1 | 2 |  | 10
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.12 | 0.12 | 0.28571 | 0.3 | 0.4 | 0.3 | Vegetation¦Treefellintoline¦Serviceconductor¦OnGround | Vegetation | Tree - fell into line | Service conductor | On Ground | FNLYEAR 2017: 1; FNLYEAR 2021: 2 | 3
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Serviceconductor¦Together | Vegetation | Tree - fell into line | Service conductor | Together | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Switch(OH)¦Broken | Vegetation | Tree - fell into line | Switch (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦Switch(OH)¦Normal | Vegetation | Tree - fell into line | Switch (OH) | Normal | [10 empty] | 2 | bar: FNLYEAR 2021; FNLYEAR 2023
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Switch(UG)¦Broken | Vegetation | Tree - fell into line | Switch (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(OH)¦ | Vegetation | Tree - fell into line | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treefellintoline¦Transformer(OH)¦ | Vegetation | Tree - fell into line | Transformer (OH) |  | FNLYEAR 2022: 1; FNLYEAR 2023: 3 | 4
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.56 | 0.56 | 2 | 1.4 | 2.8 | 1.4 | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken | Vegetation | Tree - fell into line | Transformer (OH) | Broken | FNLYEAR 2024: 14 | 14
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 2.56 | 2.56 | 6.7143 | 6.4 | 7.2 | 6.4 | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2 | 4 | 11 | 2 | 9 | 7 | 19 | 6 | 4 |  | 64
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.2 | 0.2 | 0.71429 | 0.5 | 1 | 0.5 | Vegetation¦Treefellintoline¦Transformer(OH)¦Brokenwireonground | Vegetation | Tree - fell into line | Transformer (OH) | Broken- wire on ground | FNLYEAR 2024: 5 | 5
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 1.2 | 1.2 | 3.8571 | 3 | 5.2 | 3 | Vegetation¦Treefellintoline¦Transformer(OH)¦Brokenwireonground | Vegetation | Tree - fell into line | Transformer (OH) | Broken, wire on ground | 1 |  | 2 |  | 1 |  | 8 | 6 | 12 |  | 30
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treefellintoline¦Transformer(OH)¦Burnedflashed | Vegetation | Tree - fell into line | Transformer (OH) | Burned/flashed | [10 empty] | 2 | bar: FNLYEAR 2017; FNLYEAR 2021
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(OH)¦Deteriorated | Vegetation | Tree - fell into line | Transformer (OH) | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 0.57143 | 0.4 | 0.8 | 0.4 | Vegetation¦Treefellintoline¦Transformer(OH)¦FailedFaulted | Vegetation | Tree - fell into line | Transformer (OH) | Failed/Faulted | FNLYEAR 2024: 4 | 4
Vegetation (Trunk) | None | 0% | 0 | 0 | None | 0% | 0 | 0 | 2.7143 | 2 | 3.6 | 2 | Vegetation¦Treefellintoline¦Transformer(OH)¦FailedFaulted | Vegetation | Tree - fell into line | Transformer (OH) | Failed/Faulted |  |  | 1 |  | 1 | 4 | 3 | 6 | 5 |  | 20
Vegetation (Trunk) | None | 0% | 0 | 0 | Medium | 40% | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(OH)¦Leaking | Vegetation | Tree - fell into line | Transformer (OH) | Leaking | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.28 | 0.28 | 0.71429 | 0.7 | 1 | 0.7 | Vegetation¦Treefellintoline¦Transformer(OH)¦Leaking | Vegetation | Tree - fell into line | Transformer (OH) | Leaking | FNLYEAR 2016: 1; FNLYEAR 2017: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 1; FNLYEAR 2023: 3 | 7
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(OH)¦Normal | Vegetation | Tree - fell into line | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.56 | 0.56 | 1.7143 | 1.4 | 2 | 1.4 | Vegetation¦Treefellintoline¦Transformer(OH)¦Normal | Vegetation | Tree - fell into line | Transformer (OH) | Normal |  |  | 2 |  | 2 | 2 | 6 | 1 | 1 |  | 14
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.12 | 0.12 | 0.28571 | 0.3 | 0.2 | 0.3 | Vegetation¦Treefellintoline¦Transformer(OH)¦OnGround | Vegetation | Tree - fell into line | Transformer (OH) | On Ground | [10 empty] | 3 | bar: FNLYEAR 2017; FNLYEAR 2019; FNLYEAR 2022
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(UG)¦Broken | Vegetation | Tree - fell into line | Transformer (UG) | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(UG)¦Brokenwireonground | Vegetation | Tree - fell into line | Transformer (UG) | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(UG)¦Contaminated | Vegetation | Tree - fell into line | Transformer (UG) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer(UG)¦FailedFaulted | Vegetation | Tree - fell into line | Transformer (UG) | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treefellintoline¦Transformer(UG)¦Normal | Vegetation | Tree - fell into line | Transformer (UG) | Normal | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2019
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.2 | 0 | 0.2 | Vegetation¦Treefellintoline¦Transformer¦ | Vegetation | Tree - fell into line | Transformer | [11 empty] | 2 | bar: FNLYEAR 2017 to FNLYEAR 2018
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.16 | 0.16 | 0.28571 | 0.4 | 0.2 | 0.4 | Vegetation¦Treefellintoline¦Transformer¦Arcing | Vegetation | Tree - fell into line | Transformer | Arcing | [10 empty] | 4 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019; FNLYEAR 2023
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.32 | 0.32 | 1.1429 | 0.8 | 1.2 | 0.8 | Vegetation¦Treefellintoline¦Transformer¦BentorTwisted | Vegetation | Tree - fell into line | Transformer | Bent or Twisted | FNLYEAR 2019: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 3; FNLYEAR 2023: 2 | 8
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.08 | 0.08 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦Transformer¦Broken | Vegetation | Tree - fell into line | Transformer | Broken | FNLYEAR 2024: 2 | 2
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 3.16 | 3.16 | 7.1429 | 7.9 | 6.8 | 7.9 | Vegetation¦Treefellintoline¦Transformer¦Broken | Vegetation | Tree - fell into line | Transformer | Broken | 4 | 3 | 22 | 1 | 15 | 5 | 15 | 8 | 6 |  | 79
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.24 | 0.24 | 0.85714 | 0.6 | 1.2 | 0.6 | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground | Vegetation | Tree - fell into line | Transformer | Broken- wire on ground | FNLYEAR 2024: 6 | 6
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 5.68 | 5.68 | 13.4286 | 14.2 | 9.6 | 14.2 | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 6 | 21 | 21 | 12 | 34 | 18 | 18 | 8 | 4 |  | 142
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.2 | 0.2 | 0.42857 | 0.5 | 0 | 0.5 | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonobject | Vegetation | Tree - fell into line | Transformer | Broken, wire on object | FNLYEAR 2017: 2; FNLYEAR 2019: 3 | 5
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.2 | 0.2 | 0.28571 | 0.5 | 0.2 | 0.5 | Vegetation¦Treefellintoline¦Transformer¦Burnedflashed | Vegetation | Tree - fell into line | Transformer | Burned/flashed | FNLYEAR 2015: 2; FNLYEAR 2016: 1; FNLYEAR 2018: 1; FNLYEAR 2020: 1 | 5
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | Vegetation¦Treefellintoline¦Transformer¦Contaminated | Vegetation | Tree - fell into line | Transformer | Contaminated | [10 empty] | 2 | bar: FNLYEAR 2022 to FNLYEAR 2023
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer¦Deteriorated | Vegetation | Tree - fell into line | Transformer | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.24 | 0.24 | 0.14286 | 0.6 | 0 | 0.6 | Vegetation¦Treefellintoline¦Transformer¦Deteriorated | Vegetation | Tree - fell into line | Transformer | Deteriorated | FNLYEAR 2015: 2; FNLYEAR 2016: 1; FNLYEAR 2017: 2; FNLYEAR 2019: 1 | 6
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer¦FailedFaulted | Vegetation | Tree - fell into line | Transformer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 2.4286 | 2.8 | 2 | 2.8 | Vegetation¦Treefellintoline¦Transformer¦FailedFaulted | Vegetation | Tree - fell into line | Transformer | Failed/Faulted |  | 3 | 8 | 3 | 4 | 4 | 3 |  | 3 |  | 28
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.92 | 0.92 | 2.1429 | 2.3 | 1.6 | 2.3 | Vegetation¦Treefellintoline¦Transformer¦Leaking | Vegetation | Tree - fell into line | Transformer | Leaking | 1 | 3 | 4 | 2 | 5 | 4 | 1 | 3 |  |  | 23
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treefellintoline¦Transformer¦Malfunctioning | Vegetation | Tree - fell into line | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Transformer¦Malfunctioning | Vegetation | Tree - fell into line | Transformer | Malfunctioning | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.48 | 0.48 | 0.85714 | 1.2 | 0.8 | 1.2 | Vegetation¦Treefellintoline¦Transformer¦Normal | Vegetation | Tree - fell into line | Transformer | Normal | 1 | 2 | 3 | 1 | 1 |  | 2 | 1 | 1 |  | 12
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.28 | 0.28 | 0.28571 | 0.7 | 0.4 | 0.7 | Vegetation¦Treefellintoline¦Transformer¦OnGround | Vegetation | Tree - fell into line | Transformer | On Ground | FNLYEAR 2015: 2; FNLYEAR 2016: 2; FNLYEAR 2017: 1; FNLYEAR 2020: 1; FNLYEAR 2022: 1 | 7
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.08 | 0.08 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treefellintoline¦Transformer¦Together | Vegetation | Tree - fell into line | Transformer | Together | [10 empty] | 2 | bar: FNLYEAR 2016; FNLYEAR 2021
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.16 | 0.16 | 0.42857 | 0.4 | 0.2 | 0.4 | Vegetation¦Treefellintoline¦Woodpin¦Broken | Vegetation | Tree - fell into line | Woodpin | Broken | FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 1 | 4
Vegetation (Trunk) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treefellintoline¦Woodpin¦Normal | Vegetation | Tree - fell into line | Woodpin | Normal | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0 | 0 | 0 | Medium High | 0.6 | 0.06 | 0.06 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦AnchororGuy¦BentorTwisted | Vegetation | Tree - grew into line | Anchor or Guy | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦AnchororGuy¦Broken | Vegetation | Tree - grew into line | Anchor or Guy | Broken | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (other) | None | 0 | 0 | 0 | Medium High | 0.6 | 0.06 | 0.06 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦AnchororGuy¦Deteriorated | Vegetation | Tree - grew into line | Anchor or Guy | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦CircuitBreaker¦Normal | Vegetation | Tree - grew into line | Circuit Breaker | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Arcing | Vegetation | Tree - grew into line | Conductor- Overhead | Arcing | FNLYEAR 2024: 3 | 3
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 1.17 | 1.17 | 1.5714 | 1.3 | 1.2 | 1.3 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Arcing | Vegetation | Tree - grew into line | Conductor, Overhead | Arcing |  | 2 |  |  | 5 | 2 | 1 | 1 | 2 |  | 13
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.27 | 0.27 | 0.28571 | 0.3 | 0.2 | 0.3 | Vegetation¦Treegrewintoline¦ConductorOverhead¦BentorTwisted | Vegetation | Tree - grew into line | Conductor, Overhead | Bent or Twisted | [10 empty] | 3 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2023
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Broken | Vegetation | Tree - grew into line | Conductor- Overhead | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.63 | 0.63 | 0.42857 | 0.7 | 0.6 | 0.7 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Broken | Vegetation | Tree - grew into line | Conductor, Overhead | Broken | FNLYEAR 2015: 2; FNLYEAR 2016: 2; FNLYEAR 2020: 1; FNLYEAR 2021: 2 | 7
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.68 | 0.68 | 1.8571 | 1.7 | 1.6 | 1.7 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - grew into line | Conductor, Overhead | Broken, wire on ground | 1 | 1 | 2 | 1 | 4 | 2 | 4 | 2 |  |  | 17
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Brokenwireonobject | Vegetation | Tree - grew into line | Conductor, Overhead | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2020
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.63 | 0.63 | 0.28571 | 0.7 | 0.2 | 0.7 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Burnedflashed | Vegetation | Tree - grew into line | Conductor, Overhead | Burned/flashed | FNLYEAR 2015: 2; FNLYEAR 2017: 3; FNLYEAR 2019: 1; FNLYEAR 2021: 1 | 7
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.27 | 0.27 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Contaminated | Vegetation | Tree - grew into line | Conductor- Overhead | Contaminated | FNLYEAR 2024: 3 | 3
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.45 | 0.45 | 0.71429 | 0.5 | 1 | 0.5 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Contaminated | Vegetation | Tree - grew into line | Conductor, Overhead | Contaminated | FNLYEAR 2020: 1; FNLYEAR 2021: 2; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 5
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.18 | 0.18 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Deteriorated | Vegetation | Tree - grew into line | Conductor, Overhead | Deteriorated | [10 empty] | 2 | bar: FNLYEAR 2019; FNLYEAR 2022
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 5.67 | 5.67 | 9 | 6.3 | 12.6 | 6.3 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal | Vegetation | Tree - grew into line | Conductor- Overhead | Normal | FNLYEAR 2024: 63 | 63
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 31.68 | 31.68 | 44.5714 | 35.2 | 46.6 | 35.2 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 12 | 7 | 21 | 19 | 60 | 54 | 42 | 62 | 75 |  | 352
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together | Vegetation | Tree - grew into line | Conductor- Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 2.43 | 2.43 | 2.4286 | 2.7 | 2 | 2.7 | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together | Vegetation | Tree - grew into line | Conductor, Overhead | Together |  | 3 | 7 | 6 | 1 | 4 | 5 | 1 |  |  | 27
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦CrossarmWood¦Broken | Vegetation | Tree - grew into line | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.18 | 0.18 | 0.28571 | 0.2 | 0 | 0.2 | Vegetation¦Treegrewintoline¦CrossarmWood¦Burnedflashed | Vegetation | Tree - grew into line | Crossarm, Wood | Burned/flashed | FNLYEAR 2018: 2 | 2
Vegetation (other) | None | 0 | 0 | 0 | Medium High | 0.6 | 0.06 | 0.06 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦Fuse¦BurnedOpen | Vegetation | Tree - grew into line | Fuse | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (other) | None | 0 | 0 | 0 | Medium High | 0.6 | 0.48 | 0.48 | 1 | 0.8 | 0.2 | 0.8 | Vegetation¦Treegrewintoline¦Fuse¦FailedFaulted | Vegetation | Tree - grew into line | Fuse | Failed/Faulted | FNLYEAR 2015: 1; FNLYEAR 2018: 1; FNLYEAR 2019: 5; FNLYEAR 2022: 1 | 8
Vegetation (other) | None | 0 | 0 | 0 | Very High | 0.9 | 0.54 | 0.54 | 0.57143 | 0.6 | 0.4 | 0.6 | Vegetation¦Treegrewintoline¦Fuse¦Normal | Vegetation | Tree - grew into line | Fuse | Normal | [10 empty] | 6 | bar: FNLYEAR 2016 to FNLYEAR 2021
Vegetation (other) | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treegrewintoline¦Other¦Normal | Vegetation | Tree - grew into line | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.14 | 0.14 | 0.28571 | 0.2 | 0.2 | 0.2 | Vegetation¦Treegrewintoline¦PoleWood¦Broken | Vegetation | Tree - grew into line | Pole-Wood | Broken | [10 empty] | 2 | bar: FNLYEAR 2018; FNLYEAR 2021
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦PoleWood¦Brokenwireonground | Vegetation | Tree - grew into line | Pole-Wood | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦PoleWood¦Brokenwireonground | Vegetation | Tree - grew into line | Pole-Wood | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦PoleWood¦Normal | Vegetation | Tree - grew into line | Pole-Wood | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.49 | 0.49 | 0.42857 | 0.7 | 0.2 | 0.7 | Vegetation¦Treegrewintoline¦Secondary¦Arcing | Vegetation | Tree - grew into line | Secondary | Arcing | FNLYEAR 2015: 1; FNLYEAR 2016: 3; FNLYEAR 2019: 2; FNLYEAR 2020: 1 | 7
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Secondary¦BentorTwisted | Vegetation | Tree - grew into line | Secondary | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.16 | 0.16 | 0.57143 | 0.4 | 0.6 | 0.4 | Vegetation¦Treegrewintoline¦Secondary¦Broken | Vegetation | Tree - grew into line | Secondary | Broken | [10 empty] | 4 | bar: FNLYEAR 2019 to FNLYEAR 2022
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.24 | 0.24 | 0.28571 | 0.6 | 0 | 0.6 | Vegetation¦Treegrewintoline¦Secondary¦Brokenwireonground | Vegetation | Tree - grew into line | Secondary | Broken, wire on ground | FNLYEAR 2016: 2; FNLYEAR 2017: 2; FNLYEAR 2018: 1; FNLYEAR 2019: 1 | 6
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.21 | 0.21 | 0.28571 | 0.3 | 0 | 0.3 | Vegetation¦Treegrewintoline¦Secondary¦Burnedflashed | Vegetation | Tree - grew into line | Secondary | Burned/flashed | FNLYEAR 2016: 1; FNLYEAR 2018: 2 | 3
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.21 | 0.21 | 0.42857 | 0.3 | 0.6 | 0.3 | Vegetation¦Treegrewintoline¦Secondary¦Normal | Vegetation | Tree - grew into line | Secondary | Normal | FNLYEAR 2024: 3 | 3
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 1.12 | 1.12 | 2 | 1.6 | 2.4 | 1.6 | Vegetation¦Treegrewintoline¦Secondary¦Normal | Vegetation | Tree - grew into line | Secondary | Normal |  | 2 |  |  | 2 | 3 | 3 | 4 | 2 |  | 16
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.08 | 0.08 | 0 | 0.2 | 0 | 0.2 | Vegetation¦Treegrewintoline¦Secondary¦OnGround | Vegetation | Tree - grew into line | Secondary | On Ground | [10 empty] | 2 | bar: FNLYEAR 2016 to FNLYEAR 2017
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.28 | 0.28 | 0.42857 | 0.4 | 0.2 | 0.4 | Vegetation¦Treegrewintoline¦Secondary¦Together | Vegetation | Tree - grew into line | Secondary | Together | FNLYEAR 2016: 1; FNLYEAR 2018: 2; FNLYEAR 2023: 1 | 4
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦Serviceconductor¦Broken | Vegetation | Tree - grew into line | Service conductor | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.16 | 0.16 | 0.42857 | 0.4 | 0.4 | 0.4 | Vegetation¦Treegrewintoline¦Serviceconductor¦Broken | Vegetation | Tree - grew into line | Service conductor | Broken | [10 empty] | 4 | bar: FNLYEAR 2017 to FNLYEAR 2018; FNLYEAR 2021; FNLYEAR 2023
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Serviceconductor¦Brokenwireonground | Vegetation | Tree - grew into line | Service conductor | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Serviceconductor¦Burnedflashed | Vegetation | Tree - grew into line | Service conductor | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Serviceconductor¦BurnedOpen | Vegetation | Tree - grew into line | Service conductor | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Serviceconductor¦Normal | Vegetation | Tree - grew into line | Service conductor | Normal | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Transformer(OH)¦Broken | Vegetation | Tree - grew into line | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦Transformer(OH)¦Contaminated | Vegetation | Tree - grew into line | Transformer (OH) | Contaminated | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦Transformer(OH)¦Normal | Vegetation | Tree - grew into line | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.56 | 0.56 | 1 | 0.8 | 1 | 0.8 | Vegetation¦Treegrewintoline¦Transformer(OH)¦Normal | Vegetation | Tree - grew into line | Transformer (OH) | Normal | FNLYEAR 2017: 1; FNLYEAR 2019: 2; FNLYEAR 2021: 3; FNLYEAR 2022: 1; FNLYEAR 2023: 1 | 8
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Transformer¦Annealed | Vegetation | Tree - grew into line | Transformer | Annealed | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.21 | 0.21 | 0.14286 | 0.3 | 0.2 | 0.3 | Vegetation¦Treegrewintoline¦Transformer¦Arcing | Vegetation | Tree - grew into line | Transformer | Arcing | FNLYEAR 2015: 2; FNLYEAR 2021: 1 | 3
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Transformer¦BentorTwisted | Vegetation | Tree - grew into line | Transformer | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.28 | 0.28 | 0.57143 | 0.4 | 0.4 | 0.4 | Vegetation¦Treegrewintoline¦Transformer¦Broken | Vegetation | Tree - grew into line | Transformer | Broken | [10 empty] | 4 | bar: FNLYEAR 2018 to FNLYEAR 2019; FNLYEAR 2021 to FNLYEAR 2022
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦Transformer¦Brokenwireonground | Vegetation | Tree - grew into line | Transformer | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.24 | 0.24 | 0.28571 | 0.6 | 0.2 | 0.6 | Vegetation¦Treegrewintoline¦Transformer¦Brokenwireonground | Vegetation | Tree - grew into line | Transformer | Broken, wire on ground | FNLYEAR 2015: 2; FNLYEAR 2016: 2; FNLYEAR 2018: 1; FNLYEAR 2021: 1 | 6
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Transformer¦Brokenwireonobject | Vegetation | Tree - grew into line | Transformer | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treegrewintoline¦Transformer¦Burnedflashed | Vegetation | Tree - grew into line | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2023
Vegetation (other) | None | 0 | 0 | 0 | Medium High | 0.6 | 0.06 | 0.06 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Transformer¦FailedFaulted | Vegetation | Tree - grew into line | Transformer | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.21 | 0.21 | 0.28571 | 0.3 | 0.4 | 0.3 | Vegetation¦Treegrewintoline¦Transformer¦Normal | Vegetation | Tree - grew into line | Transformer | Normal | [10 empty] | 3 | bar: FNLYEAR 2016; FNLYEAR 2021 to FNLYEAR 2022
Vegetation (other) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treegrewintoline¦Transformer¦OnGround | Vegetation | Tree - grew into line | Transformer | On Ground | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (other) | None | 0 | 0 | 0 | High | 0.7 | 0.14 | 0.14 | 0.14286 | 0.2 | 0.2 | 0.2 | Vegetation¦Treegrewintoline¦Transformer¦Together | Vegetation | Tree - grew into line | Transformer | Together | [10 empty] | 2 | bar: FNLYEAR 2015; FNLYEAR 2020
Vegetation (Branch) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦BentorTwisted | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Bent or Twisted | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Brokenwireonground | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2019
Vegetation (Branch) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Normal | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Vegetation (Branch) | None | 0 | 0 | 0 | Very High | 0.9 | 2.07 | 2.07 | 2.5714 | 2.3 | 3.2 | 2.3 | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Normal | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Normal | 1 | 2 | 2 |  | 2 | 2 | 4 | 5 | 5 |  | 23
Vegetation (Branch) | None | 0 | 0 | 0 | Very High | 0.9 | 0.18 | 0.18 | 0 | 0.2 | 0 | 0.2 | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Together | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Together | FNLYEAR 2017: 2 | 2
Vegetation (Branch) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦CrossarmWood¦Broken | Vegetation | Tree - palm frond fell into line | Crossarm, Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Branch) | None | 0 | 0 | 0 | Very High | 0.9 | 0.27 | 0.27 | 0.14286 | 0.3 | 0 | 0.3 | Vegetation¦Treepalmfrondfellintoline¦Fuse¦FailedFaulted | Vegetation | Tree - palm frond fell into line | Fuse | Failed/Faulted | [10 empty] | 3 | bar: FNLYEAR 2016 to FNLYEAR 2017; FNLYEAR 2019
Vegetation (Branch) | None | 0 | 0 | 0 | Very High | 0.9 | 0.09 | 0.09 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦Fuse¦Normal | Vegetation | Tree - palm frond fell into line | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2021
Vegetation (Branch) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦Jumper¦BurnedOpen | Vegetation | Tree - palm frond fell into line | Jumper | Burned Open | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vegetation¦Treepalmfrondfellintoline¦Other¦FailedFaulted | Vegetation | Tree - palm frond fell into line | Other | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦Recloser¦Normal | Vegetation | Tree - palm frond fell into line | Recloser | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Branch) | None | 0 | 0 | 0 | Medium | 0.4 | 0.04 | 0.04 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦Serviceconductor¦Brokenwireonground | Vegetation | Tree - palm frond fell into line | Service conductor | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2017
Vegetation (Branch) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦Transformer(OH)¦Broken | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2022
Vegetation (Branch) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0 | 0.1 | 0 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦Transformer¦Burnedflashed | Vegetation | Tree - palm frond fell into line | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2015
Vegetation (Branch) | None | 0 | 0 | 0 | High | 0.7 | 0.07 | 0.07 | 0.14286 | 0.1 | 0.2 | 0.1 | Vegetation¦Treepalmfrondfellintoline¦Transformer¦Normal | Vegetation | Tree - palm frond fell into line | Transformer | Normal | [10 empty] | 1 | bar: FNLYEAR 2022
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦CWSPVegetationRemoval¦¦ | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | FNLYEAR 2018: 53; FNLYEAR 2020: 1 | 54
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Annealed | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Annealed | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 4.2857 | 3 | 3 | 3 | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal |  |  |  | 2 | 13 | 6 | 6 | 2 | 1 |  | 30
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦Fuse¦Normal | Wildfire Mitigation | CWSP - Vegetation Removal | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦Other¦Normal | Wildfire Mitigation | CWSP - Vegetation Removal | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦PoleWood¦Broken | Wildfire Mitigation | CWSP - Vegetation Removal | Pole-Wood | Broken | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦PoleWood¦Deteriorated | Wildfire Mitigation | CWSP - Vegetation Removal | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦Secondary¦Annealed | Wildfire Mitigation | CWSP - Vegetation Removal | Secondary | Annealed | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦Secondary¦Normal | Wildfire Mitigation | CWSP - Vegetation Removal | Secondary | Normal | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦Transformer(OH)¦Normal | Wildfire Mitigation | CWSP - Vegetation Removal | Transformer (OH) | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦CWSPVegetationRemoval¦Transformer¦Burnedflashed | Wildfire Mitigation | CWSP - Vegetation Removal | Transformer | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PlannedWSIPSystemHardening¦¦ | Wildfire Mitigation | Planned - WSIP/System Hardening |  |  | FNLYEAR 2024: 7664 | 7664
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PlannedWSIPSystemHardening¦Bushing¦FailedFaulted | Wildfire Mitigation | Planned - WSIP/System Hardening | Bushing | Failed/Faulted | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PlannedWSIPSystemHardening¦ConductorOverhead¦Normal | Wildfire Mitigation | Planned - WSIP/System Hardening | Conductor- Overhead | Normal | FNLYEAR 2024: 6 | 6
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PlannedWSIPSystemHardening¦Other¦Normal | Wildfire Mitigation | Planned - WSIP/System Hardening | Other | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PlannedWSIPSystemHardening¦PoleWood¦Deteriorated | Wildfire Mitigation | Planned - WSIP/System Hardening | Pole-Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PlannedWSIPSystemHardening¦Transformer(OH)¦ | Wildfire Mitigation | Planned - WSIP/System Hardening | Transformer (OH) | [11 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PublicSafetyPowerShutoff¦¦ | Wildfire Mitigation | Public Safety Power Shut-off |  |  | FNLYEAR 2024: 10 | 10
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PublicSafetyPowerShutoff¦¦ | Wildfire Mitigation | Public Safety Power Shut-off |  |  | FNLYEAR 2018: 36; FNLYEAR 2019: 8; FNLYEAR 2020: 5; FNLYEAR 2021: 7; FNLYEAR 2023: 1 | 57
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PublicSafetyPowerShutoff¦¦Normal | Wildfire Mitigation | Public Safety Power Shut-off |  | Normal | [10 empty] | 1 | bar: FNLYEAR 2018
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 2.7143 | 1.9 | 1.6 | 1.9 | WildfireMitigation¦PublicSafetyPowerShutoff¦CircuitBreaker¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | Normal | FNLYEAR 2019: 11; FNLYEAR 2020: 7; FNLYEAR 2021: 1 | 19
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Arcing | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Arcing | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Broken | FNLYEAR 2020: 2 | 2
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Brokenwireonground | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Broken- wire on ground | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 2.7143 | 1.9 | 0.4 | 1.9 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Brokenwireonground | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Broken, wire on ground | FNLYEAR 2019: 17; FNLYEAR 2020: 2 | 19
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Brokenwireonobject | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Broken, wire on object | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Deteriorated | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 8.4286 | 5.9 | 11.8 | 5.9 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Normal | FNLYEAR 2024: 59 | 59
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 46.1429 | 32.3 | 48.6 | 32.3 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | FNLYEAR 2018: 1; FNLYEAR 2019: 79; FNLYEAR 2020: 155; FNLYEAR 2021: 58; FNLYEAR 2023: 30 | 323
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Together | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Together | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.28571 | 0.2 | 0 | 0.2 | WildfireMitigation¦PublicSafetyPowerShutoff¦ConnectororSplice(OH)¦Brokenwireonground | Wildfire Mitigation | Public Safety Power Shut-off | Connector or Splice (OH) | Broken, wire on ground | FNLYEAR 2019: 2 | 2
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.42857 | 0.3 | 0.6 | 0.3 | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Broken | FNLYEAR 2020: 3 | 3
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.42857 | 0.3 | 0 | 0.3 | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Brokenwireonground | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Broken, wire on ground | FNLYEAR 2019: 3 | 3
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Deteriorated | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Deteriorated | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Cutoutfuseholder¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Cutout, fuse holder | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Fuse¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 2.7143 | 1.9 | 2.6 | 1.9 | WildfireMitigation¦PublicSafetyPowerShutoff¦Fuse¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | FNLYEAR 2019: 6; FNLYEAR 2020: 10; FNLYEAR 2021: 3 | 19
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Generator¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Generator | Normal | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Insulator¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Insulator¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Insulator | Broken | [10 empty] | 1 | bar: FNLYEAR 2023
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PublicSafetyPowerShutoff¦Other¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Other | Broken | [10 empty] | 1 | bar: FNLYEAR 2021
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PublicSafetyPowerShutoff¦Other¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Other | Normal | FNLYEAR 2018: 1; FNLYEAR 2020: 2 | 3
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.57143 | 0.4 | 0.2 | 0.4 | WildfireMitigation¦PublicSafetyPowerShutoff¦PoleWood¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken | FNLYEAR 2019: 3; FNLYEAR 2020: 1 | 4
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.57143 | 0.4 | 0 | 0.4 | WildfireMitigation¦PublicSafetyPowerShutoff¦PoleWood¦Brokenwireonground | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken, wire on ground | FNLYEAR 2019: 4 | 4
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.28571 | 0.2 | 0.4 | 0.2 | WildfireMitigation¦PublicSafetyPowerShutoff¦Recloser¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | FNLYEAR 2024: 2 | 2
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 2.4286 | 1.7 | 1.4 | 1.7 | WildfireMitigation¦PublicSafetyPowerShutoff¦Recloser¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | FNLYEAR 2019: 10; FNLYEAR 2020: 6; FNLYEAR 2021: 1 | 17
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.28571 | 0.2 | 0 | 0.2 | WildfireMitigation¦PublicSafetyPowerShutoff¦Secondary¦Brokenwireonground | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Broken, wire on ground | FNLYEAR 2019: 2 | 2
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Secondary¦Together | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Together | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(OH)¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 1.7143 | 1.2 | 2 | 1.2 | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(OH)¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Normal | FNLYEAR 2019: 2; FNLYEAR 2020: 9; FNLYEAR 2021: 1 | 12
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(UG)¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Switch (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 1.1429 | 0.8 | 1.6 | 0.8 | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer(OH)¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (OH) | Normal | FNLYEAR 2020: 1; FNLYEAR 2021: 7 | 8
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer(UG)¦Burnedflashed | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Burned/flashed | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer(UG)¦Normal | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Normal | [10 empty] | 1 | bar: FNLYEAR 2024
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer¦Brokenwireonground | Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Broken, wire on ground | [10 empty] | 1 | bar: FNLYEAR 2019
Company Initiated | None | 0 | 0 | 0 | None | 0 | 0 | 0 | 0.14286 | 0.1 | 0.2 | 0.1 | WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken | Wildfire Mitigation | Public Safety Power Shut-off | Woodpin | Broken | [10 empty] | 1 | bar: FNLYEAR 2020
[13 empty] | Grand Total |  |  |  |  | 5634 | 6792 | 10748 | 6886 | 11692 | 8426 | 10937 | 7825 | 7660 | 25580 | 102180

## Grid Hardening SME Input_v3
Basic Cause | Supplemental Cause | Failed/Involved Equipment | Equipment Condition | Joint_Vlookup_Column | Check - Is the Failure Mode Part of the latest Set of Failure Modes from Outage Dataset |  |  | Status Quo | Covered Conductor
3rd Party | Aircraft | Conductor, Overhead | Broken | 3rdParty¦Aircraft¦ConductorOverhead¦Broken | #N/A |  |  | None | None
3rd Party | Aircraft | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Aircraft¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Aircraft | Conductor, Overhead | Normal | 3rdParty¦Aircraft¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Aircraft | Conductor, Overhead | Normal | 3rdParty¦Aircraft¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Aircraft | Conductor, Overhead | On Ground | 3rdParty¦Aircraft¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
3rd Party | Aircraft | Pole-Wood | Broken, wire on ground | 3rdParty¦Aircraft¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Annealed | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Annealed | #N/A |  |  | None | Very High
3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Broken, wire on ground | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Burned/flashed | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Burned/flashed | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Normal | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Together | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
3rd Party | Contact with High Voltage, 3rd party | Conductor, Underground | Broken | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorUnderground¦Broken | #N/A |  |  | None | None
3rdParty | ContactwithHighVoltage3rdparty | CrossarmWood | Brokenwireonground | 3rdParty¦ContactwithHighVoltage3rdparty¦CrossarmWood¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Contact with High Voltage, 3rd party | Cutout, fuse holder | Normal | 3rdParty¦ContactwithHighVoltage3rdparty¦Cutoutfuseholder¦Normal | #N/A |  |  | None | Medium
3rd Party | Contact with High Voltage, 3rd party | Fuse | Failed/Faulted | 3rdParty¦ContactwithHighVoltage3rdparty¦Fuse¦FailedFaulted | #N/A |  |  | None | Medium
3rd Party | Contact with High Voltage, 3rd party | Pole-Wood | Broken | 3rdParty¦ContactwithHighVoltage3rdparty¦PoleWood¦Broken | #N/A |  |  | None | High
3rd Party | Contact with High Voltage, 3rd party | Pole-Wood | Broken, wire on ground | 3rdParty¦ContactwithHighVoltage3rdparty¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Contact with High Voltage, 3rd party | Pothead(Riser Termination) | Broken | 3rdParty¦ContactwithHighVoltage3rdparty¦Pothead(RiserTermination)¦Broken | #N/A |  |  | None | High
3rd Party | Contact with High Voltage, 3rd party | Secondary | Broken, wire on ground | 3rdParty¦ContactwithHighVoltage3rdparty¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Contact with High Voltage, 3rd party | Secondary | Burned Open | 3rdParty¦ContactwithHighVoltage3rdparty¦Secondary¦BurnedOpen | #N/A |  |  | None | Medium
3rd Party | Customer Equipment | (blank) | Failed/Faulted | 3rdParty¦CustomerEquipment¦¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Bus | Burned/flashed | 3rdParty¦CustomerEquipment¦Bus¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Bus | Failed/Faulted | 3rdParty¦CustomerEquipment¦Bus¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Circuit Breaker | Arcing | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Arcing | #N/A |  |  | None | None
3rd Party | Customer Equipment | Circuit Breaker | Failed/Faulted | 3rdParty¦CustomerEquipment¦CircuitBreaker¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Circuit Breaker | Malfunctioning | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Malfunctioning | #N/A |  |  | None | None
3rd Party | Customer Equipment | Circuit Breaker | Normal | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | Broken | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | Broken, wire on ground | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | Burned/flashed | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | Deteriorated | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | Normal | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | Normal | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | On Ground | 3rdParty¦CustomerEquipment¦ConductorOverhead¦OnGround | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Overhead | Together | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Together | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Underground | Broken | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Underground | Broken | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Underground | Deteriorated | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Deteriorated | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Underground | Deteriorated | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Deteriorated | #N/A |  |  | None | None
3rd Party | Customer Equipment | Conductor, Underground | Normal | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Connector or Splice (OH) | Broken | 3rdParty¦CustomerEquipment¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Connector or Splice (OH) | Normal | 3rdParty¦CustomerEquipment¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Connector or Splice (UG) | Normal | 3rdParty¦CustomerEquipment¦ConnectororSplice(UG)¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Crossarm, Wood | Broken | 3rdParty¦CustomerEquipment¦CrossarmWood¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | CT | Burned/flashed | 3rdParty¦CustomerEquipment¦CT¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Arcing | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Arcing | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Bent or Twisted | 3rdParty¦CustomerEquipment¦CustomerEquipment¦BentorTwisted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Broken | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Burned/flashed | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Burned Open | 3rdParty¦CustomerEquipment¦CustomerEquipment¦BurnedOpen | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Deteriorated | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Deteriorated | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Failed/Faulted | 3rdParty¦CustomerEquipment¦CustomerEquipment¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Malfunctioning | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Normal | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Customer Equipment | Together | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Together | #N/A |  |  | None | None
3rd Party | Customer Equipment | Cutout, fuse holder | Burned/flashed | 3rdParty¦CustomerEquipment¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Cutout, fuse holder | Failed/Faulted | 3rdParty¦CustomerEquipment¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Fuse | Broken | 3rdParty¦CustomerEquipment¦Fuse¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Fuse | Burned Open | 3rdParty¦CustomerEquipment¦Fuse¦BurnedOpen | #N/A |  |  | None | None
3rd Party | Customer Equipment | Fuse | Failed/Faulted | 3rdParty¦CustomerEquipment¦Fuse¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Fuse | Normal | 3rdParty¦CustomerEquipment¦Fuse¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Generator | Normal | 3rdParty¦CustomerEquipment¦Generator¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Insulator | Broken | 3rdParty¦CustomerEquipment¦Insulator¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Lightning Arrestor | Arcing | 3rdParty¦CustomerEquipment¦LightningArrestor¦Arcing | #N/A |  |  | None | None
3rd Party | Customer Equipment | Lightning Arrestor | Broken | 3rdParty¦CustomerEquipment¦LightningArrestor¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Lightning Arrestor | Burned/flashed | 3rdParty¦CustomerEquipment¦LightningArrestor¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Lightning Arrestor | Failed/Faulted | 3rdParty¦CustomerEquipment¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Metering Equipment | Arcing | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Arcing | #N/A |  |  | None | None
3rdParty | CustomerEquipment | MeteringEquipment | Broken | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Broken |  |  |  | None | None
3rd Party | Customer Equipment | Metering Equipment | Burned/flashed | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Metering Equipment | Failed/Faulted | 3rdParty¦CustomerEquipment¦MeteringEquipment¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Metering Equipment | Malfunctioning | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Malfunctioning | #N/A |  |  | None | None
3rd Party | Customer Equipment | Metering Equipment | Normal | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Other | Broken | 3rdParty¦CustomerEquipment¦Other¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Other | Burned/flashed | 3rdParty¦CustomerEquipment¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Other | Contaminated | 3rdParty¦CustomerEquipment¦Other¦Contaminated | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Other | Deteriorated | 3rdParty¦CustomerEquipment¦Other¦Deteriorated | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Other | Failed/Faulted | 3rdParty¦CustomerEquipment¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Other | Malfunctioning | 3rdParty¦CustomerEquipment¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Other | Normal | 3rdParty¦CustomerEquipment¦Other¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Customer Equipment | Pole-Wood | Broken | 3rdParty¦CustomerEquipment¦PoleWood¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Pole-Wood | Broken, wire on ground | 3rdParty¦CustomerEquipment¦PoleWood¦Brokenwireonground | #N/A |  |  | None | None
3rd Party | Customer Equipment | Pole-Wood | Burned/flashed | 3rdParty¦CustomerEquipment¦PoleWood¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Pole-Wood | Deteriorated | 3rdParty¦CustomerEquipment¦PoleWood¦Deteriorated | #N/A |  |  | None | None
3rd Party | Customer Equipment | Pole-Wood | Normal | 3rdParty¦CustomerEquipment¦PoleWood¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Pole-Wood | On Ground | 3rdParty¦CustomerEquipment¦PoleWood¦OnGround | #N/A |  |  | None | None
3rd Party | Customer Equipment | PT/CCVT | Failed/Faulted | 3rdParty¦CustomerEquipment¦PTCCVT¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Recloser | Failed/Faulted | 3rdParty¦CustomerEquipment¦Recloser¦FailedFaulted | #N/A |  |  | None | None
3rdParty | CustomerEquipment | Recloser | Malfunctioning | 3rdParty¦CustomerEquipment¦Recloser¦Malfunctioning |  |  |  | None | None
3rd Party | Customer Equipment | Recloser | Normal | 3rdParty¦CustomerEquipment¦Recloser¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Relay | Malfunctioning | 3rdParty¦CustomerEquipment¦Relay¦Malfunctioning | #N/A |  |  | None | None
3rdParty | CustomerEquipment | Relay | Normal | 3rdParty¦CustomerEquipment¦Relay¦Normal |  |  |  | None | None
3rd Party | Customer Equipment | Secondary | Arcing | 3rdParty¦CustomerEquipment¦Secondary¦Arcing | #N/A |  |  | None | None
3rdParty | CustomerEquipment | Secondary | BentorTwisted | 3rdParty¦CustomerEquipment¦Secondary¦BentorTwisted |  |  |  | None | None
3rd Party | Customer Equipment | Secondary | Broken | 3rdParty¦CustomerEquipment¦Secondary¦Broken | #N/A |  |  | None | None
3rdParty | CustomerEquipment | Secondary | Brokenwireonground | 3rdParty¦CustomerEquipment¦Secondary¦Brokenwireonground |  |  |  | None | None
3rd Party | Customer Equipment | Secondary | Burned/flashed | 3rdParty¦CustomerEquipment¦Secondary¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Secondary | Burned Open | 3rdParty¦CustomerEquipment¦Secondary¦BurnedOpen | #N/A |  |  | None | None
3rd Party | Customer Equipment | Secondary | Deteriorated | 3rdParty¦CustomerEquipment¦Secondary¦Deteriorated | #N/A |  |  | None | None
3rd Party | Customer Equipment | Secondary | Normal | 3rdParty¦CustomerEquipment¦Secondary¦Normal | #N/A |  |  | None | None
3rdParty | CustomerEquipment | Serviceconductor | Broken | 3rdParty¦CustomerEquipment¦Serviceconductor¦Broken |  |  |  | None | None
3rd Party | Customer Equipment | Service conductor | Burned/flashed | 3rdParty¦CustomerEquipment¦Serviceconductor¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Service conductor | Normal | 3rdParty¦CustomerEquipment¦Serviceconductor¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Switch (OH) | Arcing | 3rdParty¦CustomerEquipment¦Switch(OH)¦Arcing | #N/A |  |  | None | None
3rd Party | Customer Equipment | Switch (OH) | Normal | 3rdParty¦CustomerEquipment¦Switch(OH)¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Switch (UG) | Failed/Faulted | 3rdParty¦CustomerEquipment¦Switch(UG)¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer (OH) | Broken | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer (OH) | Burned/flashed | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer (OH) | Deteriorated | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Deteriorated | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer (OH) | Failed/Faulted | 3rdParty¦CustomerEquipment¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer (OH) | Normal | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer (UG) | Failed/Faulted | 3rdParty¦CustomerEquipment¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer (UG) | Normal | 3rdParty¦CustomerEquipment¦Transformer(UG)¦Normal | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer | Annealed | 3rdParty¦CustomerEquipment¦Transformer¦Annealed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer | Arcing | 3rdParty¦CustomerEquipment¦Transformer¦Arcing | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer | Broken | 3rdParty¦CustomerEquipment¦Transformer¦Broken | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer | Broken, wire on ground | 3rdParty¦CustomerEquipment¦Transformer¦Brokenwireonground | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer | Burned/flashed | 3rdParty¦CustomerEquipment¦Transformer¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer | Failed/Faulted | 3rdParty¦CustomerEquipment¦Transformer¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Customer Equipment | Transformer | Normal | 3rdParty¦CustomerEquipment¦Transformer¦Normal | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Bushing | Broken | 3rdParty¦Digin3rdparty¦Bushing¦Broken | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Conductor, Overhead | Broken | 3rdParty¦Digin3rdparty¦ConductorOverhead¦Broken | #N/A |  |  | None | Medium
3rd Party | Dig in, 3rd party | Conductor, Overhead | Burned/flashed | 3rdParty¦Digin3rdparty¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Medium
3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Conductor, Underground | Burned/flashed | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Conductor, Underground | Normal | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Normal | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Connector or Splice (OH) | Broken | 3rdParty¦Digin3rdparty¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Very High
3rd Party | Dig in, 3rd party | Connector or Splice (UG) | Failed/Faulted | 3rdParty¦Digin3rdparty¦ConnectororSplice(UG)¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Customer Equipment | Broken | 3rdParty¦Digin3rdparty¦CustomerEquipment¦Broken | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Elbow | Broken | 3rdParty¦Digin3rdparty¦Elbow¦Broken | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Fuse | Failed/Faulted | 3rdParty¦Digin3rdparty¦Fuse¦FailedFaulted | #N/A |  |  | None | None
3rdParty | Digin3rdparty | Other | Broken | 3rdParty¦Digin3rdparty¦Other¦Broken |  |  |  | N/A | N/A
3rd Party | Dig in, 3rd party | Other | Failed/Faulted | 3rdParty¦Digin3rdparty¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Dig in, 3rd party | Secondary | Broken | 3rdParty¦Digin3rdparty¦Secondary¦Broken | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Secondary | Deteriorated | 3rdParty¦Digin3rdparty¦Secondary¦Deteriorated | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Service conductor | Annealed | 3rdParty¦Digin3rdparty¦Serviceconductor¦Annealed | #N/A |  |  | None | High
3rd Party | Dig in, 3rd party | Service conductor | Bent or Twisted | 3rdParty¦Digin3rdparty¦Serviceconductor¦BentorTwisted | #N/A |  |  | None | High
3rd Party | Dig in, 3rd party | Service conductor | Broken | 3rdParty¦Digin3rdparty¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
3rd Party | Dig in, 3rd party | Service conductor | Burned Open | 3rdParty¦Digin3rdparty¦Serviceconductor¦BurnedOpen | #N/A |  |  | None | Medium
3rd Party | Dig in, 3rd party | Transformer (OH) | Failed/Faulted | 3rdParty¦Digin3rdparty¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer (UG) | Broken | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Broken | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer (UG) | Burned/flashed | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer (UG) | Leaking | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Leaking | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer (UG) | Normal | 3rdParty¦Digin3rdparty¦Transformer(UG)¦Normal | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer | Arcing | 3rdParty¦Digin3rdparty¦Transformer¦Arcing | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer | Broken | 3rdParty¦Digin3rdparty¦Transformer¦Broken | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer | Burned/flashed | 3rdParty¦Digin3rdparty¦Transformer¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer | Burned Open | 3rdParty¦Digin3rdparty¦Transformer¦BurnedOpen | #N/A |  |  | None | None
3rd Party | Dig in, 3rd party | Transformer | Failed/Faulted | 3rdParty¦Digin3rdparty¦Transformer¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Fire, house or bldg. | (blank) | Failed/Faulted | 3rdParty¦Firehouseorbldg¦¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Conductor, Overhead | Burned/flashed | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Conductor, Overhead | Normal | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Conductor, Overhead | Together | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Together | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Conductor, Underground | Burned/flashed | 3rdParty¦Firehouseorbldg¦ConductorUnderground¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Conductor, Underground | Normal | 3rdParty¦Firehouseorbldg¦ConductorUnderground¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Connector or Splice (OH) | Burned Open | 3rdParty¦Firehouseorbldg¦ConnectororSplice(OH)¦BurnedOpen | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Crossarm, Wood | Broken | 3rdParty¦Firehouseorbldg¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Crossarm, Wood | Burned/flashed | 3rdParty¦Firehouseorbldg¦CrossarmWood¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Customer Equipment | Burned/flashed | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Customer Equipment | Burned Open | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦BurnedOpen | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Customer Equipment | Malfunctioning | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Malfunctioning | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Cutout, fuse holder | Failed/Faulted | 3rdParty¦Firehouseorbldg¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Fuse | Normal | 3rdParty¦Firehouseorbldg¦Fuse¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Jumper | Broken | 3rdParty¦Firehouseorbldg¦Jumper¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Jumper | Normal | 3rdParty¦Firehouseorbldg¦Jumper¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Metering Equipment | Arcing | 3rdParty¦Firehouseorbldg¦MeteringEquipment¦Arcing | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Metering Equipment | Burned/flashed | 3rdParty¦Firehouseorbldg¦MeteringEquipment¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Other | Burned/flashed | 3rdParty¦Firehouseorbldg¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Other | Normal | 3rdParty¦Firehouseorbldg¦Other¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Pole-Wood | Broken | 3rdParty¦Firehouseorbldg¦PoleWood¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Pole-Wood | Broken, wire on ground | 3rdParty¦Firehouseorbldg¦PoleWood¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Pole-Wood | Burned/flashed | 3rdParty¦Firehouseorbldg¦PoleWood¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Pole-Wood | Normal | 3rdParty¦Firehouseorbldg¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | Broken, wire on ground | 3rdParty¦Firehouseorbldg¦Secondary¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | Burned/flashed | 3rdParty¦Firehouseorbldg¦Secondary¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | Burned Open | 3rdParty¦Firehouseorbldg¦Secondary¦BurnedOpen | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | Normal | 3rdParty¦Firehouseorbldg¦Secondary¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | On Ground | 3rdParty¦Firehouseorbldg¦Secondary¦OnGround | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | Together | 3rdParty¦Firehouseorbldg¦Secondary¦Together | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Service conductor | Broken | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Service conductor | Broken, wire on ground | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Service conductor | Burned/flashed | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Service conductor | Burned Open | 3rdParty¦Firehouseorbldg¦Serviceconductor¦BurnedOpen | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer (OH) | Broken, wire on ground | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer (OH) | Burned/flashed | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer (OH) | Failed/Faulted | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer (OH) | Normal | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer (UG) | Normal | 3rdParty¦Firehouseorbldg¦Transformer(UG)¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer | Burned/flashed | 3rdParty¦Firehouseorbldg¦Transformer¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer | Burned Open | 3rdParty¦Firehouseorbldg¦Transformer¦BurnedOpen | #N/A |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer | Failed/Faulted | 3rdParty¦Firehouseorbldg¦Transformer¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Gun Shot | Conductor, Overhead | Broken | 3rdParty¦GunShot¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
3rd Party | Gun Shot | Conductor, Overhead | Broken, wire on ground | 3rdParty¦GunShot¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Gun Shot | Conductor, Overhead | Deteriorated | 3rdParty¦GunShot¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
3rd Party | Gun Shot | Conductor, Overhead | Together | 3rdParty¦GunShot¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
3rd Party | Gun Shot | Conductor, Underground | Broken | 3rdParty¦GunShot¦ConductorUnderground¦Broken | #N/A |  |  | None | None
3rd Party | Gun Shot | Insulator | Failed/Faulted | 3rdParty¦GunShot¦Insulator¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Gun Shot | Pothead(Riser Termination) | Burned/flashed | 3rdParty¦GunShot¦Pothead(RiserTermination)¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Gun Shot | Regulator | Leaking | 3rdParty¦GunShot¦Regulator¦Leaking | #N/A |  |  | None | None
3rd Party | Gun Shot | Secondary | Broken | 3rdParty¦GunShot¦Secondary¦Broken | #N/A |  |  | None | Medium
3rd Party | Gun Shot | Transformer (OH) | Leaking | 3rdParty¦GunShot¦Transformer(OH)¦Leaking | #N/A |  |  | None | None
3rd Party | Gun Shot | Transformer | Failed/Faulted | 3rdParty¦GunShot¦Transformer¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Kite | Conductor, Overhead | Normal | 3rdParty¦Kite¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Conductor, Overhead | Arcing | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Conductor, Overhead | Broken | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Conductor, Overhead | Broken, wire on ground | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
3rdParty | MetallicBalloon | ConductorOverhead | Burnedflashed | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Burnedflashed |  |  |  | None | Very High
3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Conductor, Overhead | Together | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Cutout, fuse holder | Failed/Faulted | 3rdParty¦MetallicBalloon¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Fuse | Failed/Faulted | 3rdParty¦MetallicBalloon¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Fuse | Normal | 3rdParty¦MetallicBalloon¦Fuse¦Normal | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Other | Normal | 3rdParty¦MetallicBalloon¦Other¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Metallic Balloon | Pole-Wood | Burned/flashed | 3rdParty¦MetallicBalloon¦PoleWood¦Burnedflashed | #N/A |  |  | None | High
3rd Party | Metallic Balloon | Pothead(Riser Termination) | Normal | 3rdParty¦MetallicBalloon¦Pothead(RiserTermination)¦Normal | #N/A |  |  | None | High
3rd Party | Metallic Balloon | Recloser | Normal | 3rdParty¦MetallicBalloon¦Recloser¦Normal | #N/A |  |  | None | Very High
3rd Party | Metallic Balloon | Transformer (OH) | Burned/flashed | 3rdParty¦MetallicBalloon¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | High
3rd Party | Metallic Balloon | Transformer (OH) | Leaking | 3rdParty¦MetallicBalloon¦Transformer(OH)¦Leaking | #N/A |  |  | None | High
3rd Party | Metallic Balloon | Transformer (OH) | Normal | 3rdParty¦MetallicBalloon¦Transformer(OH)¦Normal | #N/A |  |  | None | High
3rd Party | Other | Anchor or Guy | Broken | 3rdParty¦Other¦AnchororGuy¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Anchor or Guy | Normal | 3rdParty¦Other¦AnchororGuy¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Circuit Breaker | Normal | 3rdParty¦Other¦CircuitBreaker¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | Arcing | 3rdParty¦Other¦ConductorOverhead¦Arcing | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | Bent or Twisted | 3rdParty¦Other¦ConductorOverhead¦BentorTwisted | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | Broken | 3rdParty¦Other¦ConductorOverhead¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Other¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | Normal | 3rdParty¦Other¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | On Ground | 3rdParty¦Other¦ConductorOverhead¦OnGround | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | Together | 3rdParty¦Other¦ConductorOverhead¦Together | #N/A |  |  | N/A | N/A
3rd Party | Other | Conductor, Underground | Normal | 3rdParty¦Other¦ConductorUnderground¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Crossarm, Wood | Broken | 3rdParty¦Other¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Customer Equipment | Leaking | 3rdParty¦Other¦CustomerEquipment¦Leaking | #N/A |  |  | N/A | N/A
3rd Party | Other | Customer Equipment | Normal | 3rdParty¦Other¦CustomerEquipment¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Cutout, fuse holder | Normal | 3rdParty¦Other¦Cutoutfuseholder¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Cutout, fuse holder | On Ground | 3rdParty¦Other¦Cutoutfuseholder¦OnGround | #N/A |  |  | N/A | N/A
3rd Party | Other | Fuse | Failed/Faulted | 3rdParty¦Other¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Other | Fuse | Normal | 3rdParty¦Other¦Fuse¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Generator | Normal | 3rdParty¦Other¦Generator¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Insulator | Broken | 3rdParty¦Other¦Insulator¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Insulator | Normal | 3rdParty¦Other¦Insulator¦Normal | #N/A |  |  | N/A | N/A
3rdParty | Other | Jumper |  | 3rdParty¦Other¦Jumper¦ |  |  |  | N/A | N/A
3rd Party | Other | Jumper | Broken | 3rdParty¦Other¦Jumper¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Jumper | Normal | 3rdParty¦Other¦Jumper¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Metering Equipment | Failed/Faulted | 3rdParty¦Other¦MeteringEquipment¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Other | Metering Equipment | Normal | 3rdParty¦Other¦MeteringEquipment¦Normal | #N/A |  |  | N/A | N/A
3rdParty | Other | Other | Broken | 3rdParty¦Other¦Other¦Broken |  |  |  | N/A | N/A
3rdParty | Other | Other | Deteriorated | 3rdParty¦Other¦Other¦Deteriorated |  |  |  | N/A | N/A
3rd Party | Other | Other | Failed/Faulted | 3rdParty¦Other¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
3rdParty | Other | Other | Malfunctioning | 3rdParty¦Other¦Other¦Malfunctioning |  |  |  | N/A | N/A
3rd Party | Other | Other | Normal | 3rdParty¦Other¦Other¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Pole - Tower, steel | Normal | 3rdParty¦Other¦PoleTowersteel¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Pole-Wood | Broken | 3rdParty¦Other¦PoleWood¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Pole-Wood | Broken, wire on ground | 3rdParty¦Other¦PoleWood¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Other | Pole-Wood | Burned/flashed | 3rdParty¦Other¦PoleWood¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Other | Pole-Wood | Contaminated | 3rdParty¦Other¦PoleWood¦Contaminated | #N/A |  |  | N/A | N/A
3rd Party | Other | Pole-Wood | Deteriorated | 3rdParty¦Other¦PoleWood¦Deteriorated | #N/A |  |  | N/A | N/A
3rd Party | Other | Recloser | Normal | 3rdParty¦Other¦Recloser¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Regulator | Malfunctioning | 3rdParty¦Other¦Regulator¦Malfunctioning | #N/A |  |  | N/A | N/A
3rd Party | Other | Secondary | Burned/flashed | 3rdParty¦Other¦Secondary¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Other | Secondary | Normal | 3rdParty¦Other¦Secondary¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Service conductor | Broken | 3rdParty¦Other¦Serviceconductor¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Service conductor | Broken, wire on ground | 3rdParty¦Other¦Serviceconductor¦Brokenwireonground | #N/A |  |  | N/A | N/A
3rd Party | Other | Service conductor | Burned/flashed | 3rdParty¦Other¦Serviceconductor¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Other | Service conductor | Normal | 3rdParty¦Other¦Serviceconductor¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Switch (OH) | Normal | 3rdParty¦Other¦Switch(OH)¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer (OH) | (blank) | 3rdParty¦Other¦Transformer(OH)¦ | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer (OH) | Broken | 3rdParty¦Other¦Transformer(OH)¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer (OH) | Contaminated | 3rdParty¦Other¦Transformer(OH)¦Contaminated | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer (OH) | Failed/Faulted | 3rdParty¦Other¦Transformer(OH)¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer (OH) | Normal | 3rdParty¦Other¦Transformer(OH)¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer (UG) | Broken | 3rdParty¦Other¦Transformer(UG)¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer (UG) | Normal | 3rdParty¦Other¦Transformer(UG)¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer | Broken | 3rdParty¦Other¦Transformer¦Broken | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer | Failed/Faulted | 3rdParty¦Other¦Transformer¦FailedFaulted | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer | Malfunctioning | 3rdParty¦Other¦Transformer¦Malfunctioning | #N/A |  |  | N/A | N/A
3rd Party | Other | Transformer | Normal | 3rdParty¦Other¦Transformer¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Thrown Object | Bushing | Normal | 3rdParty¦ThrownObject¦Bushing¦Normal | #N/A |  |  | None | Medium High
3rd Party | Thrown Object | Conductor, Overhead | Normal | 3rdParty¦ThrownObject¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Thrown Object | Conductor, Overhead | Together | 3rdParty¦ThrownObject¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
3rd Party | Thrown Object | Transformer | Broken | 3rdParty¦ThrownObject¦Transformer¦Broken | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Anchor or Guy | Broken | 3rdParty¦Treecutting3rdparty¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Anchor or Guy | Normal | 3rdParty¦Treecutting3rdparty¦AnchororGuy¦Normal | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Bushing | Broken | 3rdParty¦Treecutting3rdparty¦Bushing¦Broken | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Arcing | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on object | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Burned/flashed | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Deteriorated | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | On Ground | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Together | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Conductor, Underground | Normal | 3rdParty¦Treecutting3rdparty¦ConductorUnderground¦Normal | #N/A |  |  | None | None
3rd Party | Tree - cutting, 3rd party | Connector or Splice (OH) | Broken | 3rdParty¦Treecutting3rdparty¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Connector or Splice (OH) | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken, wire on object | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Cutout, fuse holder | Normal | 3rdParty¦Treecutting3rdparty¦Cutoutfuseholder¦Normal | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Fuse | Broken | 3rdParty¦Treecutting3rdparty¦Fuse¦Broken | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Fuse | Burned Open | 3rdParty¦Treecutting3rdparty¦Fuse¦BurnedOpen | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Fuse | Normal | 3rdParty¦Treecutting3rdparty¦Fuse¦Normal | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Insulator | Broken | 3rdParty¦Treecutting3rdparty¦Insulator¦Broken | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Insulator | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦Insulator¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Jumper | Burned Open | 3rdParty¦Treecutting3rdparty¦Jumper¦BurnedOpen | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Jumper | Normal | 3rdParty¦Treecutting3rdparty¦Jumper¦Normal | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken | 3rdParty¦Treecutting3rdparty¦PoleWood¦Broken | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken, wire on object | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Recloser | Malfunctioning | 3rdParty¦Treecutting3rdparty¦Recloser¦Malfunctioning | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Recloser | Normal | 3rdParty¦Treecutting3rdparty¦Recloser¦Normal | #N/A |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Secondary | Broken | 3rdParty¦Treecutting3rdparty¦Secondary¦Broken | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Secondary | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Secondary | Normal | 3rdParty¦Treecutting3rdparty¦Secondary¦Normal | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Secondary | On Ground | 3rdParty¦Treecutting3rdparty¦Secondary¦OnGround | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Secondary | Together | 3rdParty¦Treecutting3rdparty¦Secondary¦Together | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Service conductor | Broken | 3rdParty¦Treecutting3rdparty¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Service conductor | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Service conductor | Normal | 3rdParty¦Treecutting3rdparty¦Serviceconductor¦Normal | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Broken | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Broken | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Failed/Faulted | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | Medium
3rdParty | Treecutting3rdparty | Transformer(OH) | Leaking | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Leaking |  |  |  | None | None
3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Normal | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Normal | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Transformer | Broken | 3rdParty¦Treecutting3rdparty¦Transformer¦Broken | #N/A |  |  | None | High
3rdParty | Treecutting3rdparty | Transformer | Brokenwireonground | 3rdParty¦Treecutting3rdparty¦Transformer¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Transformer | Broken, wire on object | 3rdParty¦Treecutting3rdparty¦Transformer¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Transformer | Burned/flashed | 3rdParty¦Treecutting3rdparty¦Transformer¦Burnedflashed | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Transformer | Contaminated | 3rdParty¦Treecutting3rdparty¦Transformer¦Contaminated | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Transformer | Deteriorated | 3rdParty¦Treecutting3rdparty¦Transformer¦Deteriorated | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Transformer | Failed/Faulted | 3rdParty¦Treecutting3rdparty¦Transformer¦FailedFaulted | #N/A |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Transformer | Leaking | 3rdParty¦Treecutting3rdparty¦Transformer¦Leaking | #N/A |  |  | None | High
3rd Party | Tree - cutting, 3rd party | Woodpin | Broken | 3rdParty¦Treecutting3rdparty¦Woodpin¦Broken | #N/A |  |  | None | Very High
3rd Party | Vandalism | Bushing | Broken | 3rdParty¦Vandalism¦Bushing¦Broken | #N/A |  |  | None | Medium
3rd Party | Vandalism | Circuit Breaker | Normal | 3rdParty¦Vandalism¦CircuitBreaker¦Normal | #N/A |  |  | None | None
3rd Party | Vandalism | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Vandalism¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vandalism | Conductor, Overhead | Normal | 3rdParty¦Vandalism¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rdParty | Vandalism | ConductorOverhead | Normal | 3rdParty¦Vandalism¦ConductorOverhead¦Normal |  |  |  | None | Very High
3rd Party | Vandalism | Fuse | Failed/Faulted | 3rdParty¦Vandalism¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
3rd Party | Vandalism | Metering Equipment | Failed/Faulted | 3rdParty¦Vandalism¦MeteringEquipment¦FailedFaulted | #N/A |  |  | None | None
3rdParty | Vandalism | Other | Broken | 3rdParty¦Vandalism¦Other¦Broken |  |  |  | N/A | N/A
3rd Party | Vandalism | Other | Burned/flashed | 3rdParty¦Vandalism¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
3rd Party | Vandalism | Pole-Wood | Broken | 3rdParty¦Vandalism¦PoleWood¦Broken | #N/A |  |  | None | High
3rd Party | Vandalism | Pole-Wood | Broken, wire on ground | 3rdParty¦Vandalism¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
3rdParty | Vandalism | PoleWood | Burnedflashed | 3rdParty¦Vandalism¦PoleWood¦Burnedflashed |  |  |  | None | Medium
3rd Party | Vandalism | Recloser | Broken | 3rdParty¦Vandalism¦Recloser¦Broken | #N/A |  |  | None | Medium
3rd Party | Vandalism | Secondary | Broken | 3rdParty¦Vandalism¦Secondary¦Broken | #N/A |  |  | None | Medium
3rd Party | Vandalism | Switch (OH) | Normal | 3rdParty¦Vandalism¦Switch(OH)¦Normal | #N/A |  |  | None | Very High
3rd Party | Vandalism | Transformer (OH) | Failed/Faulted | 3rdParty¦Vandalism¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | Medium High
3rd Party | Vandalism | Transformer (UG) | Broken | 3rdParty¦Vandalism¦Transformer(UG)¦Broken | #N/A |  |  | None | None
3rd Party | Vandalism | Transformer | Contaminated | 3rdParty¦Vandalism¦Transformer¦Contaminated | #N/A |  |  | None | Medium High
3rd Party | Vandalism | Transformer | Failed/Faulted | 3rdParty¦Vandalism¦Transformer¦FailedFaulted | #N/A |  |  | None | Medium High
3rd Party | Vehicle | (blank) | Burned Open | 3rdParty¦Vehicle¦¦BurnedOpen | #N/A |  |  | N/A | N/A
3rd Party | Vehicle | (blank) | Normal | 3rdParty¦Vehicle¦¦Normal | #N/A |  |  | N/A | N/A
3rd Party | Vehicle | Anchor or Guy | Bent or Twisted | 3rdParty¦Vehicle¦AnchororGuy¦BentorTwisted | #N/A |  |  | None | Very High
3rd Party | Vehicle | Anchor or Guy | Broken | 3rdParty¦Vehicle¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
3rd Party | Vehicle | Anchor or Guy | Broken, wire on ground | 3rdParty¦Vehicle¦AnchororGuy¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vehicle | Anchor or Guy | Broken, wire on object | 3rdParty¦Vehicle¦AnchororGuy¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Vehicle | Anchor or Guy | Normal | 3rdParty¦Vehicle¦AnchororGuy¦Normal | #N/A |  |  | None | Very High
3rd Party | Vehicle | Bushing | Broken | 3rdParty¦Vehicle¦Bushing¦Broken | #N/A |  |  | None | Medium
3rd Party | Vehicle | Capacitor | Burned/flashed | 3rdParty¦Vehicle¦Capacitor¦Burnedflashed | #N/A |  |  | None | Medium
3rd Party | Vehicle | Conductor, Overhead | Bent or Twisted | 3rdParty¦Vehicle¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | Broken | 3rdParty¦Vehicle¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vehicle | Conductor, Overhead | Broken, wire on object | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Vehicle | Conductor, Overhead | Burned/flashed | 3rdParty¦Vehicle¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | Contaminated | 3rdParty¦Vehicle¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | Deteriorated | 3rdParty¦Vehicle¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | Normal | 3rdParty¦Vehicle¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | On Ground | 3rdParty¦Vehicle¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
3rd Party | Vehicle | Conductor, Overhead | Together | 3rdParty¦Vehicle¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
3rd Party | Vehicle | Conductor, Underground | Broken | 3rdParty¦Vehicle¦ConductorUnderground¦Broken | #N/A |  |  | None | None
3rd Party | Vehicle | Conductor, Underground | Burned/flashed | 3rdParty¦Vehicle¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Vehicle | Connector or Splice (OH) | Broken | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Very High
3rd Party | Vehicle | Connector or Splice (OH) | Broken, wire on ground | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Very High
3rd Party | Vehicle | Connector or Splice (OH) | Normal | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
3rd Party | Vehicle | Connector or Splice (UG) | Broken | 3rdParty¦Vehicle¦ConnectororSplice(UG)¦Broken | #N/A |  |  | None | None
3rd Party | Vehicle | Connector or Splice (UG) | Burned/flashed | 3rdParty¦Vehicle¦ConnectororSplice(UG)¦Burnedflashed | #N/A |  |  | None | None
3rd Party | Vehicle | Crossarm, Wood | Broken | 3rdParty¦Vehicle¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
3rd Party | Vehicle | Crossarm, Wood | Broken, wire on ground | 3rdParty¦Vehicle¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vehicle | Crossarm, Wood | Broken, wire on object | 3rdParty¦Vehicle¦CrossarmWood¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Vehicle | Crossarm, Wood | Normal | 3rdParty¦Vehicle¦CrossarmWood¦Normal | #N/A |  |  | None | Very High
3rd Party | Vehicle | Customer Equipment | Broken | 3rdParty¦Vehicle¦CustomerEquipment¦Broken | #N/A |  |  | None | None
3rd Party | Vehicle | Cutout, fuse holder | Broken | 3rdParty¦Vehicle¦Cutoutfuseholder¦Broken | #N/A |  |  | None | Very High
3rd Party | Vehicle | Cutout, fuse holder | Failed/Faulted | 3rdParty¦Vehicle¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Very High
3rd Party | Vehicle | Cutout, fuse holder | Normal | 3rdParty¦Vehicle¦Cutoutfuseholder¦Normal | #N/A |  |  | None | Very High
3rd Party | Vehicle | Elbow | Broken | 3rdParty¦Vehicle¦Elbow¦Broken | #N/A |  |  | None | None
3rd Party | Vehicle | Fuse | Burned Open | 3rdParty¦Vehicle¦Fuse¦BurnedOpen | #N/A |  |  | None | Very High
3rd Party | Vehicle | Fuse | Failed/Faulted | 3rdParty¦Vehicle¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
3rd Party | Vehicle | Fuse | Normal | 3rdParty¦Vehicle¦Fuse¦Normal | #N/A |  |  | None | Very High
3rd Party | Vehicle | Insulator | Broken | 3rdParty¦Vehicle¦Insulator¦Broken | #N/A |  |  | None | Very High
3rd Party | Vehicle | Jumper | Broken | 3rdParty¦Vehicle¦Jumper¦Broken | #N/A |  |  | None | High
3rd Party | Vehicle | Jumper | Burned Open | 3rdParty¦Vehicle¦Jumper¦BurnedOpen | #N/A |  |  | None | High
3rd Party | Vehicle | Lightning Arrestor | Failed/Faulted | 3rdParty¦Vehicle¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Very High
3rd Party | Vehicle | Other | Broken | 3rdParty¦Vehicle¦Other¦Broken | #N/A |  |  | None | N/A
3rd Party | Vehicle | Other | Normal | 3rdParty¦Vehicle¦Other¦Normal | #N/A |  |  | None | N/A
3rd Party | Vehicle | Pole - Tower, steel | Broken | 3rdParty¦Vehicle¦PoleTowersteel¦Broken | #N/A |  |  | None | None
3rd Party | Vehicle | Pole-Wood | Broken | 3rdParty¦Vehicle¦PoleWood¦Broken | #N/A |  |  | None | Medium
3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vehicle | Pole-Wood | Broken, wire on object | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Vehicle | Pole-Wood | Burned/flashed | 3rdParty¦Vehicle¦PoleWood¦Burnedflashed | #N/A |  |  | None | Medium
3rd Party | Vehicle | Pole-Wood | Deteriorated | 3rdParty¦Vehicle¦PoleWood¦Deteriorated | #N/A |  |  | None | Medium
3rd Party | Vehicle | Pole-Wood | Normal | 3rdParty¦Vehicle¦PoleWood¦Normal | #N/A |  |  | None | High
3rd Party | Vehicle | Pole-Wood | On Ground | 3rdParty¦Vehicle¦PoleWood¦OnGround | #N/A |  |  | None | Medium
3rd Party | Vehicle | Pothead(Riser Termination) | Broken | 3rdParty¦Vehicle¦Pothead(RiserTermination)¦Broken | #N/A |  |  | None | High
3rdParty | Vehicle | Recloser | Broken | 3rdParty¦Vehicle¦Recloser¦Broken |  |  |  | None | Medium
3rd Party | Vehicle | Recloser | Burned/flashed | 3rdParty¦Vehicle¦Recloser¦Burnedflashed | #N/A |  |  | None | Medium
3rd Party | Vehicle | Secondary | Broken | 3rdParty¦Vehicle¦Secondary¦Broken | #N/A |  |  | None | Medium
3rd Party | Vehicle | Secondary | Broken, wire on ground | 3rdParty¦Vehicle¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vehicle | Secondary | Broken, wire on object | 3rdParty¦Vehicle¦Secondary¦Brokenwireonobject | #N/A |  |  | None | Medium
3rd Party | Vehicle | Secondary | Burned/flashed | 3rdParty¦Vehicle¦Secondary¦Burnedflashed | #N/A |  |  | None | High
3rd Party | Vehicle | Secondary | Burned Open | 3rdParty¦Vehicle¦Secondary¦BurnedOpen | #N/A |  |  | None | Medium
3rd Party | Vehicle | Secondary | Normal | 3rdParty¦Vehicle¦Secondary¦Normal | #N/A |  |  | None | High
3rd Party | Vehicle | Secondary | Together | 3rdParty¦Vehicle¦Secondary¦Together | #N/A |  |  | None | High
3rd Party | Vehicle | Service conductor | Broken | 3rdParty¦Vehicle¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
3rd Party | Vehicle | Service conductor | Broken, wire on ground | 3rdParty¦Vehicle¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vehicle | Service conductor | Normal | 3rdParty¦Vehicle¦Serviceconductor¦Normal | #N/A |  |  | None | High
3rd Party | Vehicle | Switch | Broken | 3rdParty¦Vehicle¦Switch¦Broken | #N/A |  |  | None | Very High
3rd Party | Vehicle | Transformer (OH) | Broken | 3rdParty¦Vehicle¦Transformer(OH)¦Broken | #N/A |  |  | None | High
3rd Party | Vehicle | Transformer (OH) | Failed/Faulted | 3rdParty¦Vehicle¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
3rd Party | Vehicle | Transformer (OH) | Normal | 3rdParty¦Vehicle¦Transformer(OH)¦Normal | #N/A |  |  | None | High
3rd Party | Vehicle | Transformer (UG) | Broken | 3rdParty¦Vehicle¦Transformer(UG)¦Broken | #N/A |  |  | None | None
3rd Party | Vehicle | Transformer (UG) | Deteriorated | 3rdParty¦Vehicle¦Transformer(UG)¦Deteriorated | #N/A |  |  | None | None
3rd Party | Vehicle | Transformer (UG) | Failed/Faulted | 3rdParty¦Vehicle¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
3rd Party | Vehicle | Transformer (UG) | Leaking | 3rdParty¦Vehicle¦Transformer(UG)¦Leaking | #N/A |  |  | None | None
3rd Party | Vehicle | Transformer (UG) | Normal | 3rdParty¦Vehicle¦Transformer(UG)¦Normal | #N/A |  |  | None | None
3rd Party | Vehicle | Transformer (UG) | On Ground | 3rdParty¦Vehicle¦Transformer(UG)¦OnGround | #N/A |  |  | None | None
3rd Party | Vehicle | Transformer | (blank) | 3rdParty¦Vehicle¦Transformer¦ | #N/A |  |  | None | High
3rd Party | Vehicle | Transformer | Arcing | 3rdParty¦Vehicle¦Transformer¦Arcing | #N/A |  |  | None | High
3rd Party | Vehicle | Transformer | Broken | 3rdParty¦Vehicle¦Transformer¦Broken | #N/A |  |  | None | High
3rd Party | Vehicle | Transformer | Broken, wire on ground | 3rdParty¦Vehicle¦Transformer¦Brokenwireonground | #N/A |  |  | None | Medium
3rd Party | Vehicle | Transformer | Failed/Faulted | 3rdParty¦Vehicle¦Transformer¦FailedFaulted | #N/A |  |  | None | High
3rd Party | Vehicle | Transformer | Leaking | 3rdParty¦Vehicle¦Transformer¦Leaking | #N/A |  |  | None | High
3rdParty | Vehicle | Transformer | Malfunctioning | 3rdParty¦Vehicle¦Transformer¦Malfunctioning |  |  |  | None | Medium
3rd Party | Vehicle | Transformer | Normal | 3rdParty¦Vehicle¦Transformer¦Normal | #N/A |  |  | None | High
Animal | Bird found | (blank) | (blank) | Animal¦Birdfound¦¦ | #N/A |  |  | N/A | N/A
Animal | Bird found | (blank) | Broken | Animal¦Birdfound¦¦Broken | #N/A |  |  | N/A | N/A
Animal | Bird found | (blank) | Failed/Faulted | Animal¦Birdfound¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Animal | Bird found | (blank) | Normal | Animal¦Birdfound¦¦Normal | #N/A |  |  | N/A | N/A
Animal | Bird found | Booster | Normal | Animal¦Birdfound¦Booster¦Normal | #N/A |  |  | None | Very High
Animal | Bird found | Bus | Burned/flashed | Animal¦Birdfound¦Bus¦Burnedflashed | #N/A |  |  | None | None
Animal | Bird found | Bus | Normal | Animal¦Birdfound¦Bus¦Normal | #N/A |  |  | None | None
Animal | Bird found | Bushing | Arcing | Animal¦Birdfound¦Bushing¦Arcing | #N/A |  |  | None | Medium
Animal | Bird found | Bushing | Burned/flashed | Animal¦Birdfound¦Bushing¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Bird found | Bushing | Failed/Faulted | Animal¦Birdfound¦Bushing¦FailedFaulted | #N/A |  |  | None | Medium
Animal | Bird found | Bushing | Normal | Animal¦Birdfound¦Bushing¦Normal | #N/A |  |  | None | Medium
Animal | Bird found | Capacitor | Burned/flashed | Animal¦Birdfound¦Capacitor¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Bird found | Capacitor | Normal | Animal¦Birdfound¦Capacitor¦Normal | #N/A |  |  | None | None
Animal | Bird found | Circuit Breaker | Normal | Animal¦Birdfound¦CircuitBreaker¦Normal | #N/A |  |  | None | High
Animal | Bird found | Conductor, Overhead | Annealed | Animal¦Birdfound¦ConductorOverhead¦Annealed | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Bent or Twisted | Animal¦Birdfound¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Broken | Animal¦Birdfound¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Broken, wire on ground | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Animal | Bird found | Conductor, Overhead | Broken, wire on object | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
Animal | Bird found | Conductor, Overhead | Burned/flashed | Animal¦Birdfound¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Contaminated | Animal¦Birdfound¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Deteriorated | Animal¦Birdfound¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Normal | Animal¦Birdfound¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | On Ground | Animal¦Birdfound¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Animal | Bird found | Conductor, Overhead | Together | Animal¦Birdfound¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Animal | Bird found | Conductor, Underground | Normal | Animal¦Birdfound¦ConductorUnderground¦Normal | #N/A |  |  | None | None
Animal | Bird found | Connector or Splice (OH) | Arcing | Animal¦Birdfound¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | None | Very High
Animal | Bird found | Connector or Splice (OH) | Burned/flashed | Animal¦Birdfound¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Bird found | Connector or Splice (OH) | Normal | Animal¦Birdfound¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
Animal | Birdfound | CrossarmWood | Broken | Animal¦Birdfound¦CrossarmWood¦Broken |  |  |  | None | Very High
Animal | Bird found | Cutout, fuse holder | Broken | Animal¦Birdfound¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
Animal | Bird found | Cutout, fuse holder | Burned/flashed | Animal¦Birdfound¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | High
Animal | Bird found | Cutout, fuse holder | Failed/Faulted | Animal¦Birdfound¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | High
Animal | Bird found | Cutout, fuse holder | Normal | Animal¦Birdfound¦Cutoutfuseholder¦Normal | #N/A |  |  | None | High
Animal | Bird found | Fuse | Broken | Animal¦Birdfound¦Fuse¦Broken | #N/A |  |  | None | High
Animal | Bird found | Fuse | Burned Open | Animal¦Birdfound¦Fuse¦BurnedOpen | #N/A |  |  | None | High
Animal | Bird found | Fuse | Failed/Faulted | Animal¦Birdfound¦Fuse¦FailedFaulted | #N/A |  |  | None | High
Animal | Bird found | Fuse | Normal | Animal¦Birdfound¦Fuse¦Normal | #N/A |  |  | None | High
Animal | Bird found | Insulator | Broken | Animal¦Birdfound¦Insulator¦Broken | #N/A |  |  | None | Very High
Animal | Bird found | Insulator | Burned/flashed | Animal¦Birdfound¦Insulator¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Bird found | Insulator | Failed/Faulted | Animal¦Birdfound¦Insulator¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Bird found | Jumper | Bent or Twisted | Animal¦Birdfound¦Jumper¦BentorTwisted | #N/A |  |  | None | High
Animal | Bird found | Jumper | Burned/flashed | Animal¦Birdfound¦Jumper¦Burnedflashed | #N/A |  |  | None | High
Animal | Bird found | Jumper | Burned Open | Animal¦Birdfound¦Jumper¦BurnedOpen | #N/A |  |  | None | High
Animal | Bird found | Jumper | Normal | Animal¦Birdfound¦Jumper¦Normal | #N/A |  |  | None | High
Animal | Bird found | Lightning Arrestor | Broken | Animal¦Birdfound¦LightningArrestor¦Broken | #N/A |  |  | None | Very High
Animal | Bird found | Lightning Arrestor | Burned/flashed | Animal¦Birdfound¦LightningArrestor¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Bird found | Lightning Arrestor | Failed/Faulted | Animal¦Birdfound¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Bird found | Lightning Arrestor | Normal | Animal¦Birdfound¦LightningArrestor¦Normal | #N/A |  |  | None | Very High
Animal | Bird found | Metering Equipment | Normal | Animal¦Birdfound¦MeteringEquipment¦Normal | #N/A |  |  | None | None
Animal | Bird found | Other | Normal | Animal¦Birdfound¦Other¦Normal | #N/A |  |  | N/A | N/A
Animal | Bird found | Pole-Wood | Broken | Animal¦Birdfound¦PoleWood¦Broken | #N/A |  |  | None | High
Animal | Bird found | Pole-Wood | Broken, wire on ground | Animal¦Birdfound¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Animal | Bird found | Pole-Wood | Deteriorated | Animal¦Birdfound¦PoleWood¦Deteriorated | #N/A |  |  | None | High
Animal | Bird found | Pole-Wood | Normal | Animal¦Birdfound¦PoleWood¦Normal | #N/A |  |  | None | High
Animal | Bird found | Pothead(Riser Termination) | Arcing | Animal¦Birdfound¦Pothead(RiserTermination)¦Arcing | #N/A |  |  | None | Medium
Animal | Bird found | Pothead(Riser Termination) | Broken | Animal¦Birdfound¦Pothead(RiserTermination)¦Broken | #N/A |  |  | None | High
Animal | Bird found | Pothead(Riser Termination) | Burned/flashed | Animal¦Birdfound¦Pothead(RiserTermination)¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Bird found | Pothead(Riser Termination) | Normal | Animal¦Birdfound¦Pothead(RiserTermination)¦Normal | #N/A |  |  | None | High
Animal | Birdfound | PTCCVT | Burnedflashed | Animal¦Birdfound¦PTCCVT¦Burnedflashed |  |  |  | N/A | N/A
Animal | Bird found | PT/CCVT | Failed/Faulted | Animal¦Birdfound¦PTCCVT¦FailedFaulted | #N/A |  |  | None | None
Animal | Bird found | Recloser | Burned/flashed | Animal¦Birdfound¦Recloser¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Bird found | Recloser | Failed/Faulted | Animal¦Birdfound¦Recloser¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Bird found | Recloser | Malfunctioning | Animal¦Birdfound¦Recloser¦Malfunctioning | #N/A |  |  | None | None
Animal | Bird found | Recloser | Normal | Animal¦Birdfound¦Recloser¦Normal | #N/A |  |  | None | Very High
Animal | Birdfound | Regulator | Burnedflashed | Animal¦Birdfound¦Regulator¦Burnedflashed |  |  |  | None | Very High
Animal | Bird found | Regulator | Normal | Animal¦Birdfound¦Regulator¦Normal | #N/A |  |  | None | Medium High
Animal | Bird found | Relay | Malfunctioning | Animal¦Birdfound¦Relay¦Malfunctioning | #N/A |  |  | None | None
Animal | Bird found | Secondary | Normal | Animal¦Birdfound¦Secondary¦Normal | #N/A |  |  | None | High
Animal | Bird found | Switch (OH) | Normal | Animal¦Birdfound¦Switch(OH)¦Normal | #N/A |  |  | None | Very High
Animal | Bird found | Switch (UG) | Normal | Animal¦Birdfound¦Switch(UG)¦Normal | #N/A |  |  | None | None
Animal | Bird found | Transformer (OH) | (blank) | Animal¦Birdfound¦Transformer(OH)¦ | #N/A |  |  | None | High
Animal | Bird found | Transformer (OH) | Broken | Animal¦Birdfound¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Animal | Bird found | Transformer (OH) | Burned/flashed | Animal¦Birdfound¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | High
Animal | Bird found | Transformer (OH) | Failed/Faulted | Animal¦Birdfound¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
Animal | Bird found | Transformer (OH) | Normal | Animal¦Birdfound¦Transformer(OH)¦Normal | #N/A |  |  | None | High
Animal | Bird found | Transformer (UG) | Failed/Faulted | Animal¦Birdfound¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
Animal | Bird found | Transformer | (blank) | Animal¦Birdfound¦Transformer¦ | #N/A |  |  | None | High
Animal | Birdfound | Transformer | Broken | Animal¦Birdfound¦Transformer¦Broken |  |  |  | None | Very High
Animal | Bird found | Transformer | Burned/flashed | Animal¦Birdfound¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Animal | Birdfound | Transformer | BurnedOpen | Animal¦Birdfound¦Transformer¦BurnedOpen |  |  |  | None | Very High
Animal | Bird found | Transformer | Failed/Faulted | Animal¦Birdfound¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Animal | Bird found | Transformer | Malfunctioning | Animal¦Birdfound¦Transformer¦Malfunctioning | #N/A |  |  | None | High
Animal | Bird found | Transformer | Normal | Animal¦Birdfound¦Transformer¦Normal | #N/A |  |  | None | High
Animal | Bird found | Transformer | On Ground | Animal¦Birdfound¦Transformer¦OnGround | #N/A |  |  | None | Medium
Animal | Other | (blank) | Burned Open | Animal¦Other¦¦BurnedOpen | #N/A |  |  | N/A | N/A
Animal | Other | (blank) | Failed/Faulted | Animal¦Other¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Animal | Other | (blank) | Normal | Animal¦Other¦¦Normal | #N/A |  |  | N/A | N/A
Animal | Other | Anchor or Guy | Bent or Twisted | Animal¦Other¦AnchororGuy¦BentorTwisted | #N/A |  |  | None | Very High
Animal | Other | Anchor or Guy | Broken | Animal¦Other¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Animal | Other | Anchor or Guy | Normal | Animal¦Other¦AnchororGuy¦Normal | #N/A |  |  | None | Very High
Animal | Other | Bus | Normal | Animal¦Other¦Bus¦Normal | Animal¦Other¦Bus¦Normal |  |  | None | None
Animal | Other | Bushing | Burned/flashed | Animal¦Other¦Bushing¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Other | Bushing | Contaminated | Animal¦Other¦Bushing¦Contaminated | Animal¦Other¦Bushing¦Contaminated |  |  | None | Medium
Animal | Other | Bushing | Normal | Animal¦Other¦Bushing¦Normal | Animal¦Other¦Bushing¦Normal |  |  | None | Medium
Animal | Other | Circuit Breaker | Normal | Animal¦Other¦CircuitBreaker¦Normal | #N/A |  |  | None | High
Animal | Other | Conductor, Overhead | Bent or Twisted | Animal¦Other¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Very High
Animal | Other | Conductor, Overhead | Broken, wire on ground | Animal¦Other¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Animal | Other | Conductor, Overhead | Burned/flashed | Animal¦Other¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Other | Conductor, Overhead | Contaminated | Animal¦Other¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Very High
Animal | Other | Conductor, Overhead | Failed/Faulted | Animal¦Other¦ConductorOverhead¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Other | Conductor, Overhead | Normal | Animal¦Other¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Animal | Other | Conductor, Overhead | On Ground | Animal¦Other¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Animal | Other | Conductor, Overhead | Together | Animal¦Other¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Animal | Other | Conductor, Underground | Broken | Animal¦Other¦ConductorUnderground¦Broken | #N/A |  |  | None | None
Animal | Other | Conductor, Underground | Burned/flashed | Animal¦Other¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
Animal | Other | Conductor, Underground | Deteriorated | Animal¦Other¦ConductorUnderground¦Deteriorated | #N/A |  |  | None | None
Animal | Other | Conductor, Underground | Normal | Animal¦Other¦ConductorUnderground¦Normal | #N/A |  |  | None | None
Animal | Other | Connector or Splice (OH) | Arcing | Animal¦Other¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | None | Very High
Animal | Other | Connector or Splice (OH) | Burned Open | Animal¦Other¦ConnectororSplice(OH)¦BurnedOpen | #N/A |  |  | None | Very High
Animal | Other | Connector or Splice (OH) | Normal | Animal¦Other¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
Animal | Other | Crossarm, Steel | Normal | Animal¦Other¦CrossarmSteel¦Normal | #N/A |  |  | None | High
Animal | Other | Crossarm, Wood | Broken | Animal¦Other¦CrossarmWood¦Broken | #N/A |  |  | None | High
Animal | Other | Crossarm, Wood | Burned/flashed | Animal¦Other¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | High
Animal | Other | Crossarm, Wood | Normal | Animal¦Other¦CrossarmWood¦Normal | #N/A |  |  | None | High
Animal | Other | Customer Equipment | Normal | Animal¦Other¦CustomerEquipment¦Normal | #N/A |  |  | None | None
Animal | Other | Cutout, fuse holder | Broken | Animal¦Other¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
Animal | Other | Cutout, fuse holder | Failed/Faulted | Animal¦Other¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | High
Animal | Other | Cutout, fuse holder | Normal | Animal¦Other¦Cutoutfuseholder¦Normal | #N/A |  |  | None | High
Animal | Other | Elbow | Failed/Faulted | Animal¦Other¦Elbow¦FailedFaulted | #N/A |  |  | None | None
Animal | Other | Fuse | Broken | Animal¦Other¦Fuse¦Broken | Animal¦Other¦Fuse¦Broken |  |  | None | Very High
Animal | Other | Fuse | Burned Open | Animal¦Other¦Fuse¦BurnedOpen | #N/A |  |  | None | Very High
Animal | Other | Fuse | Failed/Faulted | Animal¦Other¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Other | Fuse | Normal | Animal¦Other¦Fuse¦Normal | Animal¦Other¦Fuse¦Normal |  |  | None | Very High
Animal | Other | Insulator | Broken | Animal¦Other¦Insulator¦Broken | Animal¦Other¦Insulator¦Broken |  |  | None | Very High
Animal | Other | Insulator | Burned/flashed | Animal¦Other¦Insulator¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Other | Insulator | Failed/Faulted | Animal¦Other¦Insulator¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Other | Insulator | Normal | Animal¦Other¦Insulator¦Normal | Animal¦Other¦Insulator¦Normal |  |  | None | Very High
Animal | Other | Jumper | (blank) | Animal¦Other¦Jumper¦ | #N/A |  |  | N/A | N/A
Animal | Other | Jumper | Broken | Animal¦Other¦Jumper¦Broken | Animal¦Other¦Jumper¦Broken |  |  | None | High
Animal | Other | Jumper | Burned/flashed | Animal¦Other¦Jumper¦Burnedflashed | #N/A |  |  | None | High
Animal | Other | Jumper | Burned Open | Animal¦Other¦Jumper¦BurnedOpen | #N/A |  |  | None | High
Animal | Other | Jumper | Normal | Animal¦Other¦Jumper¦Normal | Animal¦Other¦Jumper¦Normal |  |  | None | High
Animal | Other | Lightning Arrestor | Broken | Animal¦Other¦LightningArrestor¦Broken | #N/A |  |  | None | Very High
Animal | Other | Lightning Arrestor | Burned/flashed | Animal¦Other¦LightningArrestor¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Other | Lightning Arrestor | Failed/Faulted | Animal¦Other¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Other | Lightning Arrestor | Normal | Animal¦Other¦LightningArrestor¦Normal | #N/A |  |  | None | Very High
Animal | Other | Other | Broken | Animal¦Other¦Other¦Broken | Animal¦Other¦Other¦Broken |  |  | N/A | N/A
Animal | Other | Other | Failed/Faulted | Animal¦Other¦Other¦FailedFaulted | #N/A |  |  | None | N/A
Animal | Other | Other | Normal | Animal¦Other¦Other¦Normal | Animal¦Other¦Other¦Normal |  |  | N/A | N/A
Animal | Other | Pole - Tower, steel | Normal | Animal¦Other¦PoleTowersteel¦Normal | #N/A |  |  | None | High
Animal | Other | Pole-Wood | Broken | Animal¦Other¦PoleWood¦Broken | #N/A |  |  | None | High
Animal | Other | Pole-Wood | Broken, wire on ground | Animal¦Other¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Animal | Other | Pole-Wood | Burned/flashed | Animal¦Other¦PoleWood¦Burnedflashed | #N/A |  |  | None | High
Animal | Other | Pole-Wood | Deteriorated | Animal¦Other¦PoleWood¦Deteriorated | #N/A |  |  | None | High
Animal | Other | Pole-Wood | Normal | Animal¦Other¦PoleWood¦Normal | #N/A |  |  | None | High
Animal | Other | Pothead(Riser Termination) | Burned/flashed | Animal¦Other¦Pothead(RiserTermination)¦Burnedflashed | #N/A |  |  | None | High
Animal | Other | Pothead(Riser Termination) | Deteriorated | Animal¦Other¦Pothead(RiserTermination)¦Deteriorated | #N/A |  |  | None | High
Animal | Other | Pothead(Riser Termination) | Normal | Animal¦Other¦Pothead(RiserTermination)¦Normal | #N/A |  |  | None | High
Animal | Other | Pothead/Riser Termination | Normal | Animal¦Other¦PotheadRiserTermination¦Normal | #N/A |  |  | None | High
Animal | Other | PT/CCVT | Burned/flashed | Animal¦Other¦PTCCVT¦Burnedflashed | #N/A |  |  | None | None
Animal | Other | Recloser | Burned/flashed | Animal¦Other¦Recloser¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Other | Recloser | Failed/Faulted | Animal¦Other¦Recloser¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Other | Recloser | Malfunctioning | Animal¦Other¦Recloser¦Malfunctioning | Animal¦Other¦Recloser¦Malfunctioning |  |  | None | Very High
Animal | Other | Recloser | Normal | Animal¦Other¦Recloser¦Normal | Animal¦Other¦Recloser¦Normal |  |  | None | Very High
Animal | Other | Regulator | Burned/flashed | Animal¦Other¦Regulator¦Burnedflashed | #N/A |  |  | None | Medium High
Animal | Other | Secondary | Burned/flashed | Animal¦Other¦Secondary¦Burnedflashed | #N/A |  |  | None | High
Animal | Other | Secondary | Failed/Faulted | Animal¦Other¦Secondary¦FailedFaulted | #N/A |  |  | None | High
Animal | Other | Secondary | Normal | Animal¦Other¦Secondary¦Normal |  |  |  | None | High
Animal | Other | Sectionalizer | Burned/flashed | Animal¦Other¦Sectionalizer¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Other | Sectionalizer | Normal | Animal¦Other¦Sectionalizer¦Normal | Animal¦Other¦Sectionalizer¦Normal |  |  | None | Medium
Animal | Other | Switch (OH) | Broken | Animal¦Other¦Switch(OH)¦Broken | #N/A |  |  | None | Very High
Animal | Other | Switch (OH) | Burned/flashed | Animal¦Other¦Switch(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Other | Switch (OH) | Normal | Animal¦Other¦Switch(OH)¦Normal | #N/A |  |  | None | Very High
Animal | Other | Transformer (OH) | (blank) | Animal¦Other¦Transformer(OH)¦ | #N/A |  |  | None | High
Animal | Other | Transformer (OH) | Broken | Animal¦Other¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Animal | Other | Transformer (OH) | Burned/flashed | Animal¦Other¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | High
Animal | Other | Transformer (OH) | Failed/Faulted | Animal¦Other¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
Animal | Other | Transformer (OH) | Normal | Animal¦Other¦Transformer(OH)¦Normal | #N/A |  |  | None | High
Animal | Other | Transformer (UG) | Arcing | Animal¦Other¦Transformer(UG)¦Arcing | #N/A |  |  | None | None
Animal | Other | Transformer (UG) | Burned/flashed | Animal¦Other¦Transformer(UG)¦Burnedflashed | #N/A |  |  | None | None
Animal | Other | Transformer (UG) | Failed/Faulted | Animal¦Other¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
Animal | Other | Transformer (UG) | Normal | Animal¦Other¦Transformer(UG)¦Normal | #N/A |  |  | None | None
Animal | Other | Transformer | Broken | Animal¦Other¦Transformer¦Broken | Animal¦Other¦Transformer¦Broken |  |  | None | High
Animal | Other | Transformer | Burned/flashed | Animal¦Other¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Animal | Other | Transformer | Failed/Faulted | Animal¦Other¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Animal | Other | Transformer Power | Normal | Animal¦Other¦TransformerPower¦Normal | #N/A |  |  | None | None
Animal | Other | Woodpin | Broken | Animal¦Other¦Woodpin¦Broken | Animal¦Other¦Woodpin¦Broken |  |  | None | Very High
Animal | Squirrel | (blank) | (blank) | Animal¦Squirrel¦¦ | #N/A |  |  | N/A | N/A
Animal | Squirrel | (blank) | Broken | Animal¦Squirrel¦¦Broken | #N/A |  |  | N/A | N/A
Animal | Squirrel | (blank) | Burned Open | Animal¦Squirrel¦¦BurnedOpen | #N/A |  |  | N/A | N/A
Animal | Squirrel | (blank) | Failed/Faulted | Animal¦Squirrel¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Animal | Squirrel | (blank) | Normal | Animal¦Squirrel¦¦Normal | #N/A |  |  | N/A | N/A
Animal | Squirrel | Bus | Normal | Animal¦Squirrel¦Bus¦Normal | Animal¦Squirrel¦Bus¦Normal |  |  | None | None
Animal | Squirrel | Bushing | Broken | Animal¦Squirrel¦Bushing¦Broken | Animal¦Squirrel¦Bushing¦Broken |  |  | None | Medium
Animal | Squirrel | Bushing | Burned/flashed | Animal¦Squirrel¦Bushing¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Squirrel | Bushing | Failed/Faulted | Animal¦Squirrel¦Bushing¦FailedFaulted | #N/A |  |  | None | Medium
Animal | Squirrel | Bushing | Normal | Animal¦Squirrel¦Bushing¦Normal | Animal¦Squirrel¦Bushing¦Normal |  |  | None | Medium
Animal | Squirrel | Capacitor | Failed/Faulted | Animal¦Squirrel¦Capacitor¦FailedFaulted | #N/A |  |  | None | Medium
Animal | Squirrel | Conductor, Overhead | (blank) | Animal¦Squirrel¦ConductorOverhead¦ | #N/A |  |  | N/A | N/A
Animal | Squirrel | Conductor, Overhead | Arcing | Animal¦Squirrel¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
Animal | Squirrel | ConductorOverhead | Broken | Animal¦Squirrel¦ConductorOverhead¦Broken |  |  |  | None | Very High
Animal | Squirrel | Conductor, Overhead | Broken, wire on ground | Animal¦Squirrel¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Animal | Squirrel | Conductor, Overhead | Burned/flashed | Animal¦Squirrel¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Squirrel | Conductor, Overhead | Deteriorated | Animal¦Squirrel¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
Animal | Squirrel | Conductor, Overhead | Normal | Animal¦Squirrel¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Animal | Squirrel | Conductor, Overhead | Together | Animal¦Squirrel¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Animal | Squirrel | Conductor, Underground | Broken | Animal¦Squirrel¦ConductorUnderground¦Broken | #N/A |  |  | None | None
Animal | Squirrel | Conductor, Underground | Burned/flashed | Animal¦Squirrel¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
Animal | Squirrel | Conductor, Underground | Normal | Animal¦Squirrel¦ConductorUnderground¦Normal | #N/A |  |  | None | None
Animal | Squirrel | Connector or Splice (OH) | Normal | Animal¦Squirrel¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
Animal | Squirrel | Connector or Splice (UG) | Normal | Animal¦Squirrel¦ConnectororSplice(UG)¦Normal | #N/A |  |  | None | None
Animal | Squirrel | Crossarm, Steel | Normal | Animal¦Squirrel¦CrossarmSteel¦Normal | #N/A |  |  | None | High
Animal | Squirrel | Crossarm, Wood | Broken | Animal¦Squirrel¦CrossarmWood¦Broken | #N/A |  |  | None | High
Animal | Squirrel | Crossarm, Wood | Burned/flashed | Animal¦Squirrel¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Crossarm, Wood | Normal | Animal¦Squirrel¦CrossarmWood¦Normal | #N/A |  |  | None | High
Animal | Squirrel | Cutout, Fused, Distribution | Failed/Faulted | Animal¦Squirrel¦CutoutFusedDistribution¦FailedFaulted | #N/A |  |  | None | High
Animal | Squirrel | Cutout, fuse holder | Broken | Animal¦Squirrel¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
Animal | Squirrel | Cutout, fuse holder | Burned/flashed | Animal¦Squirrel¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Cutout, fuse holder | Failed/Faulted | Animal¦Squirrel¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | High
Animal | Squirrel | Cutout, fuse holder | Normal | Animal¦Squirrel¦Cutoutfuseholder¦Normal | #N/A |  |  | None | High
Animal | Squirrel | Footings, Tower or Pole | Burned/flashed | Animal¦Squirrel¦FootingsTowerorPole¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Fuse | Broken | Animal¦Squirrel¦Fuse¦Broken | Animal¦Squirrel¦Fuse¦Broken |  |  | None | High
Animal | Squirrel | Fuse | Burned Open | Animal¦Squirrel¦Fuse¦BurnedOpen | #N/A |  |  | None | High
Animal | Squirrel | Fuse | Failed/Faulted | Animal¦Squirrel¦Fuse¦FailedFaulted | #N/A |  |  | None | High
Animal | Squirrel | Fuse | Normal | Animal¦Squirrel¦Fuse¦Normal | Animal¦Squirrel¦Fuse¦Normal |  |  | None | High
Animal | Squirrel | Insulator | Broken | Animal¦Squirrel¦Insulator¦Broken | Animal¦Squirrel¦Insulator¦Broken |  |  | None | Very High
Animal | Squirrel | Insulator | Burned/flashed | Animal¦Squirrel¦Insulator¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Squirrel | Insulator | FailedFaulted | Animal¦Squirrel¦Insulator¦FailedFaulted |  |  |  | None | Very High
Animal | Squirrel | Insulator | Normal | Animal¦Squirrel¦Insulator¦Normal | Animal¦Squirrel¦Insulator¦Normal |  |  | None | Very High
Animal | Squirrel | Jumper | (blank) | Animal¦Squirrel¦Jumper¦ | #N/A |  |  | N/A | N/A
Animal | Squirrel | Jumper | Broken | Animal¦Squirrel¦Jumper¦Broken | Animal¦Squirrel¦Jumper¦Broken |  |  | None | High
Animal | Squirrel | Jumper | Burned/flashed | Animal¦Squirrel¦Jumper¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Jumper | Burned Open | Animal¦Squirrel¦Jumper¦BurnedOpen | #N/A |  |  | None | High
Animal | Squirrel | Jumper | Normal | Animal¦Squirrel¦Jumper¦Normal | Animal¦Squirrel¦Jumper¦Normal |  |  | None | High
Animal | Squirrel | Lightning Arrestor | Broken | Animal¦Squirrel¦LightningArrestor¦Broken | #N/A |  |  | None | Very High
Animal | Squirrel | Lightning Arrestor | Burned/flashed | Animal¦Squirrel¦LightningArrestor¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Squirrel | Lightning Arrestor | Failed/Faulted | Animal¦Squirrel¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Squirrel | Lightning Arrestor | Normal | Animal¦Squirrel¦LightningArrestor¦Normal | #N/A |  |  | None | Very High
Animal | Squirrel | Other | Normal | Animal¦Squirrel¦Other¦Normal | Animal¦Squirrel¦Other¦Normal |  |  | N/A | N/A
Animal | Squirrel | Pole-Wood | Burned/flashed | Animal¦Squirrel¦PoleWood¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Pole-Wood | Normal | Animal¦Squirrel¦PoleWood¦Normal | #N/A |  |  | None | High
Animal | Squirrel | Pothead(Riser Termination) | Broken | Animal¦Squirrel¦Pothead(RiserTermination)¦Broken | #N/A |  |  | None | High
Animal | Squirrel | Pothead(Riser Termination) | Burned/flashed | Animal¦Squirrel¦Pothead(RiserTermination)¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Squirrel | Pothead(Riser Termination) | Failed/Faulted | Animal¦Squirrel¦Pothead(RiserTermination)¦FailedFaulted | #N/A |  |  | None | High
Animal | Squirrel | Pothead(Riser Termination) | Normal | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal | #N/A |  |  | None | High
Animal | Squirrel | Pothead/Riser Termination | Burned/flashed | Animal¦Squirrel¦PotheadRiserTermination¦Burnedflashed | #N/A |  |  | None | Medium
Animal | Squirrel | Pothead/Riser Termination | Failed/Faulted | Animal¦Squirrel¦PotheadRiserTermination¦FailedFaulted | #N/A |  |  | None | Medium
Animal | Squirrel | PT/CCVT | Normal | Animal¦Squirrel¦PTCCVT¦Normal | #N/A |  |  | None | None
Animal | Squirrel | Recloser | Broken | Animal¦Squirrel¦Recloser¦Broken | Animal¦Squirrel¦Recloser¦Broken |  |  | None | Medium
Animal | Squirrel | Recloser | Broken, wire on ground | Animal¦Squirrel¦Recloser¦Brokenwireonground | #N/A |  |  | None | Medium
Animal | Squirrel | Recloser | Burned/flashed | Animal¦Squirrel¦Recloser¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Squirrel | Recloser | Failed/Faulted | Animal¦Squirrel¦Recloser¦FailedFaulted | #N/A |  |  | None | Very High
Animal | Squirrel | Recloser | Normal | Animal¦Squirrel¦Recloser¦Normal | Animal¦Squirrel¦Recloser¦Normal |  |  | None | Very High
Animal | Squirrel | Regulator | Burned/flashed | Animal¦Squirrel¦Regulator¦Burnedflashed | #N/A |  |  | None | Medium High
Animal | Squirrel | Regulator | Normal | Animal¦Squirrel¦Regulator¦Normal |  |  |  | None | Very High
Animal | Squirrel | Riser | Normal | Animal¦Squirrel¦Riser¦Normal | Animal¦Squirrel¦Riser¦Normal |  |  | None | High
Animal | Squirrel | Secondary | Broken | Animal¦Squirrel¦Secondary¦Broken | Animal¦Squirrel¦Secondary¦Broken |  |  | None | Medium
Animal | Squirrel | Secondary | Burned/flashed | Animal¦Squirrel¦Secondary¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Secondary | Burned Open | Animal¦Squirrel¦Secondary¦BurnedOpen | #N/A |  |  | None | Medium
Animal | Squirrel | Secondary | Normal | Animal¦Squirrel¦Secondary¦Normal | Animal¦Squirrel¦Secondary¦Normal |  |  | None | High
Animal | Squirrel | Switch (OH) | Burned/flashed | Animal¦Squirrel¦Switch(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Animal | Squirrel | Switch (OH) | Normal | Animal¦Squirrel¦Switch(OH)¦Normal | #N/A |  |  | None | Very High
Animal | Squirrel | Switch (UG) | Leaking | Animal¦Squirrel¦Switch(UG)¦Leaking | #N/A |  |  | None | None
Animal | Squirrel | Switch | Normal | Animal¦Squirrel¦Switch¦Normal | Animal¦Squirrel¦Switch¦Normal |  |  | None | High
Animal | Squirrel | Transformer (OH) | Arcing | Animal¦Squirrel¦Transformer(OH)¦Arcing | #N/A |  |  | None | High
Animal | Squirrel | Transformer (OH) | Broken | Animal¦Squirrel¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Animal | Squirrel | Transformer (OH) | Burned/flashed | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Transformer (OH) | Failed/Faulted | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
Animal | Squirrel | Transformer (OH) | Leaking | Animal¦Squirrel¦Transformer(OH)¦Leaking | #N/A |  |  | None | High
Animal | Squirrel | Transformer (OH) | Normal | Animal¦Squirrel¦Transformer(OH)¦Normal | #N/A |  |  | None | High
Animal | Squirrel | Transformer (UG) | Normal | Animal¦Squirrel¦Transformer(UG)¦Normal | #N/A |  |  | None | None
Animal | Squirrel | Transformer | (blank) | Animal¦Squirrel¦Transformer¦ | #N/A |  |  | None | High
Animal | Squirrel | Transformer | Broken | Animal¦Squirrel¦Transformer¦Broken | Animal¦Squirrel¦Transformer¦Broken |  |  | None | High
Animal | Squirrel | Transformer | Burned/flashed | Animal¦Squirrel¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Animal | Squirrel | Transformer | Burned Open | Animal¦Squirrel¦Transformer¦BurnedOpen | #N/A |  |  | None | High
Animal | Squirrel | Transformer | Deteriorated | Animal¦Squirrel¦Transformer¦Deteriorated | Animal¦Squirrel¦Transformer¦Deteriorated |  |  | None | High
Animal | Squirrel | Transformer | Failed/Faulted | Animal¦Squirrel¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Animal | Squirrel | Transformer | Malfunctioning | Animal¦Squirrel¦Transformer¦Malfunctioning | Animal¦Squirrel¦Transformer¦Malfunctioning |  |  | None | High
Animal | Squirrel | Transformer | Normal | Animal¦Squirrel¦Transformer¦Normal | Animal¦Squirrel¦Transformer¦Normal |  |  | None | High
Animal | Squirrel | Transformer | On Ground | Animal¦Squirrel¦Transformer¦OnGround | #N/A |  |  | None | Medium
Animal | Squirrel | Transformer, STA SVC | Failed/Faulted | Animal¦Squirrel¦TransformerSTASVC¦FailedFaulted | #N/A |  |  | None | None
Company Initiated | Construction Activity/equip, company | (blank) | (blank) | CompanyInitiated¦ConstructionActivityequipcompany¦¦ | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | (blank) | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | AnchororGuy | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Broken |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Anchor or Guy | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Anchor or Guy | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Bus | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Bus¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | Capacitor | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Capacitor¦Broken |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Arcing | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Broken, wire on ground | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Burned/flashed | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Burnedflashed | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | ConductorOverhead | Contaminated | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Contaminated |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | On Ground | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦OnGround | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Together | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Together | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Underground | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorUnderground¦Deteriorated | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | ConductorUnderground | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorUnderground¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Broken, wire on ground | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Broken, wire on object | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Brokenwireonobject | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Burned/flashed | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | Cutoutfuseholder | FailedFaulted | CompanyInitiated¦ConstructionActivityequipcompany¦Cutoutfuseholder¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Cutout, fuse holder | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Cutoutfuseholder¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Elbow | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Elbow¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | Elbow | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Elbow¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Fuse | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Fuse | Failed/Faulted | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Fuse | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Generator | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Generator¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Generator | Malfunctioning | CompanyInitiated¦ConstructionActivityequipcompany¦Generator¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Insulator | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Insulator | Broken, wire on ground | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Brokenwireonground | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Insulator | Burned/flashed | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Jumper | Arcing | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Jumper | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Jumper | Burned/flashed | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Jumper | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Other | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Other | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Pole-Wood | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Pole-Wood | Burned/flashed | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Pole-Wood | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | Recloser | Malfunctioning | CompanyInitiated¦ConstructionActivityequipcompany¦Recloser¦Malfunctioning |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Recloser | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Recloser¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Regulator | Malfunctioning | CompanyInitiated¦ConstructionActivityequipcompany¦Regulator¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Secondary | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Secondary¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | Serviceconductor | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Serviceconductor¦Broken |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Service conductor | Broken, wire on object | CompanyInitiated¦ConstructionActivityequipcompany¦Serviceconductor¦Brokenwireonobject | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Switch (OH) | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Switch(OH)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) | (blank) | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦ | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) | Failed/Faulted | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (UG) | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(UG)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (UG) | Failed/Faulted | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(UG)¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (UG) | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(UG)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer | Leaking | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Leaking | #N/A |  |  | N/A | N/A
CompanyInitiated | ConstructionActivityequipcompany | Transformer | Malfunctioning | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Malfunctioning |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Contact with High Voltage, company | (blank) | Failed/Faulted | CompanyInitiated¦ContactwithHighVoltagecompany¦¦FailedFaulted | #N/A |  |  | N/A | N/A
CompanyInitiated | ContactwithHighVoltagecompany | ConductorOverhead | Brokenwireonground | CompanyInitiated¦ContactwithHighVoltagecompany¦ConductorOverhead¦Brokenwireonground |  |  |  | N/A | N/A
Company Initiated | Contact with High Voltage, company | Conductor, Overhead | Normal | CompanyInitiated¦ContactwithHighVoltagecompany¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Contact with High Voltage, company | Fuse | Failed/Faulted | CompanyInitiated¦ContactwithHighVoltagecompany¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Contact with High Voltage, company | Fuse | Normal | CompanyInitiated¦ContactwithHighVoltagecompany¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Contact with High Voltage, company | Transformer (OH) | Failed/Faulted | CompanyInitiated¦ContactwithHighVoltagecompany¦Transformer(OH)¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Contact with High Voltage, company | Transformer | Broken | CompanyInitiated¦ContactwithHighVoltagecompany¦Transformer¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Circuit Breaker | Normal | CompanyInitiated¦Coordinationfailure¦CircuitBreaker¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Coordinationfailure | ConductorOverhead | Brokenwireonground | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Brokenwireonground |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Conductor, Overhead | Burned/flashed | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Conductor, Overhead | Normal | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Coordinationfailure | CustomerEquipment | Normal | CompanyInitiated¦Coordinationfailure¦CustomerEquipment¦Normal |  |  |  | N/A | N/A
CompanyInitiated | Coordinationfailure | Cutoutfuseholder | Normal | CompanyInitiated¦Coordinationfailure¦Cutoutfuseholder¦Normal |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Fuse | Failed/Faulted | CompanyInitiated¦Coordinationfailure¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Fuse | Normal | CompanyInitiated¦Coordinationfailure¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Generator | Normal | CompanyInitiated¦Coordinationfailure¦Generator¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Coordinationfailure | Interrupter | Malfunctioning | CompanyInitiated¦Coordinationfailure¦Interrupter¦Malfunctioning |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Jumper | Normal | CompanyInitiated¦Coordinationfailure¦Jumper¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Coordinationfailure | Other | BurnedOpen | CompanyInitiated¦Coordinationfailure¦Other¦BurnedOpen |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Other | Malfunctioning | CompanyInitiated¦Coordinationfailure¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Other | Normal | CompanyInitiated¦Coordinationfailure¦Other¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Coordinationfailure | PoleWood | Broken | CompanyInitiated¦Coordinationfailure¦PoleWood¦Broken |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Recloser | Malfunctioning | CompanyInitiated¦Coordinationfailure¦Recloser¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Recloser | Normal | CompanyInitiated¦Coordinationfailure¦Recloser¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Relay | Normal | CompanyInitiated¦Coordinationfailure¦Relay¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Service conductor | Normal | CompanyInitiated¦Coordinationfailure¦Serviceconductor¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Transformer | Burned Open | CompanyInitiated¦Coordinationfailure¦Transformer¦BurnedOpen | #N/A |  |  | N/A | N/A
Company Initiated | Coordination failure | Transformer | Failed/Faulted | CompanyInitiated¦Coordinationfailure¦Transformer¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Dig in, company | Conductor, Underground | Broken | CompanyInitiated¦Digincompany¦ConductorUnderground¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Dig in, company | Connector or Splice (UG) | Broken | CompanyInitiated¦Digincompany¦ConnectororSplice(UG)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Dig in, company | Pole-Wood | Normal | CompanyInitiated¦Digincompany¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Dig in, company | Secondary | Broken | CompanyInitiated¦Digincompany¦Secondary¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Dig in, company | Service conductor | Broken | CompanyInitiated¦Digincompany¦Serviceconductor¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Anchor or Guy | Broken | CompanyInitiated¦ImproperConstruction¦AnchororGuy¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Arcing | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Bent or Twisted | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦BentorTwisted | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Broken | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Broken, wire on ground | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
CompanyInitiated | ImproperConstruction | ConductorOverhead | Burnedflashed | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Burnedflashed |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Deteriorated | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Normal | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Together | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Together | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Underground | Normal | CompanyInitiated¦ImproperConstruction¦ConductorUnderground¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Connector or Splice (OH) | Arcing | CompanyInitiated¦ImproperConstruction¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Connector or Splice (OH) | Broken | CompanyInitiated¦ImproperConstruction¦ConnectororSplice(OH)¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | ImproperConstruction | ConnectororSplice(OH) | Normal | CompanyInitiated¦ImproperConstruction¦ConnectororSplice(OH)¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Crossarm, Wood | Broken | CompanyInitiated¦ImproperConstruction¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Crossarm, Wood | Normal | CompanyInitiated¦ImproperConstruction¦CrossarmWood¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ImproperConstruction | Cutoutfuseholder | Broken | CompanyInitiated¦ImproperConstruction¦Cutoutfuseholder¦Broken |  |  |  | N/A | N/A
CompanyInitiated | ImproperConstruction | Cutoutfuseholder | Normal | CompanyInitiated¦ImproperConstruction¦Cutoutfuseholder¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Fuse | Arcing | CompanyInitiated¦ImproperConstruction¦Fuse¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Fuse | Burned Open | CompanyInitiated¦ImproperConstruction¦Fuse¦BurnedOpen | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Fuse | Failed/Faulted | CompanyInitiated¦ImproperConstruction¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Fuse | Normal | CompanyInitiated¦ImproperConstruction¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Jumper | (blank) | CompanyInitiated¦ImproperConstruction¦Jumper¦ | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Jumper | Arcing | CompanyInitiated¦ImproperConstruction¦Jumper¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Jumper | Broken | CompanyInitiated¦ImproperConstruction¦Jumper¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Jumper | Normal | CompanyInitiated¦ImproperConstruction¦Jumper¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Other | Broken | CompanyInitiated¦ImproperConstruction¦Other¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Other | Malfunctioning | CompanyInitiated¦ImproperConstruction¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Pole-Wood | Broken | CompanyInitiated¦ImproperConstruction¦PoleWood¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Pole-Wood | Normal | CompanyInitiated¦ImproperConstruction¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Switch (OH) | Arcing | CompanyInitiated¦ImproperConstruction¦Switch(OH)¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Switch (UG) | Broken | CompanyInitiated¦ImproperConstruction¦Switch(UG)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Transformer (OH) | Broken | CompanyInitiated¦ImproperConstruction¦Transformer(OH)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Transformer (OH) | Failed/Faulted | CompanyInitiated¦ImproperConstruction¦Transformer(OH)¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Improper Construction | Transformer (UG) | Normal | CompanyInitiated¦ImproperConstruction¦Transformer(UG)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Insulator washing | Bus | Contaminated | CompanyInitiated¦Insulatorwashing¦Bus¦Contaminated | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | (blank) | (blank) | CompanyInitiated¦Operatingerror¦¦ | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Circuit Breaker | Normal | CompanyInitiated¦Operatingerror¦CircuitBreaker¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Conductor, Overhead | Normal | CompanyInitiated¦Operatingerror¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Connector or Splice (OH) | Broken | CompanyInitiated¦Operatingerror¦ConnectororSplice(OH)¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | Operatingerror | ConnectororSplice(OH) | Normal | CompanyInitiated¦Operatingerror¦ConnectororSplice(OH)¦Normal |  |  |  | N/A | N/A
CompanyInitiated | Operatingerror | Cutoutfuseholder | Normal | CompanyInitiated¦Operatingerror¦Cutoutfuseholder¦Normal |  |  |  | N/A | N/A
Company Initiated | Operating error | Fuse | (blank) | CompanyInitiated¦Operatingerror¦Fuse¦ | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Fuse | Burned Open | CompanyInitiated¦Operatingerror¦Fuse¦BurnedOpen | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Fuse | Failed/Faulted | CompanyInitiated¦Operatingerror¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Fuse | Normal | CompanyInitiated¦Operatingerror¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Jumper | Normal | CompanyInitiated¦Operatingerror¦Jumper¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Other | Normal | CompanyInitiated¦Operatingerror¦Other¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Pole-Wood | Normal | CompanyInitiated¦Operatingerror¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Recloser | Normal | CompanyInitiated¦Operatingerror¦Recloser¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Relay | Normal | CompanyInitiated¦Operatingerror¦Relay¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Switch (OH) | Normal | CompanyInitiated¦Operatingerror¦Switch(OH)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Switch (UG) | Normal | CompanyInitiated¦Operatingerror¦Switch(UG)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Switch | Normal | CompanyInitiated¦Operatingerror¦Switch¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Operating error | Transformer Power | Normal | CompanyInitiated¦Operatingerror¦TransformerPower¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | (blank) | (blank) | CompanyInitiated¦OtherCircuits¦¦ | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Circuit Breaker | Normal | CompanyInitiated¦OtherCircuits¦CircuitBreaker¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Conductor, Overhead | Arcing | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Conductor, Overhead | Deteriorated | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Conductor, Overhead | Normal | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Conductor, Overhead | Together | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Together | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Crossarm, Wood | Broken | CompanyInitiated¦OtherCircuits¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | OtherCircuits | Fuse | Arcing | CompanyInitiated¦OtherCircuits¦Fuse¦Arcing |  |  |  | N/A | N/A
Company Initiated | Other Circuits | Fuse | Normal | CompanyInitiated¦OtherCircuits¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Generator | Malfunctioning | CompanyInitiated¦OtherCircuits¦Generator¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Insulator | Broken | CompanyInitiated¦OtherCircuits¦Insulator¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Jumper | Broken | CompanyInitiated¦OtherCircuits¦Jumper¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Lightning Arrestor | Failed/Faulted | CompanyInitiated¦OtherCircuits¦LightningArrestor¦FailedFaulted | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Other | Broken | CompanyInitiated¦OtherCircuits¦Other¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Other | Normal | CompanyInitiated¦OtherCircuits¦Other¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Pole-Wood | Burned/flashed | CompanyInitiated¦OtherCircuits¦PoleWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Other Circuits | Pole-Wood | Deteriorated | CompanyInitiated¦OtherCircuits¦PoleWood¦Deteriorated | #N/A |  |  | N/A | N/A
CompanyInitiated | OtherCircuits | Recloser | Normal | CompanyInitiated¦OtherCircuits¦Recloser¦Normal |  |  |  | N/A | N/A
Company Initiated | Other Circuits | Regulator | Broken | CompanyInitiated¦OtherCircuits¦Regulator¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | OtherCircuits | Regulator | Normal | CompanyInitiated¦OtherCircuits¦Regulator¦Normal |  |  |  | N/A | N/A
CompanyInitiated | OtherCircuits | Secondary | Normal | CompanyInitiated¦OtherCircuits¦Secondary¦Normal |  |  |  | N/A | N/A
CompanyInitiated | OtherCircuits | Switch(UG) | Broken | CompanyInitiated¦OtherCircuits¦Switch(UG)¦Broken |  |  |  | N/A | N/A
CompanyInitiated | OtherCircuits | Transformer(OH) | Normal | CompanyInitiated¦OtherCircuits¦Transformer(OH)¦Normal |  |  |  | N/A | N/A
CompanyInitiated | OtherCircuits | Transformer | Normal | CompanyInitiated¦OtherCircuits¦Transformer¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | (blank) | (blank) | CompanyInitiated¦Personnelcompany¦¦ | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | (blank) | Broken | CompanyInitiated¦Personnelcompany¦¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Bus | Normal | CompanyInitiated¦Personnelcompany¦Bus¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Capacitor | Normal | CompanyInitiated¦Personnelcompany¦Capacitor¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Circuit Breaker | Normal | CompanyInitiated¦Personnelcompany¦CircuitBreaker¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | ConductorOverhead |  | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦ |  |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | ConductorOverhead | Broken | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Broken |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Conductor, Overhead | Broken, wire on ground | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | ConductorOverhead | Deteriorated | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Deteriorated |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Conductor, Overhead | Normal | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | ConductorOverhead | Together | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Together |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Conductor, Underground | Burned/flashed | CompanyInitiated¦Personnelcompany¦ConductorUnderground¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Conductor, Underground | Normal | CompanyInitiated¦Personnelcompany¦ConductorUnderground¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Connector or Splice (OH) | Broken | CompanyInitiated¦Personnelcompany¦ConnectororSplice(OH)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Connector or Splice (OH) | Normal | CompanyInitiated¦Personnelcompany¦ConnectororSplice(OH)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Crossarm, Wood | Broken | CompanyInitiated¦Personnelcompany¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Crossarm, Wood | Deteriorated | CompanyInitiated¦Personnelcompany¦CrossarmWood¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | CT | Normal | CompanyInitiated¦Personnelcompany¦CT¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Cutoutfuseholder | Normal | CompanyInitiated¦Personnelcompany¦Cutoutfuseholder¦Normal |  |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Elbow | Normal | CompanyInitiated¦Personnelcompany¦Elbow¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Fuse | Burned Open | CompanyInitiated¦Personnelcompany¦Fuse¦BurnedOpen | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Fuse | Normal | CompanyInitiated¦Personnelcompany¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Generator | Broken | CompanyInitiated¦Personnelcompany¦Generator¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Generator | Malfunctioning | CompanyInitiated¦Personnelcompany¦Generator¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Generator | Normal | CompanyInitiated¦Personnelcompany¦Generator¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Insulator | Broken | CompanyInitiated¦Personnelcompany¦Insulator¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Insulator | Normal | CompanyInitiated¦Personnelcompany¦Insulator¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Jumper | Broken | CompanyInitiated¦Personnelcompany¦Jumper¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Jumper | Normal | CompanyInitiated¦Personnelcompany¦Jumper¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | LightningArrestor |  | CompanyInitiated¦Personnelcompany¦LightningArrestor¦ |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Lightning Arrestor | Burned/flashed | CompanyInitiated¦Personnelcompany¦LightningArrestor¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Metering Equipment | (blank) | CompanyInitiated¦Personnelcompany¦MeteringEquipment¦ | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Other | Arcing | CompanyInitiated¦Personnelcompany¦Other¦Arcing | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Other | Broken | CompanyInitiated¦Personnelcompany¦Other¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Other | Deteriorated | CompanyInitiated¦Personnelcompany¦Other¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Other | Normal | CompanyInitiated¦Personnelcompany¦Other¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Pole-Wood | Broken | CompanyInitiated¦Personnelcompany¦PoleWood¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Pole-Wood | Deteriorated | CompanyInitiated¦Personnelcompany¦PoleWood¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Pole-Wood | Normal | CompanyInitiated¦Personnelcompany¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Recloser | Malfunctioning | CompanyInitiated¦Personnelcompany¦Recloser¦Malfunctioning |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Recloser | Normal | CompanyInitiated¦Personnelcompany¦Recloser¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Regulator | Normal | CompanyInitiated¦Personnelcompany¦Regulator¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Relay | Malfunctioning | CompanyInitiated¦Personnelcompany¦Relay¦Malfunctioning | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Relay | Normal | CompanyInitiated¦Personnelcompany¦Relay¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Secondary | Broken, wire on ground | CompanyInitiated¦Personnelcompany¦Secondary¦Brokenwireonground | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Sectionalizer | Normal | CompanyInitiated¦Personnelcompany¦Sectionalizer¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Serviceconductor | Broken | CompanyInitiated¦Personnelcompany¦Serviceconductor¦Broken |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Switch (OH) | Normal | CompanyInitiated¦Personnelcompany¦Switch(OH)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Switch | Normal | CompanyInitiated¦Personnelcompany¦Switch¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Transformer (OH) | (blank) | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦ | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Transformer(OH) | Broken | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Broken |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Transformer (OH) | Burned/flashed | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Burnedflashed | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Transformer(OH) | FailedFaulted | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Transformer (OH) | Leaking | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Leaking | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Transformer (OH) | Normal | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | Personnelcompany | Transformer | Deteriorated | CompanyInitiated¦Personnelcompany¦Transformer¦Deteriorated |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Transformer | Normal | CompanyInitiated¦Personnelcompany¦Transformer¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Personnel, company | Transformer | Together | CompanyInitiated¦Personnelcompany¦Transformer¦Together | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | CompanyInitiated¦ReturnCircuitNormal¦CircuitBreaker¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Overhead | Broken, wire on ground | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | ConductorOverhead | Brokenwireonground | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Brokenwireonground |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Overhead | Deteriorated | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Overhead | Normal | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | ConductorOverhead | Together | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Together |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Underground | Broken | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Underground | Deteriorated | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Underground | Normal | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Normal | CompanyInitiated¦ReturnCircuitNormal¦ConnectororSplice(UG)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Crossarm, Wood | Broken | CompanyInitiated¦ReturnCircuitNormal¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Cutout, fuse holder | Broken | CompanyInitiated¦ReturnCircuitNormal¦Cutoutfuseholder¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | Elbow | Normal | CompanyInitiated¦ReturnCircuitNormal¦Elbow¦Normal |  |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | Fuse | BurnedOpen | CompanyInitiated¦ReturnCircuitNormal¦Fuse¦BurnedOpen |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Fuse | Normal | CompanyInitiated¦ReturnCircuitNormal¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Generator | Normal | CompanyInitiated¦ReturnCircuitNormal¦Generator¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Interrupter | Normal | CompanyInitiated¦ReturnCircuitNormal¦Interrupter¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Jumper | Normal | CompanyInitiated¦ReturnCircuitNormal¦Jumper¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | Jumper | Normal | CompanyInitiated¦ReturnCircuitNormal¦Jumper¦Normal |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Other | Normal | CompanyInitiated¦ReturnCircuitNormal¦Other¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | PoleWood | Broken | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Broken |  |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | PoleWood | Brokenwireonground | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Brokenwireonground |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Pole-Wood | Burned/flashed | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Pole-Wood | Deteriorated | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Deteriorated | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Pole-Wood | Normal | CompanyInitiated¦ReturnCircuitNormal¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | PT/CCVT | Normal | CompanyInitiated¦ReturnCircuitNormal¦PTCCVT¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Recloser | Normal | CompanyInitiated¦ReturnCircuitNormal¦Recloser¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Regulator | Normal | CompanyInitiated¦ReturnCircuitNormal¦Regulator¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Secondary | Normal | CompanyInitiated¦ReturnCircuitNormal¦Secondary¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Switch (OH) | Broken | CompanyInitiated¦ReturnCircuitNormal¦Switch(OH)¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Switch (OH) | Normal | CompanyInitiated¦ReturnCircuitNormal¦Switch(OH)¦Normal | #N/A |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | Switch(UG) | Normal | CompanyInitiated¦ReturnCircuitNormal¦Switch(UG)¦Normal |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Switch | Normal | CompanyInitiated¦ReturnCircuitNormal¦Switch¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Transformer (OH) | Broken | CompanyInitiated¦ReturnCircuitNormal¦Transformer(OH)¦Broken | #N/A |  |  | N/A | N/A
CompanyInitiated | ReturnCircuitNormal | Transformer(OH) | FailedFaulted | CompanyInitiated¦ReturnCircuitNormal¦Transformer(OH)¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Transformer (OH) | Normal | CompanyInitiated¦ReturnCircuitNormal¦Transformer(OH)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Transformer (UG) | Normal | CompanyInitiated¦ReturnCircuitNormal¦Transformer(UG)¦Normal | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Transformer | Broken | CompanyInitiated¦ReturnCircuitNormal¦Transformer¦Broken | #N/A |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Transformer | Normal | CompanyInitiated¦ReturnCircuitNormal¦Transformer¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Earthquake | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Earthquake | Conductor, Overhead | Normal | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Normal | #N/A |  |  | None | None
Environmental/External | Earthquake | Conductor, Overhead | Together | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Environmental/External | Earthquake | Fuse | Normal | EnvironmentalExternal¦Earthquake¦Fuse¦Normal | #N/A |  |  | None | None
Environmental/External | Earthquake | Other | Normal | EnvironmentalExternal¦Earthquake¦Other¦Normal | #N/A |  |  | None | N/A
Environmental/External | Earthquake | Pole-Wood | Burned/flashed | EnvironmentalExternal¦Earthquake¦PoleWood¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Earthquake | Pole-Wood | Deteriorated | EnvironmentalExternal¦Earthquake¦PoleWood¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Earthquake | Transformer | (blank) | EnvironmentalExternal¦Earthquake¦Transformer¦ | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Anchor or Guy | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦AnchororGuy¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Circuit Breaker | Normal | EnvironmentalExternal¦FireForestGrass¦CircuitBreaker¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Bent or Twisted | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦BentorTwisted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Contaminated | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Contaminated | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Deteriorated | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Deteriorated | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | On Ground | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦OnGround | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Underground | Broken | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Underground | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Underground | Normal | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Connector or Splice (OH) | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Broken | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Broken, wire on ground | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Brokenwireonground | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Customer Equipment | Broken | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Customer Equipment | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Customer Equipment | Burned Open | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦BurnedOpen | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Customer Equipment | On Ground | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦OnGround | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Cutout, fuse holder | Broken | EnvironmentalExternal¦FireForestGrass¦Cutoutfuseholder¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Cutout, fuse holder | Normal | EnvironmentalExternal¦FireForestGrass¦Cutoutfuseholder¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Elbow | Failed/Faulted | EnvironmentalExternal¦FireForestGrass¦Elbow¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Footings, Tower or Pole | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦FootingsTowerorPole¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Footings, Tower or Pole | Normal | EnvironmentalExternal¦FireForestGrass¦FootingsTowerorPole¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Fuse | Burned Open | EnvironmentalExternal¦FireForestGrass¦Fuse¦BurnedOpen | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Fuse | Failed/Faulted | EnvironmentalExternal¦FireForestGrass¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Fuse | Normal | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Insulator | Broken | EnvironmentalExternal¦FireForestGrass¦Insulator¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Insulator | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Insulator¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Insulator | Normal | EnvironmentalExternal¦FireForestGrass¦Insulator¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Jumper | Broken | EnvironmentalExternal¦FireForestGrass¦Jumper¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Jumper | Normal | EnvironmentalExternal¦FireForestGrass¦Jumper¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Metering Equipment | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦MeteringEquipment¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Other | Broken, wire on ground | EnvironmentalExternal¦FireForestGrass¦Other¦Brokenwireonground | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Other | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Other | Burned Open | EnvironmentalExternal¦FireForestGrass¦Other¦BurnedOpen | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Other | Deteriorated | EnvironmentalExternal¦FireForestGrass¦Other¦Deteriorated | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Other | Failed/Faulted | EnvironmentalExternal¦FireForestGrass¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Other | Normal | EnvironmentalExternal¦FireForestGrass¦Other¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole - Tower, steel | Broken | EnvironmentalExternal¦FireForestGrass¦PoleTowersteel¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole - Tower, steel | Broken, wire on ground | EnvironmentalExternal¦FireForestGrass¦PoleTowersteel¦Brokenwireonground | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on object | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonobject | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Deteriorated | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Deteriorated | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | On Ground | EnvironmentalExternal¦FireForestGrass¦PoleWood¦OnGround | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pothead(Riser Termination) | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Pothead(RiserTermination)¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Recloser | Broken | EnvironmentalExternal¦FireForestGrass¦Recloser¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Recloser | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Recloser¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Recloser | Normal | EnvironmentalExternal¦FireForestGrass¦Recloser¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Regulator | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Regulator¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Regulator | Failed/Faulted | EnvironmentalExternal¦FireForestGrass¦Regulator¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Secondary | Arcing | EnvironmentalExternal¦FireForestGrass¦Secondary¦Arcing | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Secondary | Broken | EnvironmentalExternal¦FireForestGrass¦Secondary¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Secondary | Broken, wire on ground | EnvironmentalExternal¦FireForestGrass¦Secondary¦Brokenwireonground | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Secondary | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Secondary¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Secondary | Burned Open | EnvironmentalExternal¦FireForestGrass¦Secondary¦BurnedOpen | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Secondary | Together | EnvironmentalExternal¦FireForestGrass¦Secondary¦Together | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Service conductor | Broken | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Service conductor | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Service conductor | Burned Open | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦BurnedOpen | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Service conductor | On Ground | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦OnGround | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Switch (OH) | Normal | EnvironmentalExternal¦FireForestGrass¦Switch(OH)¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Switch (UG) | Normal | EnvironmentalExternal¦FireForestGrass¦Switch(UG)¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Switch | Normal | EnvironmentalExternal¦FireForestGrass¦Switch¦Normal | #N/A |  |  | N/A | N/A
EnvironmentalExternal | FireForestGrass | Transformer(OH) |  | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦ |  |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (OH) | Broken | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (OH) | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (OH) | Deteriorated | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Deteriorated | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (OH) | Failed/Faulted | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (OH) | Normal | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (UG) | Broken | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (UG) | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer (UG) | Failed/Faulted | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer | Broken | EnvironmentalExternal¦FireForestGrass¦Transformer¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦Transformer¦Burnedflashed | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer | Burned Open | EnvironmentalExternal¦FireForestGrass¦Transformer¦BurnedOpen | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer | Failed/Faulted | EnvironmentalExternal¦FireForestGrass¦Transformer¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Transformer | Normal | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Flood/Erosion | Anchor or Guy | Broken | EnvironmentalExternal¦FloodErosion¦AnchororGuy¦Broken | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Anchor or Guy | Deteriorated | EnvironmentalExternal¦FloodErosion¦AnchororGuy¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | Arcing | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Arcing | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | Broken | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Broken | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on object | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | On Ground | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦OnGround | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | Together | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Together | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Underground | Normal | EnvironmentalExternal¦FloodErosion¦ConductorUnderground¦Normal | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Crossarm, Wood | Broken | EnvironmentalExternal¦FloodErosion¦CrossarmWood¦Broken | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Crossarm, Wood | Broken, wire on ground | EnvironmentalExternal¦FloodErosion¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Crossarm, Wood | Deteriorated | EnvironmentalExternal¦FloodErosion¦CrossarmWood¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Customer Equipment | Normal | EnvironmentalExternal¦FloodErosion¦CustomerEquipment¦Normal | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Cutout, fuse holder | Failed/Faulted | EnvironmentalExternal¦FloodErosion¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Fuse | Failed/Faulted | EnvironmentalExternal¦FloodErosion¦Fuse¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Fuse | Normal | EnvironmentalExternal¦FloodErosion¦Fuse¦Normal | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Other | Deteriorated | EnvironmentalExternal¦FloodErosion¦Other¦Deteriorated | #N/A |  |  | N/A | N/A
Environmental/External | Flood/Erosion | Other | Normal | EnvironmentalExternal¦FloodErosion¦Other¦Normal | #N/A |  |  | N/A | N/A
EnvironmentalExternal | FloodErosion | Other | OnGround | EnvironmentalExternal¦FloodErosion¦Other¦OnGround |  |  |  | N/A | N/A
Environmental/External | Flood/Erosion | Pole - Tower, steel | Deteriorated | EnvironmentalExternal¦FloodErosion¦PoleTowersteel¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Pole-Wood | Broken | EnvironmentalExternal¦FloodErosion¦PoleWood¦Broken | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Pole-Wood | Broken, wire on ground | EnvironmentalExternal¦FloodErosion¦PoleWood¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Pole-Wood | Normal | EnvironmentalExternal¦FloodErosion¦PoleWood¦Normal | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Pole-Wood | On Ground | EnvironmentalExternal¦FloodErosion¦PoleWood¦OnGround | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Switch (UG) | Normal | EnvironmentalExternal¦FloodErosion¦Switch(UG)¦Normal | #N/A |  |  | None | None
EnvironmentalExternal | FloodErosion | Transformer(OH) |  | EnvironmentalExternal¦FloodErosion¦Transformer(OH)¦ |  |  |  | N/A | N/A
Environmental/External | Flood/Erosion | Transformer (OH) | Broken | EnvironmentalExternal¦FloodErosion¦Transformer(OH)¦Broken | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Transformer (OH) | Normal | EnvironmentalExternal¦FloodErosion¦Transformer(OH)¦Normal | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Transformer | Broken | EnvironmentalExternal¦FloodErosion¦Transformer¦Broken | #N/A |  |  | None | None
Environmental/External | Flood/Erosion | Transformer | Failed/Faulted | EnvironmentalExternal¦FloodErosion¦Transformer¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Ice or snow | (blank) | Failed/Faulted | EnvironmentalExternal¦Iceorsnow¦¦FailedFaulted | #N/A |  |  | N/A | N/A
EnvironmentalExternal | Iceorsnow | AnchororGuy | Broken | EnvironmentalExternal¦Iceorsnow¦AnchororGuy¦Broken |  |  |  | N/A | N/A
Environmental/External | Ice or snow | Circuit Breaker | Normal | EnvironmentalExternal¦Iceorsnow¦CircuitBreaker¦Normal | #N/A |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Arcing | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Arcing | #N/A |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Bent or Twisted | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Broken | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Burned/flashed | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | None
EnvironmentalExternal | Iceorsnow | ConductorOverhead | Deteriorated | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Deteriorated |  |  |  | N/A | N/A
Environmental/External | Ice or snow | Conductor, Overhead | Normal | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal | #N/A |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | On Ground | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦OnGround | #N/A |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Together | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Together | #N/A |  |  | None | None
Environmental/External | Ice or snow | Connector or Splice (OH) | Broken | EnvironmentalExternal¦Iceorsnow¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Very High
Environmental/External | Ice or snow | Connector or Splice (OH) | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Very High
Environmental/External | Ice or snow | Crossarm, Wood | Broken | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Crossarm, Wood | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Ice or snow | Crossarm, Wood | Broken, wire on object | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Brokenwireonobject | #N/A |  |  | None | None
Environmental/External | Ice or snow | Cutout, fuse holder | Arcing | EnvironmentalExternal¦Iceorsnow¦Cutoutfuseholder¦Arcing | #N/A |  |  | None | None
Environmental/External | Ice or snow | Cutout, fuse holder | Broken | EnvironmentalExternal¦Iceorsnow¦Cutoutfuseholder¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Fuse | Broken | EnvironmentalExternal¦Iceorsnow¦Fuse¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Fuse | Burned Open | EnvironmentalExternal¦Iceorsnow¦Fuse¦BurnedOpen | #N/A |  |  | None | None
Environmental/External | Ice or snow | Fuse | Failed/Faulted | EnvironmentalExternal¦Iceorsnow¦Fuse¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Ice or snow | Fuse | Normal | EnvironmentalExternal¦Iceorsnow¦Fuse¦Normal | #N/A |  |  | None | None
Environmental/External | Ice or snow | Insulator | Broken | EnvironmentalExternal¦Iceorsnow¦Insulator¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Insulator | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦Insulator¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Ice or snow | Insulator | Broken, wire on object | EnvironmentalExternal¦Iceorsnow¦Insulator¦Brokenwireonobject | #N/A |  |  | None | None
Environmental/External | Ice or snow | Jumper | Broken | EnvironmentalExternal¦Iceorsnow¦Jumper¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Lightning Arrestor | Failed/Faulted | EnvironmentalExternal¦Iceorsnow¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Ice or snow | Other | Annealed | EnvironmentalExternal¦Iceorsnow¦Other¦Annealed | #N/A |  |  | None | N/A
Environmental/External | Ice or snow | Other | Broken | EnvironmentalExternal¦Iceorsnow¦Other¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Ice or snow | Pole-Wood | Broken | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground | #N/A |  |  | None | None
EnvironmentalExternal | Iceorsnow | PoleWood | Normal | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Normal |  |  |  | N/A | N/A
Environmental/External | Ice or snow | Recloser | Normal | EnvironmentalExternal¦Iceorsnow¦Recloser¦Normal | #N/A |  |  | None | None
Environmental/External | Ice or snow | Secondary | Broken | EnvironmentalExternal¦Iceorsnow¦Secondary¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Secondary | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦Secondary¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Ice or snow | Service conductor | Bent or Twisted | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦BentorTwisted | #N/A |  |  | None | None
EnvironmentalExternal | Iceorsnow | Serviceconductor | Broken | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦Broken |  |  |  | N/A | N/A
Environmental/External | Ice or snow | Service conductor | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Ice or snow | Switch (OH) | Normal | EnvironmentalExternal¦Iceorsnow¦Switch(OH)¦Normal | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer (OH) | Broken | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer (OH) | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer (OH) | Failed/Faulted | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer (OH) | Leaking | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Leaking | #N/A |  |  | None | None
EnvironmentalExternal | Iceorsnow | Transformer(OH) | Normal | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Normal |  |  |  | N/A | N/A
EnvironmentalExternal | Iceorsnow | Transformer | Arcing | EnvironmentalExternal¦Iceorsnow¦Transformer¦Arcing |  |  |  | N/A | N/A
Environmental/External | Ice or snow | Transformer | Broken | EnvironmentalExternal¦Iceorsnow¦Transformer¦Broken | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦Transformer¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer | Burned/flashed | EnvironmentalExternal¦Iceorsnow¦Transformer¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer | Deteriorated | EnvironmentalExternal¦Iceorsnow¦Transformer¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer | Failed/Faulted | EnvironmentalExternal¦Iceorsnow¦Transformer¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Ice or snow | Transformer | Normal | EnvironmentalExternal¦Iceorsnow¦Transformer¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | (blank) | (blank) | EnvironmentalExternal¦Lightning¦¦ | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | (blank) | Broken | EnvironmentalExternal¦Lightning¦¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | (blank) | Failed/Faulted | EnvironmentalExternal¦Lightning¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | (blank) | Normal | EnvironmentalExternal¦Lightning¦¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | Bus | Normal | EnvironmentalExternal¦Lightning¦Bus¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Bushing | Broken | EnvironmentalExternal¦Lightning¦Bushing¦Broken | #N/A |  |  | None | None
Environmental/External | Lightning | Bushing | Failed/Faulted | EnvironmentalExternal¦Lightning¦Bushing¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Capacitor | Burned/flashed | EnvironmentalExternal¦Lightning¦Capacitor¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Circuit Breaker | Burned/flashed | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Circuit Breaker | Malfunctioning | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Malfunctioning | #N/A |  |  | None | None
Environmental/External | Lightning | Circuit Breaker | Normal | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Lightning | Conductor, Overhead | Burned/flashed | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Conductor, Overhead | Normal | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Conductor, Overhead | On Ground | EnvironmentalExternal¦Lightning¦ConductorOverhead¦OnGround | #N/A |  |  | None | None
Environmental/External | Lightning | Conductor, Overhead | Together | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Together | #N/A |  |  | None | None
Environmental/External | Lightning | Conductor, Underground | Burned/flashed | EnvironmentalExternal¦Lightning¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Connector or Splice (OH) | Broken, wire on ground | EnvironmentalExternal¦Lightning¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Very High
Environmental/External | Lightning | Connector or Splice (OH) | Normal | EnvironmentalExternal¦Lightning¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
Environmental/External | Lightning | Connector or Splice (UG) | Failed/Faulted | EnvironmentalExternal¦Lightning¦ConnectororSplice(UG)¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Crossarm, Steel | Normal | EnvironmentalExternal¦Lightning¦CrossarmSteel¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Crossarm, Wood | Broken | EnvironmentalExternal¦Lightning¦CrossarmWood¦Broken | #N/A |  |  | None | None
EnvironmentalExternal | Lightning | CT | Burnedflashed | EnvironmentalExternal¦Lightning¦CT¦Burnedflashed |  |  |  | None | None
Environmental/External | Lightning | Customer Equipment | Failed/Faulted | EnvironmentalExternal¦Lightning¦CustomerEquipment¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Cutout, fuse holder | Arcing | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Arcing | #N/A |  |  | None | None
Environmental/External | Lightning | Cutout, fuse holder | Broken | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Broken | #N/A |  |  | None | None
Environmental/External | Lightning | Cutout, fuse holder | Burned/flashed | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Cutout, fuse holder | Failed/Faulted | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Cutout, fuse holder | Normal | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Elbow | Failed/Faulted | EnvironmentalExternal¦Lightning¦Elbow¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Fuse | Arcing | EnvironmentalExternal¦Lightning¦Fuse¦Arcing | #N/A |  |  | None | None
Environmental/External | Lightning | Fuse | Burned Open | EnvironmentalExternal¦Lightning¦Fuse¦BurnedOpen | #N/A |  |  | None | None
Environmental/External | Lightning | Fuse | Failed/Faulted | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Fuse | Normal | EnvironmentalExternal¦Lightning¦Fuse¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Insulator | Broken | EnvironmentalExternal¦Lightning¦Insulator¦Broken | #N/A |  |  | None | None
Environmental/External | Lightning | Insulator | Broken, wire on ground | EnvironmentalExternal¦Lightning¦Insulator¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Lightning | Insulator | Burned/flashed | EnvironmentalExternal¦Lightning¦Insulator¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Insulator | Failed/Faulted | EnvironmentalExternal¦Lightning¦Insulator¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Jumper | Broken, wire on object | EnvironmentalExternal¦Lightning¦Jumper¦Brokenwireonobject | #N/A |  |  | None | None
Environmental/External | Lightning | Jumper | Burned Open | EnvironmentalExternal¦Lightning¦Jumper¦BurnedOpen | #N/A |  |  | None | None
Environmental/External | Lightning | Lightning Arrestor | Broken | EnvironmentalExternal¦Lightning¦LightningArrestor¦Broken | #N/A |  |  | None | None
Environmental/External | Lightning | Lightning Arrestor | Burned/flashed | EnvironmentalExternal¦Lightning¦LightningArrestor¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Lightning Arrestor | Failed/Faulted | EnvironmentalExternal¦Lightning¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Very High
Environmental/External | Lightning | Other | Broken | EnvironmentalExternal¦Lightning¦Other¦Broken | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | Other | Failed/Faulted | EnvironmentalExternal¦Lightning¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | Other | Malfunctioning | EnvironmentalExternal¦Lightning¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | Other | Normal | EnvironmentalExternal¦Lightning¦Other¦Normal | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | Pole-Wood | Broken | EnvironmentalExternal¦Lightning¦PoleWood¦Broken | #N/A |  |  | None | None
Environmental/External | Lightning | Pole-Wood | Broken, wire on ground | EnvironmentalExternal¦Lightning¦PoleWood¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Lightning | Pole-Wood | Burned/flashed | EnvironmentalExternal¦Lightning¦PoleWood¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Pole-Wood | Deteriorated | EnvironmentalExternal¦Lightning¦PoleWood¦Deteriorated | #N/A |  |  | None | None
EnvironmentalExternal | Lightning | Pothead(RiserTermination) | Burnedflashed | EnvironmentalExternal¦Lightning¦Pothead(RiserTermination)¦Burnedflashed |  |  |  | None | None
Environmental/External | Lightning | Pothead(Riser Termination) | Failed/Faulted | EnvironmentalExternal¦Lightning¦Pothead(RiserTermination)¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Pothead(Riser Termination) | Normal | EnvironmentalExternal¦Lightning¦Pothead(RiserTermination)¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | PT/CCVT | Burned/flashed | EnvironmentalExternal¦Lightning¦PTCCVT¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | PT/CCVT | Failed/Faulted | EnvironmentalExternal¦Lightning¦PTCCVT¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Recloser | Burned/flashed | EnvironmentalExternal¦Lightning¦Recloser¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Recloser | Failed/Faulted | EnvironmentalExternal¦Lightning¦Recloser¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Recloser | Normal | EnvironmentalExternal¦Lightning¦Recloser¦Normal | #N/A |  |  | None | None
EnvironmentalExternal | Lightning | Recloser | Normal | EnvironmentalExternal¦Lightning¦Recloser¦Normal |  |  |  | None | None
Environmental/External | Lightning | Regulator | Broken, wire on ground | EnvironmentalExternal¦Lightning¦Regulator¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Lightning | Secondary | Broken, wire on ground | EnvironmentalExternal¦Lightning¦Secondary¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Lightning | Secondary | Burned/flashed | EnvironmentalExternal¦Lightning¦Secondary¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Service conductor | Broken, wire on ground | EnvironmentalExternal¦Lightning¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Lightning | Street Light Equipment | Failed/Faulted | EnvironmentalExternal¦Lightning¦StreetLightEquipment¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Switch (OH) | Failed/Faulted | EnvironmentalExternal¦Lightning¦Switch(OH)¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Switch (OH) | Normal | EnvironmentalExternal¦Lightning¦Switch(OH)¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Switch | Broken | EnvironmentalExternal¦Lightning¦Switch¦Broken | #N/A |  |  | None | None
Environmental/External | Lightning | Switch | Normal | EnvironmentalExternal¦Lightning¦Switch¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (OH) | Broken | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (OH) | Broken, wire on ground | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (OH) | Burned/flashed | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (OH) | Deteriorated | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (OH) | Normal | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (UG) | Burned/flashed | EnvironmentalExternal¦Lightning¦Transformer(UG)¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (UG) | Deteriorated | EnvironmentalExternal¦Lightning¦Transformer(UG)¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer (UG) | Failed/Faulted | EnvironmentalExternal¦Lightning¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | (blank) | EnvironmentalExternal¦Lightning¦Transformer¦ | #N/A |  |  | N/A | N/A
Environmental/External | Lightning | Transformer | Arcing | EnvironmentalExternal¦Lightning¦Transformer¦Arcing | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | Broken | EnvironmentalExternal¦Lightning¦Transformer¦Broken | #N/A |  |  | None | None
EnvironmentalExternal | Lightning | Transformer | Brokenwireonground | EnvironmentalExternal¦Lightning¦Transformer¦Brokenwireonground |  |  |  | None | Medium
Environmental/External | Lightning | Transformer | Burned/flashed | EnvironmentalExternal¦Lightning¦Transformer¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | Contaminated | EnvironmentalExternal¦Lightning¦Transformer¦Contaminated | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | Deteriorated | EnvironmentalExternal¦Lightning¦Transformer¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | Failed/Faulted | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | Leaking | EnvironmentalExternal¦Lightning¦Transformer¦Leaking | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | Malfunctioning | EnvironmentalExternal¦Lightning¦Transformer¦Malfunctioning | #N/A |  |  | None | None
Environmental/External | Lightning | Transformer | Normal | EnvironmentalExternal¦Lightning¦Transformer¦Normal | #N/A |  |  | None | None
Environmental/External | Water | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦Water¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Water | Conductor, Overhead | On Ground | EnvironmentalExternal¦Water¦ConductorOverhead¦OnGround | #N/A |  |  | None | None
Environmental/External | Water | Conductor, Underground | Deteriorated | EnvironmentalExternal¦Water¦ConductorUnderground¦Deteriorated | #N/A |  |  | None | None
Environmental/External | Water | Connector or Splice (UG) | Normal | EnvironmentalExternal¦Water¦ConnectororSplice(UG)¦Normal | #N/A |  |  | None | None
Environmental/External | Water | Crossarm, Wood | Broken | EnvironmentalExternal¦Water¦CrossarmWood¦Broken | #N/A |  |  | None | None
Environmental/External | Water | Crossarm, Wood | Burned/flashed | EnvironmentalExternal¦Water¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | None
Environmental/External | Water | Fuse | Failed/Faulted | EnvironmentalExternal¦Water¦Fuse¦FailedFaulted | #N/A |  |  | None | None
Environmental/External | Water | Other | Leaking | EnvironmentalExternal¦Water¦Other¦Leaking | #N/A |  |  | None | N/A
Environmental/External | Water | Other | Normal | EnvironmentalExternal¦Water¦Other¦Normal | #N/A |  |  | None | N/A
EnvironmentalExternal | Water | PoleWood | Broken | EnvironmentalExternal¦Water¦PoleWood¦Broken |  |  |  | N/A | N/A
Environmental/External | Water | Pole-Wood | Broken, wire on ground | EnvironmentalExternal¦Water¦PoleWood¦Brokenwireonground | #N/A |  |  | None | None
Environmental/External | Water | Pole-Wood | Normal | EnvironmentalExternal¦Water¦PoleWood¦Normal | #N/A |  |  | None | None
EnvironmentalExternal | Water | PoleWood | OnGround | EnvironmentalExternal¦Water¦PoleWood¦OnGround |  |  |  | N/A | N/A
EnvironmentalExternal | Water | Switch(OH) | Normal | EnvironmentalExternal¦Water¦Switch(OH)¦Normal |  |  |  | N/A | N/A
EnvironmentalExternal | Water | Transformer | Arcing | EnvironmentalExternal¦Water¦Transformer¦Arcing |  |  |  | N/A | N/A
Environmental/External | Water | Transformer | Broken | EnvironmentalExternal¦Water¦Transformer¦Broken | #N/A |  |  | None | High
Environmental/External | Water | Transformer | Broken, wire on ground | EnvironmentalExternal¦Water¦Transformer¦Brokenwireonground | #N/A |  |  | None | None
EnvironmentalExternal | Water | Transformer | Brokenwireonobject | EnvironmentalExternal¦Water¦Transformer¦Brokenwireonobject |  |  |  | N/A | N/A
Environmental/External | Water | Transformer | Burned Open | EnvironmentalExternal¦Water¦Transformer¦BurnedOpen | #N/A |  |  | None | High
Environmental/External | Water | Transformer | Failed/Faulted | EnvironmentalExternal¦Water¦Transformer¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | (blank) | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | (blank) | Broken | EquipmentFailureInvolved¦ElectricalOverload¦¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | (blank) | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | (blank) | Normal | EquipmentFailureInvolved¦ElectricalOverload¦¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | Anchor or Guy | Broken | EquipmentFailureInvolved¦ElectricalOverload¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Anchor or Guy | Broken, wire on ground | EquipmentFailureInvolved¦ElectricalOverload¦AnchororGuy¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Electrical Overload | Bushing | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Bushing¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Electrical Overload | Capacitor | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Capacitor¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Electrical Overload | Circuit Breaker | Normal | EquipmentFailureInvolved¦ElectricalOverload¦CircuitBreaker¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Annealed | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Annealed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Broken | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Broken, wire on ground | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Normal | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Together | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken, wire on ground | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned Open | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦BurnedOpen | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Deteriorated | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Deteriorated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Normal | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(UG)¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Crossarm, Wood | Broken | EquipmentFailureInvolved¦ElectricalOverload¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Crossarm, Wood | Normal | EquipmentFailureInvolved¦ElectricalOverload¦CrossarmWood¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Customer Equipment | Malfunctioning | EquipmentFailureInvolved¦ElectricalOverload¦CustomerEquipment¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Fuse | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦BurnedOpen | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Fuse | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
EquipmentFailureInvolved | ElectricalOverload | Fuse | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦Normal |  |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | Generator | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Generator¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Insulator | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Insulator | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Insulator | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Insulator | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Interrupter | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Interrupter¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Jumper | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Jumper | Bent or Twisted | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦BentorTwisted | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Jumper | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Jumper | Burned Open | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦BurnedOpen | #N/A |  |  | None | High
EquipmentFailureInvolved | ElectricalOverload | Jumper | Deteriorated | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦Deteriorated |  |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Broken | EquipmentFailureInvolved¦ElectricalOverload¦LightningArrestor¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦LightningArrestor¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Other | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Other¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | Other | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | Other | Malfunctioning | EquipmentFailureInvolved¦ElectricalOverload¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | Other | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Other¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Electrical Overload | Pole-Wood | Broken | EquipmentFailureInvolved¦ElectricalOverload¦PoleWood¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Pole-Wood | Deteriorated | EquipmentFailureInvolved¦ElectricalOverload¦PoleWood¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Pothead(RiserTermination)¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Recloser | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Recloser¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Regulator | Malfunctioning | EquipmentFailureInvolved¦ElectricalOverload¦Regulator¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Secondary | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Secondary | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Electrical Overload | Secondary | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Secondary | Burned Open | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦BurnedOpen | #N/A |  |  | None | Medium
Equipment Failure/Involved | Electrical Overload | Secondary | Deteriorated | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Service conductor | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦Serviceconductor¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Service conductor | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Serviceconductor¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Switch (OH) | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦Switch(OH)¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Switch (OH) | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Switch(OH)¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Switch | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Switch¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | (blank) | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦ | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Deteriorated | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Leaking | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Leaking | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Transformer | (blank) | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦ | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Annealed | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Annealed | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Arcing | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Broken, wire on ground | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Brokenwireonground | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Burned Open | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦BurnedOpen | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Deteriorated | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Leaking | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Leaking | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Malfunctioning | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Malfunctioning | #N/A |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Transformer | Normal | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Fire, pole | Anchor or Guy | Deteriorated | EquipmentFailureInvolved¦Firepole¦AnchororGuy¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Fire, pole | Capacitor | Burned/flashed | EquipmentFailureInvolved¦Firepole¦Capacitor¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Arcing | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Arcing | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Broken | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Broken, wire on ground | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Burned/flashed | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Normal | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Normal | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Conductor, Overhead | On Ground | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Conductor, Underground | Burned/flashed | EquipmentFailureInvolved¦Firepole¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Fire, pole | Connector or Splice (OH) | Burned/flashed | EquipmentFailureInvolved¦Firepole¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Crossarm, Steel | Deteriorated | EquipmentFailureInvolved¦Firepole¦CrossarmSteel¦Deteriorated | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Broken | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Broken, wire on ground | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Burned/flashed | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Fire, pole | Cutout, fuse holder | Burned/flashed | EquipmentFailureInvolved¦Firepole¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Footings, Tower or Pole | Burned/flashed | EquipmentFailureInvolved¦Firepole¦FootingsTowerorPole¦Burnedflashed | #N/A |  |  | None | Medium
EquipmentFailureInvolved | Firepole | Fuse | Broken | EquipmentFailureInvolved¦Firepole¦Fuse¦Broken |  |  |  | N/A | N/A
Equipment Failure/Involved | Fire, pole | Fuse | Burned Open | EquipmentFailureInvolved¦Firepole¦Fuse¦BurnedOpen | #N/A |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Insulator | Broken | EquipmentFailureInvolved¦Firepole¦Insulator¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Insulator | Burned/flashed | EquipmentFailureInvolved¦Firepole¦Insulator¦Burnedflashed | #N/A |  |  | None | Medium High
Equipment Failure/Involved | Fire, pole | Insulator | Failed/Faulted | EquipmentFailureInvolved¦Firepole¦Insulator¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Jumper | Burned Open | EquipmentFailureInvolved¦Firepole¦Jumper¦BurnedOpen | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Jumper | Deteriorated | EquipmentFailureInvolved¦Firepole¦Jumper¦Deteriorated | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Other | Broken | EquipmentFailureInvolved¦Firepole¦Other¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Fire, pole | Pole - Tower, steel | Normal | EquipmentFailureInvolved¦Firepole¦PoleTowersteel¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken, wire on ground | EquipmentFailureInvolved¦Firepole¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken, wire on object | EquipmentFailureInvolved¦Firepole¦PoleWood¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed | #N/A |  |  | None | Medium High
Equipment Failure/Involved | Fire, pole | Pole-Wood | Deteriorated | EquipmentFailureInvolved¦Firepole¦PoleWood¦Deteriorated | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Pole-Wood | Normal | EquipmentFailureInvolved¦Firepole¦PoleWood¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Fire, pole | Pole-Wood | On Ground | EquipmentFailureInvolved¦Firepole¦PoleWood¦OnGround | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Pothead(Riser Termination) | Failed/Faulted | EquipmentFailureInvolved¦Firepole¦Pothead(RiserTermination)¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Recloser | Normal | EquipmentFailureInvolved¦Firepole¦Recloser¦Normal | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Secondary | Burned/flashed | EquipmentFailureInvolved¦Firepole¦Secondary¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Fire, pole | Service conductor | Burned/flashed | EquipmentFailureInvolved¦Firepole¦Serviceconductor¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Fire, pole | Transformer (OH) | Burned/flashed | EquipmentFailureInvolved¦Firepole¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Fire, pole | Transformer (OH) | Failed/Faulted | EquipmentFailureInvolved¦Firepole¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Fire, pole | Transformer (UG) | Broken | EquipmentFailureInvolved¦Firepole¦Transformer(UG)¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Fire, pole | Transformer | Failed/Faulted | EquipmentFailureInvolved¦Firepole¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Ice or snow | Conductor, Overhead | Broken, wire on object | EquipmentFailureInvolved¦Iceorsnow¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | High
Equipment Failure/Involved | Ice or snow | Conductor, Overhead | Normal | EquipmentFailureInvolved¦Iceorsnow¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Lightning | Connector or Splice (OH) | Broken | EquipmentFailureInvolved¦Lightning¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Lightning | Cutout, Fused, Distribution | Failed/Faulted | EquipmentFailureInvolved¦Lightning¦CutoutFusedDistribution¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Lightning | Cutout, fuse holder | Failed/Faulted | EquipmentFailureInvolved¦Lightning¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Lightning | Fuse | Arcing | EquipmentFailureInvolved¦Lightning¦Fuse¦Arcing | #N/A |  |  | None | Medium
Equipment Failure/Involved | Lightning | Fuse | Failed/Faulted | EquipmentFailureInvolved¦Lightning¦Fuse¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Lightning | Lightning Arrestor | Failed/Faulted | EquipmentFailureInvolved¦Lightning¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Lightning | Other | Bent or Twisted | EquipmentFailureInvolved¦Lightning¦Other¦BentorTwisted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Lightning | Other | Failed/Faulted | EquipmentFailureInvolved¦Lightning¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Lightning | Other | Malfunctioning | EquipmentFailureInvolved¦Lightning¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Lightning | Transformer | Broken | EquipmentFailureInvolved¦Lightning¦Transformer¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Lightning | Transformer | Burned/flashed | EquipmentFailureInvolved¦Lightning¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Lightning | Transformer | Failed/Faulted | EquipmentFailureInvolved¦Lightning¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Lightning | Transformer | Malfunctioning | EquipmentFailureInvolved¦Lightning¦Transformer¦Malfunctioning | #N/A |  |  | None | High
Equipment Failure/Involved | Other | (blank) | Broken | EquipmentFailureInvolved¦Other¦¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | (blank) | Failed/Faulted | EquipmentFailureInvolved¦Other¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Bent or Twisted | EquipmentFailureInvolved¦Other¦ConductorOverhead¦BentorTwisted | #N/A |  |  | N/A | Very High
Equipment Failure/Involved | Other | Conductor, Overhead | Broken | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on ground | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on object | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Burned/flashed | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Burned Open | EquipmentFailureInvolved¦Other¦ConductorOverhead¦BurnedOpen | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Deteriorated | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Deteriorated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Malfunctioning | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Normal | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | On Ground | EquipmentFailureInvolved¦Other¦ConductorOverhead¦OnGround | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Overhead | Together | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Together | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Underground | Broken | EquipmentFailureInvolved¦Other¦ConductorUnderground¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Conductor, Underground | Failed/Faulted | EquipmentFailureInvolved¦Other¦ConductorUnderground¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Connector or Splice (OH) | Arcing | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken, wire on ground | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned/flashed | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned Open | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦BurnedOpen | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Connector or Splice (OH) | Deteriorated | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Deteriorated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Connector or Splice (UG) | Failed/Faulted | EquipmentFailureInvolved¦Other¦ConnectororSplice(UG)¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Crossarm, Wood | (blank) | EquipmentFailureInvolved¦Other¦CrossarmWood¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Crossarm, Wood | Broken | EquipmentFailureInvolved¦Other¦CrossarmWood¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Crossarm, Wood | Broken, wire on ground | EquipmentFailureInvolved¦Other¦CrossarmWood¦Brokenwireonground | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Crossarm, Wood | Burned/flashed | EquipmentFailureInvolved¦Other¦CrossarmWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Crossarm, Wood | Deteriorated | EquipmentFailureInvolved¦Other¦CrossarmWood¦Deteriorated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Customer Equipment | Burned/flashed | EquipmentFailureInvolved¦Other¦CustomerEquipment¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Customer Equipment | Deteriorated | EquipmentFailureInvolved¦Other¦CustomerEquipment¦Deteriorated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Customer Equipment | Malfunctioning | EquipmentFailureInvolved¦Other¦CustomerEquipment¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Cutout, fuse holder | Arcing | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Cutout, fuse holder | Broken | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Cutout, fuse holder | Burned/flashed | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Cutout, fuse holder | Failed/Faulted | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Elbow | Malfunctioning | EquipmentFailureInvolved¦Other¦Elbow¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Fuse | Arcing | EquipmentFailureInvolved¦Other¦Fuse¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Fuse | Broken | EquipmentFailureInvolved¦Other¦Fuse¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Fuse | Failed/Faulted | EquipmentFailureInvolved¦Other¦Fuse¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Insulator | Broken | EquipmentFailureInvolved¦Other¦Insulator¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Insulator | Broken, wire on object | EquipmentFailureInvolved¦Other¦Insulator¦Brokenwireonobject | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Insulator | Burned/flashed | EquipmentFailureInvolved¦Other¦Insulator¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Insulator | Failed/Faulted | EquipmentFailureInvolved¦Other¦Insulator¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Insulator | Malfunctioning | EquipmentFailureInvolved¦Other¦Insulator¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Jumper | Arcing | EquipmentFailureInvolved¦Other¦Jumper¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Jumper | Broken | EquipmentFailureInvolved¦Other¦Jumper¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Jumper | Burned/flashed | EquipmentFailureInvolved¦Other¦Jumper¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Jumper | Burned Open | EquipmentFailureInvolved¦Other¦Jumper¦BurnedOpen | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Lightning Arrestor | Broken | EquipmentFailureInvolved¦Other¦LightningArrestor¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Lightning Arrestor | Failed/Faulted | EquipmentFailureInvolved¦Other¦LightningArrestor¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Metering Equipment | Malfunctioning | EquipmentFailureInvolved¦Other¦MeteringEquipment¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Other | Broken | EquipmentFailureInvolved¦Other¦Other¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Other | Burned/flashed | EquipmentFailureInvolved¦Other¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Other | Deteriorated | EquipmentFailureInvolved¦Other¦Other¦Deteriorated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Other | Failed/Faulted | EquipmentFailureInvolved¦Other¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Other | Leaking | EquipmentFailureInvolved¦Other¦Other¦Leaking | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Other | Malfunctioning | EquipmentFailureInvolved¦Other¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Pole-Wood | Bent or Twisted | EquipmentFailureInvolved¦Other¦PoleWood¦BentorTwisted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Pole-Wood | Broken | EquipmentFailureInvolved¦Other¦PoleWood¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Pole-Wood | Broken, wire on ground | EquipmentFailureInvolved¦Other¦PoleWood¦Brokenwireonground | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Pole-Wood | Burned/flashed | EquipmentFailureInvolved¦Other¦PoleWood¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Pothead/Riser Termination | Burned/flashed | EquipmentFailureInvolved¦Other¦PotheadRiserTermination¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Riser | Failed/Faulted | EquipmentFailureInvolved¦Other¦Riser¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Secondary | Broken | EquipmentFailureInvolved¦Other¦Secondary¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Secondary | Malfunctioning | EquipmentFailureInvolved¦Other¦Secondary¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Service conductor | Broken | EquipmentFailureInvolved¦Other¦Serviceconductor¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Switch | Malfunctioning | EquipmentFailureInvolved¦Other¦Switch¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer (OH) | Broken | EquipmentFailureInvolved¦Other¦Transformer(OH)¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | (blank) | EquipmentFailureInvolved¦Other¦Transformer¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Arcing | EquipmentFailureInvolved¦Other¦Transformer¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Broken | EquipmentFailureInvolved¦Other¦Transformer¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Burned/flashed | EquipmentFailureInvolved¦Other¦Transformer¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Burned Open | EquipmentFailureInvolved¦Other¦Transformer¦BurnedOpen | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Contaminated | EquipmentFailureInvolved¦Other¦Transformer¦Contaminated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Deteriorated | EquipmentFailureInvolved¦Other¦Transformer¦Deteriorated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Failed/Faulted | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Leaking | EquipmentFailureInvolved¦Other¦Transformer¦Leaking | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Malfunctioning | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Transformer | Normal | EquipmentFailureInvolved¦Other¦Transformer¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Other | Woodpin | Broken | EquipmentFailureInvolved¦Other¦Woodpin¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | (blank) | Arcing | EquipmentFailureInvolved¦Overhead¦¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | (blank) | Broken | EquipmentFailureInvolved¦Overhead¦¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | (blank) | Burned Open | EquipmentFailureInvolved¦Overhead¦¦BurnedOpen | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | (blank) | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | (blank) | Normal | EquipmentFailureInvolved¦Overhead¦¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Anchor or Guy | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦BentorTwisted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Anchor or Guy | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Anchor or Guy | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Anchor or Guy | Burned/flashed | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Anchor or Guy | Deteriorated | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Deteriorated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Anchor or Guy | Normal | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Booster | Arcing | EquipmentFailureInvolved¦Overhead¦Booster¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Booster | Broken | EquipmentFailureInvolved¦Overhead¦Booster¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Booster | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Booster¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Booster | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Booster¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Booster | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Booster¦Malfunctioning | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Bus | Annealed | EquipmentFailureInvolved¦Overhead¦Bus¦Annealed | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Bus | Burned Open | EquipmentFailureInvolved¦Overhead¦Bus¦BurnedOpen | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Bus | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Bus¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Bus | Normal | EquipmentFailureInvolved¦Overhead¦Bus¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Bushing | Arcing | EquipmentFailureInvolved¦Overhead¦Bushing¦Arcing | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Bushing | Broken | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Bushing | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Bushing¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Bushing | Burned Open | EquipmentFailureInvolved¦Overhead¦Bushing¦BurnedOpen | #N/A |  |  | None | Medium
EquipmentFailureInvolved | Overhead | Bushing | Deteriorated | EquipmentFailureInvolved¦Overhead¦Bushing¦Deteriorated |  |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Bushing | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Bushing¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Bushing | Leaking | EquipmentFailureInvolved¦Overhead¦Bushing¦Leaking | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Capacitor | Arcing | EquipmentFailureInvolved¦Overhead¦Capacitor¦Arcing | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Capacitor | Broken | EquipmentFailureInvolved¦Overhead¦Capacitor¦Broken | #N/A |  |  | None | Medium
EquipmentFailureInvolved | Overhead | Capacitor | Broken | EquipmentFailureInvolved¦Overhead¦Capacitor¦Broken |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Capacitor | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Capacitor¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Capacitor | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Capacitor¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Contaminated | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Underground | Burned/flashed | EquipmentFailureInvolved¦Overhead¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonobject | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Contaminated | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Contaminated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Normal | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Deteriorated | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(UG)¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Normal | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(UG)¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Crossarm, Steel | Broken | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Steel | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Crossarm, Steel | Burned/flashed | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Steel | Deteriorated | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Deteriorated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Normal | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | CT | Deteriorated | EquipmentFailureInvolved¦Overhead¦CT¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | CT | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦CT¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Customer Equipment | Arcing | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Customer Equipment | Broken | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Customer Equipment | Burned/flashed | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Customer Equipment | Deteriorated | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Customer Equipment | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Customer Equipment | Normal | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Customer Equipment | Together | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Together | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
EquipmentFailureInvolved | Overhead | Cutoutfuseholder | Brokenwireonground | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned Open | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦BurnedOpen | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Malfunctioning | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Footings, Tower or Pole | Broken | EquipmentFailureInvolved¦Overhead¦FootingsTowerorPole¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Footings, Tower or Pole | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦FootingsTowerorPole¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Footings, Tower or Pole | Normal | EquipmentFailureInvolved¦Overhead¦FootingsTowerorPole¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Fuse | (blank) | EquipmentFailureInvolved¦Overhead¦Fuse¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Fuse | Arcing | EquipmentFailureInvolved¦Overhead¦Fuse¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Fuse | Broken | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Fuse | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Fuse¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Fuse | Burned Open | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
EquipmentFailureInvolved | Overhead | Fuse | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Fuse¦Malfunctioning |  |  |  | None | High
Equipment Failure/Involved | Overhead | Fuse | Normal | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Generator | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Generator¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Generator | Normal | EquipmentFailureInvolved¦Overhead¦Generator¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Insulator | Arcing | EquipmentFailureInvolved¦Overhead¦Insulator¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Insulator | Broken | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Insulator | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Insulator | Normal | EquipmentFailureInvolved¦Overhead¦Insulator¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Jumper | (blank) | EquipmentFailureInvolved¦Overhead¦Jumper¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Jumper | Arcing | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Jumper | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦Jumper¦BentorTwisted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Jumper | Broken | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Jumper | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Jumper¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Jumper | Burned Open | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Jumper | Deteriorated | EquipmentFailureInvolved¦Overhead¦Jumper¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Jumper | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Jumper¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Jumper | Normal | EquipmentFailureInvolved¦Overhead¦Jumper¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Lightning Arrestor | Arcing | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Brokenwireonground | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Metering Equipment | (blank) | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Metering Equipment | Broken | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Metering Equipment | Burned/flashed | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Metering Equipment | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Metering Equipment | Malfunctioning | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Other | Arcing | EquipmentFailureInvolved¦Overhead¦Other¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦Other¦BentorTwisted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Broken | EquipmentFailureInvolved¦Overhead¦Other¦Broken | #N/A |  |  | N/A | N/A
EquipmentFailureInvolved | Overhead | Other | Brokenwireonground | EquipmentFailureInvolved¦Overhead¦Other¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Other | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Other¦Brokenwireonobject | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Burned Open | EquipmentFailureInvolved¦Overhead¦Other¦BurnedOpen | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Deteriorated | EquipmentFailureInvolved¦Overhead¦Other¦Deteriorated | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Leaking | EquipmentFailureInvolved¦Overhead¦Other¦Leaking | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Normal | EquipmentFailureInvolved¦Overhead¦Other¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Other | Together | EquipmentFailureInvolved¦Overhead¦Other¦Together | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | PGs, Kearneys | Broken | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | PGs, Kearneys | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | PGs, Kearneys | Burned/flashed | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | PGs, Kearneys | Burned Open | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦BurnedOpen | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | PGs, Kearneys | Deteriorated | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pole - Tower, steel | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦BentorTwisted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Pole - Tower, steel | Broken | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Pole - Tower, steel | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Pole - Tower, steel | Deteriorated | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦Deteriorated | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Pole-Wood | Broken | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pole-Wood | Contaminated | EquipmentFailureInvolved¦Overhead¦PoleWood¦Contaminated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pole-Wood | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦PoleWood¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pole-Wood | Normal | EquipmentFailureInvolved¦Overhead¦PoleWood¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pole-Wood | On Ground | EquipmentFailureInvolved¦Overhead¦PoleWood¦OnGround | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Arcing | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Deteriorated | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Leaking | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Leaking | #N/A |  |  | None | High
EquipmentFailureInvolved | Overhead | PotheadRiserTermination | Burnedflashed | EquipmentFailureInvolved¦Overhead¦PotheadRiserTermination¦Burnedflashed |  |  |  | None | High
Equipment Failure/Involved | Overhead | PT/CCVT | Burned/flashed | EquipmentFailureInvolved¦Overhead¦PTCCVT¦Burnedflashed | #N/A |  |  | None | None
EquipmentFailureInvolved | Overhead | PTCCVT | BurnedOpen | EquipmentFailureInvolved¦Overhead¦PTCCVT¦BurnedOpen |  |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | PT/CCVT | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦PTCCVT¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | PT/CCVT | Leaking | EquipmentFailureInvolved¦Overhead¦PTCCVT¦Leaking | #N/A |  |  | None | None
EquipmentFailureInvolved | Overhead | Recloser | Arcing | EquipmentFailureInvolved¦Overhead¦Recloser¦Arcing |  |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Recloser | Broken | EquipmentFailureInvolved¦Overhead¦Recloser¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Recloser | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Recloser¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Recloser | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Recloser¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Recloser | Leaking | EquipmentFailureInvolved¦Overhead¦Recloser¦Leaking | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Recloser | Normal | EquipmentFailureInvolved¦Overhead¦Recloser¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Regulator | Arcing | EquipmentFailureInvolved¦Overhead¦Regulator¦Arcing | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Regulator | Broken | EquipmentFailureInvolved¦Overhead¦Regulator¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Regulator | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Regulator¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Regulator | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Regulator¦FailedFaulted | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Regulator | Leaking | EquipmentFailureInvolved¦Overhead¦Regulator¦Leaking | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Regulator¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Regulator | Normal | EquipmentFailureInvolved¦Overhead¦Regulator¦Normal | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Regulator, LTC substation | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦RegulatorLTCsubstation¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Relay | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Relay¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | SCADA | Malfunctioning | EquipmentFailureInvolved¦Overhead¦SCADA¦Malfunctioning | #N/A |  |  | None | None
EquipmentFailureInvolved | Overhead | SCADA | Malfunctioning | EquipmentFailureInvolved¦Overhead¦SCADA¦Malfunctioning |  |  |  | None | None
Equipment Failure/Involved | Overhead | Secondary | (blank) | EquipmentFailureInvolved¦Overhead¦Secondary¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Secondary | Arcing | EquipmentFailureInvolved¦Overhead¦Secondary¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Secondary | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦Secondary¦BentorTwisted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Secondary | Broken | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Secondary | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Secondary¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Secondary | Burned Open | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Secondary | Contaminated | EquipmentFailureInvolved¦Overhead¦Secondary¦Contaminated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Secondary | Deteriorated | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Secondary | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Secondary¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Secondary | Normal | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Secondary | On Ground | EquipmentFailureInvolved¦Overhead¦Secondary¦OnGround | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Secondary | Together | EquipmentFailureInvolved¦Overhead¦Secondary¦Together | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Sectionalizer | Broken | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Sectionalizer | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Sectionalizer | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Malfunctioning | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Service conductor | Annealed | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Annealed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Service conductor | Arcing | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Service conductor | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦BentorTwisted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Service conductor | Broken | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Service conductor | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Service conductor | Burned Open | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦BurnedOpen | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Service conductor | Deteriorated | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Deteriorated | #N/A |  |  | None | High
EquipmentFailureInvolved | Overhead | Serviceconductor | FailedFaulted | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦FailedFaulted |  |  |  | None | High
Equipment Failure/Involved | Overhead | Service conductor | Normal | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Service conductor | On Ground | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦OnGround | #N/A |  |  | None | Medium
EquipmentFailureInvolved | Overhead | Serviceconductor | Together | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Together |  |  |  | None | High
Equipment Failure/Involved | Overhead | Stepdown | Arcing | EquipmentFailureInvolved¦Overhead¦Stepdown¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Stepdown | Broken | EquipmentFailureInvolved¦Overhead¦Stepdown¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Stepdown | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Stepdown¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Stepdown | Deteriorated | EquipmentFailureInvolved¦Overhead¦Stepdown¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Stepdown | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Stepdown¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Stepdown | Normal | EquipmentFailureInvolved¦Overhead¦Stepdown¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Street Light Equipment | Broken | EquipmentFailureInvolved¦Overhead¦StreetLightEquipment¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Street Light Equipment | On Ground | EquipmentFailureInvolved¦Overhead¦StreetLightEquipment¦OnGround | #N/A |  |  | None | None
Equipment Failure/Involved | Overhead | Switch (OH) | Arcing | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Switch (OH) | Broken | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Switch (OH) | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Switch (OH) | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦FailedFaulted | #N/A |  |  | None | Very High
EquipmentFailureInvolved | Overhead | Switch(OH) | Leaking | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Leaking |  |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Switch (OH) | Normal | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Switch | Arcing | EquipmentFailureInvolved¦Overhead¦Switch¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Switch | Broken | EquipmentFailureInvolved¦Overhead¦Switch¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Switch | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Switch¦FailedFaulted | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Switch | Normal | EquipmentFailureInvolved¦Overhead¦Switch¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Transformer (OH) | (blank) | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer (OH) | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Transformer (OH) | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | (blank) | EquipmentFailureInvolved¦Overhead¦Transformer¦ | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Overhead | Transformer | Arcing | EquipmentFailureInvolved¦Overhead¦Transformer¦Arcing | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦Transformer¦BentorTwisted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Broken | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Transformer | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Burned Open | EquipmentFailureInvolved¦Overhead¦Transformer¦BurnedOpen | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Contaminated | EquipmentFailureInvolved¦Overhead¦Transformer¦Contaminated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Deteriorated | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Leaking | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Malfunctioning | EquipmentFailureInvolved¦Overhead¦Transformer¦Malfunctioning | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | Normal | EquipmentFailureInvolved¦Overhead¦Transformer¦Normal | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Transformer | On Ground | EquipmentFailureInvolved¦Overhead¦Transformer¦OnGround | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Transformer | Together | EquipmentFailureInvolved¦Overhead¦Transformer¦Together | #N/A |  |  | None | High
Equipment Failure/Involved | Overhead | Woodpin | Broken | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken | #N/A |  |  | None | Very High
Equipment Failure/Involved | Overhead | Woodpin | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Woodpin¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Woodpin | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦Woodpin¦Brokenwireonobject | #N/A |  |  | None | Medium
Equipment Failure/Involved | Overhead | Woodpin | Normal | EquipmentFailureInvolved¦Overhead¦Woodpin¦Normal | #N/A |  |  | None | Very High
Equipment Failure/Involved | Rock/mud slide | Pole-Wood | Broken, wire on ground | EquipmentFailureInvolved¦Rockmudslide¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Equipment Failure/Involved | Substation | Bus | Normal | EquipmentFailureInvolved¦Substation¦Bus¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Bushing | Burned/flashed | EquipmentFailureInvolved¦Substation¦Bushing¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Bushing | Deteriorated | EquipmentFailureInvolved¦Substation¦Bushing¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Bushing | Failed/Faulted | EquipmentFailureInvolved¦Substation¦Bushing¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Circuit Breaker | Broken | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Circuit Breaker | Failed/Faulted | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Circuit Breaker | Malfunctioning | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Circuit Breaker | Normal | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Conductor, Underground | Broken | EquipmentFailureInvolved¦Substation¦ConductorUnderground¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Control Circuit/Wiring | Broken | EquipmentFailureInvolved¦Substation¦ControlCircuitWiring¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | CT | Broken | EquipmentFailureInvolved¦Substation¦CT¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Generator | Burned/flashed | EquipmentFailureInvolved¦Substation¦Generator¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Generator | Failed/Faulted | EquipmentFailureInvolved¦Substation¦Generator¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Generator | Malfunctioning | EquipmentFailureInvolved¦Substation¦Generator¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Generator | Normal | EquipmentFailureInvolved¦Substation¦Generator¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Insulator | Broken | EquipmentFailureInvolved¦Substation¦Insulator¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Insulator | Failed/Faulted | EquipmentFailureInvolved¦Substation¦Insulator¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Lightning Arrestor | Failed/Faulted | EquipmentFailureInvolved¦Substation¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Other | Arcing | EquipmentFailureInvolved¦Substation¦Other¦Arcing | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | Other | Bent or Twisted | EquipmentFailureInvolved¦Substation¦Other¦BentorTwisted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | Other | Broken | EquipmentFailureInvolved¦Substation¦Other¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | Other | Burned/flashed | EquipmentFailureInvolved¦Substation¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | Other | Failed/Faulted | EquipmentFailureInvolved¦Substation¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | Other | Leaking | EquipmentFailureInvolved¦Substation¦Other¦Leaking | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | Other | Malfunctioning | EquipmentFailureInvolved¦Substation¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | Other | Normal | EquipmentFailureInvolved¦Substation¦Other¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Substation | PT/CCVT | Burned/flashed | EquipmentFailureInvolved¦Substation¦PTCCVT¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | PT/CCVT | Failed/Faulted | EquipmentFailureInvolved¦Substation¦PTCCVT¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Regulator, LTC substation | Broken | EquipmentFailureInvolved¦Substation¦RegulatorLTCsubstation¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Regulator, LTC substation | Failed/Faulted | EquipmentFailureInvolved¦Substation¦RegulatorLTCsubstation¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Relay | Failed/Faulted | EquipmentFailureInvolved¦Substation¦Relay¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Relay | Malfunctioning | EquipmentFailureInvolved¦Substation¦Relay¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Relay | Normal | EquipmentFailureInvolved¦Substation¦Relay¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Secondary | Broken | EquipmentFailureInvolved¦Substation¦Secondary¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Switch | Broken | EquipmentFailureInvolved¦Substation¦Switch¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Switch | Failed/Faulted | EquipmentFailureInvolved¦Substation¦Switch¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Transformer | Broken | EquipmentFailureInvolved¦Substation¦Transformer¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Transformer | Failed/Faulted | EquipmentFailureInvolved¦Substation¦Transformer¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Transformer Power | Burned/flashed | EquipmentFailureInvolved¦Substation¦TransformerPower¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Transformer Power | Failed/Faulted | EquipmentFailureInvolved¦Substation¦TransformerPower¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Substation | Transformer Power | Malfunctioning | EquipmentFailureInvolved¦Substation¦TransformerPower¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bus | Burned/flashed | EquipmentFailureInvolved¦Underground¦Bus¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bus | Contaminated | EquipmentFailureInvolved¦Underground¦Bus¦Contaminated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bus | Deteriorated | EquipmentFailureInvolved¦Underground¦Bus¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bus | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Bus¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bushing | Arcing | EquipmentFailureInvolved¦Underground¦Bushing¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bushing | Broken | EquipmentFailureInvolved¦Underground¦Bushing¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bushing | Burned/flashed | EquipmentFailureInvolved¦Underground¦Bushing¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Bushing | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Bushing¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Cable Termination(live front) | Broken | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Cable Termination(live front) | Burned/flashed | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Cable Termination(live front) | Contaminated | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦Contaminated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Cable Termination(live front) | Failed/Faulted | EquipmentFailureInvolved¦Underground¦CableTermination(livefront)¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Broken | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Failed/Faulted | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Normal | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Connector or Splice (OH) | Arcing | EquipmentFailureInvolved¦Underground¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | None | Very High
Equipment Failure/Involved | Underground | Connector or Splice (OH) | Burned/flashed | EquipmentFailureInvolved¦Underground¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Equipment Failure/Involved | Underground | Connector or Splice (UG) | Broken | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Connector or Splice (UG) | Burned/flashed | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Connector or Splice (UG) | Contaminated | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Contaminated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Connector or Splice (UG) | Deteriorated | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Connector or Splice (UG) | Failed/Faulted | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Customer Equipment | Burned/flashed | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Customer Equipment | Malfunctioning | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦Malfunctioning | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Elbow | Broken | EquipmentFailureInvolved¦Underground¦Elbow¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Elbow | Burned/flashed | EquipmentFailureInvolved¦Underground¦Elbow¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Elbow | Deteriorated | EquipmentFailureInvolved¦Underground¦Elbow¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Elbow | Normal | EquipmentFailureInvolved¦Underground¦Elbow¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Fuse | Arcing | EquipmentFailureInvolved¦Underground¦Fuse¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Fuse | Broken | EquipmentFailureInvolved¦Underground¦Fuse¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Fuse | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Fuse¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Metering Equipment | Broken | EquipmentFailureInvolved¦Underground¦MeteringEquipment¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Other | Broken | EquipmentFailureInvolved¦Underground¦Other¦Broken | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Underground | Other | Burned/flashed | EquipmentFailureInvolved¦Underground¦Other¦Burnedflashed | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Underground | Other | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Underground | Other | Leaking | EquipmentFailureInvolved¦Underground¦Other¦Leaking | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Underground | Other | Malfunctioning | EquipmentFailureInvolved¦Underground¦Other¦Malfunctioning | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Underground | Other | Normal | EquipmentFailureInvolved¦Underground¦Other¦Normal | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Underground | Other | Together | EquipmentFailureInvolved¦Underground¦Other¦Together | #N/A |  |  | N/A | N/A
Equipment Failure/Involved | Underground | Pothead/Riser Termination | Broken | EquipmentFailureInvolved¦Underground¦PotheadRiserTermination¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Pothead/Riser Termination | Failed/Faulted | EquipmentFailureInvolved¦Underground¦PotheadRiserTermination¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Recloser | Burned/flashed | EquipmentFailureInvolved¦Underground¦Recloser¦Burnedflashed | #N/A |  |  | None | Medium
Equipment Failure/Involved | Underground | Secondary | Arcing | EquipmentFailureInvolved¦Underground¦Secondary¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Secondary | Broken | EquipmentFailureInvolved¦Underground¦Secondary¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Secondary | Burned/flashed | EquipmentFailureInvolved¦Underground¦Secondary¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Secondary | Burned Open | EquipmentFailureInvolved¦Underground¦Secondary¦BurnedOpen | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Secondary | Contaminated | EquipmentFailureInvolved¦Underground¦Secondary¦Contaminated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Secondary | Deteriorated | EquipmentFailureInvolved¦Underground¦Secondary¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Secondary | Normal | EquipmentFailureInvolved¦Underground¦Secondary¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Secondary | Together | EquipmentFailureInvolved¦Underground¦Secondary¦Together | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Service conductor | Arcing | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Service conductor | Broken | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Service conductor | Burned Open | EquipmentFailureInvolved¦Underground¦Serviceconductor¦BurnedOpen | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Service conductor | Deteriorated | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Stepdown | Broken | EquipmentFailureInvolved¦Underground¦Stepdown¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Stepdown | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Stepdown¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Switch (UG) | Broken | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Switch (UG) | Burned/flashed | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Switch (UG) | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Switch(UG)¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Switch (UG) | Leaking | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Leaking | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Switch | Arcing | EquipmentFailureInvolved¦Underground¦Switch¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Switch | Burned/flashed | EquipmentFailureInvolved¦Underground¦Switch¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (OH) | Deteriorated | EquipmentFailureInvolved¦Underground¦Transformer(OH)¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (OH) | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Arcing | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Broken | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Burned/flashed | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Contaminated | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Contaminated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (UG) | Normal | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Normal | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer | Arcing | EquipmentFailureInvolved¦Underground¦Transformer¦Arcing | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer | Broken | EquipmentFailureInvolved¦Underground¦Transformer¦Broken | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer | Burned/flashed | EquipmentFailureInvolved¦Underground¦Transformer¦Burnedflashed | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer | Deteriorated | EquipmentFailureInvolved¦Underground¦Transformer¦Deteriorated | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer | Leaking | EquipmentFailureInvolved¦Underground¦Transformer¦Leaking | #N/A |  |  | None | None
Equipment Failure/Involved | Underground | Transformer | Normal | EquipmentFailureInvolved¦Underground¦Transformer¦Normal | #N/A |  |  | None | None
Unknown Cause | Patrol - found nothing | (blank) | (blank) | UnknownCause¦Patrolfoundnothing¦¦ | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - found nothing | (blank) | Broken | UnknownCause¦Patrolfoundnothing¦¦Broken | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - found nothing | (blank) | Burned Open | UnknownCause¦Patrolfoundnothing¦¦BurnedOpen | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - found nothing | (blank) | Failed/Faulted | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - found nothing | (blank) | Normal | UnknownCause¦Patrolfoundnothing¦¦Normal | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - found nothing | Conductor, Overhead | Bent or Twisted | UnknownCause¦Patrolfoundnothing¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Conductor, Overhead | Broken | UnknownCause¦Patrolfoundnothing¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Conductor, Overhead | Normal | UnknownCause¦Patrolfoundnothing¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Crossarm, Wood | Broken | UnknownCause¦Patrolfoundnothing¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Cutout, fuse holder | Failed/Faulted | UnknownCause¦Patrolfoundnothing¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Very High
UnknownCause | Patrolfoundnothing | Fuse | Broken | UnknownCause¦Patrolfoundnothing¦Fuse¦Broken |  |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Fuse | Failed/Faulted | UnknownCause¦Patrolfoundnothing¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Insulator | Broken | UnknownCause¦Patrolfoundnothing¦Insulator¦Broken | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Other | Broken | UnknownCause¦Patrolfoundnothing¦Other¦Broken | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - found nothing | Pole-Wood | Burned/flashed | UnknownCause¦Patrolfoundnothing¦PoleWood¦Burnedflashed | #N/A |  |  | None | High
Unknown Cause | Patrol - found nothing | Recloser | Malfunctioning | UnknownCause¦Patrolfoundnothing¦Recloser¦Malfunctioning | #N/A |  |  | None | Medium
Unknown Cause | Patrol - found nothing | Recloser | Normal | UnknownCause¦Patrolfoundnothing¦Recloser¦Normal | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Sectionalizer | Normal | UnknownCause¦Patrolfoundnothing¦Sectionalizer¦Normal | #N/A |  |  | None | Very High
Unknown Cause | Patrol - found nothing | Transformer (OH) | Failed/Faulted | UnknownCause¦Patrolfoundnothing¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | High
Unknown Cause | Patrol - found nothing | Transformer | Broken | UnknownCause¦Patrolfoundnothing¦Transformer¦Broken | #N/A |  |  | None | High
Unknown Cause | Patrol - found nothing | Transformer | Burned/flashed | UnknownCause¦Patrolfoundnothing¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Unknown Cause | Patrol - found nothing | Transformer | Failed/Faulted | UnknownCause¦Patrolfoundnothing¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Unknown Cause | Patrol - found nothing | Transformer | Normal | UnknownCause¦Patrolfoundnothing¦Transformer¦Normal | #N/A |  |  | None | High
Unknown Cause | Patrol - not conducted | (blank) | (blank) | UnknownCause¦Patrolnotconducted¦¦ | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - not conducted | (blank) | Failed/Faulted | UnknownCause¦Patrolnotconducted¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Unknown Cause | Patrol - not conducted | Circuit Breaker | Malfunctioning | UnknownCause¦Patrolnotconducted¦CircuitBreaker¦Malfunctioning | #N/A |  |  | None | None
Unknown Cause | Patrol - not conducted | Conductor, Overhead | Arcing | UnknownCause¦Patrolnotconducted¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
Unknown Cause | Patrol - not conducted | Conductor, Overhead | Broken, wire on ground | UnknownCause¦Patrolnotconducted¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Unknown Cause | Patrol - not conducted | Conductor, Overhead | Together | UnknownCause¦Patrolnotconducted¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Unknown Cause | Patrol - not conducted | Customer Equipment | Malfunctioning | UnknownCause¦Patrolnotconducted¦CustomerEquipment¦Malfunctioning | #N/A |  |  | None | None
Unknown Cause | Patrol - not conducted | Cutout, fuse holder | Broken | UnknownCause¦Patrolnotconducted¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
Unknown Cause | Patrol - not conducted | Pole-Wood | Broken | UnknownCause¦Patrolnotconducted¦PoleWood¦Broken | #N/A |  |  | None | High
Unknown Cause | Patrol - not conducted | Transformer | Failed/Faulted | UnknownCause¦Patrolnotconducted¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Unknown Cause | Patrol - not conducted | Transformer | Malfunctioning | UnknownCause¦Patrolnotconducted¦Transformer¦Malfunctioning | #N/A |  |  | None | High
Vegetation | Othergroundvegetation | AnchororGuy | Normal | Vegetation¦Othergroundvegetation¦AnchororGuy¦Normal |  |  |  | N/A | N/A
Vegetation | Other ground vegetation | Conductor, Overhead | Broken | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Conductor, Overhead | Contaminated | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Conductor, Overhead | Normal | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Conductor, Overhead | Together | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Crossarm, Wood | Broken | Vegetation¦Othergroundvegetation¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Cutout, fuse holder | Normal | Vegetation¦Othergroundvegetation¦Cutoutfuseholder¦Normal | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Fuse | Failed/Faulted | Vegetation¦Othergroundvegetation¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Fuse | Normal | Vegetation¦Othergroundvegetation¦Fuse¦Normal | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Insulator | Arcing | Vegetation¦Othergroundvegetation¦Insulator¦Arcing | #N/A |  |  | None | Very High
Vegetation | Other ground vegetation | Other | Normal | Vegetation¦Othergroundvegetation¦Other¦Normal | #N/A |  |  | N/A | N/A
Vegetation | Other ground vegetation | Pole-Wood | Broken | Vegetation¦Othergroundvegetation¦PoleWood¦Broken | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Pole-Wood | Normal | Vegetation¦Othergroundvegetation¦PoleWood¦Normal | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Pothead(Riser Termination) | Burned/flashed | Vegetation¦Othergroundvegetation¦Pothead(RiserTermination)¦Burnedflashed | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Secondary | Burned/flashed | Vegetation¦Othergroundvegetation¦Secondary¦Burnedflashed | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Secondary | Contaminated | Vegetation¦Othergroundvegetation¦Secondary¦Contaminated | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Transformer (UG) | Broken | Vegetation¦Othergroundvegetation¦Transformer(UG)¦Broken | #N/A |  |  | None | None
Vegetation | Other ground vegetation | Transformer | Arcing | Vegetation¦Othergroundvegetation¦Transformer¦Arcing | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Transformer | Broken | Vegetation¦Othergroundvegetation¦Transformer¦Broken | #N/A |  |  | None | High
Vegetation | Other ground vegetation | Transformer | Broken, wire on ground | Vegetation¦Othergroundvegetation¦Transformer¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Othergroundvegetation | Transformer | Normal | Vegetation¦Othergroundvegetation¦Transformer¦Normal |  |  |  | N/A | N/A
Vegetation | Tree - bark fell into line | (blank) | Failed/Faulted | Vegetation¦Treebarkfellintoline¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Vegetation | Tree - bark fell into line | Anchor or Guy | Broken | Vegetation¦Treebarkfellintoline¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Vegetation | Treebarkfellintoline | Bus | FailedFaulted | Vegetation¦Treebarkfellintoline¦Bus¦FailedFaulted |  |  |  | N/A | N/A
Vegetation | Tree - bark fell into line | Conductor, Overhead | Arcing | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on object | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Conductor, Overhead | Burned/flashed | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Contaminated | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Deteriorated | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Failed/Faulted | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦FailedFaulted | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | On Ground | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Conductor, Overhead | Together | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Arcing | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Arcing | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Broken | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Burned/flashed | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Normal | Vegetation¦Treebarkfellintoline¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Crossarm, Wood | Broken | Vegetation¦Treebarkfellintoline¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Crossarm, Wood | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Crossarm, Wood | Burned/flashed | Vegetation¦Treebarkfellintoline¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Cutout, fuse holder | Broken | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Cutout, fuse holder | Failed/Faulted | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Cutout, fuse holder | Normal | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦Normal | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Fuse | Burned Open | Vegetation¦Treebarkfellintoline¦Fuse¦BurnedOpen | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Fuse | Normal | Vegetation¦Treebarkfellintoline¦Fuse¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Insulator | Broken | Vegetation¦Treebarkfellintoline¦Insulator¦Broken | #N/A |  |  | None | Very High
Vegetation | Treebarkfellintoline | Insulator | Normal | Vegetation¦Treebarkfellintoline¦Insulator¦Normal |  |  |  | None | Very High
Vegetation | Tree - bark fell into line | Pole-Wood | Broken | Vegetation¦Treebarkfellintoline¦PoleWood¦Broken | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Pole-Wood | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Treebarkfellintoline | PoleWood | Normal | Vegetation¦Treebarkfellintoline¦PoleWood¦Normal |  |  |  | None | Very High
Vegetation | Tree - bark fell into line | Recloser | Normal | Vegetation¦Treebarkfellintoline¦Recloser¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - bark fell into line | Secondary | Broken | Vegetation¦Treebarkfellintoline¦Secondary¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Secondary | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Secondary | Broken, wire on object | Vegetation¦Treebarkfellintoline¦Secondary¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Secondary | On Ground | Vegetation¦Treebarkfellintoline¦Secondary¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Secondary | Together | Vegetation¦Treebarkfellintoline¦Secondary¦Together | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Service conductor | Broken | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Service conductor | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Service conductor | Normal | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Normal | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer (OH) | Broken | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer (OH) | Leaking | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Leaking | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer (OH) | Normal | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Normal | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer | Bent or Twisted | Vegetation¦Treebarkfellintoline¦Transformer¦BentorTwisted | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer | Broken | Vegetation¦Treebarkfellintoline¦Transformer¦Broken | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦Transformer¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - bark fell into line | Transformer | Failed/Faulted | Vegetation¦Treebarkfellintoline¦Transformer¦FailedFaulted | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer | Normal | Vegetation¦Treebarkfellintoline¦Transformer¦Normal | #N/A |  |  | None | High
Vegetation | Tree - bark fell into line | Transformer | Together | Vegetation¦Treebarkfellintoline¦Transformer¦Together | #N/A |  |  | None | High
Vegetation | Tree - branch fell on line | (blank) | (blank) | Vegetation¦Treebranchfellonline¦¦ | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | (blank) | Broken | Vegetation¦Treebranchfellonline¦¦Broken | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | (blank) | Burned Open | Vegetation¦Treebranchfellonline¦¦BurnedOpen | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | (blank) | Failed/Faulted | Vegetation¦Treebranchfellonline¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | Anchor or Guy | Broken | Vegetation¦Treebranchfellonline¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - branch fell on line | Anchor or Guy | Normal | Vegetation¦Treebranchfellonline¦AnchororGuy¦Normal | #N/A |  |  | None | Very High
Vegetation | Treebranchfellonline | Bushing | Arcing | Vegetation¦Treebranchfellonline¦Bushing¦Arcing |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Bushing | Broken | Vegetation¦Treebranchfellonline¦Bushing¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Bushing | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Bushing¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Bushing | Normal | Vegetation¦Treebranchfellonline¦Bushing¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Capacitor | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Capacitor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Circuit Breaker | Normal | Vegetation¦Treebranchfellonline¦CircuitBreaker¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Annealed | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Annealed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Bent or Twisted | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Burned/flashed | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Contaminated | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Deteriorated | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Failed/Faulted | Vegetation¦Treebranchfellonline¦ConductorOverhead¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Malfunctioning | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Malfunctioning | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Underground | Normal | Vegetation¦Treebranchfellonline¦ConductorUnderground¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on ground | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on object | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Burned/flashed | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Normal | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Steel | Broken, wire on ground | Vegetation¦Treebranchfellonline¦CrossarmSteel¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on object | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Wood | Burned/flashed | Vegetation¦Treebranchfellonline¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Wood | Normal | Vegetation¦Treebranchfellonline¦CrossarmWood¦Normal | #N/A |  |  | None | Medium
Vegetation | Treebranchfellonline | CustomerEquipment | Arcing | Vegetation¦Treebranchfellonline¦CustomerEquipment¦Arcing |  |  |  | None | None
Vegetation | Tree - branch fell on line | Customer Equipment | Broken | Vegetation¦Treebranchfellonline¦CustomerEquipment¦Broken | #N/A |  |  | None | None
Vegetation | Tree - branch fell on line | Customer Equipment | Normal | Vegetation¦Treebranchfellonline¦CustomerEquipment¦Normal | #N/A |  |  | None | None
Vegetation | Tree - branch fell on line | Cutout, Fused, Distribution | Failed/Faulted | Vegetation¦Treebranchfellonline¦CutoutFusedDistribution¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Cutout, fuse holder | Broken | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Cutout, fuse holder | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Cutout, fuse holder | Burned/flashed | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Cutout, fuse holder | Failed/Faulted | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Cutout, fuse holder | Normal | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Fuse | Broken | Vegetation¦Treebranchfellonline¦Fuse¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Fuse | Burned Open | Vegetation¦Treebranchfellonline¦Fuse¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Fuse | Normal | Vegetation¦Treebranchfellonline¦Fuse¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Fuse | On Ground | Vegetation¦Treebranchfellonline¦Fuse¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Insulator | Broken | Vegetation¦Treebranchfellonline¦Insulator¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Insulator | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Insulator¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Insulator | Broken, wire on object | Vegetation¦Treebranchfellonline¦Insulator¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Insulator | Burned/flashed | Vegetation¦Treebranchfellonline¦Insulator¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Insulator | Normal | Vegetation¦Treebranchfellonline¦Insulator¦Normal | #N/A |  |  | None | Medium High
Vegetation | Tree - branch fell on line | Interrupter | Normal | Vegetation¦Treebranchfellonline¦Interrupter¦Normal | #N/A |  |  | None | None
Vegetation | Tree - branch fell on line | Jumper | Bent or Twisted | Vegetation¦Treebranchfellonline¦Jumper¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Jumper | Broken | Vegetation¦Treebranchfellonline¦Jumper¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Jumper | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Jumper¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Jumper | Burned Open | Vegetation¦Treebranchfellonline¦Jumper¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Jumper | Normal | Vegetation¦Treebranchfellonline¦Jumper¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Lightning Arrestor | Broken | Vegetation¦Treebranchfellonline¦LightningArrestor¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Lightning Arrestor | Normal | Vegetation¦Treebranchfellonline¦LightningArrestor¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Other | Bent or Twisted | Vegetation¦Treebranchfellonline¦Other¦BentorTwisted | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | Other | Broken | Vegetation¦Treebranchfellonline¦Other¦Broken | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | Other | Broken, wire on object | Vegetation¦Treebranchfellonline¦Other¦Brokenwireonobject | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | Other | Normal | Vegetation¦Treebranchfellonline¦Other¦Normal | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | Other | On Ground | Vegetation¦Treebranchfellonline¦Other¦OnGround | #N/A |  |  | N/A | N/A
Vegetation | Tree - branch fell on line | Pole - Tower, steel | Normal | Vegetation¦Treebranchfellonline¦PoleTowersteel¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Pole-Wood | Broken | Vegetation¦Treebranchfellonline¦PoleWood¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on object | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Treebranchfellonline | PoleWood | Contaminated | Vegetation¦Treebranchfellonline¦PoleWood¦Contaminated |  |  |  | None | Medium
Vegetation | Treebranchfellonline | PoleWood | Deteriorated | Vegetation¦Treebranchfellonline¦PoleWood¦Deteriorated |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Failed/Faulted | Vegetation¦Treebranchfellonline¦Pothead(RiserTermination)¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Normal | Vegetation¦Treebranchfellonline¦Pothead(RiserTermination)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Recloser | Normal | Vegetation¦Treebranchfellonline¦Recloser¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Regulator | Normal | Vegetation¦Treebranchfellonline¦Regulator¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Annealed | Vegetation¦Treebranchfellonline¦Secondary¦Annealed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Arcing | Vegetation¦Treebranchfellonline¦Secondary¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Bent or Twisted | Vegetation¦Treebranchfellonline¦Secondary¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Broken | Vegetation¦Treebranchfellonline¦Secondary¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Broken, wire on object | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Deteriorated | Vegetation¦Treebranchfellonline¦Secondary¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Normal | Vegetation¦Treebranchfellonline¦Secondary¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | On Ground | Vegetation¦Treebranchfellonline¦Secondary¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Together | Vegetation¦Treebranchfellonline¦Secondary¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Service conductor | Broken | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on object | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Service conductor | Normal | Vegetation¦Treebranchfellonline¦Serviceconductor¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Service conductor | On Ground | Vegetation¦Treebranchfellonline¦Serviceconductor¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Service conductor | Together | Vegetation¦Treebranchfellonline¦Serviceconductor¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Switch (OH) | Broken | Vegetation¦Treebranchfellonline¦Switch(OH)¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Switch (OH) | Failed/Faulted | Vegetation¦Treebranchfellonline¦Switch(OH)¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Switch (OH) | Normal | Vegetation¦Treebranchfellonline¦Switch(OH)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | (blank) | Vegetation¦Treebranchfellonline¦Transformer(OH)¦ | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Arcing | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Burned/flashed | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Treebranchfellonline | Transformer(OH) | Deteriorated | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Deteriorated |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Failed/Faulted | Vegetation¦Treebranchfellonline¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Leaking | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Leaking | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | (blank) | Vegetation¦Treebranchfellonline¦Transformer¦ | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Arcing | Vegetation¦Treebranchfellonline¦Transformer¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Bent or Twisted | Vegetation¦Treebranchfellonline¦Transformer¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Broken | Vegetation¦Treebranchfellonline¦Transformer¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Broken, wire on object | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Burned/flashed | Vegetation¦Treebranchfellonline¦Transformer¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Burned Open | Vegetation¦Treebranchfellonline¦Transformer¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Deteriorated | Vegetation¦Treebranchfellonline¦Transformer¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Failed/Faulted | Vegetation¦Treebranchfellonline¦Transformer¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Leaking | Vegetation¦Treebranchfellonline¦Transformer¦Leaking | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Normal | Vegetation¦Treebranchfellonline¦Transformer¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | On Ground | Vegetation¦Treebranchfellonline¦Transformer¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Together | Vegetation¦Treebranchfellonline¦Transformer¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - branch fell on line | Woodpin | Broken | Vegetation¦Treebranchfellonline¦Woodpin¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Together | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Together | #N/A |  |  | None | High
Vegetation | Tree - cutting, 3rd party | Crossarm, Wood | Broken | Vegetation¦Treecutting3rdparty¦CrossarmWood¦Broken | #N/A |  |  | None | Medium High
Vegetation | Tree - cutting, PG&E contractor | Anchor or Guy | Broken | Vegetation¦TreecuttingPG&Econtractor¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Vegetation | TreecuttingPG&Econtractor | CircuitBreaker | Normal | Vegetation¦TreecuttingPG&Econtractor¦CircuitBreaker¦Normal |  |  |  | N/A | N/A
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Annealed | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Annealed | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Arcing | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Burned/flashed | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Contaminated | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | On Ground | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Together | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Connector or Splice (OH) | Normal | Vegetation¦TreecuttingPG&Econtractor¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - cutting, PG&E contractor | Crossarm, Wood | Broken | Vegetation¦TreecuttingPG&Econtractor¦CrossarmWood¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Crossarm, Wood | Broken, wire on ground | Vegetation¦TreecuttingPG&Econtractor¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Fuse | Failed/Faulted | Vegetation¦TreecuttingPG&Econtractor¦Fuse¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Insulator | Broken | Vegetation¦TreecuttingPG&Econtractor¦Insulator¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Other | Broken | Vegetation¦TreecuttingPG&Econtractor¦Other¦Broken | #N/A |  |  | N/A | N/A
Vegetation | Tree - cutting, PG&E contractor | Other | Normal | Vegetation¦TreecuttingPG&Econtractor¦Other¦Normal | #N/A |  |  | N/A | N/A
Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken, wire on ground | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Recloser | Normal | Vegetation¦TreecuttingPG&Econtractor¦Recloser¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Secondary | Broken | Vegetation¦TreecuttingPG&Econtractor¦Secondary¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Secondary | Normal | Vegetation¦TreecuttingPG&Econtractor¦Secondary¦Normal | #N/A |  |  | None | High
Vegetation | Tree - cutting, PG&E contractor | Service conductor | Broken | Vegetation¦TreecuttingPG&Econtractor¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
Vegetation | TreecuttingPG&Econtractor | Transformer(OH) | Brokenwireonground | Vegetation¦TreecuttingPG&Econtractor¦Transformer(OH)¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Transformer (OH) | Normal | Vegetation¦TreecuttingPG&Econtractor¦Transformer(OH)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Transformer | Normal | Vegetation¦TreecuttingPG&Econtractor¦Transformer¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | (blank) | (blank) | Vegetation¦Treefellintoline¦¦ | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | (blank) | Burned Open | Vegetation¦Treefellintoline¦¦BurnedOpen | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | (blank) | Failed/Faulted | Vegetation¦Treefellintoline¦¦FailedFaulted | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | (blank) | Normal | Vegetation¦Treefellintoline¦¦Normal | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | Anchor or Guy | Broken | Vegetation¦Treefellintoline¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - fell into line | Anchor or Guy | Broken, wire on ground | Vegetation¦Treefellintoline¦AnchororGuy¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Anchor or Guy | Deteriorated | Vegetation¦Treefellintoline¦AnchororGuy¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Anchor or Guy | Normal | Vegetation¦Treefellintoline¦AnchororGuy¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - fell into line | Bushing | Broken | Vegetation¦Treefellintoline¦Bushing¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Capacitor | Broken, wire on ground | Vegetation¦Treefellintoline¦Capacitor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Circuit Breaker | Normal | Vegetation¦Treefellintoline¦CircuitBreaker¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Communication Equipment | Broken | Vegetation¦Treefellintoline¦CommunicationEquipment¦Broken | #N/A |  |  | None | N/A
Vegetation | Tree - fell into line | Conductor, Overhead | (blank) | Vegetation¦Treefellintoline¦ConductorOverhead¦ | #N/A |  |  | None | N/A
Vegetation | Tree - fell into line | Conductor, Overhead | Annealed | Vegetation¦Treefellintoline¦ConductorOverhead¦Annealed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Broken | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Contaminated | Vegetation¦Treefellintoline¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Deteriorated | Vegetation¦Treefellintoline¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Failed/Faulted | Vegetation¦Treefellintoline¦ConductorOverhead¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Normal | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Together | Vegetation¦Treefellintoline¦ConductorOverhead¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Underground | Broken | Vegetation¦Treefellintoline¦ConductorUnderground¦Broken | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Conductor, Underground | Broken, wire on ground | Vegetation¦Treefellintoline¦ConductorUnderground¦Brokenwireonground | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | Conductor, Underground | Normal | Vegetation¦Treefellintoline¦ConductorUnderground¦Normal | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on object | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Connector or Splice (OH) | Burned Open | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦BurnedOpen | #N/A |  |  | None | Very High
Vegetation | Tree - fell into line | Connector or Splice (OH) | Normal | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Steel | Broken | Vegetation¦Treefellintoline¦CrossarmSteel¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Steel | Broken, wire on ground | Vegetation¦Treefellintoline¦CrossarmSteel¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Wood | Broken | Vegetation¦Treefellintoline¦CrossarmWood¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on object | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Wood | Burned/flashed | Vegetation¦Treefellintoline¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Customer Equipment | Broken | Vegetation¦Treefellintoline¦CustomerEquipment¦Broken | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Customer Equipment | On Ground | Vegetation¦Treefellintoline¦CustomerEquipment¦OnGround | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Cutout, fuse holder | Broken | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken | #N/A |  |  | None | High
Vegetation | Tree - fell into line | Cutout, fuse holder | Broken, wire on ground | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Cutout, fuse holder | Burned/flashed | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Cutout, fuse holder | Burned Open | Vegetation¦Treefellintoline¦Cutoutfuseholder¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Cutout, fuse holder | Failed/Faulted | Vegetation¦Treefellintoline¦Cutoutfuseholder¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Cutout, fuse holder | Normal | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Fuse | Arcing | Vegetation¦Treefellintoline¦Fuse¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Fuse | Broken | Vegetation¦Treefellintoline¦Fuse¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Fuse | Burned Open | Vegetation¦Treefellintoline¦Fuse¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Fuse | Failed/Faulted | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Fuse | Normal | Vegetation¦Treefellintoline¦Fuse¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Insulator | Broken | Vegetation¦Treefellintoline¦Insulator¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - fell into line | Insulator | Broken, wire on ground | Vegetation¦Treefellintoline¦Insulator¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Insulator | Broken, wire on object | Vegetation¦Treefellintoline¦Insulator¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Insulator | Normal | Vegetation¦Treefellintoline¦Insulator¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Jumper | Broken | Vegetation¦Treefellintoline¦Jumper¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Jumper | Burned/flashed | Vegetation¦Treefellintoline¦Jumper¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Jumper | Burned Open | Vegetation¦Treefellintoline¦Jumper¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Jumper | Normal | Vegetation¦Treefellintoline¦Jumper¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Lightning Arrestor | Broken, wire on ground | Vegetation¦Treefellintoline¦LightningArrestor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Treefellintoline | LightningArrestor | Burnedflashed | Vegetation¦Treefellintoline¦LightningArrestor¦Burnedflashed |  |  |  | None | Medium
Vegetation | Tree - fell into line | Lightning Arrestor | Failed/Faulted | Vegetation¦Treefellintoline¦LightningArrestor¦FailedFaulted | #N/A |  |  | None | Medium
Vegetation | Treefellintoline | MeteringEquipment | FailedFaulted | Vegetation¦Treefellintoline¦MeteringEquipment¦FailedFaulted |  |  |  | N/A | N/A
Vegetation | Tree - fell into line | Other | Arcing | Vegetation¦Treefellintoline¦Other¦Arcing | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | Other | Broken | Vegetation¦Treefellintoline¦Other¦Broken | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | Other | Broken, wire on ground | Vegetation¦Treefellintoline¦Other¦Brokenwireonground | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | Other | Normal | Vegetation¦Treefellintoline¦Other¦Normal | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | Other | Together | Vegetation¦Treefellintoline¦Other¦Together | #N/A |  |  | N/A | N/A
Vegetation | Tree - fell into line | Pole - Tower, steel | Burned/flashed | Vegetation¦Treefellintoline¦PoleTowersteel¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole - Tower, steel | Normal | Vegetation¦Treefellintoline¦PoleTowersteel¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | Broken | Vegetation¦Treefellintoline¦PoleWood¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on object | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | Burned/flashed | Vegetation¦Treefellintoline¦PoleWood¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | Deteriorated | Vegetation¦Treefellintoline¦PoleWood¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | Normal | Vegetation¦Treefellintoline¦PoleWood¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | On Ground | Vegetation¦Treefellintoline¦PoleWood¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Pole-Wood | Together | Vegetation¦Treefellintoline¦PoleWood¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Recloser | Arcing | Vegetation¦Treefellintoline¦Recloser¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Recloser | Burned/flashed | Vegetation¦Treefellintoline¦Recloser¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Recloser | Normal | Vegetation¦Treefellintoline¦Recloser¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Arcing | Vegetation¦Treefellintoline¦Secondary¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Bent or Twisted | Vegetation¦Treefellintoline¦Secondary¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Broken | Vegetation¦Treefellintoline¦Secondary¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Broken, wire on object | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Burned/flashed | Vegetation¦Treefellintoline¦Secondary¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Normal | Vegetation¦Treefellintoline¦Secondary¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | On Ground | Vegetation¦Treefellintoline¦Secondary¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Together | Vegetation¦Treefellintoline¦Secondary¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Sectionalizer | Normal | Vegetation¦Treefellintoline¦Sectionalizer¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Bent or Twisted | Vegetation¦Treefellintoline¦Serviceconductor¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Broken | Vegetation¦Treefellintoline¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Broken, wire on object | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Burned Open | Vegetation¦Treefellintoline¦Serviceconductor¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Deteriorated | Vegetation¦Treefellintoline¦Serviceconductor¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Normal | Vegetation¦Treefellintoline¦Serviceconductor¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | On Ground | Vegetation¦Treefellintoline¦Serviceconductor¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Together | Vegetation¦Treefellintoline¦Serviceconductor¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Switch (OH) | Broken | Vegetation¦Treefellintoline¦Switch(OH)¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Switch (OH) | Normal | Vegetation¦Treefellintoline¦Switch(OH)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Switch (UG) | Broken | Vegetation¦Treefellintoline¦Switch(UG)¦Broken | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer (OH) | (blank) | Vegetation¦Treefellintoline¦Transformer(OH)¦ | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer (OH) | Broken | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer (OH) | Broken, wire on ground | Vegetation¦Treefellintoline¦Transformer(OH)¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer (OH) | Burned/flashed | Vegetation¦Treefellintoline¦Transformer(OH)¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer (OH) | Deteriorated | Vegetation¦Treefellintoline¦Transformer(OH)¦Deteriorated | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer (OH) | Failed/Faulted | Vegetation¦Treefellintoline¦Transformer(OH)¦FailedFaulted | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer (OH) | Leaking | Vegetation¦Treefellintoline¦Transformer(OH)¦Leaking | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer (OH) | Normal | Vegetation¦Treefellintoline¦Transformer(OH)¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer (OH) | On Ground | Vegetation¦Treefellintoline¦Transformer(OH)¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer (UG) | Broken, wire on ground | Vegetation¦Treefellintoline¦Transformer(UG)¦Brokenwireonground | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer (UG) | Contaminated | Vegetation¦Treefellintoline¦Transformer(UG)¦Contaminated | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer (UG) | Failed/Faulted | Vegetation¦Treefellintoline¦Transformer(UG)¦FailedFaulted | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer (UG) | Normal | Vegetation¦Treefellintoline¦Transformer(UG)¦Normal | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer | (blank) | Vegetation¦Treefellintoline¦Transformer¦ | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer | Arcing | Vegetation¦Treefellintoline¦Transformer¦Arcing | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Bent or Twisted | Vegetation¦Treefellintoline¦Transformer¦BentorTwisted | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Broken | Vegetation¦Treefellintoline¦Transformer¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Broken, wire on object | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Burned/flashed | Vegetation¦Treefellintoline¦Transformer¦Burnedflashed | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Contaminated | Vegetation¦Treefellintoline¦Transformer¦Contaminated | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer | Deteriorated | Vegetation¦Treefellintoline¦Transformer¦Deteriorated | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Failed/Faulted | Vegetation¦Treefellintoline¦Transformer¦FailedFaulted | #N/A |  |  | None | None
Vegetation | Tree - fell into line | Transformer | Leaking | Vegetation¦Treefellintoline¦Transformer¦Leaking | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Malfunctioning | Vegetation¦Treefellintoline¦Transformer¦Malfunctioning | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Normal | Vegetation¦Treefellintoline¦Transformer¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | On Ground | Vegetation¦Treefellintoline¦Transformer¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Together | Vegetation¦Treefellintoline¦Transformer¦Together | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Woodpin | Broken | Vegetation¦Treefellintoline¦Woodpin¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - fell into line | Woodpin | Normal | Vegetation¦Treefellintoline¦Woodpin¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Anchor or Guy | Bent or Twisted | Vegetation¦Treegrewintoline¦AnchororGuy¦BentorTwisted | #N/A |  |  | None | Medium High
Vegetation | Tree - grew into line | Anchor or Guy | Broken | Vegetation¦Treegrewintoline¦AnchororGuy¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Anchor or Guy | Deteriorated | Vegetation¦Treegrewintoline¦AnchororGuy¦Deteriorated | #N/A |  |  | None | Medium High
Vegetation | Tree - grew into line | Circuit Breaker | Normal | Vegetation¦Treegrewintoline¦CircuitBreaker¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Arcing | Vegetation¦Treegrewintoline¦ConductorOverhead¦Arcing | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Bent or Twisted | Vegetation¦Treegrewintoline¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Broken | Vegetation¦Treegrewintoline¦ConductorOverhead¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treegrewintoline¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Conductor, Overhead | Broken, wire on object | Vegetation¦Treegrewintoline¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Conductor, Overhead | Burned/flashed | Vegetation¦Treegrewintoline¦ConductorOverhead¦Burnedflashed | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Contaminated | Vegetation¦Treegrewintoline¦ConductorOverhead¦Contaminated | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Deteriorated | Vegetation¦Treegrewintoline¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Normal | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Together | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Crossarm, Wood | Broken | Vegetation¦Treegrewintoline¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Crossarm, Wood | Burned/flashed | Vegetation¦Treegrewintoline¦CrossarmWood¦Burnedflashed | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Fuse | Burned Open | Vegetation¦Treegrewintoline¦Fuse¦BurnedOpen | #N/A |  |  | None | Medium High
Vegetation | Tree - grew into line | Fuse | Failed/Faulted | Vegetation¦Treegrewintoline¦Fuse¦FailedFaulted | #N/A |  |  | None | Medium High
Vegetation | Tree - grew into line | Fuse | Normal | Vegetation¦Treegrewintoline¦Fuse¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - grew into line | Other | Normal | Vegetation¦Treegrewintoline¦Other¦Normal | #N/A |  |  | N/A | N/A
Vegetation | Tree - grew into line | Pole-Wood | Broken | Vegetation¦Treegrewintoline¦PoleWood¦Broken | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Pole-Wood | Broken, wire on ground | Vegetation¦Treegrewintoline¦PoleWood¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Pole-Wood | Normal | Vegetation¦Treegrewintoline¦PoleWood¦Normal | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Secondary | Arcing | Vegetation¦Treegrewintoline¦Secondary¦Arcing | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Secondary | Bent or Twisted | Vegetation¦Treegrewintoline¦Secondary¦BentorTwisted | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Secondary | Broken | Vegetation¦Treegrewintoline¦Secondary¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Secondary | Broken, wire on ground | Vegetation¦Treegrewintoline¦Secondary¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Secondary | Burned/flashed | Vegetation¦Treegrewintoline¦Secondary¦Burnedflashed | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Secondary | Normal | Vegetation¦Treegrewintoline¦Secondary¦Normal | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Secondary | On Ground | Vegetation¦Treegrewintoline¦Secondary¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Secondary | Together | Vegetation¦Treegrewintoline¦Secondary¦Together | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Service conductor | Broken | Vegetation¦Treegrewintoline¦Serviceconductor¦Broken | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Service conductor | Broken, wire on ground | Vegetation¦Treegrewintoline¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Service conductor | Burned/flashed | Vegetation¦Treegrewintoline¦Serviceconductor¦Burnedflashed | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Service conductor | Burned Open | Vegetation¦Treegrewintoline¦Serviceconductor¦BurnedOpen | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Service conductor | Normal | Vegetation¦Treegrewintoline¦Serviceconductor¦Normal | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Transformer (OH) | Broken | Vegetation¦Treegrewintoline¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Vegetation | Treegrewintoline | Transformer(OH) | Contaminated | Vegetation¦Treegrewintoline¦Transformer(OH)¦Contaminated |  |  |  | None | High
Vegetation | Tree - grew into line | Transformer (OH) | Normal | Vegetation¦Treegrewintoline¦Transformer(OH)¦Normal | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Transformer | Annealed | Vegetation¦Treegrewintoline¦Transformer¦Annealed | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Transformer | Arcing | Vegetation¦Treegrewintoline¦Transformer¦Arcing | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Transformer | Bent or Twisted | Vegetation¦Treegrewintoline¦Transformer¦BentorTwisted | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Transformer | Broken | Vegetation¦Treegrewintoline¦Transformer¦Broken | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Transformer | Broken, wire on ground | Vegetation¦Treegrewintoline¦Transformer¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Transformer | Broken, wire on object | Vegetation¦Treegrewintoline¦Transformer¦Brokenwireonobject | #N/A |  |  | None | Medium
Vegetation | Treegrewintoline | Transformer | Burnedflashed | Vegetation¦Treegrewintoline¦Transformer¦Burnedflashed |  |  |  | None | High
Vegetation | Tree - grew into line | Transformer | Failed/Faulted | Vegetation¦Treegrewintoline¦Transformer¦FailedFaulted | #N/A |  |  | None | Medium High
Vegetation | Tree - grew into line | Transformer | Normal | Vegetation¦Treegrewintoline¦Transformer¦Normal | #N/A |  |  | None | High
Vegetation | Tree - grew into line | Transformer | On Ground | Vegetation¦Treegrewintoline¦Transformer¦OnGround | #N/A |  |  | None | Medium
Vegetation | Tree - grew into line | Transformer | Together | Vegetation¦Treegrewintoline¦Transformer¦Together | #N/A |  |  | None | High
Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Bent or Twisted | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦BentorTwisted | #N/A |  |  | None | Very High
Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Normal | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Together | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Together | #N/A |  |  | None | Very High
Vegetation | Tree - palm frond fell into line | Crossarm, Wood | Broken | Vegetation¦Treepalmfrondfellintoline¦CrossarmWood¦Broken | #N/A |  |  | None | Very High
Vegetation | Tree - palm frond fell into line | Fuse | Failed/Faulted | Vegetation¦Treepalmfrondfellintoline¦Fuse¦FailedFaulted | #N/A |  |  | None | Very High
Vegetation | Tree - palm frond fell into line | Fuse | Normal | Vegetation¦Treepalmfrondfellintoline¦Fuse¦Normal | #N/A |  |  | None | Very High
Vegetation | Tree - palm frond fell into line | Jumper | Burned Open | Vegetation¦Treepalmfrondfellintoline¦Jumper¦BurnedOpen | #N/A |  |  | None | High
Vegetation | Tree - palm frond fell into line | Other | Failed/Faulted | Vegetation¦Treepalmfrondfellintoline¦Other¦FailedFaulted | #N/A |  |  | N/A | N/A
Vegetation | Tree - palm frond fell into line | Recloser | Normal | Vegetation¦Treepalmfrondfellintoline¦Recloser¦Normal | #N/A |  |  | None | Medium
Vegetation | Tree - palm frond fell into line | Service conductor | Broken, wire on ground | Vegetation¦Treepalmfrondfellintoline¦Serviceconductor¦Brokenwireonground | #N/A |  |  | None | Medium
Vegetation | Tree - palm frond fell into line | Transformer (OH) | Broken | Vegetation¦Treepalmfrondfellintoline¦Transformer(OH)¦Broken | #N/A |  |  | None | High
Vegetation | Tree - palm frond fell into line | Transformer | Burned/flashed | Vegetation¦Treepalmfrondfellintoline¦Transformer¦Burnedflashed | #N/A |  |  | None | High
Vegetation | Tree - palm frond fell into line | Transformer | Normal | Vegetation¦Treepalmfrondfellintoline¦Transformer¦Normal | #N/A |  |  | None | High
Wildfire Mitigation | CWSP - Vegetation Removal | (blank) | (blank) | WildfireMitigation¦CWSPVegetationRemoval¦¦ | #N/A |  |  | N/A | N/A
Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Annealed | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Annealed | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Fuse | Normal | WildfireMitigation¦CWSPVegetationRemoval¦Fuse¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Other | Normal | WildfireMitigation¦CWSPVegetationRemoval¦Other¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Pole-Wood | Broken | WildfireMitigation¦CWSPVegetationRemoval¦PoleWood¦Broken | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Pole-Wood | Deteriorated | WildfireMitigation¦CWSPVegetationRemoval¦PoleWood¦Deteriorated | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Secondary | Annealed | WildfireMitigation¦CWSPVegetationRemoval¦Secondary¦Annealed | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Secondary | Normal | WildfireMitigation¦CWSPVegetationRemoval¦Secondary¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Transformer (OH) | Normal | WildfireMitigation¦CWSPVegetationRemoval¦Transformer(OH)¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | CWSP - Vegetation Removal | Transformer | Burned/flashed | WildfireMitigation¦CWSPVegetationRemoval¦Transformer¦Burnedflashed | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | (blank) | (blank) | WildfireMitigation¦PublicSafetyPowerShutoff¦¦ | #N/A |  |  | N/A | N/A
Wildfire Mitigation | Public Safety Power Shut-off | (blank) | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦¦Normal | #N/A |  |  | N/A | N/A
Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | (blank) | WildfireMitigation¦PublicSafetyPowerShutoff¦CircuitBreaker¦ | #N/A |  |  | N/A | N/A
Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦CircuitBreaker¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Arcing | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Arcing | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Broken | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Broken, wire on ground | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Brokenwireonground | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Broken, wire on object | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Brokenwireonobject | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Deteriorated | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Deteriorated | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Together | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Together | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Connector or Splice (OH) | Broken, wire on ground | WildfireMitigation¦PublicSafetyPowerShutoff¦ConnectororSplice(OH)¦Brokenwireonground | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Broken | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Broken, wire on ground | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Brokenwireonground | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Deteriorated | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Deteriorated | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Customer Equipment | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦CustomerEquipment¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Cutout, fuse holder | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦Cutoutfuseholder¦Broken | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Fuse¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Generator | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Generator¦Normal | #N/A |  |  | None | None
WildfireMitigation | PublicSafetyPowerShutoff | Insulator | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦Insulator¦Broken |  |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Other | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦Other¦Broken | #N/A |  |  | N/A | N/A
Wildfire Mitigation | Public Safety Power Shut-off | Other | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Other¦Normal | #N/A |  |  | N/A | N/A
Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦PoleWood¦Broken | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken, wire on ground | WildfireMitigation¦PublicSafetyPowerShutoff¦PoleWood¦Brokenwireonground | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Recloser¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Broken, wire on ground | WildfireMitigation¦PublicSafetyPowerShutoff¦Secondary¦Brokenwireonground | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Together | WildfireMitigation¦PublicSafetyPowerShutoff¦Secondary¦Together | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(OH)¦Broken | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(OH)¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Switch | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Transformer (OH) | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer(OH)¦Normal | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Burned/flashed | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer(UG)¦Burnedflashed | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Broken, wire on ground | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer¦Brokenwireonground | #N/A |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Woodpin | Broken | WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken | PublicSafetyPowerShutoff¦Woodpin¦Broken¦WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken | Woodpin¦Broken¦WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken¦PublicSafetyPowerShutoff¦Woodpin¦Broken¦WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken | Broken¦WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken¦PublicSafetyPowerShutoff¦Woodpin¦Broken¦WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken¦Woodpin¦Broken¦WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken¦PublicSafetyPowerShutoff¦Woodpin¦Broken¦WildfireMitigation¦PublicSafetyPowerShutoff¦Woodpin¦Broken | None | None
3rd Party | Customer Equipment | Crossarm, Wood | Broken | 3rdParty¦CustomerEquipment¦CrossarmWood¦Broken | CustomerEquipment¦CrossarmWood¦Broken¦3rdParty¦CustomerEquipment¦CrossarmWood¦Broken | CrossarmWood¦Broken¦3rdParty¦CustomerEquipment¦CrossarmWood¦Broken¦CustomerEquipment¦CrossarmWood¦Broken¦3rdParty¦CustomerEquipment¦CrossarmWood¦Broken | Broken¦3rdParty¦CustomerEquipment¦CrossarmWood¦Broken¦CustomerEquipment¦CrossarmWood¦Broken¦3rdParty¦CustomerEquipment¦CrossarmWood¦Broken¦CrossarmWood¦Broken¦3rdParty¦CustomerEquipment¦CrossarmWood¦Broken¦CustomerEquipment¦CrossarmWood¦Broken¦3rdParty¦CustomerEquipment¦CrossarmWood¦Broken | None | None
3rd Party | Customer Equipment | Transformer | Broken, wire on ground | 3rdParty¦CustomerEquipment¦Transformer¦Brokenwireonground |  |  |  | None | None
3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken |  |  |  | None | None
3rd Party | Dig in, 3rd party | Conductor, Underground | Normal | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Normal |  |  |  | None | None
3rd Party | Dig in, 3rd party | Secondary | Broken | 3rdParty¦Digin3rdparty¦Secondary¦Broken |  |  |  | None | None
3rd Party | Dig in, 3rd party | Service conductor | Bent or Twisted | 3rdParty¦Digin3rdparty¦Serviceconductor¦BentorTwisted |  |  |  | None | High
3rd Party | Dig in, 3rd party | Service conductor | Broken | 3rdParty¦Digin3rdparty¦Serviceconductor¦Broken |  |  |  | None | Medium
3rd Party | Fire, house or bldg. | Conductor, Overhead | Normal | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Customer Equipment | Burned/flashed | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Burnedflashed |  |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | Burned/flashed | 3rdParty¦Firehouseorbldg¦Secondary¦Burnedflashed |  |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Secondary | Burned Open | 3rdParty¦Firehouseorbldg¦Secondary¦BurnedOpen |  |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Service conductor | Broken, wire on ground | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Brokenwireonground |  |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Service conductor | Burned/flashed | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Burnedflashed |  |  |  | N/A | N/A
3rd Party | Fire, house or bldg. | Transformer (OH) | Burned/flashed | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Burnedflashed |  |  |  | N/A | N/A
3rd Party | Gun Shot | Conductor, Overhead | Broken | 3rdParty¦GunShot¦ConductorOverhead¦Broken |  |  |  | None | Very High
3rd Party | Gun Shot | Conductor, Overhead | Broken, wire on ground | 3rdParty¦GunShot¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Gun Shot | Conductor, Overhead | Deteriorated | 3rdParty¦GunShot¦ConductorOverhead¦Deteriorated |  |  |  | None | Very High
3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal |  |  |  | None | Very High
3rd Party | Other | Conductor, Overhead | Normal | 3rdParty¦Other¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
3rd Party | Other | Conductor, Overhead | Together | 3rdParty¦Other¦ConductorOverhead¦Together |  |  |  | N/A | N/A
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal |  |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Broken |  |  |  | None | Very High
3rd Party | Tree - cutting, 3rd party | Service conductor | Broken, wire on ground | 3rdParty¦Treecutting3rdparty¦Serviceconductor¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Failed/Faulted | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦FailedFaulted |  |  |  | None | Medium
3rd Party | Tree - cutting, 3rd party | Transformer | Broken | 3rdParty¦Treecutting3rdparty¦Transformer¦Broken |  |  |  | None | High
3rd Party | Vandalism | Conductor, Overhead | Normal | 3rdParty¦Vandalism¦ConductorOverhead¦Normal |  |  |  | None | Very High
3rd Party | Vehicle | Anchor or Guy | Broken, wire on ground | 3rdParty¦Vehicle¦AnchororGuy¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Vehicle | Conductor, Overhead | Burned/flashed | 3rdParty¦Vehicle¦ConductorOverhead¦Burnedflashed |  |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | Normal | 3rdParty¦Vehicle¦ConductorOverhead¦Normal |  |  |  | None | Very High
3rd Party | Vehicle | Conductor, Overhead | Together | 3rdParty¦Vehicle¦ConductorOverhead¦Together |  |  |  | None | Very High
3rd Party | Vehicle | Crossarm, Wood | Broken | 3rdParty¦Vehicle¦CrossarmWood¦Broken |  |  |  | None | Very High
3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Vehicle | Service conductor | Broken, wire on ground | 3rdParty¦Vehicle¦Serviceconductor¦Brokenwireonground |  |  |  | None | Medium
3rd Party | Vehicle | Transformer | Broken, wire on ground | 3rdParty¦Vehicle¦Transformer¦Brokenwireonground |  |  |  | None | Medium
Animal | Bird found | Conductor, Overhead | Bent or Twisted | Animal¦Birdfound¦ConductorOverhead¦BentorTwisted |  |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Broken, wire on ground | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
Animal | Bird found | Conductor, Overhead | Normal | Animal¦Birdfound¦ConductorOverhead¦Normal |  |  |  | None | Very High
Animal | Bird found | Conductor, Overhead | Together | Animal¦Birdfound¦ConductorOverhead¦Together |  |  |  | None | Very High
Animal | Bird found | Cutout, fuse holder | Failed/Faulted | Animal¦Birdfound¦Cutoutfuseholder¦FailedFaulted |  |  |  | None | High
Animal | Bird found | Cutout, fuse holder | Normal | Animal¦Birdfound¦Cutoutfuseholder¦Normal |  |  |  | None | High
Animal | Other | Conductor, Overhead | Burned/flashed | Animal¦Other¦ConductorOverhead¦Burnedflashed |  |  |  | None | Very High
Animal | Other | Conductor, Overhead | Normal | Animal¦Other¦ConductorOverhead¦Normal |  |  |  | None | Very High
Animal | Other | Conductor, Overhead | Together | Animal¦Other¦ConductorOverhead¦Together |  |  |  | None | Very High
Animal | Other | Cutout, fuse holder | Failed/Faulted | Animal¦Other¦Cutoutfuseholder¦FailedFaulted |  |  |  | None | High
Animal | Other | Cutout, fuse holder | Normal | Animal¦Other¦Cutoutfuseholder¦Normal |  |  |  | None | High
Animal | Squirrel | Conductor, Overhead | Normal | Animal¦Squirrel¦ConductorOverhead¦Normal |  |  |  | None | Very High
Animal | Squirrel | Conductor, Overhead | Together | Animal¦Squirrel¦ConductorOverhead¦Together |  |  |  | None | Very High
Animal | Squirrel | Conductor, Underground | Normal | Animal¦Squirrel¦ConductorUnderground¦Normal |  |  |  | None | None
Animal | Squirrel | Crossarm, Wood | Burned/flashed | Animal¦Squirrel¦CrossarmWood¦Burnedflashed |  |  |  | None | High
Animal | Squirrel | Cutout, fuse holder | Broken | Animal¦Squirrel¦Cutoutfuseholder¦Broken |  |  |  | None | High
Animal | Squirrel | Cutout, fuse holder | Failed/Faulted | Animal¦Squirrel¦Cutoutfuseholder¦FailedFaulted |  |  |  | None | High
Animal | Squirrel | Cutout, fuse holder | Normal | Animal¦Squirrel¦Cutoutfuseholder¦Normal |  |  |  | None | High
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | On Ground | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦OnGround |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Together | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Together |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Cutout, fuse holder | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Cutoutfuseholder¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Other | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Pole-Wood | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Secondary | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Secondary¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) |  | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦ |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) | Failed/Faulted | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (OH) | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer (UG) | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(UG)¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer | Leaking | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Leaking |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip, company | Transformer | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Normal |  |  |  | N/A | N/A
Company Initiated | Contact with High Voltage, company | Conductor, Overhead | Normal | CompanyInitiated¦ContactwithHighVoltagecompany¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Conductor, Overhead | Normal | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Normal | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Overhead | Together | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Together |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor, Underground | Normal | CompanyInitiated¦ImproperConstruction¦ConductorUnderground¦Normal |  |  |  | N/A | N/A
Company Initiated | Operating error | Conductor, Overhead | Normal | CompanyInitiated¦Operatingerror¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Other Circuits | Conductor, Overhead | Normal | CompanyInitiated¦OtherCircuits¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company |  |  | CompanyInitiated¦Personnelcompany¦¦ |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Circuit Breaker | Normal | CompanyInitiated¦Personnelcompany¦CircuitBreaker¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Conductor, Overhead | Normal | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Conductor, Underground | Normal | CompanyInitiated¦Personnelcompany¦ConductorUnderground¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Fuse | Normal | CompanyInitiated¦Personnelcompany¦Fuse¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Jumper | Normal | CompanyInitiated¦Personnelcompany¦Jumper¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Other | Normal | CompanyInitiated¦Personnelcompany¦Other¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Recloser | Normal | CompanyInitiated¦Personnelcompany¦Recloser¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Switch (OH) | Normal | CompanyInitiated¦Personnelcompany¦Switch(OH)¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Transformer (OH) | Normal | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Normal |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Overhead | Broken, wire on ground | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Brokenwireonground |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Overhead | Normal | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Conductor, Underground | Normal | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Normal |  |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed |  |  |  | N/A | N/A
Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal |  |  |  | N/A | N/A
Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground |  |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal |  |  |  | None | None
Environmental/External | Flood/Erosion | Pole-Wood | Broken, wire on ground | EnvironmentalExternal¦FloodErosion¦PoleWood¦Brokenwireonground |  |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground |  |  |  | None | None
Environmental/External | Ice or snow | Conductor, Overhead | Normal | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal |  |  |  | None | None
Environmental/External | Ice or snow | Crossarm, Wood | Broken | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Broken |  |  |  | None | None
Environmental/External | Ice or snow | Crossarm, Wood | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Brokenwireonground |  |  |  | None | None
Environmental/External | Ice or snow | Cutout, fuse holder | Broken | EnvironmentalExternal¦Iceorsnow¦Cutoutfuseholder¦Broken |  |  |  | None | None
Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground |  |  |  | None | None
Environmental/External | Lightning | Conductor, Overhead | Broken, wire on ground | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Brokenwireonground |  |  |  | None | None
Environmental/External | Lightning | Conductor, Overhead | Normal | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal |  |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Broken | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦Broken |  |  |  | None | High
Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Failed/Faulted | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦FailedFaulted |  |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Burned/flashed | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Burnedflashed |  |  |  | None | High
Equipment Failure/Involved | Fire, pole | Insulator | Broken | EquipmentFailureInvolved¦Firepole¦Insulator¦Broken |  |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Insulator | Burned/flashed | EquipmentFailureInvolved¦Firepole¦Insulator¦Burnedflashed |  |  |  | None | Medium High
Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken |  |  |  | None | Very High
Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed |  |  |  | None | Medium High
Equipment Failure/Involved | Fire, pole | Pole-Wood | Deteriorated | EquipmentFailureInvolved¦Firepole¦PoleWood¦Deteriorated |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Steel | Broken | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Broken |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on object | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonobject |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Crossarm, Wood | Normal | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Normal |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken |  |  |  | None | High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed |  |  |  | None | High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted |  |  |  | None | Very High
Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal |  |  |  | None | High
Equipment Failure/Involved | Overhead | PGs, Kearneys | Deteriorated | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Deteriorated |  |  |  | None | High
Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Transformer (OH) | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Overhead | Transformer | Broken, wire on ground | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground |  |  |  | None | Medium
Equipment Failure/Involved | Underground | Conductor, Underground | Broken | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken |  |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed |  |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated |  |  |  | None | None
Equipment Failure/Involved | Underground | Conductor, Underground | Normal | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Normal |  |  |  | None | None
Vegetation | Other ground vegetation | Conductor, Overhead | Normal | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal |  |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal |  |  |  | None | Very High
Vegetation | Tree - bark fell into line | Conductor, Overhead | Together | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Together |  |  |  | None | Very High
Vegetation | Tree - bark fell into line | Transformer | Broken, wire on ground | Vegetation¦Treebarkfellintoline¦Transformer¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Bent or Twisted | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Burned/flashed | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Burnedflashed |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Contaminated | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Contaminated |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Deteriorated | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Deteriorated |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on ground | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Cutout, fuse holder | Failed/Faulted | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦FailedFaulted |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Cutout, fuse holder | Normal | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Normal |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Insulator | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Insulator¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer (OH) | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Broken |  |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal |  |  |  | None | Medium
Vegetation | Tree - fell into line | Anchor or Guy | Broken, wire on ground | Vegetation¦Treefellintoline¦AnchororGuy¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Annealed | Vegetation¦Treefellintoline¦ConductorOverhead¦Annealed |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Broken | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Contaminated | Vegetation¦Treefellintoline¦ConductorOverhead¦Contaminated |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Deteriorated | Vegetation¦Treefellintoline¦ConductorOverhead¦Deteriorated |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Normal | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround |  |  |  | None | Medium
Vegetation | Tree - fell into line | Conductor, Overhead | Together | Vegetation¦Treefellintoline¦ConductorOverhead¦Together |  |  |  | None | Medium
Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Wood | Broken | Vegetation¦Treefellintoline¦CrossarmWood¦Broken |  |  |  | None | Medium
Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Cutout, fuse holder | Broken | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken |  |  |  | None | High
Vegetation | Tree - fell into line | Cutout, fuse holder | Normal | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Normal |  |  |  | None | Medium
Vegetation | Tree - fell into line | Other | Broken, wire on ground | Vegetation¦Treefellintoline¦Other¦Brokenwireonground |  |  |  | N/A | N/A
Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Service conductor | Broken, wire on object | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonobject |  |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer (OH) | Broken, wire on ground | Vegetation¦Treefellintoline¦Transformer(OH)¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground |  |  |  | None | Medium
Vegetation | Tree - grew into line | Conductor, Overhead | Arcing | Vegetation¦Treegrewintoline¦ConductorOverhead¦Arcing |  |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Bent or Twisted | Vegetation¦Treegrewintoline¦ConductorOverhead¦BentorTwisted |  |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Contaminated | Vegetation¦Treegrewintoline¦ConductorOverhead¦Contaminated |  |  |  | None | Very High
Vegetation | Tree - grew into line | Conductor, Overhead | Normal | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal |  |  |  | None | Very High
Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Normal | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Normal |  |  |  | None | Very High
Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal |  |  |  | None | None
Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal |  |  |  | None | None
3rd Party | Vehicle | Other | Together | 3rdParty¦Vehicle¦Other¦Together |  |  |  | None | N/A
Company Initiated | Operating error | Regulator, LTC substation | Normal | CompanyInitiated¦Operatingerror¦RegulatorLTCsubstation¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel, company | Regulator | Failed/Faulted | CompanyInitiated¦Personnelcompany¦Regulator¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Cutout, fuse holder | Normal | CompanyInitiated¦ReturnCircuitNormal¦Cutoutfuseholder¦Normal |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Insulator | Broken | CompanyInitiated¦ReturnCircuitNormal¦Insulator¦Broken |  |  |  | N/A | N/A
3rdParty | CustomerEquipment | AnchororGuy | Brokenwireonground | 3rdParty¦CustomerEquipment¦AnchororGuy¦Brokenwireonground |  |  |  | None | None
3rdParty | CustomerEquipment | CircuitBreaker | Broken | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Broken |  |  |  | None | None
3rdParty | CustomerEquipment | ConductorUnderground | Contaminated | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Contaminated |  |  |  | None | None
3rdParty | CustomerEquipment | CT | FailedFaulted | 3rdParty¦CustomerEquipment¦CT¦FailedFaulted |  |  |  | None | None
3rdParty | Firehouseorbldg | Capacitor | Burnedflashed | 3rdParty¦Firehouseorbldg¦Capacitor¦Burnedflashed |  |  |  | N/A | N/A
3rdParty | Firehouseorbldg | CustomerEquipment | Contaminated | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Contaminated |  |  |  | N/A | N/A
3rdParty | Firehouseorbldg | Insulator | FailedFaulted | 3rdParty¦Firehouseorbldg¦Insulator¦FailedFaulted |  |  |  | N/A | N/A
3rdParty | Firehouseorbldg | MeteringEquipment | Normal | 3rdParty¦Firehouseorbldg¦MeteringEquipment¦Normal |  |  |  | N/A | N/A
3rdParty | Firehouseorbldg | Serviceconductor | Normal | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Normal |  |  |  | N/A | N/A
3rdParty | GunShot | Fuse | BurnedOpen | 3rdParty¦GunShot¦Fuse¦BurnedOpen |  |  |  | None | None
3rdParty | Kite | ConductorOverhead | Contaminated | 3rdParty¦Kite¦ConductorOverhead¦Contaminated |  |  |  | None | Very High
3rdParty | MetallicBalloon | ConductorOverhead | Contaminated | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Contaminated |  |  |  | None | Very High
3rdParty | Other | ConductorOverhead | Deteriorated | 3rdParty¦Other¦ConductorOverhead¦Deteriorated |  |  |  | None | Very High
3rdParty | Other | Other | Brokenwireonground | 3rdParty¦Other¦Other¦Brokenwireonground |  |  |  | N/A | N/A
3rdParty | ThrownObject | Fuse | Normal | 3rdParty¦ThrownObject¦Fuse¦Normal |  |  |  | None | Very High
3rdParty | Treecutting3rdparty | PoleWood | Normal | 3rdParty¦Treecutting3rdparty¦PoleWood¦Normal |  |  |  | None | High
3rdParty | Treecutting3rdparty | Transformer(OH) | Brokenwireonground | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Brokenwireonground |  |  |  | None | Medium
3rdParty | Treecutting3rdparty | Transformer(UG) | Normal | 3rdParty¦Treecutting3rdparty¦Transformer(UG)¦Normal |  |  |  | None | None
3rdParty | Vandalism | Transformer(OH) | Burnedflashed | 3rdParty¦Vandalism¦Transformer(OH)¦Burnedflashed |  |  |  | None | Medium High
3rdParty | Vehicle | ConductorUnderground | Normal | 3rdParty¦Vehicle¦ConductorUnderground¦Normal |  |  |  | None | None
3rdParty | Vehicle | CrossarmWood | Burnedflashed | 3rdParty¦Vehicle¦CrossarmWood¦Burnedflashed |  |  |  | None | Very High
Animal | Birdfound | CrossarmWood | Burnedflashed | Animal¦Birdfound¦CrossarmWood¦Burnedflashed |  |  |  | None | Very High
Animal | Birdfound | Insulator | Normal | Animal¦Birdfound¦Insulator¦Normal |  |  |  | None | Very High
Animal | Birdfound | Switch | Burnedflashed | Animal¦Birdfound¦Switch¦Burnedflashed |  |  |  | None | Very High
Animal | Other | Capacitor | Broken | Animal¦Other¦Capacitor¦Broken |  |  |  | None | Medium
Animal | Other | Capacitor | Burnedflashed | Animal¦Other¦Capacitor¦Burnedflashed |  |  |  | None | Very High
Animal | Other | ConductorOverhead | Arcing | Animal¦Other¦ConductorOverhead¦Arcing |  |  |  | None | Very High
Animal | Other | Sectionalizer | FailedFaulted | Animal¦Other¦Sectionalizer¦FailedFaulted |  |  |  | None | Medium
Animal | Other | Transformer(OH) | Contaminated | Animal¦Other¦Transformer(OH)¦Contaminated |  |  |  | None | High
Animal | Squirrel | Transformer(OH) |  | Animal¦Squirrel¦Transformer(OH)¦ |  |  |  | None | Very High
Animal | Squirrel | TransformerSTASVC | Normal | Animal¦Squirrel¦TransformerSTASVC¦Normal |  |  |  | N/A | N/A
EnvironmentalExternal | Earthquake | Fuse | FailedFaulted | EnvironmentalExternal¦Earthquake¦Fuse¦FailedFaulted |  |  |  | None | None
EnvironmentalExternal | FireForestGrass | Transformer | Brokenwireonground | EnvironmentalExternal¦FireForestGrass¦Transformer¦Brokenwireonground |  |  |  | N/A | N/A
EnvironmentalExternal | FireForestGrass | Transformer(UG) | Normal | EnvironmentalExternal¦FireForestGrass¦Transformer(UG)¦Normal |  |  |  | N/A | N/A
EnvironmentalExternal | FloodErosion | Transformer(UG) | Normal | EnvironmentalExternal¦FloodErosion¦Transformer(UG)¦Normal |  |  |  | None | None
EnvironmentalExternal | Lightning | Capacitor | Broken | EnvironmentalExternal¦Lightning¦Capacitor¦Broken |  |  |  | None | None
EnvironmentalExternal | Lightning | Transformer(OH) |  | EnvironmentalExternal¦Lightning¦Transformer(OH)¦ |  |  |  | None | None
EnvironmentalExternal | Water | Recloser | Leaking | EnvironmentalExternal¦Water¦Recloser¦Leaking |  |  |  | None | None
EnvironmentalExternal | Water | Recloser | Malfunctioning | EnvironmentalExternal¦Water¦Recloser¦Malfunctioning |  |  |  | None | None
EnvironmentalExternal | Water | Transformer | Normal | EnvironmentalExternal¦Water¦Transformer¦Normal |  |  |  | None | None
EnvironmentalExternal | Water | Transformer(UG) | Normal | EnvironmentalExternal¦Water¦Transformer(UG)¦Normal |  |  |  | None | None
EquipmentFailureInvolved | ElectricalOverload | CrossarmWood | Deteriorated | EquipmentFailureInvolved¦ElectricalOverload¦CrossarmWood¦Deteriorated |  |  |  | None | Very High
EquipmentFailureInvolved | Firepole | CrossarmSteel | Burnedflashed | EquipmentFailureInvolved¦Firepole¦CrossarmSteel¦Burnedflashed |  |  |  | None | High
EquipmentFailureInvolved | Firepole | Jumper | Broken | EquipmentFailureInvolved¦Firepole¦Jumper¦Broken |  |  |  | None | Medium
EquipmentFailureInvolved | Firepole | StreetLightEquipment | Burnedflashed | EquipmentFailureInvolved¦Firepole¦StreetLightEquipment¦Burnedflashed |  |  |  | None | None
EquipmentFailureInvolved | Overhead | Booster | Leaking | EquipmentFailureInvolved¦Overhead¦Booster¦Leaking |  |  |  | None | Very High
EquipmentFailureInvolved | Overhead | Capacitor | Normal | EquipmentFailureInvolved¦Overhead¦Capacitor¦Normal |  |  |  | None | Medium
EquipmentFailureInvolved | Overhead | ConnectorBolted | Annealed | EquipmentFailureInvolved¦Overhead¦ConnectorBolted¦Annealed |  |  |  | None | Very High
EquipmentFailureInvolved | Overhead | PotheadRiserTermination | Broken | EquipmentFailureInvolved¦Overhead¦PotheadRiserTermination¦Broken |  |  |  | None | High
EquipmentFailureInvolved | Overhead | PTCCVT | Broken | EquipmentFailureInvolved¦Overhead¦PTCCVT¦Broken |  |  |  | N/A | N/A
EquipmentFailureInvolved | Overhead | Serviceconductor | Contaminated | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Contaminated |  |  |  | None | High
EquipmentFailureInvolved | Overhead | StreetLightEquipment | Malfunctioning | EquipmentFailureInvolved¦Overhead¦StreetLightEquipment¦Malfunctioning |  |  |  | None | None
EquipmentFailureInvolved | Substation | RegulatorLTCsubstation | Malfunctioning | EquipmentFailureInvolved¦Substation¦RegulatorLTCsubstation¦Malfunctioning |  |  |  | N/A | N/A
EquipmentFailureInvolved | Underground |  | Malfunctioning | EquipmentFailureInvolved¦Underground¦¦Malfunctioning |  |  |  | None | None
EquipmentFailureInvolved | Underground | CustomerEquipment | FailedFaulted | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦FailedFaulted |  |  |  | None | None
EquipmentFailureInvolved | Underground | Fuse | BurnedOpen | EquipmentFailureInvolved¦Underground¦Fuse¦BurnedOpen |  |  |  | None | None
EquipmentFailureInvolved | Underground | Other | Contaminated | EquipmentFailureInvolved¦Underground¦Other¦Contaminated |  |  |  | None | None
EquipmentFailureInvolved | Underground | Other | Deteriorated | EquipmentFailureInvolved¦Underground¦Other¦Deteriorated |  |  |  | None | None
EquipmentFailureInvolved | Underground | Splicebox | FailedFaulted | EquipmentFailureInvolved¦Underground¦Splicebox¦FailedFaulted |  |  |  | None | None
EquipmentFailureInvolved | Underground | Transformer | BurnedOpen | EquipmentFailureInvolved¦Underground¦Transformer¦BurnedOpen |  |  |  | None | None
UnknownCause | Patrolnotconducted | Transformer | Broken | UnknownCause¦Patrolnotconducted¦Transformer¦Broken |  |  |  | None | High
Vegetation | Othergroundvegetation | Fuse | BurnedOpen | Vegetation¦Othergroundvegetation¦Fuse¦BurnedOpen |  |  |  | None | Very High
Vegetation | Othergroundvegetation | Transformer(OH) | FailedFaulted | Vegetation¦Othergroundvegetation¦Transformer(OH)¦FailedFaulted |  |  |  | None | High
Vegetation | Treebarkfellintoline | Pothead(RiserTermination) | Normal | Vegetation¦Treebarkfellintoline¦Pothead(RiserTermination)¦Normal |  |  |  | None | Very High
Vegetation | Treebarkfellintoline | Serviceconductor | Together | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Together |  |  |  | None | High
Vegetation | Treebarkfellintoline | Transformer | Arcing | Vegetation¦Treebarkfellintoline¦Transformer¦Arcing |  |  |  | None | High
Vegetation | Treebarkfellintoline | Transformer | Burnedflashed | Vegetation¦Treebarkfellintoline¦Transformer¦Burnedflashed |  |  |  | None | High
Vegetation | Treebranchfellonline | Capacitor | Normal | Vegetation¦Treebranchfellonline¦Capacitor¦Normal |  |  |  | None | Medium
Vegetation | Treebranchfellonline | Other | FailedFaulted | Vegetation¦Treebranchfellonline¦Other¦FailedFaulted |  |  |  | N/A | N/A
Vegetation | Treebranchfellonline | PoleWood | Normal | Vegetation¦Treebranchfellonline¦PoleWood¦Normal |  |  |  | None | Medium
Vegetation | Treebranchfellonline | Recloser | Malfunctioning | Vegetation¦Treebranchfellonline¦Recloser¦Malfunctioning |  |  |  | None | Medium
Vegetation | Treefellintoline | ConductorUnderground | Burnedflashed | Vegetation¦Treefellintoline¦ConductorUnderground¦Burnedflashed |  |  |  | None | None
Vegetation | Treefellintoline | CrossarmWood | Normal | Vegetation¦Treefellintoline¦CrossarmWood¦Normal |  |  |  | None | Medium
Vegetation | Treefellintoline | Serviceconductor | FailedFaulted | Vegetation¦Treefellintoline¦Serviceconductor¦FailedFaulted |  |  |  | None | Medium
Vegetation | Treefellintoline | Transformer(UG) | Broken | Vegetation¦Treefellintoline¦Transformer(UG)¦Broken |  |  |  | None | None
Company Initiated | Construction Activity/equip- company | Generator | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Generator¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip- company | Insulator | Failed/Faulted | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip- company | Lightning Arrestor | Failed/Faulted | CompanyInitiated¦ConstructionActivityequipcompany¦LightningArrestor¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip- company | Other | Malfunctioning | CompanyInitiated¦ConstructionActivityequipcompany¦Other¦Malfunctioning |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip- company | Regulator | Normal | CompanyInitiated¦ConstructionActivityequipcompany¦Regulator¦Normal |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip- company | Secondary | Broken | CompanyInitiated¦ConstructionActivityequipcompany¦Secondary¦Broken |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip- company | Transformer (OH) | Leaking | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Leaking |  |  |  | N/A | N/A
Company Initiated | Construction Activity/equip- company | Transformer | Failed/Faulted | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Conductor- Underground | Normal | CompanyInitiated¦Coordinationfailure¦ConductorUnderground¦Normal |  |  |  | N/A | N/A
Company Initiated | Coordination failure | Service conductor | Broken- wire on ground | CompanyInitiated¦Coordinationfailure¦Serviceconductor¦Brokenwireonground |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Conductor- Underground | Broken | CompanyInitiated¦ImproperConstruction¦ConductorUnderground¦Broken |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Elbow | Normal | CompanyInitiated¦ImproperConstruction¦Elbow¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Insulator | Normal | CompanyInitiated¦ImproperConstruction¦Insulator¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Interrupter | Normal | CompanyInitiated¦ImproperConstruction¦Interrupter¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Other | Failed/Faulted | CompanyInitiated¦ImproperConstruction¦Other¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Secondary | Burned Open | CompanyInitiated¦ImproperConstruction¦Secondary¦BurnedOpen |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Secondary | Normal | CompanyInitiated¦ImproperConstruction¦Secondary¦Normal |  |  |  | N/A | N/A
Company Initiated | Improper Construction | Switch (OH) | Normal | CompanyInitiated¦ImproperConstruction¦Switch(OH)¦Normal |  |  |  | N/A | N/A
Company Initiated | Insulator washing | Pole-Wood | Contaminated | CompanyInitiated¦Insulatorwashing¦PoleWood¦Contaminated |  |  |  | N/A | N/A
Company Initiated | Operating error | Generator | Failed/Faulted | CompanyInitiated¦Operatingerror¦Generator¦FailedFaulted |  |  |  | N/A | N/A
Company Initiated | Other Circuits | Pole-Wood | Normal | CompanyInitiated¦OtherCircuits¦PoleWood¦Normal |  |  |  | N/A | N/A
Company Initiated | Other Circuits | Relay | Normal | CompanyInitiated¦OtherCircuits¦Relay¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel- company | Conductor- Overhead | Annealed | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Annealed |  |  |  | N/A | N/A
Company Initiated | Personnel- company | Pothead(Riser Termination) | Burned/flashed | CompanyInitiated¦Personnelcompany¦Pothead(RiserTermination)¦Burnedflashed |  |  |  | N/A | N/A
Company Initiated | Personnel- company | Transformer (OH) | Deteriorated | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Deteriorated |  |  |  | N/A | N/A
Company Initiated | Personnel- company | Transformer (UG) | Normal | CompanyInitiated¦Personnelcompany¦Transformer(UG)¦Normal |  |  |  | N/A | N/A
Company Initiated | Personnel- company | Transformer | Broken | CompanyInitiated¦Personnelcompany¦Transformer¦Broken |  |  |  | N/A | N/A
Company Initiated | Personnel- company | Transformer | Malfunctioning | CompanyInitiated¦Personnelcompany¦Transformer¦Malfunctioning |  |  |  | N/A | N/A
Company Initiated | Planned- capital |  |  | CompanyInitiated¦Plannedcapital¦¦ |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Conductor- Overhead | Normal | CompanyInitiated¦Plannedcapital¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Connector or Splice (UG) | Arcing | CompanyInitiated¦Plannedcapital¦ConnectororSplice(UG)¦Arcing |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Elbow | Normal | CompanyInitiated¦Plannedcapital¦Elbow¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Fuse | Normal | CompanyInitiated¦Plannedcapital¦Fuse¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Interrupter |  | CompanyInitiated¦Plannedcapital¦Interrupter¦ |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Other | Normal | CompanyInitiated¦Plannedcapital¦Other¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Pole-Wood | Normal | CompanyInitiated¦Plannedcapital¦PoleWood¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Transformer (OH) |  | CompanyInitiated¦Plannedcapital¦Transformer(OH)¦ |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Transformer (UG) | Normal | CompanyInitiated¦Plannedcapital¦Transformer(UG)¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Transformer | Broken | CompanyInitiated¦Plannedcapital¦Transformer¦Broken |  |  |  | N/A | N/A
Company Initiated | Planned- capital | Transformer | Normal | CompanyInitiated¦Plannedcapital¦Transformer¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- customer |  |  | CompanyInitiated¦Plannedcustomer¦¦ |  |  |  | N/A | N/A
Company Initiated | Planned- customer | Service conductor | Normal | CompanyInitiated¦Plannedcustomer¦Serviceconductor¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- customer | Transformer (OH) |  | CompanyInitiated¦Plannedcustomer¦Transformer(OH)¦ |  |  |  | N/A | N/A
Company Initiated | Planned- customer | Transformer | Normal | CompanyInitiated¦Plannedcustomer¦Transformer¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance |  |  | CompanyInitiated¦Plannedmaintenance¦¦ |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Conductor- Overhead | Broken- wire on object | CompanyInitiated¦Plannedmaintenance¦ConductorOverhead¦Brokenwireonobject |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Conductor- Underground | Normal | CompanyInitiated¦Plannedmaintenance¦ConductorUnderground¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Cutout- fuse holder | Normal | CompanyInitiated¦Plannedmaintenance¦Cutoutfuseholder¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Other | Normal | CompanyInitiated¦Plannedmaintenance¦Other¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Pole-Wood | Normal | CompanyInitiated¦Plannedmaintenance¦PoleWood¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Secondary | Normal | CompanyInitiated¦Plannedmaintenance¦Secondary¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Transformer (OH) |  | CompanyInitiated¦Plannedmaintenance¦Transformer(OH)¦ |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Transformer (UG) | Normal | CompanyInitiated¦Plannedmaintenance¦Transformer(UG)¦Normal |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Transformer | Deteriorated | CompanyInitiated¦Plannedmaintenance¦Transformer¦Deteriorated |  |  |  | N/A | N/A
Company Initiated | Planned- maintenance | Transformer | Normal | CompanyInitiated¦Plannedmaintenance¦Transformer¦Normal |  |  |  | N/A | N/A
Company Initiated | Return Circuit Normal | Jumper | Broken | CompanyInitiated¦ReturnCircuitNormal¦Jumper¦Broken |  |  |  | N/A | N/A
Wildfire Mitigation | Planned - WSIP/System Hardening |  |  | WildfireMitigation¦PlannedWSIPSystemHardening¦¦ |  |  |  | N/A | N/A
Wildfire Mitigation | Planned - WSIP/System Hardening | Bushing | Failed/Faulted | WildfireMitigation¦PlannedWSIPSystemHardening¦Bushing¦FailedFaulted |  |  |  | N/A | N/A
Wildfire Mitigation | Planned - WSIP/System Hardening | Conductor- Overhead | Normal | WildfireMitigation¦PlannedWSIPSystemHardening¦ConductorOverhead¦Normal |  |  |  | N/A | N/A
Wildfire Mitigation | Planned - WSIP/System Hardening | Other | Normal | WildfireMitigation¦PlannedWSIPSystemHardening¦Other¦Normal |  |  |  | N/A | N/A
Wildfire Mitigation | Planned - WSIP/System Hardening | Pole-Wood | Deteriorated | WildfireMitigation¦PlannedWSIPSystemHardening¦PoleWood¦Deteriorated |  |  |  | N/A | N/A
Wildfire Mitigation | Planned - WSIP/System Hardening | Transformer (OH) |  | WildfireMitigation¦PlannedWSIPSystemHardening¦Transformer(OH)¦ |  |  |  | N/A | N/A
Wildfire Mitigation | Public Safety Power Shut-off | Switch (UG) | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(UG)¦Normal |  |  |  | N/A | N/A
Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Normal | WildfireMitigation¦PublicSafetyPowerShutoff¦Transformer(UG)¦Normal |  |  |  | N/A | N/A
3rd Party | Other | Conductor, Underground | Burned/flashed | 3rdParty¦Other¦ConductorUnderground¦Burnedflashed |  |  |  | None | None
3rd Party | Vandalism | Conductor, Underground | Broken | 3rdParty¦Vandalism¦ConductorUnderground¦Broken |  |  |  | None | None
3rd Party | Vandalism | Conductor, Underground | Burned/flashed | 3rdParty¦Vandalism¦ConductorUnderground¦Burnedflashed |  |  |  | None | None
Animal | Bird found | Transformer (UG) | Normal | Animal¦Birdfound¦Transformer(UG)¦Normal |  |  |  | None | None
Animal | Squirrel | Switch (UG) | Normal | Animal¦Squirrel¦Switch(UG)¦Normal |  |  |  | None | None
Environmental/External | Flood/Erosion | Conductor, Underground | Contaminated | EnvironmentalExternal¦FloodErosion¦ConductorUnderground¦Contaminated |  |  |  | None | None
Environmental/External | Flood/Erosion | Transformer (UG) | Deteriorated | EnvironmentalExternal¦FloodErosion¦Transformer(UG)¦Deteriorated |  |  |  | None | None
Environmental/External | Lightning | Conductor, Underground | Normal | EnvironmentalExternal¦Lightning¦ConductorUnderground¦Normal |  |  |  | None | None
Environmental/External | Water | Transformer (UG) | Contaminated | EnvironmentalExternal¦Water¦Transformer(UG)¦Contaminated |  |  |  | None | None
Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Burned/flashed | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(UG)¦Burnedflashed |  |  |  | None | None
Equipment Failure/Involved | Underground | Cable Termination(live front | Broken | EquipmentFailureInvolved¦Underground¦CableTermination(livefront¦Broken |  |  |  | None | None
Equipment Failure/Involved | Underground | Customer Equipment | Normal | EquipmentFailureInvolved¦Underground¦CustomerEquipment¦Normal |  |  |  | None | None
Equipment Failure/Involved | Underground | Transformer (OH) | Burned/flashed | EquipmentFailureInvolved¦Underground¦Transformer(OH)¦Burnedflashed |  |  |  | None | None

## Outages_HFTD
ODB_EVENT_LOG_ID | BASIC_CAUSE | SUPPLEMENTAL_CAUSE | EQUIPINVOLVED | EQUIPCONDITION | FNLYEAR | hftd_tier | DESCRIPTION | FNL Month | FNL Day | FNL DATE | OISOUTAGENUMBER | Mom/Sus | MayNov | JointForLookup
15-0007589 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2015-01-28 | 1169228 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0010490 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1176855 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0019594 | Equipment Failure/Involved | Other | Switch | Malfunctioning | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2015-03-14 | 1203590 | Sus | N | EquipmentFailureInvolved¦Other¦Switch¦Malfunctioning
15-0038575 | Environmental/External | Lightning | Bushing | Broken | 2015 | Tier 3 - Extreme | Transformer only | 6 | 4 | 2015-06-04 | 1243809 | Sus | Y | EnvironmentalExternal¦Lightning¦Bushing¦Broken
15-0042304 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 20 | 2015-06-20 | 1253914 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0050074 | 3rd Party | Dig in, 3rd party | Secondary | Broken | 2015 | Tier 3 - Extreme | Transformer only | 7 | 23 | 2015-07-23 | 1276136 | Sus | Y | 3rdParty¦Digin3rdparty¦Secondary¦Broken
15-0051918 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2015-07-31 | 1280804 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0052736 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2015-08-04 | 1282774 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
15-0056721 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2015-08-22 | 1292969 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
15-0059400 | Equipment Failure/Involved | Substation | Other | Bent or Twisted | 2015 | Tier 2 - Elevated | Substation - Distribution | 9 | 4 | 2015-09-04 | 1300362 | Sus | Y | EquipmentFailureInvolved¦Substation¦Other¦BentorTwisted
15-0060916 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2015-09-11 | 1304179 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0063104 | 3rd Party | Vehicle | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 24 | 2015-09-24 | 1311253 | Sus | Y | 3rdParty¦Vehicle¦Fuse¦FailedFaulted
15-0066363 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 29 | 2015-09-29 | 1313781 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
15-0070604 | Equipment Failure/Involved | Substation | Circuit Breaker | Malfunctioning | 2015 | Tier 3 - Extreme | Substation - Transmission | 10 | 15 | 2015-10-15 | 1322787 | Sus | Y | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Malfunctioning
15-0071234 | Environmental/External | Lightning | Transformer (OH) | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324164 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Deteriorated
15-0071246 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324166 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0072631 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2015-10-21 | 1327565 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0072872 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 3 - Extreme | Transformer only | 10 | 22 | 2015-10-22 | 1328083 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0077971 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342198 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0083689 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 9 | 2015-12-09 | 1356509 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0085207 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 13 | 2015-12-13 | 1363005 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0085214 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2015-12-14 | 1363057 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0086324 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2015-12-20 | 1367156 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0005980 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385789 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0006088 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2016-01-18 | 1386299 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0007569 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2016-01-22 | 1390342 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0013549 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406567 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013622 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2016-02-18 | 1407678 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0018010 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420623 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
16-0018874 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2016-03-07 | 1423345 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0019818 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2016-03-09 | 1426180 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0019818 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2016-03-09 | 1426180 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0032135 | Environmental/External | Lightning | Transformer | Broken | 2016 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2016-04-27 | 1460574 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦Broken
16-0043645 | Equipment Failure/Involved | Overhead | Fuse | Arcing | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2016-06-16 | 1489800 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Arcing
16-0044151 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 6 | 17 | 2016-06-17 | 1491407 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0046924 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Transformer only | 6 | 30 | 2016-06-30 | 1498914 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0047641 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2016-07-03 | 1500379 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0053552 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2016-07-29 | 1518328 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0057472 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2016-08-15 | 1526829 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0065085 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2016-09-16 | 1542606 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0065268 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2016-09-16 | 1542895 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0067109 | Vegetation | Tree - branch fell on line | Jumper | Burned Open | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 23 | 2016-09-23 | 1546817 | Sus | Y | Vegetation¦Treebranchfellonline¦Jumper¦BurnedOpen
16-0074375 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2016 | Tier 3 - Extreme | Transformer only | 10 | 20 | 2016-10-20 | 1566585 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
16-0074992 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 10 | 24 | 2016-10-24 | 1568579 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0075252 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2016-10-25 | 1569249 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0076775 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2016-10-30 | 1573149 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0082476 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 11 | 27 | 2016-11-27 | 1589991 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
16-0083518 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2016-12-02 | 1593120 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0084911 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 10 | 2016-12-10 | 1598262 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0003657 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1618008 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0003707 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2017-01-04 | 1618541 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0004345 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2017-01-06 | 1620257 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0004355 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2017-01-06 | 1620483 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0004686 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1620985 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0005263 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624830 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005805 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2017-01-08 | 1628129 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0005986 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 9 | 2017-01-09 | 1630461 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0006234 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628654 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006571 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1633185 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007024 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1636825 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0007548 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639488 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
17-0007598 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639574 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0007807 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639632 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0010237 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1646750 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0010643 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2017-01-19 | 1649766 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0011631 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653756 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011849 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transmission line | 1 | 20 | 2017-01-20 | 1655283 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0012104 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1655231 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed
17-0012112 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1656150 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0013085 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658396 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject
17-0013276 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658371 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0017524 | Company Initiated | Other Circuits | Other | Normal | 2017 | Tier 3 - Extreme | Transmission line | 2 | 5 | 2017-02-05 | 1675216 | Sus | N | CompanyInitiated¦OtherCircuits¦Other¦Normal
17-0025285 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704602 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0035397 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2017 | Tier 3 - Extreme | Transmission line | 3 | 31 | 2017-03-31 | 1740601 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
17-0037640 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1749635 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038125 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2017-04-07 | 1751290 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0038257 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 8 | 2017-04-08 | 1752500 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0040613 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2017-04-16 | 1758888 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0041829 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 20 | 2017-04-20 | 1762284 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0045082 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 3 | 2017-05-03 | 1773642 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0045838 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2017-05-06 | 1776465 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0046706 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2017-05-09 | 1778966 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0049189 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2017-05-19 | 1785451 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0051728 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2017-05-31 | 1793689 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0056077 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 18 | 2017-06-18 | 1807518 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0057566 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2017-06-21 | 1814475 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0060275 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2017-07-03 | 1822900 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0066147 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2017-07-28 | 1841343 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0068599 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2017-08-07 | 1848174 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
17-0069802 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2017-08-12 | 1850979 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0070583 | Vegetation | Tree - bark fell into line | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2017-08-15 | 1853256 | Sus | Y | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦Broken
17-0073275 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 28 | 2017-08-28 | 1861006 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
17-0074089 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2017-08-30 | 1863031 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0074913 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2017-09-01 | 1865217 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0084917 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2017-10-07 | 1892380 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086662 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2017-10-12 | 1898937 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
17-0087861 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2017-10-16 | 1902313 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
17-0090595 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 10 | 26 | 2017-10-26 | 1910148 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0095542 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2017-11-16 | 1923849 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0096498 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2017-11-20 | 1926521 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0097135 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2017-11-22 | 1928007 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0097626 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2017-11-26 | 1929446 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0097696 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2017 | Tier 2 - Elevated | Transformer only | 11 | 27 | 2017-11-27 | 1929709 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
17-0097962 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 11 | 27 | 2017-11-27 | 1930611 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0100905 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 9 | 2017-12-09 | 1939361 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0103579 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2017-12-29 | 1952818 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0003587 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2018-01-04 | 1748 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0011310 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2018-02-03 | 18838 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0018625 | Environmental/External | Lightning |  | Broken | 2018 | Tier 2 - Elevated | Transformer only | 3 | 1 | 2018-03-01 | 34728 | Sus | N | EnvironmentalExternal¦Lightning¦¦Broken
18-0019284 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2018-03-02 | 36815 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0019372 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2018-03-03 | 37041 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0022234 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2018-03-13 | 43229 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0028294 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 1 | 2018-04-01 | 57565 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0030362 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2018-04-08 | 62497 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0031475 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2018-04-11 | 65049 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0032416 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2018-04-15 | 67299 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0033587 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2018-04-19 | 69849 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0036420 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2018-04-27 | 75712 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0037467 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 5 | 2 | 2018-05-02 | 77919 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
18-0044861 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2018-05-28 | 95025 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0047556 | Equipment Failure/Involved | Overhead | Pole-Wood | Normal | 2018 | Tier 2 - Elevated | Transformer only | 6 | 5 | 2018-06-05 | 101904 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Normal
18-0055479 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2018-06-28 | 120300 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0057966 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2018-07-09 | 127221 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
18-0059869 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 7 | 14 | 2018-07-14 | 131913 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0063804 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2018-07-25 | 140314 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0065475 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 31 | 2018-07-31 | 146158 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0068598 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2018-08-10 | 152748 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
18-0071570 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2018-08-20 | 158371 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0078987 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2018-09-12 | 173055 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0079186 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2018-09-12 | 173348 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0082634 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2018-09-23 | 179905 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0087188 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2018-10-05 | 188834 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0099175 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 12 | 2018-11-12 | 213860 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0100529 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2018-11-16 | 217056 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0101468 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219102 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101909 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2018-11-21 | 220034 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0106707 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2018-12-04 | 233247 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0107611 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2018-12-06 | 235019 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109296 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 240506 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0110754 | 3rd Party | Customer Equipment | Other | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 12 | 26 | 2018-12-26 | 247513 | Sus | N | 3rdParty¦CustomerEquipment¦Other¦FailedFaulted
19-0004954 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 254879 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0006609 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2019-01-08 | 261097 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0008268 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 1 | 12 | 2019-01-12 | 263878 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0009337 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2019-01-15 | 266081 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010875 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 272316 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011912 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2019-01-18 | 276036 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011945 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 276146 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0013230 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2019-01-22 | 279181 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0016056 | 3rd Party | Vandalism | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2019-01-30 | 284226 | Sus | N | 3rdParty¦Vandalism¦PoleWood¦Broken
19-0017998 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 290383 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018454 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 292523 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0019331 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 294665 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019771 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 |  | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0020001 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 296140 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0022441 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301317 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0022860 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303648 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024050 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2019-02-15 | 311845 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025657 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2019-02-18 | 317624 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025692 | Environmental/External | Ice or snow | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 317972 | Sus | N | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Broken
19-0028598 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325303 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0029366 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 327832 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0029621 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2019-02-28 | 328473 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0030757 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2019-03-05 | 331210 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0032022 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2019-03-08 | 334385 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0035191 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2019-03-19 | 343203 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0035537 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2019-03-20 | 344048 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
19-0036677 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2019-03-25 | 346904 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed
19-0037117 | Equipment Failure/Involved | Underground | Fuse | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2019-03-26 | 347767 | Sus | N | EquipmentFailureInvolved¦Underground¦Fuse¦Broken
19-0039668 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 4 | 2019-04-04 | 353621 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0041198 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2019-04-10 | 357641 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0041779 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2019-04-11 | 359236 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
19-0043757 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2019-04-17 | 362558 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0046361 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2019-04-26 | 368460 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0053964 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2019-05-19 | 385296 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0055480 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2019 | Tier 3 - Extreme | Transformer only | 5 | 22 | 2019-05-22 | 388179 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
19-0057549 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 5 | 25 | 2019-05-25 | 389936 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0058533 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2019-05-28 | 391750 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0060809 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2019-05-31 | 394563 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0068579 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2019-06-17 | 417406 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0069869 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 6 | 19 | 2019-06-19 | 422032 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0075039 | Equipment Failure/Involved | Underground | Secondary | Broken | 2019 | Tier 2 - Elevated | Transformer only | 7 | 7 | 2019-07-07 | 442203 | Sus | Y | EquipmentFailureInvolved¦Underground¦Secondary¦Broken
19-0075101 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2019-07-08 | 442390 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0084364 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2019-08-05 | 484000 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0096372 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 9 | 7 | 2019-09-07 | 559834 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0102133 | Animal | Bird found | Jumper | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2019-09-21 | 602615 | Sus | Y | Animal¦Birdfound¦Jumper¦Normal
19-0104054 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2019-09-26 | 617873 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0105846 | Equipment Failure/Involved | Overhead | Other | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2019-10-01 | 633575 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
19-0118194 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2019-10-29 | 693127 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0119463 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2019-10-31 | 696353 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0119613 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2019-10-31 | 696791 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0128601 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 25 | 2019-11-25 | 714510 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130608 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 722025 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
19-0130788 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722616 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
19-0131000 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 11 | 28 | 2019-11-28 | 723248 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0131374 | Vegetation | Tree - branch fell on line | Secondary | Together | 2019 | Tier 3 - Extreme | Transformer only | 11 | 30 | 2019-11-30 | 724033 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Together
19-0131507 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724775 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0131935 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2019-12-01 | 725723 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0131991 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 726211 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0132016 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 726302 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
19-0134770 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 732657 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137129 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 18 | 2019-12-18 | 745502 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
19-0137285 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 20 | 2019-12-20 | 746724 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0137611 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2019-12-22 | 748216 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0004794 | Animal | Squirrel | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2020-01-03 | 754207 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
20-0005766 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2020-01-07 | 755988 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0006678 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2020-01-09 | 757720 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
20-0009484 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 761908 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0011068 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2020-01-18 | 765631 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0016271 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2020-02-02 | 775420 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0019168 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782866 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0019180 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782204 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0019242 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 783980 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0019242 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 783980 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0019656 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 786017 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0021277 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2020-02-12 | 789924 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0029765 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2020-03-07 | 838046 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031666 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2020-03-13 | 848453 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031925 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 13 | 2020-03-13 | 850635 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0032274 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 851774 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032892 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855307 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0035826 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 3 | 24 | 2020-03-24 | 863819 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0037649 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 1 | 2020-04-01 | 875032 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0039984 | Company Initiated | Improper Construction | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2020-04-09 | 892864 | Sus | N | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Normal
20-0044535 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2020-04-25 | 901360 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
20-0044648 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2020-04-26 | 901710 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0047650 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2020-05-05 | 907755 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0049720 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 3 - Extreme | Transformer only | 5 | 13 | 2020-05-13 | 912932 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0056906 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2020-06-03 | 929274 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
20-0064310 | Animal | Squirrel | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 6 | 24 | 2020-06-24 | 945885 | Sus | Y | Animal¦Squirrel¦Transformer¦FailedFaulted
20-0067675 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 2 | 2020-07-02 | 956732 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0068920 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2020-07-06 | 958971 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0072561 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2020-07-16 | 965830 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
20-0073455 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 7 | 19 | 2020-07-19 | 967776 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0085015 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1010609 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0085284 | Environmental/External | Lightning | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 8 | 16 | 2020-08-16 | 1011399 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken
20-0085613 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transmission line | 8 | 17 | 2020-08-17 | 1015353 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0087656 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2020-08-19 | 1023950 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing
20-0088226 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 20 | 2020-08-20 | 1025683 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0088819 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2020-08-22 | 1026877 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0092114 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2020-09-01 | 1045793 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0100380 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1088649 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0110770 | Animal | Squirrel | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2020-10-20 | 1121435 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
20-0111841 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2020-10-22 | 1123665 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0116318 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 11 | 2 | 2020-11-02 | 1134825 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0118417 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2020-11-08 | 1139111 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0118541 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2020-11-08 | 1139532 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0126424 | Animal | Squirrel | Pothead(Riser Termination) | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2020-12-01 | 1157277 | Sus | N | Animal¦Squirrel¦Pothead(RiserTermination)¦Burnedflashed
20-0128359 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167254 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0131567 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Transformer only | 12 | 23 | 2020-12-23 | 1197650 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0131837 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 12 | 25 | 2020-12-25 | 1198801 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0131970 | 3rd Party | Fire, house or bldg. | Metering Equipment | Burned/flashed | 2020 | Tier 3 - Extreme | Transformer only | 12 | 27 | 2020-12-27 | 1199603 | Sus | N | 3rdParty¦Firehouseorbldg¦MeteringEquipment¦Burnedflashed
21-0011335 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2021-01-20 | 1218337 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013980 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223753 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0015713 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232826 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0017745 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1240057 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0018671 | Vegetation | Other ground vegetation | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 29 | 2021-01-29 | 1242105 | Sus | N | Vegetation¦Othergroundvegetation¦Transformer¦Broken
21-0037284 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2021-03-16 | 1285289 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
21-0041728 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2021-03-27 | 1300144 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
21-0043009 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 30 | 2021-03-30 | 1303893 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0049817 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 16 | 2021-04-16 | 1320419 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
21-0056977 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 4 | 2021-05-04 | 1341076 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0067862 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2021-05-30 | 1361890 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0068011 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2021-05-31 | 1362199 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0068122 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 1 | 2021-06-01 | 1362643 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0068382 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | 2021 | Tier 2 - Elevated | Transformer only | 6 | 1 | 2021-06-01 | 1363078 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed
21-0076372 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2021-06-18 | 1378141 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0076488 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2021-06-18 | 1378538 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0084866 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2021-07-05 | 1392151 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
21-0094788 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 7 | 26 | 2021-07-26 | 1414568 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0096302 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2021-07-28 | 1417711 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0101438 | Animal | Squirrel | Transformer (OH) | Normal | 2021 | Tier 3 - Extreme | Transformer only | 8 | 7 | 2021-08-07 | 1436288 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
21-0107482 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2021-08-20 | 1448800 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0109570 | Equipment Failure/Involved | Overhead | Other | Normal | 2021 | Tier 2 - Elevated | Transformer only | 8 | 26 | 2021-08-26 | 1453803 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Normal
21-0113972 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2021-09-07 | 1463338 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0119589 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2021-09-19 | 1475653 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0126500 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Deteriorated | 2021 | Tier 3 - Extreme | Transformer only | 10 | 6 | 2021-10-06 | 1488443 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Deteriorated
21-0128407 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492078 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0135317 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2021-10-22 | 1506242 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0136043 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1510794 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136878 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1516952 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0157366 | Vegetation | Tree - bark fell into line | Transformer (OH) | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1566797 | Sus | N | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Normal
21-0158460 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1572754 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0159317 | Environmental/External | Ice or snow | Transformer | Broken, wire on ground | 2021 | Tier 3 - Extreme | Transformer only | 12 | 16 | 2021-12-16 | 1575194 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Transformer¦Brokenwireonground
21-0161204 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1586148 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161373 | Equipment Failure/Involved | Overhead | Recloser | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2021-12-28 | 1587099 | Sus | N | EquipmentFailureInvolved¦Overhead¦Recloser¦FailedFaulted
21-0161392 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2021-12-28 | 1586733 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0161676 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588965 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0005543 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591869 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0005700 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1594073 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0005983 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2022-01-04 | 1594868 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0006183 | Vegetation | Tree - fell into line | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 1 | 4 | 2022-01-04 | 1595102 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Broken
22-0007281 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1597194 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0010762 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2022-01-18 | 1604581 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0012784 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Transformer only | 1 | 21 | 2022-01-21 | 1607794 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0020891 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2022-02-10 | 1624915 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
22-0030207 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Transformer only | 3 | 4 | 2022-03-04 | 1642601 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0037087 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2022-03-22 | 1653724 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0039167 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2022-03-28 | 1657513 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0039737 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 3 | 28 | 2022-03-28 | 1658179 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0059484 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2022-05-08 | 1691407 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0066580 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 25 | 2022-05-25 | 1710830 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0073278 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2022-06-11 | 1728599 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0076704 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 6 | 21 | 2022-06-21 | 1737299 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0078941 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 6 | 26 | 2022-06-26 | 1742828 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0080126 | Vegetation | Tree - grew into line | Secondary | Normal | 2022 | Tier 2 - Elevated | Transformer only | 6 | 29 | 2022-06-29 | 1745618 | Sus | Y | Vegetation¦Treegrewintoline¦Secondary¦Normal
22-0095240 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2022-08-09 | 1776636 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
22-0097341 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 8 | 14 | 2022-08-14 | 1780771 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0100068 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 8 | 20 | 2022-08-20 | 1785798 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100568 | Company Initiated | Coordination failure | Other | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2022-08-22 | 1787419 | Sus | Y | CompanyInitiated¦Coordinationfailure¦Other¦Normal
22-0102202 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 26 | 2022-08-26 | 1791944 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0105165 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 9 | 2 | 2022-09-02 | 1797661 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0105461 | Animal | Other | Fuse | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2022-09-03 | 1798267 | Sus | Y | Animal¦Other¦Fuse¦Normal
22-0105991 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 5 | 2022-09-05 | 1800264 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0107714 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2022-09-07 | 1805302 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0108990 | Animal | Other | Bushing | Contaminated | 2022 | Tier 2 - Elevated | Transformer only | 9 | 11 | 2022-09-11 | 1808393 | Sus | Y | Animal¦Other¦Bushing¦Contaminated
22-0112389 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 19 | 2022-09-19 | 1816774 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0113331 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 21 | 2022-09-21 | 1818579 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0118900 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Transformer only | 10 | 6 | 2022-10-06 | 1830751 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
22-0121361 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2022-10-14 | 1836939 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0122272 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2022-10-17 | 1839228 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0124042 | Equipment Failure/Involved | Overhead | Pole - Tower, steel | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2022-10-23 | 1843465 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleTowersteel¦Deteriorated
22-0126460 | Unknown Cause | Patrol - found nothing | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2022-11-01 | 1850028 | Sus | Y | UnknownCause¦Patrolfoundnothing¦Transformer(OH)¦FailedFaulted
22-0128277 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 11 | 6 | 2022-11-06 | 1855045 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
22-0128993 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857065 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0129082 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857170 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0129213 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857767 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0129365 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2022-11-08 | 1858342 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
22-0130146 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2022 | Tier 3 - Extreme | Transformer only | 11 | 10 | 2022-11-10 | 1860124 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
22-0130164 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2022-11-09 | 1859397 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
22-0132696 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865704 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0136088 | Equipment Failure/Involved | Overhead | Secondary | Normal | 2022 | Tier 2 - Elevated | Transformer only | 12 | 2 | 2022-12-02 | 1874349 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal
22-0136297 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2022-12-03 | 1875116 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0136297 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2022-12-03 | 1875116 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0138476 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882514 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138858 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 2 - Elevated | Transformer only | 12 | 11 | 2022-12-11 | 1884539 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0138939 | Animal | Squirrel | Transformer (OH) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885451 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦Normal
22-0141544 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Transformer only | 12 | 27 | 2022-12-27 | 1898618 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0141864 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 12 | 27 | 2022-12-27 | 1899959 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken
22-0142442 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 12 | 30 | 2022-12-30 | 1902687 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0142662 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1904851 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
15-0005749 | Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2015-01-20 | 1166179 | Sus | N | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
15-0010527 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1175745 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
15-0010847 | Equipment Failure/Involved | Lightning | Lightning Arrestor | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1179485 | Sus | N | EquipmentFailureInvolved¦Lightning¦LightningArrestor¦FailedFaulted
15-0011956 | Equipment Failure/Involved | Other | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2015-02-08 | 1183931 | Sus | N | EquipmentFailureInvolved¦Other¦PoleWood¦Broken
15-0012272 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2015-02-08 | 1185637 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
15-0012792 | Vegetation | Tree - fell into line | Pole-Wood | Together | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2015-02-11 | 1188622 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Together
15-0014956 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2015-02-23 | 1194341 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0016298 | Equipment Failure/Involved | Lightning | Transformer | Malfunctioning | 2015 | Tier 3 - Extreme | Transformer only | 2 | 27 | 2015-02-27 | 1196974 | Sus | N | EquipmentFailureInvolved¦Lightning¦Transformer¦Malfunctioning
15-0032348 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230203 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0036840 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 5 | 27 | 2015-05-27 | 1240337 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0038552 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2015-06-04 | 1243711 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0040500 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2015 | Tier 3 - Extreme | Transformer only | 6 | 11 | 2015-06-11 | 1249414 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
15-0041163 | 3rd Party | Customer Equipment | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 15 | 2015-06-15 | 1251206 | Sus | Y | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Brokenwireonground
15-0043807 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2015-06-28 | 1258012 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0049324 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2015-07-20 | 1274240 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0050011 | 3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 23 | 2015-07-23 | 1275985 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦FailedFaulted
15-0050364 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 24 | 2015-07-24 | 1276602 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0054253 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 11 | 2015-08-11 | 1286479 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0057069 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2015-08-24 | 1293914 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0062227 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 18 | 2015-09-18 | 1308395 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
15-0071448 | Environmental/External | Lightning | Transformer (OH) | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324468 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Deteriorated
15-0071572 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 18 | 2015-10-18 | 1325555 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0078186 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342582 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0084229 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 11 | 2015-12-11 | 1358671 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0084609 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1360571 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0085209 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2015 | Tier 3 - Extreme | Transformer only | 12 | 14 | 2015-12-14 | 1363059 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
16-0002448 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 1 | 1 | 2016-01-01 | 1375677 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0003479 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378130 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
16-0004310 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned Open | 2016 | Tier 2 - Elevated | Transformer only | 1 | 9 | 2016-01-09 | 1380948 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦BurnedOpen
16-0012941 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2016-02-16 | 1404391 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0014607 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2016-02-21 | 1410167 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0014750 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2016-02-22 | 1410449 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0014919 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2016-02-23 | 1410767 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017400 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416339 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017902 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418810 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017987 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1419389 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
16-0018081 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1419221 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018140 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2016-03-06 | 1420777 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018300 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421095 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0020989 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430191 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0027432 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2016-04-09 | 1447603 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0030947 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 23 | 2016-04-23 | 1456769 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
16-0031446 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 4 | 25 | 2016-04-25 | 1459001 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0034772 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 9 | 2016-05-09 | 1466856 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0035614 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2016-05-12 | 1468708 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0035908 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 13 | 2016-05-13 | 1469220 | Sus | Y | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
16-0038900 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 27 | 2016-05-27 | 1477914 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0040386 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 1 | 2016-06-01 | 1481076 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0042043 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2016 | Tier 3 - Extreme | Transformer only | 6 | 8 | 2016-06-08 | 1485575 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
16-0050783 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2016-07-19 | 1512302 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0057044 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2016-08-12 | 1525606 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0057593 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2016-08-16 | 1527202 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0059510 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 23 | 2016-08-23 | 1531138 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0068831 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2016-09-30 | 1550733 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0069412 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2016-10-03 | 1552327 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
16-0072176 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2016-10-14 | 1559738 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072343 | Equipment Failure/Involved | Overhead | Jumper | Arcing | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2016-10-14 | 1560337 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing
16-0072926 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1563140 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
16-0072982 | Vegetation | Tree - fell into line | Service conductor | Broken | 2016 | Tier 2 - Elevated | Transformer only | 10 | 16 | 2016-10-16 | 1563356 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
16-0074874 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2016-10-23 | 1568274 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
16-0074894 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2016-10-24 | 1568311 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0075174 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2016-10-24 | 1569031 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0082192 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 11 | 25 | 2016-11-25 | 1588577 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0082563 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 11 | 28 | 2016-11-28 | 1590262 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0082882 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2016-11-29 | 1591165 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0087258 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2016-12-28 | 1612389 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0002830 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 2 | 2017-01-02 | 1615178 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0006757 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1633498 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007574 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638854 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0008420 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1640661 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0008689 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2017-01-13 | 1642317 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0008753 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 13 | 2017-01-13 | 1642179 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0011252 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652308 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011322 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653014 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011870 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1655300 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011942 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 21 | 2017-01-21 | 1656154 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0012818 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1659131 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0012931 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1659271 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0013015 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1659548 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013876 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664337 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0014027 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664713 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0019448 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683406 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019705 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1684033 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0020990 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2017-02-14 | 1687949 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0021532 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2017-02-16 | 1690102 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023511 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Transformer only | 2 | 19 | 2017-02-19 | 1701828 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0024165 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705161 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
17-0024326 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705933 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0024844 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706778 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0029820 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2017-03-09 | 1723422 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0031967 | 3rd Party | Customer Equipment | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2017-03-20 | 1730667 | Sus | N | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Brokenwireonground
17-0035360 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 30 | 2017-03-30 | 1739774 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038030 | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1751246 | Sus | N | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal
17-0041845 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2017-04-21 | 1762356 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0052605 | 3rd Party | Other | Customer Equipment | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2017-06-04 | 1796585 | Sus | Y | 3rdParty¦Other¦CustomerEquipment¦Normal
17-0054331 | Animal | Other | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2017-06-11 | 1801976 | Sus | Y | Animal¦Other¦Jumper¦BurnedOpen
17-0054384 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2017-06-11 | 1802159 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
17-0059157 | Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2017-06-28 | 1819742 | Sus | Y | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal
17-0062165 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 11 | 2017-07-11 | 1829268 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0063203 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2017-07-16 | 1832612 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0068311 | Animal | Other | Recloser | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2017-08-06 | 1847502 | Sus | Y | Animal¦Other¦Recloser¦Burnedflashed
17-0069929 | Animal | Squirrel | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2017-08-13 | 1851453 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
17-0073298 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2017-08-28 | 1861035 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0075541 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2017-09-03 | 1867841 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0075992 | Equipment Failure/Involved | Overhead |  | Broken | 2017 | Tier 2 - Elevated | Transformer only | 9 | 5 | 2017-09-05 | 1870297 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦Broken
17-0076801 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2017-09-07 | 1872795 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0083697 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2017-10-03 | 1889920 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0084288 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2017-10-04 | 1891074 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0089451 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2017-10-22 | 1907112 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0090089 | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2017-10-24 | 1908633 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted
17-0093324 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2017 | Tier 2 - Elevated | Transformer only | 11 | 7 | 2017-11-07 | 1917757 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
17-0094100 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 11 | 9 | 2017-11-09 | 1919786 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0094109 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 10 | 2017-11-10 | 1919797 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0097403 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 24 | 2017-11-24 | 1928726 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0097666 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2017-11-27 | 1929599 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0098620 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2017-11-30 | 1932645 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0099600 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1934647 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0099694 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1935401 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0102251 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2017-12-16 | 1945893 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
17-0102326 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 12 | 17 | 2017-12-17 | 1946201 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0102406 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2017-12-18 | 1946537 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0102463 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2017-12-18 | 1947089 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0004006 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2018-01-06 | 3141 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0009504 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2018-01-27 | 14971 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0012719 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2018-02-09 | 21759 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0013109 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2018-02-10 | 22430 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0013965 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 2 - Elevated | Transformer only | 2 | 13 | 2018-02-13 | 24208 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0014660 | Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2018-02-15 | 25383 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed
18-0015430 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2018-02-19 | 27351 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0017558 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2018-02-26 | 32242 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0019832 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2018-03-05 | 38208 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023588 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46275 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023731 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2018-03-17 | 46606 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0026073 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2018-03-23 | 52017 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
18-0028650 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2018-04-02 | 58321 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
18-0044488 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2018-05-25 | 93756 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0044765 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2018-05-27 | 94934 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0046684 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2018-06-02 | 99748 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0049004 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2018 | Tier 2 - Elevated | Transformer only | 6 | 8 | 2018-06-08 | 104562 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
18-0049530 | Company Initiated | Operating error | Other | Normal | 2018 | Tier 2 - Elevated | Transmission line | 8 | 22 | 2018-08-22 | 159974 | Sus | Y | CompanyInitiated¦Operatingerror¦Other¦Normal
18-0052964 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 6 | 20 | 2018-06-20 | 114058 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
18-0056849 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2018-07-03 | 124103 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0064384 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 27 | 2018-07-27 | 141768 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0065881 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2018-08-01 | 146856 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0067616 | Animal | Other | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2018-08-07 | 150965 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
18-0068998 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 11 | 2018-08-11 | 153714 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0073104 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2018 | Tier 3 - Extreme | Transformer only | 8 | 24 | 2018-08-24 | 161532 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
18-0083939 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Transformer only | 9 | 26 | 2018-09-26 | 182102 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0090175 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2018-10-14 | 194669 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0099631 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2018-11-13 | 215059 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101126 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218382 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101250 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218617 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104986 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228614 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
18-0105048 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228729 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
18-0106131 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2018-12-02 | 231854 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0109252 | Equipment Failure/Involved | Substation | Bus | Normal | 2018 | Tier 2 - Elevated | Generation | 12 | 14 | 2018-12-14 | 240489 | Sus | N | EquipmentFailureInvolved¦Substation¦Bus¦Normal
18-0109452 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2018-12-16 | 241322 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
18-0109453 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2018-12-16 | 241298 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0109704 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2018 | Tier 3 - Extreme | Transformer only | 12 | 17 | 2018-12-17 | 242176 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0004922 | Vegetation | Tree - fell into line | Secondary | Bent or Twisted | 2019 | Tier 2 - Elevated | Transformer only | 1 | 5 | 2019-01-05 | 254547 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦BentorTwisted
19-0005664 | Vegetation | Tree - bark fell into line | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Transformer only | 1 | 6 | 2019-01-06 | 258837 | Sus | N | Vegetation¦Treebarkfellintoline¦Transformer(OH)¦Broken
19-0005791 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 257006 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009634 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 266923 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0011309 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 270264 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011867 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2019-01-18 | 275973 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011869 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2019-01-18 | 275979 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0018723 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 293099 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
19-0018794 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 5 | 2019-02-05 | 293795 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
19-0019080 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2019-02-06 | 293847 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0019447 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294962 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019685 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2019-02-06 | 294123 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020240 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2019-02-09 | 296658 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0021186 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 300150 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022539 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 305331 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0022721 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 306057 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0022751 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 306236 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0024259 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 306336 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024524 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 313615 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0030112 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2019-03-02 | 329746 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030266 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 3 | 3 | 2019-03-03 | 330048 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0031707 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 7 | 2019-03-07 | 333638 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0033414 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2019-03-13 | 338459 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0034068 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2019-03-15 | 339841 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
19-0035334 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2019-03-20 | 343433 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0039260 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2019-04-02 | 352737 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
19-0040910 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2019-04-09 | 356511 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0041735 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2019-04-11 | 359065 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0042909 | Equipment Failure/Involved | Other | Customer Equipment | Malfunctioning | 2019 | Tier 2 - Elevated | Transformer only | 4 | 16 | 2019-04-16 | 361834 | Sus | N | EquipmentFailureInvolved¦Other¦CustomerEquipment¦Malfunctioning
19-0047888 | 3rd Party | Other | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2019-05-01 | 371714 | Sus | Y | 3rdParty¦Other¦ConductorOverhead¦Normal
19-0048959 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 4 | 2019-05-04 | 373891 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0052626 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2019-05-16 | 382198 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0058361 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2019-05-28 | 391489 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0058666 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2019-05-28 | 392102 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0061564 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 6 | 2 | 2019-06-02 | 395964 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0067208 | Vegetation | Tree - fell into line | Insulator | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 13 | 2019-06-13 | 408883 | Sus | Y | Vegetation¦Treefellintoline¦Insulator¦Broken
19-0082102 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2019-07-29 | 474291 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0091585 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 23 | 2019-08-23 | 534719 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0099821 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2019-09-16 | 585382 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0103456 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2019-09-25 | 612897 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
19-0104922 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2019-09-28 | 624219 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0106209 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 1 | 2019-10-01 | 634954 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0106371 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2019-10-01 | 635691 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0125226 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2019-11-15 | 707810 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
19-0127820 | Vegetation | Tree - bark fell into line | Cutout, fuse holder | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 11 | 22 | 2019-11-22 | 713026 | Sus | Y | Vegetation¦Treebarkfellintoline¦Cutoutfuseholder¦FailedFaulted
19-0127955 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2019-11-23 | 713471 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0129978 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 720287 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130309 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 721010 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0130462 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 721805 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0134065 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Transformer only | 12 | 5 | 2019-12-05 | 730796 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0137792 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2019-12-24 | 749785 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0006098 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2020-01-07 | 756675 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0012573 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2020-01-23 | 768408 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0019794 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2020 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2020-02-10 | 786981 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
20-0027485 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 1 | 2020-03-01 | 820503 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0028110 | Animal | Other | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2020-03-03 | 824115 | Sus | N | Animal¦Other¦ConductorOverhead¦Normal
20-0034544 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2020-03-18 | 859431 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0035457 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2020-03-23 | 862574 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0035464 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 3 | 23 | 2020-03-23 | 862563 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0037822 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 4 | 1 | 2020-04-01 | 877874 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0039307 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2020-04-07 | 889435 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
20-0051402 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2020-05-18 | 916075 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0053873 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 5 | 25 | 2020-05-25 | 921126 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0055957 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 30 | 2020-05-30 | 926414 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0058506 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 6 | 2020-06-06 | 933201 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0058680 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2020-06-06 | 933769 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0060265 | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2020-06-11 | 936977 | Sus | Y | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted
20-0060813 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 6 | 12 | 2020-06-12 | 938118 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0072551 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2020-07-16 | 965818 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
20-0073335 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2020-07-18 | 967400 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0078182 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2020-07-30 | 975729 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0081331 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2020-08-09 | 987133 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
20-0083411 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2020-08-14 | 997414 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0084898 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2020-08-15 | 1011436 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0087837 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1024353 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
20-0089898 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 25 | 2020-08-25 | 1029441 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0091916 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1045050 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0092510 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2020-09-02 | 1048273 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0094346 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1058815 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0095023 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2020-08-18 | 1061085 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0095395 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2020-09-09 | 1061841 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0101706 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2020-09-25 | 1093242 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0107346 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2020-10-11 | 1115250 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0108954 | 3rd Party | Vehicle | Anchor or Guy | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2020-10-14 | 1118178 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Normal
20-0110656 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2020 | Tier 2 - Elevated | Transformer only | 10 | 20 | 2020-10-20 | 1121398 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
20-0113605 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2020-10-26 | 1129429 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0115797 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Transformer only | 10 | 31 | 2020-10-31 | 1133230 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0116282 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1134780 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0128362 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167267 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0004297 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 1 | 1 | 2021-01-01 | 1202232 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0012253 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2021-01-20 | 1219263 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
21-0012441 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2021-01-22 | 1220447 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0015705 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 27 | 2021-01-27 | 1232653 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
21-0017754 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1239902 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
21-0019227 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2021 | Tier 3 - Extreme | Transformer only | 1 | 30 | 2021-01-30 | 1242945 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0021681 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2021-02-04 | 1247683 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Deteriorated
21-0026775 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2021-02-18 | 1257011 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0027718 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 2 | 20 | 2021-02-20 | 1258552 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0036233 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2021-03-14 | 1281976 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0039041 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 3 | 20 | 2021-03-20 | 1290494 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0039581 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2021-03-22 | 1292549 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
21-0041204 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2021-03-25 | 1298393 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0041843 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2021-03-27 | 1301648 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
21-0042479 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2021-03-30 | 1303093 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0057470 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 5 | 2021-05-05 | 1341776 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0060030 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2021-05-11 | 1346359 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0070673 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2021-06-06 | 1367140 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0071132 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2021-06-07 | 1367872 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0073599 | Animal | Squirrel | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2021-06-13 | 1372043 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
21-0074963 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2021-06-16 | 1375067 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0076707 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2021-06-19 | 1380018 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0076789 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 20 | 2021-06-20 | 1380180 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0076815 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 20 | 2021-06-20 | 1380333 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0081493 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 29 | 2021-06-29 | 1387981 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0082372 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 30 | 2021-06-30 | 1388771 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0084775 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 4 | 2021-07-04 | 1391573 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0086678 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2021-07-08 | 1394720 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0087556 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2021-07-10 | 1398648 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0087583 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 10 | 2021-07-10 | 1398868 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0100099 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 8 | 4 | 2021-08-04 | 1434334 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0105725 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445370 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0106041 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2021-08-17 | 1446006 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0112022 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2021-09-01 | 1459813 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0117587 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 14 | 2021-09-14 | 1471902 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0118001 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 15 | 2021-09-15 | 1472615 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0131557 | Animal | Squirrel | Fuse | Burned Open | 2021 | Tier 3 - Extreme | Transformer only | 10 | 15 | 2021-10-15 | 1498215 | Sus | Y | Animal¦Squirrel¦Fuse¦BurnedOpen
21-0134291 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 21 | 2021-10-21 | 1504064 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0135645 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1507900 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0135663 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1507896 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0136362 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1510018 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
21-0136398 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513682 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0136447 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513218 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0137638 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2021-10-25 | 1518319 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137705 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1519612 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137733 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1519895 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0137755 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2021 | Tier 3 - Extreme | Transformer only | 10 | 25 | 2021-10-25 | 1520128 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
21-0138364 | Vegetation | Tree - branch fell on line | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 26 | 2021-10-26 | 1522157 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Broken
21-0140028 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 10 | 29 | 2021-10-29 | 1525368 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0140910 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2021-11-01 | 1527593 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0143486 | Animal | Bird found |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1537640 | Sus | Y | Animal¦Birdfound¦¦
21-0152318 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2021-11-28 | 1555257 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0154506 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | 2021 | Tier 3 - Extreme | Transformer only | 12 | 3 | 2021-12-03 | 1558621 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Normal
21-0155141 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2021-12-06 | 1559910 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157520 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568074 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158581 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573324 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0159698 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 19 | 2021-12-19 | 1577171 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0160144 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 12 | 22 | 2021-12-22 | 1579237 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0160638 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581225 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0160704 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581892 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
21-0161892 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1590106 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0005212 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591492 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0006345 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 1 | 4 | 2022-01-04 | 1595284 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0008201 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2022-01-10 | 1599451 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0010393 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2022-01-17 | 1603731 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
22-0012802 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607869 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0013412 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 1 | 24 | 2022-01-24 | 1610177 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0014616 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2022 | Tier 2 - Elevated | Transformer only | 1 | 26 | 2022-01-26 | 1612826 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
22-0018851 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2022-02-04 | 1621291 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0025175 | Vegetation | Tree - fell into line | Pole-Wood | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2022-02-22 | 1634009 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Normal
22-0030306 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2022-03-05 | 1642836 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0038983 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2022-03-27 | 1656632 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0045478 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1668399 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0051224 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Transformer only | 4 | 18 | 2022-04-18 | 1676134 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
22-0058838 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2022-05-06 | 1689670 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0065221 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2022-05-23 | 1707996 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
22-0066064 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2022-05-25 | 1709719 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0067966 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2022-05-29 | 1713628 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0073439 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2022-06-12 | 1729554 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0074964 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2022-06-16 | 1732844 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0084123 | Animal | Squirrel | Pothead/Riser Termination | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2022-07-11 | 1753882 | Sus | Y | Animal¦Squirrel¦PotheadRiserTermination¦Burnedflashed
22-0086044 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2022-07-15 | 1757525 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0087357 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2022 | Tier 2 - Elevated | Transformer only | 7 | 19 | 2022-07-19 | 1760315 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
22-0097275 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 14 | 2022-08-14 | 1780516 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0098490 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2022-08-17 | 1783161 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
22-0105811 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 3 - Extreme | Transformer only | 9 | 4 | 2022-09-04 | 1799241 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0111735 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1815080 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0115183 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 9 | 27 | 2022-09-27 | 1822507 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
22-0117484 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 4 | 2022-10-04 | 1827363 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0123077 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2022-10-19 | 1841067 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0129104 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857083 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0129542 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Transformer only | 12 | 6 | 2022-12-06 | 1877175 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0137012 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2022-12-06 | 1877301 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
22-0138861 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2022-12-11 | 1884954 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
23-0004513 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1905713 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0010465 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1175931 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
15-0011037 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2015-02-07 | 1180207 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0012383 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2015-02-10 | 1187544 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
15-0016361 | Equipment Failure/Involved | Lightning | Other | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 2 | 28 | 2015-02-28 | 1197120 | Sus | N | EquipmentFailureInvolved¦Lightning¦Other¦FailedFaulted
15-0017619 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2015-03-05 | 1199775 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0032660 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230294 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0038923 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2015-06-05 | 1244422 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0038954 | Equipment Failure/Involved | Overhead | Regulator | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2015-06-05 | 1244584 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Regulator¦FailedFaulted
15-0043238 | Animal | Squirrel | Cutout, fuse holder | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2015-06-25 | 1256195 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
15-0049383 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 20 | 2015-07-20 | 1274229 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0049770 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2015-07-22 | 1275226 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0051478 | Vegetation | Tree - branch fell on line | Transformer | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 7 | 29 | 2015-07-29 | 1279835 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Deteriorated
15-0053954 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2015-08-10 | 1285649 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0057398 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2015-08-26 | 1294707 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0071519 | Environmental/External | Lightning | Transformer (OH) | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324470 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Deteriorated
15-0073219 | Animal | Squirrel | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2015-10-25 | 1328910 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
15-0078269 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2015-11-16 | 1343018 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0078822 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2015-11-18 | 1344537 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0080592 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 24 | 2015-11-24 | 1347888 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0083742 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1356895 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083853 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357078 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083919 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357312 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0085051 | Vegetation | Tree - fell into line | Transformer | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 12 | 13 | 2015-12-13 | 1361855 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Burnedflashed
15-0087302 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2015-12-25 | 1371761 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0006326 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2016-01-19 | 1387268 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0007124 | Equipment Failure/Involved | Underground | Secondary | Deteriorated | 2016 | Tier 2 - Elevated | Transformer only | 1 | 21 | 2016-01-21 | 1389187 | Sus | N | EquipmentFailureInvolved¦Underground¦Secondary¦Deteriorated
16-0007999 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2016-01-25 | 1391677 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
16-0009906 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2016-02-01 | 1396636 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0012970 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1404470 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0013124 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1405151 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013781 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407146 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0017619 | Vegetation | Tree - fell into line | Insulator | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417511 | Sus | N | Vegetation¦Treefellintoline¦Insulator¦Broken
16-0019013 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2016-03-07 | 1424306 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0020909 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1429940 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
16-0026749 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2016-04-07 | 1446090 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0031889 | Animal | Squirrel | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2016-04-27 | 1459828 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
16-0034419 | Animal | Other | Recloser | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2016-05-06 | 1465877 | Sus | Y | Animal¦Other¦Recloser¦Burnedflashed
16-0041871 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 8 | 2016-06-08 | 1485222 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0046744 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 6 | 29 | 2016-06-29 | 1498422 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0054908 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 8 | 3 | 2016-08-03 | 1521198 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0056498 | Animal | Squirrel |  | Normal | 2016 | Tier 2 - Elevated | Transformer only | 8 | 11 | 2016-08-11 | 1524642 | Sus | Y | Animal¦Squirrel¦¦Normal
16-0057341 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2016-08-15 | 1526625 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
16-0069112 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 10 | 2 | 2016-10-02 | 1551687 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0072729 | Animal | Other | Crossarm, Wood | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562114 | Sus | Y | Animal¦Other¦CrossarmWood¦Burnedflashed
16-0074873 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2016-10-23 | 1568134 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
16-0077241 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2016-11-01 | 1574337 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0077821 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2016-11-03 | 1575979 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0078926 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2016-11-09 | 1578834 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
16-0079357 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2016-11-11 | 1579713 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0079766 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2016-11-14 | 1581085 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing
16-0079766 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 14 | 2016-11-14 | 1581085 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing
16-0083157 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2016 | Tier 2 - Elevated | Transformer only | 11 | 30 | 2016-11-30 | 1592080 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
16-0084376 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Contaminated | 2016 | Tier 3 - Extreme | Transformer only | 12 | 7 | 2016-12-07 | 1596155 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Contaminated
16-0086606 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2016-12-21 | 1608181 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0003166 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1615913 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
17-0004925 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622600 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005573 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628291 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0005794 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2017-01-08 | 1625679 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006050 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1630918 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006803 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634159 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007363 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1635359 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0008440 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 12 | 2017-01-12 | 1641410 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0008512 | Environmental/External | Flood/Erosion | Pole-Wood | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 12 | 2017-01-12 | 1641850 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Normal
17-0012014 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655730 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
17-0014476 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2017-01-24 | 1666077 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0015378 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2017-01-26 | 1667834 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0017916 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 6 | 2017-02-06 | 1676925 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0018828 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2017-02-08 | 1681229 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0023662 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1702537 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023852 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703538 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0024022 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705188 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0024539 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706072 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0025453 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1708955 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0032539 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2017-03-21 | 1732149 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0033377 | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 3 | 24 | 2017-03-24 | 1734345 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground
17-0035637 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2017-03-31 | 1741439 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0037442 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748168 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0039470 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 12 | 2017-04-12 | 1755887 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0041734 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 20 | 2017-04-20 | 1761891 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0042483 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2017-04-24 | 1766038 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0043533 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2017-04-27 | 1769048 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0044675 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 2 | 2017-05-02 | 1772673 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0045707 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2017-05-05 | 1775854 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0051303 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | 2017 | Tier 3 - Extreme | Transformer only | 5 | 29 | 2017-05-29 | 1792597 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Burnedflashed
17-0077897 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2017-09-11 | 1876190 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
17-0078320 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 12 | 2017-09-12 | 1877505 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0079536 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 17 | 2017-09-17 | 1880407 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
17-0085318 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1894687 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0085703 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Transformer only | 10 | 9 | 2017-10-09 | 1896000 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086335 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2017-10-10 | 1898318 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0086659 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2017-10-12 | 1899020 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0087541 | Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1901358 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Broken
17-0092603 | Animal | Squirrel | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2017-11-04 | 1915740 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
17-0094789 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2017-11-13 | 1921780 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0095417 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2017-11-16 | 1923465 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
17-0097677 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2017-11-27 | 1929638 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0101599 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2017-12-14 | 1942480 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0002995 | Animal | Squirrel | Transformer, STA SVC | Failed/Faulted | 2018 | Tier 2 - Elevated | Substation - Distribution | 1 | 2 | 2018-01-02 | 541 | Sus | N | Animal¦Squirrel¦TransformerSTASVC¦FailedFaulted
18-0003186 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2018-01-03 | 885 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0005660 | Animal | Squirrel | Recloser | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2018-01-12 | 7278 | Sus | N | Animal¦Squirrel¦Recloser¦FailedFaulted
18-0007480 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2018-01-19 | 10795 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
18-0015280 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2018-02-18 | 26869 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0017016 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2018-02-24 | 31068 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0018568 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 34434 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0029328 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 5 | 2018-04-05 | 60368 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
18-0032839 | Environmental/External | Lightning | Other | Broken | 2018 | Tier 2 - Elevated | Transformer only | 4 | 16 | 2018-04-16 | 68271 | Sus | N | EnvironmentalExternal¦Lightning¦Other¦Broken
18-0044551 | Animal | Other | Transformer (UG) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2018-05-25 | 94093 | Sus | Y | Animal¦Other¦Transformer(UG)¦Normal
18-0058680 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 10 | 2018-07-10 | 128625 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0064546 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2018-07-28 | 142250 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0067402 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 7 | 2018-08-07 | 150603 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0068518 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2018-08-09 | 152450 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0069824 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 14 | 2018-08-14 | 155354 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0071245 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2018-08-17 | 157223 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0071406 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2018-08-19 | 157916 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0079400 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2018-09-13 | 173808 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0079527 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 9 | 13 | 2018-09-13 | 173877 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0083808 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 26 | 2018-09-26 | 181863 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Together
18-0085405 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 1 | 2018-10-01 | 185296 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0094655 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2018-10-26 | 203029 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0100785 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217759 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101424 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218994 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102467 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2018-11-23 | 222522 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0103582 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 225207 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0110229 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2018-12-21 | 245012 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0005495 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 256307 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0007503 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2019-01-10 | 262380 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0008350 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2019-01-13 | 264205 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0010449 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 271355 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011114 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 274210 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0011832 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2019-01-18 | 275903 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0018024 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 290365 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018701 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292996 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0019247 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2019-02-06 | 294033 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020762 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298976 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
19-0021240 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2019-02-11 | 300242 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0021658 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301453 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0022321 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 304724 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0022513 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 304258 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0023240 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 309139 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024031 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 312097 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024253 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 308228 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0024732 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314596 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0025143 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 315874 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025204 | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 316325 | Sus | N | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Normal
19-0025268 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 315353 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0026299 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 19 | 2019-02-19 | 319291 | Sus | N | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
19-0027943 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2019-02-25 | 323275 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028205 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 323852 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0029044 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326439 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0029546 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 328298 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030122 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2019-03-02 | 329705 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030609 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2019-03-04 | 331059 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030633 | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2019-03-04 | 331115 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated
19-0034453 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2019-03-17 | 341220 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0035331 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2019-03-20 | 343971 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
19-0036724 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2019-03-25 | 347145 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0037601 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348706 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0038063 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2019-03-28 | 349655 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0038198 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2019-03-29 | 350029 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0038297 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 3 | 29 | 2019-03-29 | 350262 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0038626 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2019-03-31 | 351189 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
19-0042346 | Animal | Bird found | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2019-04-14 | 360661 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
19-0042829 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 16 | 2019-04-16 | 361657 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0043900 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2019-04-18 | 362893 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing
19-0044155 | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2019-04-18 | 363201 | Sus | N | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Broken
19-0055083 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2019-05-21 | 387471 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0057973 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2019-05-27 | 391265 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0060030 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2019-05-30 | 393558 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0069407 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2019-06-18 | 420660 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0079475 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 7 | 20 | 2019-07-20 | 463073 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Burnedflashed
19-0085483 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2019-08-08 | 491145 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0088175 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 15 | 2019-08-15 | 511500 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0102125 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2019-09-21 | 602548 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0109108 | Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2019-10-09 | 649315 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦CircuitBreaker¦Normal
19-0116644 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 683273 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0125541 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2019-11-17 | 708862 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0130115 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 720891 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0130947 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 721997 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131460 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724377 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0131482 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724467 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0133912 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 5 | 2019-12-05 | 730775 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
19-0134673 | Equipment Failure/Involved | Overhead | Transformer | On Ground | 2019 | Tier 2 - Elevated | Transformer only | 12 | 7 | 2019-12-07 | 732147 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦OnGround
19-0136054 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2019-12-11 | 736891 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137242 | Vegetation | Tree - grew into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 19 | 2019-12-19 | 746344 | Sus | N | Vegetation¦Treegrewintoline¦Fuse¦FailedFaulted
19-0138200 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2019-12-30 | 752237 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0138237 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2019 | Tier 2 - Elevated | Transformer only | 12 | 30 | 2019-12-30 | 752672 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
20-0007462 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2020-01-10 | 758963 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0011299 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2020-01-19 | 766285 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0011474 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2020-01-21 | 766935 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0019413 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2020 | Tier 2 - Elevated | Transformer only | 2 | 9 | 2020-02-09 | 785180 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
20-0019966 | Vegetation | Tree - fell into line | Service conductor | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782262 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
20-0024948 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Arcing | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2020-02-22 | 800816 | Sus | N | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Arcing
20-0025115 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2020-02-24 | 801217 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0027277 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 29 | 2020-02-29 | 819945 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
20-0028014 | Vegetation | Tree - grew into line | Secondary | Broken | 2020 | Tier 3 - Extreme | Transformer only | 3 | 3 | 2020-03-03 | 824054 | Sus | N | Vegetation¦Treegrewintoline¦Secondary¦Broken
20-0032462 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 853070 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0033634 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2020-03-18 | 857509 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033917 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 858447 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0035475 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2020 | Tier 2 - Elevated | Transformer only | 3 | 23 | 2020-03-23 | 862573 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
20-0042564 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2020-04-18 | 897488 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0046139 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2020-05-01 | 904957 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0048884 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 5 | 10 | 2020-05-10 | 910642 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0049240 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2020-05-11 | 911673 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0054840 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2020-05-27 | 923413 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0062646 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2020-06-18 | 941943 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0065559 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 26 | 2020-06-26 | 948393 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0067040 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2020-07-01 | 955507 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0085450 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2020-08-17 | 1014760 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0085970 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2020-08-17 | 1017286 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0096046 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 19 | 2020-08-19 | 1063539 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0096705 | Equipment Failure/Involved | Overhead |  | Broken | 2020 | Tier 2 - Elevated | Transformer only | 9 | 11 | 2020-09-11 | 1065282 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦Broken
20-0101924 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2020-09-27 | 1095528 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0105147 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 5 | 2020-10-05 | 1111261 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together
20-0112754 | Company Initiated | Return Circuit Normal | Conductor, Underground | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2020-11-06 | 1137385 | Sus | Y | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Normal
20-0113188 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1127408 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0117002 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2020-11-04 | 1135777 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0118069 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2020 | Tier 2 - Elevated | Transformer only | 11 | 6 | 2020-11-06 | 1137918 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
20-0122969 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2020-11-19 | 1149586 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
20-0128386 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167290 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0129537 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 12 | 10 | 2020-12-10 | 1177687 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0130668 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 12 | 15 | 2020-12-15 | 1189808 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0131093 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 18 | 2020-12-18 | 1193880 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0131463 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2020-12-22 | 1197064 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
20-0131733 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 12 | 25 | 2020-12-25 | 1198408 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0004921 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 1 | 4 | 2021-01-04 | 1204119 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0013241 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 1 | 23 | 2021-01-23 | 1221692 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013570 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223108 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013849 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224137 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
21-0013988 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224519 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0014752 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226433 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016141 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1231878 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0016165 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 1 | 26 | 2021-01-26 | 1228602 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0018660 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1242111 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0019314 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1241488 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0020202 | Equipment Failure/Involved | Overhead | Switch | Arcing | 2021 | Tier 2 - Elevated | Transmission line | 2 | 1 | 2021-02-01 | 1244548 | Sus | N | EquipmentFailureInvolved¦Overhead¦Switch¦Arcing
21-0020595 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1245452 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020879 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2021-02-02 | 1245782 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0022187 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2021-02-05 | 1248451 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0031872 | Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2021-03-03 | 1266469 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦LightningArrestor¦Burnedflashed
21-0041208 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 25 | 2021-03-25 | 1298404 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0041685 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2021-03-26 | 1300073 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
21-0050579 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 4 | 19 | 2021-04-19 | 1324094 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0051131 | 3rd Party | Other | Transformer (OH) |  | 2021 | Tier 2 - Elevated | Transformer only | 4 | 20 | 2021-04-20 | 1325868 | Sus | N | 3rdParty¦Other¦Transformer(OH)¦
21-0053762 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2021-04-27 | 1335109 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0059001 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 9 | 2021-05-09 | 1344326 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0060055 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2021-05-12 | 1346513 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0073732 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2021-06-14 | 1372332 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0073939 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2021-06-15 | 1374279 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0087628 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 10 | 2021-07-10 | 1398693 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0097929 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2021-07-31 | 1424450 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0104679 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 14 | 2021-08-14 | 1442960 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
21-0104807 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2021-08-15 | 1443377 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
21-0105255 | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2021-08-16 | 1444247 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦BurnedOpen
21-0108702 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Transformer only | 8 | 24 | 2021-08-24 | 1452040 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0113630 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 4 | 2021-09-04 | 1462019 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0114040 | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2021-09-07 | 1463399 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed
21-0115688 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2021-09-10 | 1467202 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
21-0116305 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 9 | 10 | 2021-09-10 | 1468612 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0124310 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Transformer only | 9 | 30 | 2021-09-30 | 1484155 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0125492 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2021-10-04 | 1486406 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
21-0126121 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2021-10-05 | 1487424 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
21-0128423 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492255 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0129486 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1495114 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
21-0132325 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 18 | 2021-10-18 | 1500568 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0133438 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2021-10-20 | 1502583 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135922 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509913 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0136103 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511375 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
21-0136695 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1515366 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
21-0138389 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1520843 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0140307 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2021-10-30 | 1526182 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0142119 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2021-11-04 | 1534681 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
21-0156490 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2021-12-10 | 1563498 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0158749 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573489 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0159741 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 12 | 19 | 2021-12-19 | 1577389 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160471 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2021-12-24 | 1580890 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0160809 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582731 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0161637 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588850 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161883 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1590093 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0005214 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1592537 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0007071 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2022-01-05 | 1596195 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0007775 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2022-01-09 | 1598703 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0010384 | Equipment Failure/Involved | Overhead | Secondary | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2022-01-16 | 1603701 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen
22-0012215 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607150 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0012263 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2022-01-21 | 1606915 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0030202 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 4 | 2022-03-04 | 1642664 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0030255 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2022-03-05 | 1642834 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0045491 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2022-04-11 | 1668445 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0058864 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2022-05-06 | 1689729 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0071068 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 7 | 2022-06-07 | 1721517 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0073279 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 3 - Extreme | Transformer only | 6 | 11 | 2022-06-11 | 1728777 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0075679 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2022-06-17 | 1734070 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed
22-0076641 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2022-06-21 | 1736839 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0078981 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 27 | 2022-06-27 | 1743306 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0085188 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2022-07-14 | 1755935 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
22-0091143 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2022-07-29 | 1767846 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0111722 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1815018 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0114585 | Animal | Squirrel | Pole-Wood | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2022-09-25 | 1821045 | Sus | Y | Animal¦Squirrel¦PoleWood¦Normal
22-0123849 | Company Initiated | Return Circuit Normal | Transformer | Normal | 2022 | Tier 3 - Extreme | Transformer only | 10 | 22 | 2022-10-22 | 1842701 | Sus | Y | CompanyInitiated¦ReturnCircuitNormal¦Transformer¦Normal
22-0129787 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2022-11-09 | 1859188 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0129816 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2022-11-09 | 1859363 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
22-0131059 | Company Initiated | Return Circuit Normal | Conductor, Underground | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2022-12-30 | 1902180 | Sus | N | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Normal
22-0131493 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2022-11-16 | 1863771 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0134128 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 25 | 2022-11-25 | 1869116 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0136249 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2022-12-03 | 1874844 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0138180 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880603 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139180 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1884213 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0141193 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2022-12-24 | 1896913 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0141846 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899961 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0142631 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1904907 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0010098 | Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1174721 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonground
15-0014797 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2015-02-22 | 1193778 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0014934 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2015-02-23 | 1194329 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0019713 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2015-03-16 | 1203963 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0025021 | Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2015-04-07 | 1215066 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonground
15-0032506 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230631 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0039873 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2015-06-09 | 1247991 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed
15-0040866 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2015 | Tier 2 - Elevated | Transformer only | 6 | 13 | 2015-06-13 | 1250432 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
15-0044082 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2015-06-29 | 1258860 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
15-0047974 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2015-07-16 | 1269057 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0049388 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2015-07-21 | 1274322 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0056677 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2015-08-21 | 1292831 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0061089 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1304989 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0063592 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2015-09-25 | 1311935 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
15-0070187 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2015-10-14 | 1321669 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0073699 | Equipment Failure/Involved | Overhead | Insulator | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 28 | 2015-10-28 | 1330272 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Normal
15-0074099 | Animal | Bird found | Pothead(Riser Termination) | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2015-10-29 | 1331176 | Sus | Y | Animal¦Birdfound¦Pothead(RiserTermination)¦Burnedflashed
15-0078650 | Equipment Failure/Involved | Overhead | Other | Broken | 2015 | Tier 2 - Elevated | Transformer only | 11 | 17 | 2015-11-17 | 1344174 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
15-0079878 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2015-11-21 | 1346486 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0084080 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 12 | 10 | 2015-12-10 | 1358131 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0084858 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361363 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086310 | Equipment Failure/Involved | Electrical Overload | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2015-12-20 | 1367113 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Cutoutfuseholder¦FailedFaulted
15-0086749 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1368812 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
15-0087498 | Vegetation | Tree - fell into line | Other | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2015-12-24 | 1370919 | Sus | N | Vegetation¦Treefellintoline¦Other¦Broken
15-0087624 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2015-12-28 | 1373164 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0003675 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2016-01-07 | 1379217 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0005798 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2016-01-16 | 1385147 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0005871 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385336 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0009566 | Vegetation | Tree - fell into line | Transformer | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 1 | 31 | 2016-01-31 | 1395439 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Burnedflashed
16-0009751 | 3rd Party | Other | Conductor, Overhead | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2016-02-01 | 1396295 | Sus | N | 3rdParty¦Other¦ConductorOverhead¦Broken
16-0013889 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2016 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2016-02-18 | 1408355 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
16-0016138 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 29 | 2016-02-29 | 1413463 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017374 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416235 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0017870 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418915 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018037 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418135 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0018046 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420049 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0018439 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 3 | 6 | 2016-03-06 | 1421190 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
16-0019870 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2016-03-10 | 1426333 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
16-0020054 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2016-03-10 | 1426720 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0020697 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1428957 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0020946 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430209 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0022928 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2016-03-21 | 1435193 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0023820 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2016-03-24 | 1437763 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0026325 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 5 | 2016-04-05 | 1444757 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0027725 | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2016-04-11 | 1448673 | Sus | N | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted
16-0028185 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2016-04-12 | 1449729 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0032131 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2016-04-27 | 1460566 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0035906 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 13 | 2016-05-13 | 1469273 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
16-0037513 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 20 | 2016-05-20 | 1473871 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0042075 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2016-06-09 | 1485682 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0048655 | Equipment Failure/Involved | Underground | Transformer | Broken | 2016 | Tier 2 - Elevated | Transformer only | 7 | 8 | 2016-07-08 | 1502850 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦Broken
16-0055342 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 8 | 5 | 2016-08-05 | 1522037 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
16-0055597 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 7 | 2016-08-07 | 1522802 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0056080 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2016-08-09 | 1523856 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072843 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562665 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0077093 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 31 | 2016-10-31 | 1574250 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0077177 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2016-11-01 | 1574603 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0085608 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2016-12-14 | 1602060 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0085854 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1603713 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0086229 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2016-12-18 | 1606004 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0086535 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 20 | 2016-12-20 | 1607480 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0086929 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2016-12-24 | 1610519 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0087054 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 26 | 2016-12-26 | 1611136 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
17-0004851 | Equipment Failure/Involved | Overhead | Jumper | Arcing | 2017 | Tier 3 - Extreme | Transformer only | 1 | 7 | 2017-01-07 | 1622191 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing
17-0004872 | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 1 | 7 | 2017-01-07 | 1622064 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground
17-0004889 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622402 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005190 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625486 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006646 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1633157 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0010376 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1647821 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011363 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653204 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011445 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653712 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011921 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655700 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0015895 | Animal | Other | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2017-01-29 | 1669819 | Sus | N | Animal¦Other¦ConductorOverhead¦Normal
17-0017618 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2017-02-05 | 1675588 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0017806 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2017-02-06 | 1676551 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0018622 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679906 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0019202 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1682645 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0019698 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1684114 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken
17-0022153 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1694634 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023913 | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703624 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground
17-0025099 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707680 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0028548 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 5 | 2017-03-05 | 1720336 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0028584 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720526 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0030619 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2017-03-14 | 1726617 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0035565 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2017-03-31 | 1741214 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0037244 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745973 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0037877 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1750633 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0040304 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 14 | 2017-04-14 | 1757633 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0043200 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2017-04-26 | 1768104 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0047959 | 3rd Party | Vehicle | Pole-Wood | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2017-05-15 | 1782187 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
17-0048467 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 17 | 2017-05-17 | 1783717 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0049340 | 3rd Party | Metallic Balloon | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2017-05-20 | 1786058 | Sus | Y | 3rdParty¦MetallicBalloon¦Fuse¦FailedFaulted
17-0054373 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 11 | 2017-06-11 | 1802104 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0060014 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2017-07-01 | 1822184 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0060629 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 5 | 2017-07-05 | 1824030 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0063038 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2017-07-14 | 1831713 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0066473 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2017-07-29 | 1842236 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal
17-0067207 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 2 | 2017-08-02 | 1844294 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0074457 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 31 | 2017-08-31 | 1864071 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0074931 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Transformer only | 9 | 1 | 2017-09-01 | 1865125 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0075276 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2017-09-02 | 1867115 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0075489 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2017-09-03 | 1867803 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0075892 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 4 | 2017-09-04 | 1870069 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0081594 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2017-09-25 | 1885557 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0085309 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893962 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0091371 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2017-10-30 | 1912539 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0092617 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2017-11-04 | 1915895 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0095394 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 11 | 15 | 2017-11-15 | 1923203 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0096955 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2017-11-21 | 1927445 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0103318 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2017-12-26 | 1951202 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0004975 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2018-01-10 | 5792 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0005981 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2018-01-13 | 7825 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0009070 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2018-01-25 | 14017 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0015705 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2018-02-20 | 27700 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
18-0016317 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2018-02-22 | 29286 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0016494 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2018-02-22 | 29526 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0017191 | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2018-02-26 | 31537 | Sus | N | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted
18-0019356 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2018-03-03 | 37256 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0022753 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 44062 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0031432 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 4 | 11 | 2018-04-11 | 64763 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0034884 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Transformer only | 4 | 24 | 2018-04-24 | 72612 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0035828 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2018-04-26 | 74354 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0036128 | Equipment Failure/Involved | Substation | Relay | Malfunctioning | 2018 | Tier 2 - Elevated | Substation - Transmission | 4 | 27 | 2018-04-27 | 75011 | Sus | N | EquipmentFailureInvolved¦Substation¦Relay¦Malfunctioning
18-0040519 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2018-05-12 | 84843 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0044636 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 26 | 2018-05-26 | 94502 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0044675 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2018-05-26 | 94605 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0045504 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2018-05-30 | 96627 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0049171 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2018-06-09 | 104872 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
18-0056036 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Transformer only | 6 | 30 | 2018-06-30 | 122024 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Normal
18-0056359 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2018-07-02 | 123126 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0074371 | Animal | Squirrel | Pothead(Riser Termination) | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2018-08-28 | 164142 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Burnedflashed
18-0098865 | Equipment Failure/Involved | Substation | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2018-11-11 | 213452 | Sus | Y | EquipmentFailureInvolved¦Substation¦Insulator¦Broken
18-0100034 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2018-11-15 | 215716 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
18-0100217 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2018-11-16 | 216398 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0100786 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2018-11-18 | 217735 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0101104 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218366 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102244 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2018-11-22 | 221692 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0102340 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2018-11-22 | 221843 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0104795 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 227840 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0108327 | Animal | Squirrel |  | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 12 | 10 | 2018-12-10 | 237289 | Sus | N | Animal¦Squirrel¦¦FailedFaulted
18-0110539 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 12 | 24 | 2018-12-24 | 246633 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0111172 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2018-12-31 | 249970 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0004642 | Vegetation | Tree - fell into line | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 253584 | Sus | N | Vegetation¦Treefellintoline¦Insulator¦Broken
19-0004772 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 3 - Extreme | Transformer only | 1 | 5 | 2019-01-05 | 253899 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0005957 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2019-01-07 | 259368 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
19-0006593 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2019-01-08 | 261048 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0009394 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 1 | 15 | 2019-01-15 | 266498 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0010154 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 270284 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0015630 | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2019-01-29 | 283439 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround
19-0017685 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289374 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦Normal
19-0018473 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292101 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0019597 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2019-02-07 | 295026 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0020585 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 297821 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0022299 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 304687 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0022416 | Animal | Bird found | Transformer (OH) | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 305141 | Sus | N | Animal¦Birdfound¦Transformer(OH)¦Normal
19-0022452 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 302898 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022510 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 13 | 2019-02-13 | 305407 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0023217 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 309054 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0023971 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 311922 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0024439 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 313514 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0025324 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 316545 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0032348 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2019-03-09 | 335298 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0042342 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2019-04-14 | 360649 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0045232 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2019-04-23 | 366325 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject
19-0046718 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2019-04-27 | 369259 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0049199 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 6 | 2019-05-06 | 374506 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0061567 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2019-06-02 | 395887 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0062774 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2019-06-04 | 397803 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0062775 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 6 | 4 | 2019-06-04 | 397783 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0064555 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 8 | 2019-06-08 | 401340 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0071984 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2019-06-25 | 428913 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0075412 | Equipment Failure/Involved | Overhead |  | Broken | 2019 | Tier 2 - Elevated | Transformer only | 7 | 8 | 2019-07-08 | 443080 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦Broken
19-0076574 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2019-07-11 | 445523 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0076966 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2019-07-12 | 447759 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0079192 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2019-07-19 | 461114 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0082201 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2019-07-29 | 474459 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0085310 | Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2019-08-07 | 490956 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Broken
19-0099775 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2019-09-16 | 584754 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0099781 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2019-09-16 | 585229 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0101513 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 19 | 2019-09-19 | 595788 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0115887 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 684483 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0117217 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2019-10-26 | 687124 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Brokenwireonground
19-0117452 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 688974 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0120501 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2019-11-03 | 698487 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0123664 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2019-11-11 | 704639 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0129933 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 719887 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0130399 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 718602 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0131476 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 30 | 2019-11-30 | 724358 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0132046 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2019-12-01 | 726421 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0133340 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2019-12-04 | 729686 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0010186 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 763146 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0010211 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 763291 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0010211 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 763291 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0010232 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 763185 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0014016 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2020-01-27 | 770901 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0019862 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 783861 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0020536 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2020-02-11 | 788257 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0023403 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2020-02-19 | 795275 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032366 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852506 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032670 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Transmission line | 3 | 16 | 2020-03-16 | 854221 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0033374 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Transmission line | 3 | 17 | 2020-03-17 | 856615 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0033737 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2020-03-18 | 857476 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033893 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 17 | 2020-03-17 | 857094 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0039003 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2020-04-06 | 885954 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0040854 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2020-04-13 | 894411 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0047532 | 3rd Party | Vehicle | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 5 | 2020-05-05 | 907562 | Sus | Y | 3rdParty¦Vehicle¦Transformer(OH)¦Broken
20-0048290 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 5 | 7 | 2020-05-07 | 909207 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0057621 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2020-06-04 | 930511 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0064167 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 945580 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0071064 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2020-07-12 | 963103 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
20-0081201 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 8 | 2020-08-08 | 984391 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0084615 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1009752 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0085136 | Vegetation | Tree - fell into line | Pole-Wood | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1012084 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Normal
20-0090266 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2020-08-26 | 1032584 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0090272 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1032614 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091986 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2020-09-01 | 1045412 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
20-0092189 | Company Initiated | Coordination failure | Other | Malfunctioning | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2020-09-01 | 1046014 | Sus | Y | CompanyInitiated¦Coordinationfailure¦Other¦Malfunctioning
20-0092901 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 9 | 2 | 2020-09-02 | 1050883 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0093643 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2020-09-05 | 1055494 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0094422 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1058925 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0103785 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 3 - Extreme | Transformer only | 10 | 1 | 2020-10-01 | 1103122 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0111160 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2020-10-22 | 1122836 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0113371 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2020-10-25 | 1127219 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0114070 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2020 | Tier 3 - Extreme | Transformer only | 10 | 27 | 2020-10-27 | 1130197 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
20-0119602 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2020-11-11 | 1141778 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0122201 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 17 | 2020-11-17 | 1148081 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0128371 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167295 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0131256 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transformer only | 12 | 19 | 2020-12-19 | 1195780 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0132231 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2020 | Tier 2 - Elevated | Transformer only | 12 | 29 | 2020-12-29 | 1200919 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
21-0004279 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2021-01-01 | 1202288 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0004840 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2021-01-04 | 1203977 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0010541 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1215489 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0010555 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214200 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0010794 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216627 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011134 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1217895 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0012734 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1221146 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0014477 | Vegetation | Tree - branch fell on line | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 1 | 25 | 2021-01-25 | 1225012 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦FailedFaulted
21-0015318 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1230339 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0017394 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1238203 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0018268 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2021-01-28 | 1240426 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0018365 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2021-01-29 | 1241475 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0019991 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1243878 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0022062 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2021-02-04 | 1248309 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0029348 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261721 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
21-0030156 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2021-02-26 | 1263151 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0034298 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2021-03-10 | 1276638 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0034580 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2021-03-10 | 1277220 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0034760 | Animal | Squirrel | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2021-03-10 | 1277360 | Sus | N | Animal¦Squirrel¦Transformer¦FailedFaulted
21-0036012 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2021-03-13 | 1280641 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0058671 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2021-05-07 | 1343267 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0066922 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 27 | 2021-05-27 | 1359984 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0068456 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2021-06-01 | 1363146 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0070415 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2021-06-05 | 1366350 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0071118 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2021-06-07 | 1367753 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0072889 | Vegetation | Tree - grew into line | Conductor, Overhead | Contaminated | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2021-06-10 | 1370398 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Contaminated
21-0078860 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2021-06-24 | 1383815 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0082843 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 6 | 30 | 2021-06-30 | 1389216 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0087429 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 7 | 10 | 2021-07-10 | 1397021 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0098276 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2021-08-01 | 1428314 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0100306 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2021-08-09 | 1438067 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0109397 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 25 | 2021-08-25 | 1453345 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0110525 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 28 | 2021-08-28 | 1456205 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0112519 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2021-09-02 | 1460611 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0117092 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2021-09-13 | 1471189 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
21-0120827 | Animal | Squirrel | Transformer (OH) | Normal | 2021 | Tier 3 - Extreme | Transformer only | 9 | 22 | 2021-09-22 | 1477697 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
21-0124128 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2021-09-30 | 1483841 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0131840 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 10 | 15 | 2021-10-15 | 1498632 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0135547 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2021-10-23 | 1507064 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136952 | Vegetation | Tree - fell into line | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1515946 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Broken
21-0137930 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2021-10-26 | 1520943 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0140813 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Zone 1 - HHZ | Distribution Circuit | 11 | 1 | 2021-11-01 | 1527263 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0143691 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2021-11-09 | 1538341 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0149672 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2021-11-22 | 1553187 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0157354 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1566863 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0157527 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568480 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0157860 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569703 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0158146 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569587 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158554 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573244 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0158809 | 3rd Party | Vehicle | Pole-Wood | On Ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574359 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦OnGround
21-0158913 | Equipment Failure/Involved | Overhead | Transformer | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 12 | 16 | 2021-12-16 | 1574407 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦BurnedOpen
21-0159823 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2021-12-20 | 1577991 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0160961 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584419 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005040 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591601 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
22-0005699 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2022-01-03 | 1594060 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0006500 | Environmental/External | Ice or snow | Transformer (OH) | Broken | 2022 | Tier 3 - Extreme | Transformer only | 1 | 5 | 2022-01-05 | 1595837 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Transformer(OH)¦Broken
22-0006747 | Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582879 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground
22-0007578 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2022-01-05 | 1595720 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0008507 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2022-01-11 | 1600195 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0013044 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2022-01-22 | 1609263 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0017282 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2022 | Tier 3 - Extreme | Transformer only | 2 | 1 | 2022-02-01 | 1618693 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
22-0019013 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2022-02-05 | 1621839 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0025061 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2022-02-22 | 1633488 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0025859 | Vegetation | Tree - branch fell on line | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2022-02-23 | 1634935 | Sus | N | Vegetation¦Treebranchfellonline¦Insulator¦Broken
22-0028482 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2022-03-02 | 1640212 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0044456 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2022-04-08 | 1665863 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
22-0044777 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2022-04-08 | 1666268 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0053791 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2022-04-24 | 1680453 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0059445 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2022-05-08 | 1691289 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0068110 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2022-05-31 | 1714229 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0068363 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2022-05-31 | 1714756 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
22-0075121 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 2 - Elevated | Transformer only | 6 | 16 | 2022-06-16 | 1733119 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0080868 | Vegetation | Tree - fell into line | Transformer (OH) | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 6 | 30 | 2022-06-30 | 1746811 | Sus | Y | Vegetation¦Treefellintoline¦Transformer(OH)¦Brokenwireonground
22-0085070 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2022-07-13 | 1755831 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0093272 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2022-08-03 | 1772245 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0100882 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2022-08-23 | 1788038 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100913 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2022-08-23 | 1788151 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
22-0101575 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2022-08-24 | 1790736 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0103551 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 8 | 30 | 2022-08-30 | 1794652 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0106392 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2022-09-06 | 1801698 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0111475 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 17 | 2022-09-17 | 1813288 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0114594 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2022-09-25 | 1821089 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0115353 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2022-09-27 | 1822732 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0131482 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2022-11-16 | 1863656 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0132399 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865152 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
22-0132716 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865714 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
22-0135753 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2022-12-01 | 1873398 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0141082 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2022-12-23 | 1896451 | Sus | N | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Broken
22-0141380 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2022-12-26 | 1897699 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0142461 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1902960 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0142657 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903931 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0009269 | Vegetation | Tree - fell into line | Transformer | On Ground | 2015 | Tier 3 - Extreme | Transformer only | 2 | 4 | 2015-02-04 | 1172076 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦OnGround
15-0010649 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1176263 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0012281 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1187089 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0025062 | Equipment Failure/Involved | Ice or snow | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2015-04-07 | 1214883 | Sus | N | EquipmentFailureInvolved¦Iceorsnow¦ConductorOverhead¦Normal
15-0026015 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 3 - Extreme | Transformer only | 4 | 11 | 2015-04-11 | 1217446 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0032797 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 5 | 7 | 2015-05-07 | 1231406 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0032908 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2015-05-08 | 1231630 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0033919 | Equipment Failure/Involved | Underground | Secondary | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 5 | 13 | 2015-05-13 | 1233973 | Sus | Y | EquipmentFailureInvolved¦Underground¦Secondary¦Burnedflashed
15-0038597 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2015-06-04 | 1243842 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
15-0038911 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2015-06-05 | 1244388 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0041205 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 6 | 15 | 2015-06-15 | 1251417 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0043915 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 29 | 2015-06-29 | 1258431 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0045405 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 3 | 2015-07-03 | 1262528 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0050803 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 27 | 2015-07-27 | 1277938 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0052452 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2015-08-03 | 1282104 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0054906 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2015 | Tier 3 - Extreme | Transformer only | 8 | 13 | 2015-08-13 | 1287621 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
15-0058480 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 31 | 2015-08-31 | 1297813 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0059557 | Animal | Squirrel | Cutout, fuse holder | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 6 | 2015-09-06 | 1300797 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Burnedflashed
15-0062405 | Animal | Bird found | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2015-09-20 | 1308985 | Sus | Y | Animal¦Birdfound¦Fuse¦Normal
15-0063650 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2015-09-25 | 1312057 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
15-0068457 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 10 | 6 | 2015-10-06 | 1317978 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0070498 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2015-10-15 | 1322382 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
15-0071222 | Environmental/External | Lightning | Other | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324006 | Sus | Y | EnvironmentalExternal¦Lightning¦Other¦Normal
15-0073705 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 27 | 2015-10-27 | 1330032 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0074450 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 31 | 2015-10-31 | 1331993 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0076921 | Equipment Failure/Involved | Other | Insulator | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2015-11-10 | 1338605 | Sus | Y | EquipmentFailureInvolved¦Other¦Insulator¦Burnedflashed
15-0077964 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342155 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0079571 | Equipment Failure/Involved | Substation | Switch | Broken | 2015 | Tier 2 - Elevated | Substation - Distribution | 11 | 20 | 2015-11-20 | 1346106 | Sus | Y | EquipmentFailureInvolved¦Substation¦Switch¦Broken
15-0081830 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 30 | 2015-11-30 | 1350950 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
15-0083847 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357168 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0083882 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357315 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0084240 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1358289 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0084687 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1360310 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0085042 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1362883 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
15-0085526 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2015-12-15 | 1364251 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0086192 | Animal | Squirrel | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 19 | 2015-12-19 | 1366689 | Sus | N | Animal¦Squirrel¦Fuse¦Normal
15-0087643 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2015-12-28 | 1373152 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0003753 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2016-01-07 | 1379488 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0004626 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2016 | Tier 2 - Elevated | Transformer only | 1 | 11 | 2016-01-11 | 1381811 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
16-0005158 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2016-01-13 | 1383063 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0005853 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2016-01-16 | 1385239 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0009750 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2016-02-01 | 1396284 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0013379 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406414 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
16-0013765 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408161 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0014331 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 20 | 2016-02-20 | 1409576 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0017818 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417980 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0018198 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420699 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0018967 | Company Initiated | Personnel, company | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2016-03-07 | 1423949 | Sus | N | CompanyInitiated¦Personnelcompany¦CrossarmWood¦Broken
16-0020980 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430215 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0021755 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2016-03-15 | 1432235 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0022748 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2016-03-20 | 1434682 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
16-0023479 | 3rd Party | Vehicle | Pole-Wood | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2016-03-23 | 1436789 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Normal
16-0023760 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2016-03-24 | 1437884 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0027570 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2016-04-10 | 1448111 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0029045 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2016-04-15 | 1451621 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0030788 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 22 | 2016-04-22 | 1456062 | Sus | N | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonground
16-0032106 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2016-04-27 | 1460402 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0034712 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2016-05-08 | 1466655 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0038591 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 25 | 2016-05-25 | 1477280 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0040691 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 2 | 2016-06-02 | 1481769 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0041653 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 6 | 7 | 2016-06-07 | 1484429 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0043255 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2016 | Tier 2 - Elevated | Transformer only | 6 | 14 | 2016-06-14 | 1488990 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
16-0059175 | Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2016-08-22 | 1530499 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Brokenwireonground
16-0065772 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2016-09-19 | 1544251 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0073136 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2016-10-17 | 1563975 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0074741 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2016-10-22 | 1567435 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0076652 | Animal | Squirrel | Jumper | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2016-10-29 | 1572559 | Sus | Y | Animal¦Squirrel¦Jumper¦Normal
16-0078066 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2016-11-04 | 1576513 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0082159 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 24 | 2016-11-24 | 1588385 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
16-0082159 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 24 | 2016-11-24 | 1588385 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
16-0082387 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589532 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
16-0084707 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2016-12-08 | 1597370 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0085652 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602283 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0003559 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1618123 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0003712 | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2017-01-04 | 1617919 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Brokenwireonground
17-0005437 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623944 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0005454 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2017-01-08 | 1627737 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006530 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632862 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0008507 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2017-01-12 | 1641719 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0010092 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1646384 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011219 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652574 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0011882 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655484 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0012806 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658604 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0013100 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660301 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0013536 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660997 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
17-0014870 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 25 | 2017-01-25 | 1667279 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0017296 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2017-02-03 | 1674073 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0017912 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2017-02-06 | 1676966 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0018163 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1678062 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0018354 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1678652 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018795 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679617 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019957 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720740 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
17-0021980 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1693622 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023325 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 17 | 2017-02-17 | 1691316 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0023451 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 19 | 2017-02-19 | 1701490 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
17-0025537 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 2 | 21 | 2017-02-21 | 1710500 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0026062 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2017-02-23 | 1711905 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028133 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2017-03-03 | 1718531 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦OnGround
17-0029427 | Equipment Failure/Involved | Electrical Overload | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 8 | 2017-03-08 | 1722537 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦FailedFaulted
17-0030829 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2017-03-14 | 1727334 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0032726 | Vegetation | Tree - fell into line | Service conductor | Broken | 2017 | Tier 3 - Extreme | Transformer only | 3 | 22 | 2017-03-22 | 1732695 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
17-0037121 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745488 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0038428 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2017-04-09 | 1753397 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0039951 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757060 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0048606 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 5 | 17 | 2017-05-17 | 1784013 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0053646 | Equipment Failure/Involved | Fire, pole | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2017-06-08 | 1799541 | Sus | Y | EquipmentFailureInvolved¦Firepole¦Insulator¦Broken
17-0055493 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2017-06-15 | 1805110 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
17-0055944 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 17 | 2017-06-17 | 1806791 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0055966 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 17 | 2017-06-17 | 1807049 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0058722 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 26 | 2017-06-26 | 1818554 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0075888 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2017-09-04 | 1870000 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0078440 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2017-09-13 | 1877950 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0087324 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 10 | 14 | 2017-10-14 | 1900507 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0088522 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2017-10-19 | 1903895 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0088953 | Vegetation | Tree - grew into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1905445 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Brokenwireonground
17-0089529 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2017-10-22 | 1907353 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
17-0090425 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2017-10-25 | 1909649 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0093547 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2017-11-08 | 1918268 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0094745 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 13 | 2017-11-13 | 1921420 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0096420 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2017-11-20 | 1926265 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0100991 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2017-12-10 | 1939888 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0101384 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2017-12-12 | 1941524 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0103338 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2017-12-26 | 1951448 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
17-0103657 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2017-12-30 | 1953297 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0013258 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2018-02-11 | 22818 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0014993 | Animal | Squirrel | Fuse | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2018-02-16 | 25974 | Sus | N | Animal¦Squirrel¦Fuse¦Normal
18-0019288 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2018-03-02 | 36870 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0023193 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2018-03-15 | 45080 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023683 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2018-03-17 | 46433 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023695 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2018-03-17 | 46471 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0029162 | 3rd Party | Other | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 4 | 2018-04-04 | 59463 | Sus | N | 3rdParty¦Other¦ConductorOverhead¦Normal
18-0031438 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2018 | Tier 2 - Elevated | Transformer only | 4 | 11 | 2018-04-11 | 64971 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
18-0031453 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2018-04-11 | 64718 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0032213 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2018-04-14 | 66711 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0036046 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2018-04-27 | 74749 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0042992 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2018 | Tier 3 - Extreme | Transformer only | 5 | 21 | 2018-05-21 | 90940 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
18-0044577 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2018-05-25 | 94257 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
18-0047079 | 3rd Party | Fire, house or bldg. | Conductor, Underground | Normal | 2018 | Tier 2 - Elevated | Transformer only | 6 | 4 | 2018-06-04 | 100890 | Sus | Y | 3rdParty¦Firehouseorbldg¦ConductorUnderground¦Normal
18-0049308 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2018-06-09 | 105508 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0049442 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2018-06-10 | 105849 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0055146 | Equipment Failure/Involved | Overhead | Stepdown | Broken | 2018 | Tier 3 - Extreme | Transformer only | 6 | 27 | 2018-06-27 | 119572 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Stepdown¦Broken
18-0057190 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2018-07-05 | 124934 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
18-0059840 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2018-07-14 | 131652 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0063758 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2018-07-25 | 140305 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0065579 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 31 | 2018-07-31 | 146299 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0067945 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 8 | 2018-08-08 | 151361 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal
18-0069044 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2018-08-12 | 153829 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0073193 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2018-08-24 | 161492 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0077755 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2018-09-08 | 170495 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
18-0081598 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2018-09-20 | 177894 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0083311 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2018-09-25 | 180905 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0084217 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2018-09-27 | 182769 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0086553 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2018-10-03 | 187756 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0091977 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2018-10-19 | 198566 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0092530 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2018-10-21 | 199502 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
18-0100453 | Environmental/External | Fire, Forest/Grass | Crossarm, Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 216959 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦CrossarmWood¦Burnedflashed
18-0106133 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 12 | 2 | 2018-12-02 | 231817 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0106718 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2018-12-04 | 233243 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0107270 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 5 | 2018-12-05 | 234194 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0107494 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2018-12-06 | 234709 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0003391 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2019-01-01 | 251246 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0004808 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2019-01-05 | 254256 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0006636 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2019-01-09 | 261160 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0009200 | Vegetation | Tree - fell into line | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2019-01-15 | 265969 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦Normal
19-0009518 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 1 | 16 | 2019-01-16 | 266616 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0011168 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 272796 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0011322 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 274703 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011475 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 272963 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0013655 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 1 | 23 | 2019-01-23 | 279678 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0016346 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 31 | 2019-01-31 | 284806 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0017100 | Vegetation | Tree - branch fell on line | Insulator | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286920 | Sus | N | Vegetation¦Treebranchfellonline¦Insulator¦Brokenwireonground
19-0017352 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287502 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0017512 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 288041 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018353 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292108 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0018679 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2019-02-05 | 292995 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0018724 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 293109 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
19-0018727 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 293118 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0019333 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 294675 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020326 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2019-02-09 | 296874 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0021744 | Vegetation | Tree - fell into line | Service conductor | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 302313 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Together
19-0023571 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 310413 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023926 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2019-02-15 | 311536 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
19-0024078 | Environmental/External | Ice or snow | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 312215 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Broken
19-0024709 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314892 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0025440 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 317037 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028469 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324866 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0031221 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2019-03-06 | 332574 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0031542 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2019-03-06 | 333335 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0033827 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2019-03-10 | 335402 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
19-0038397 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 29 | 2019-03-29 | 350443 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0039644 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 4 | 2019-04-04 | 353586 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0041059 | 3rd Party | Customer Equipment | Customer Equipment | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2019-04-09 | 356743 | Sus | N | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Together
19-0042248 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2019-04-13 | 360341 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0044696 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2019-04-21 | 364965 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0046815 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2019-04-27 | 369381 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0052315 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2019-05-15 | 381394 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0054882 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 21 | 2019-05-21 | 386939 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0057622 | Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2019-05-25 | 390221 | Sus | Y | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal
19-0059172 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2019-05-29 | 392835 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0060959 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2019-05-31 | 394756 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0061068 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 31 | 2019-05-31 | 394806 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0061216 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2019-06-01 | 395408 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0074636 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 4 | 2019-07-04 | 441018 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0076519 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2019-07-11 | 445382 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0079343 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2019-07-19 | 462353 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0082554 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2019-07-30 | 475494 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Brokenwireonobject
19-0084386 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2019-08-05 | 484153 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0085049 | 3rd Party | Vehicle | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2019-08-07 | 487620 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Together
19-0085527 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2019-08-08 | 491477 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0086406 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2019-08-09 | 498083 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0090935 | 3rd Party | Fire, house or bldg. | Secondary | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2019-08-22 | 531276 | Sus | Y | 3rdParty¦Firehouseorbldg¦Secondary¦Burnedflashed
19-0091077 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2019-08-22 | 532597 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0095407 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2019-09-04 | 553816 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0110877 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 10 | 12 | 2019-10-12 | 655434 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0112152 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2019-10-16 | 660050 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0115374 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2019-10-23 | 679262 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0126615 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 20 | 2019-11-20 | 710634 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0129981 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 720166 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0130254 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 719705 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130853 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 722874 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0130858 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 719126 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0133282 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2019-12-04 | 729344 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0135010 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2019-12-08 | 733626 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137204 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 19 | 2019-12-19 | 746070 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0137870 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2019-12-25 | 750112 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0137960 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2019-12-26 | 750609 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
19-0138278 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2019-12-31 | 752983 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0018847 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2020-02-08 | 780747 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0019569 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 784247 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0021977 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2020-02-13 | 790356 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0027531 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2020-03-01 | 820853 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0029490 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2020-03-06 | 836214 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032253 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852104 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
20-0032642 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 854044 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0033026 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855693 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0033253 | Unknown Cause | Patrol - not conducted | Customer Equipment | Malfunctioning | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2020-03-15 | 856452 | Sus | N | UnknownCause¦Patrolnotconducted¦CustomerEquipment¦Malfunctioning
20-0033534 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2020-03-17 | 857096 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0033936 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 18 | 2020-03-18 | 858549 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0034361 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2020-03-19 | 859098 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0035669 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2020-03-24 | 863215 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0037012 | Vegetation | Tree - fell into line | Transformer | Leaking | 2020 | Tier 2 - Elevated | Transformer only | 3 | 29 | 2020-03-29 | 869263 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Leaking
20-0037663 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 1 | 2020-04-01 | 875818 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
20-0042496 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 4 | 17 | 2020-04-17 | 897300 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0042514 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 18 | 2020-04-18 | 897366 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0046234 | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2020-05-01 | 905101 | Sus | Y | 3rdParty¦Treecutting3rdparty¦PoleWood¦Broken
20-0049822 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2020 | Tier 3 - Extreme | Transformer only | 5 | 13 | 2020-05-13 | 913127 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
20-0050958 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 16 | 2020-05-16 | 914905 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0051656 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2020-05-18 | 917207 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0057581 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2020-06-04 | 930528 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0060781 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 12 | 2020-06-12 | 938106 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0061025 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2020-06-14 | 938804 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0064617 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2020-06-24 | 946569 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0065102 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2020-06-25 | 947504 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0065766 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 27 | 2020-06-27 | 949159 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0068425 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2020-07-05 | 957993 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0071021 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 7 | 12 | 2020-07-12 | 963023 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0072382 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Transformer only | 7 | 15 | 2020-07-15 | 965467 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0077301 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2020-07-29 | 974112 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0078841 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2020-08-02 | 977075 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0084118 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2020-08-15 | 1003748 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0085073 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1013244 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0085882 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1016967 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0088964 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2020-08-22 | 1027303 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0089378 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 24 | 2020-08-24 | 1028441 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0091298 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2020-08-29 | 1039553 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0094734 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2020-09-08 | 1060222 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
20-0096960 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1067314 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0099650 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1085673 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100351 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1088615 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100726 | Environmental/External | Fire, Forest/Grass | Other | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2020-08-19 | 1090495 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Other¦Deteriorated
20-0105006 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2020-10-04 | 1111036 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0106189 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 10 | 7 | 2020-10-07 | 1112837 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0108713 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 10 | 14 | 2020-10-14 | 1117294 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0112231 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2020-10-23 | 1124140 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
20-0112824 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1125931 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0118200 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2020-11-07 | 1138493 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0121685 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 17 | 2020-11-17 | 1146772 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0122450 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 18 | 2020-11-18 | 1148552 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0122953 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2020-11-19 | 1149334 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
20-0125554 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2020-11-28 | 1155420 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0130291 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2020-12-14 | 1183025 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0130974 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2020-12-17 | 1192964 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0131882 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2020-12-26 | 1198947 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0132272 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 12 | 30 | 2020-12-30 | 1201315 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0006546 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2021-01-08 | 1206793 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011127 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1217999 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011298 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2021-01-20 | 1218215 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0013892 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223848 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0014462 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1225617 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
21-0015545 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232251 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0015598 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232369 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
21-0015598 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232369 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
21-0016209 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234322 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0018667 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1242454 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0019295 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1243189 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0021881 | Vegetation | Tree - branch fell on line | Transformer | Broken | 2021 | Tier 3 - Extreme | Transformer only | 2 | 4 | 2021-02-04 | 1247949 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦Broken
21-0030219 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2021-02-27 | 1263382 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0035847 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 12 | 2021-03-12 | 1280034 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0036307 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 14 | 2021-03-14 | 1282309 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0040790 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2021-03-25 | 1296693 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0042391 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2021-03-29 | 1302891 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0047498 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2021-04-12 | 1313481 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0050056 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2021-04-18 | 1321976 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0052034 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 22 | 2021-04-22 | 1328863 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0055718 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 5 | 1 | 2021-05-01 | 1338540 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
21-0059932 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 11 | 2021-05-11 | 1346271 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal
21-0060370 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2021-05-12 | 1347119 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0087481 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 7 | 10 | 2021-07-10 | 1398146 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0088605 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2021-07-13 | 1402596 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0088605 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2021-07-13 | 1402596 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0090463 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2021-07-15 | 1405643 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0091859 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2021-07-19 | 1408136 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0100124 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 5 | 2021-08-05 | 1434436 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0115679 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2021-09-09 | 1466819 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0116106 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 10 | 2021-09-10 | 1467196 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0128431 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492027 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0129017 | Vegetation | Tree - fell into line | Bushing | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1493473 | Sus | Y | Vegetation¦Treefellintoline¦Bushing¦Broken
21-0131595 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2021-10-15 | 1498262 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
21-0132038 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499598 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0134670 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2021-10-21 | 1504829 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
21-0136848 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1516805 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0137857 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2021-10-26 | 1520800 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0140189 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2021-10-30 | 1525967 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0140805 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2021-11-01 | 1527384 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0143079 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 6 | 2021-11-06 | 1536502 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0147386 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Transmission line | 11 | 17 | 2021-11-17 | 1548502 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0161555 | Environmental/External | Ice or snow | Recloser | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588429 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Recloser¦Normal
21-0161716 | Vegetation | Tree - grew into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2021-12-30 | 1589307 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Brokenwireonground
22-0005223 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Transformer only | 1 | 2 | 2022-01-02 | 1592454 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0005943 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2022-01-04 | 1594715 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
22-0006764 | 3rd Party | Customer Equipment | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2022-01-06 | 1596505 | Sus | N | 3rdParty¦CustomerEquipment¦Fuse¦BurnedOpen
22-0007080 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1596906 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0007538 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1597627 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0008208 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2022-01-10 | 1599505 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken
22-0012224 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2022-01-21 | 1606800 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0014023 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2022-01-25 | 1611783 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0015172 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2022-01-27 | 1613804 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0019311 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2022-02-07 | 1622740 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0025665 | Equipment Failure/Involved | Underground | Secondary | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 2 | 23 | 2022-02-23 | 1634766 | Sus | N | EquipmentFailureInvolved¦Underground¦Secondary¦Deteriorated
22-0026064 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 2 | 24 | 2022-02-24 | 1635198 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0030452 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 3 | 6 | 2022-03-06 | 1643455 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0038985 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2022-03-27 | 1656652 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0043542 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 4 | 6 | 2022-04-06 | 1664170 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0045533 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2022-04-11 | 1668876 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0060962 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 5 | 11 | 2022-05-11 | 1694148 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0075562 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2022-06-17 | 1733930 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0075945 | 3rd Party | Customer Equipment | Conductor, Underground | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 18 | 2022-06-18 | 1734803 | Sus | Y | 3rdParty¦CustomerEquipment¦ConductorUnderground¦Broken
22-0078207 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2022-06-24 | 1741247 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0081437 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2022-07-02 | 1748017 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0084535 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Transformer only | 7 | 13 | 2022-07-13 | 1754810 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
22-0085962 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2022-07-15 | 1757220 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0086182 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 7 | 16 | 2022-07-16 | 1757960 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0088949 | Animal | Squirrel | Fuse | Burned Open | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 23 | 2022-07-23 | 1763834 | Sus | Y | Animal¦Squirrel¦Fuse¦BurnedOpen
22-0089945 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2022-07-26 | 1766063 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0093501 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2022-08-04 | 1772838 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0095027 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 8 | 2022-08-08 | 1776148 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0097347 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2022-08-14 | 1780797 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100215 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2022-08-21 | 1786656 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0100435 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2022-08-22 | 1787306 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100886 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 8 | 23 | 2022-08-23 | 1787758 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0103564 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 8 | 30 | 2022-08-30 | 1794789 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0116884 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2022-10-01 | 1825415 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0123686 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2022-10-21 | 1842278 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0124077 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2022-10-23 | 1843501 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0128415 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2022-11-07 | 1855742 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0134419 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2022-11-28 | 1870284 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0138465 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882791 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
22-0138609 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1881342 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0140199 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2022-12-15 | 1890467 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
22-0140751 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | 2022 | Tier 2 - Elevated | Transformer only | 12 | 20 | 2022-12-20 | 1894172 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken
22-0140801 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 20 | 2022-12-20 | 1894528 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0141923 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2022-12-28 | 1900281 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0142562 | Environmental/External | Flood/Erosion | Transformer (OH) | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903835 | Sus | N | EnvironmentalExternal¦FloodErosion¦Transformer(OH)¦Normal
22-0142624 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903819 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
23-0004311 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1907978 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
15-0006538 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 1 | 23 | 2015-01-23 | 1167567 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0009869 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1173389 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
15-0010677 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1177547 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0010883 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1179792 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0010891 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Transformer only | 2 | 6 | 2015-02-06 | 1175387 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0012121 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2015-02-09 | 1186349 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0014979 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2015-02-23 | 1194429 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0018393 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Transformer only | 3 | 9 | 2015-03-09 | 1201229 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0019624 | Animal | Bird found | Conductor, Overhead | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2015-03-14 | 1203585 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Broken
15-0025002 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2015-04-07 | 1215132 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0032433 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230510 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
15-0037434 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2015 | Tier 2 - Elevated | Transformer only | 5 | 30 | 2015-05-30 | 1241452 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
15-0040970 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 15 | 2015-06-15 | 1250904 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0045591 | Vegetation | Tree - fell into line | Secondary | Together | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2015-07-05 | 1263293 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Together
15-0046637 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2015-07-09 | 1265770 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0048525 | Environmental/External | Lightning |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 18 | 2015-07-18 | 1270293 | Sus | Y | EnvironmentalExternal¦Lightning¦¦FailedFaulted
15-0049302 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 20 | 2015-07-20 | 1274201 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0050048 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 23 | 2015-07-23 | 1276064 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0052250 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2015-08-03 | 1281883 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0060342 | Animal | Bird found | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1303032 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
15-0062003 | Environmental/External | Fire, Forest/Grass | Secondary | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 9 | 11 | 2015-09-11 | 1307789 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Secondary¦Burnedflashed
15-0062439 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1309160 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062768 | Animal | Squirrel | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2015-09-22 | 1310218 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0067763 | Unknown Cause | Patrol - found nothing | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2015-10-04 | 1316507 | Sus | Y | UnknownCause¦Patrolfoundnothing¦Transformer¦FailedFaulted
15-0067978 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2015-10-05 | 1316983 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0069437 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 10 | 2015-10-10 | 1319997 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0077687 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2015-11-13 | 1340706 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0083070 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 6 | 2015-12-06 | 1354825 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
15-0084650 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1360465 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0084894 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361650 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0085044 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1362856 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086769 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369330 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
15-0087863 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 3 - Extreme | Transformer only | 12 | 30 | 2015-12-30 | 1374860 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0003008 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2016-01-05 | 1377274 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0005890 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385452 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0011003 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2016-02-05 | 1399159 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0011182 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2016-02-07 | 1399867 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0011552 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2016-02-09 | 1400699 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
16-0013829 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408427 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013998 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408857 | Sus | N | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
16-0014001 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408884 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017655 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417737 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0019875 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2016-03-10 | 1426292 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0021011 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430358 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0021129 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2016-03-14 | 1430816 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0021639 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2016-03-15 | 1431859 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0027512 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2016-04-09 | 1447961 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0030393 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 21 | 2016-04-21 | 1455339 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0030954 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2016-04-23 | 1456801 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0032899 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 30 | 2016-04-30 | 1462313 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0037516 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 20 | 2016-05-20 | 1473931 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0039521 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2016-05-28 | 1478496 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0042736 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2016-06-12 | 1487690 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
16-0048056 | Equipment Failure/Involved | Overhead | Switch (OH) | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2016-08-25 | 1532277 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Burnedflashed
16-0051691 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 21 | 2016-07-21 | 1513898 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0059785 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | 2016 | Tier 3 - Extreme | Transformer only | 8 | 24 | 2016-08-24 | 1531588 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken
16-0060436 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2016-08-27 | 1532872 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0066438 | Environmental/External | Lightning | Lightning Arrestor | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2016-09-21 | 1545746 | Sus | Y | EnvironmentalExternal¦Lightning¦LightningArrestor¦Burnedflashed
16-0086237 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2016 | Tier 2 - Elevated | Transformer only | 12 | 18 | 2016-12-18 | 1606083 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
17-0002962 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1615561 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0005077 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624454 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0005235 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625921 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
17-0005320 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626791 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005499 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 8 | 2017-01-08 | 1624399 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
17-0005912 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1630335 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0006107 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625129 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0006463 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623812 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0006824 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 |  | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007217 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637018 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0008425 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 12 | 2017-01-12 | 1641352 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0008514 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 1 | 12 | 2017-01-12 | 1641592 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
17-0011420 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652881 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013124 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660916 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013999 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664775 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0016802 | Vegetation | Tree - fell into line | Transformer | On Ground | 2017 | Tier 2 - Elevated | Transformer only | 2 | 2 | 2017-02-02 | 1672626 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦OnGround
17-0018491 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679861 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0022791 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1691120 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0022811 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1697192 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0022905 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2017-02-18 | 1699084 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024707 | Environmental/External | Flood/Erosion | Other | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1706952 | Sus | N | EnvironmentalExternal¦FloodErosion¦Other¦Normal
17-0024727 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706528 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0025065 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705272 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025246 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1708756 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025286 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 21 | 2017-02-21 | 1709216 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0031381 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2017-03-16 | 1728684 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0032116 | Animal | Other | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2017-03-20 | 1731230 | Sus | N | Animal¦Other¦ConductorOverhead¦Normal
17-0033400 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2017-03-24 | 1734429 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0045079 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 3 - Extreme | Transformer only | 5 | 3 | 2017-05-03 | 1774004 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0049584 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2017-05-22 | 1787344 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0049763 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 22 | 2017-05-22 | 1787918 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0052492 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2017-06-03 | 1796008 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0054433 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2017-06-12 | 1802327 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0057567 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2017-06-21 | 1814506 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0058882 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 27 | 2017-06-27 | 1818982 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0067328 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2017-08-02 | 1844564 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
17-0069441 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2017-08-10 | 1850031 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0073823 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2017-08-29 | 1862552 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
17-0073898 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2017-08-29 | 1862588 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0083544 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Leaking | 2017 | Tier 2 - Elevated | Transformer only | 10 | 2 | 2017-10-02 | 1889621 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Leaking
17-0086188 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 10 | 2017-10-10 | 1898034 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086200 | Environmental/External | Fire, Forest/Grass | Elbow | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1898095 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Elbow¦FailedFaulted
17-0086408 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2017-10-10 | 1897824 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0087316 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2017-10-14 | 1900663 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0087453 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2017-10-15 | 1901070 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
17-0088579 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2017-10-19 | 1903899 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0088697 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1904437 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0089982 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2017-10-24 | 1908525 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
17-0090563 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2017-10-26 | 1910029 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0092321 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2017-11-03 | 1914875 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0092558 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2017-11-03 | 1915540 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0094300 | Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2017-11-10 | 1920146 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Broken
17-0094526 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 12 | 2017-11-12 | 1920916 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0094598 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2017-11-13 | 1921093 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0097733 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2017-11-27 | 1929813 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0097819 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2017-11-27 | 1930053 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0103319 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2017-12-26 | 1951218 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0103667 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2017-12-30 | 1953364 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0004393 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2018-01-08 | 4048 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0019614 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 38156 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0022804 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 14 | 2018-03-14 | 44120 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
18-0023805 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2018-03-17 | 46994 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
18-0025578 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 50810 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0025775 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 22 | 2018-03-22 | 51188 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0033530 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2018 | Tier 2 - Elevated | Transformer only | 4 | 18 | 2018-04-18 | 69627 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
18-0036444 | Animal | Bird found | Pole-Wood | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 28 | 2018-04-28 | 75794 | Sus | N | Animal¦Birdfound¦PoleWood¦Normal
18-0036675 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 29 | 2018-04-29 | 76345 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0039960 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2018-05-10 | 83241 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0045396 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2018-05-29 | 96185 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0054222 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 25 | 2018-06-25 | 117611 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together
18-0055858 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2018-06-30 | 121550 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
18-0065129 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 145314 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
18-0067651 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2018-08-07 | 151002 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal
18-0068778 | 3rd Party | Other | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Transformer only | 8 | 10 | 2018-08-10 | 152987 | Sus | Y | 3rdParty¦Other¦Transformer(OH)¦Normal
18-0072178 | Animal | Squirrel | Insulator | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2018-08-21 | 159619 | Sus | Y | Animal¦Squirrel¦Insulator¦Normal
18-0078810 | 3rd Party | Customer Equipment | Recloser | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2018-09-11 | 172755 | Sus | Y | 3rdParty¦CustomerEquipment¦Recloser¦FailedFaulted
18-0084012 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2018-09-27 | 182249 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0084998 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 30 | 2018-09-30 | 184556 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0086488 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2018-10-03 | 187829 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0088139 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 7 | 2018-10-07 | 190308 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0091674 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 18 | 2018-10-18 | 197936 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦¦
18-0105605 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2018-11-30 | 230273 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0108090 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2018-12-08 | 236341 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109600 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2018-12-17 | 242036 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0110315 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2018-12-22 | 245452 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0110338 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2018-12-22 | 245672 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0005118 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255405 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
19-0005932 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 256499 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009720 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 1 | 16 | 2019-01-16 | 266882 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0009925 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 267446 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0010833 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 272681 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011324 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 273882 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0011389 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 269281 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0011626 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 274361 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
19-0016836 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 285901 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0017125 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286569 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017401 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287472 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0019029 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294017 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0022803 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 306748 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0023052 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 307903 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0024145 | Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 312440 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground
19-0024376 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2019-02-15 | 313214 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025136 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315550 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
19-0026553 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 20 | 2019-02-20 | 319859 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0028010 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2019-02-25 | 323549 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0029222 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 327675 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030513 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2019-03-04 | 330860 | Sus | N | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal
19-0034403 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 3 - Extreme | Transformer only | 3 | 16 | 2019-03-16 | 340848 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
19-0035389 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2019-03-21 | 344595 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0035921 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2019-03-21 | 344998 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0037598 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348792 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0037677 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 3 | 27 | 2019-03-27 | 349018 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0040291 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2019-04-06 | 354854 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0041301 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2019-04-10 | 357973 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
19-0044584 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2019-04-20 | 364491 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0045492 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2019-04-24 | 366774 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0052611 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2019-05-16 | 382168 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0054016 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2019-05-19 | 385155 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0063225 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2019-06-05 | 398494 | Sus | Y | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken
19-0068613 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2019-06-17 | 417578 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0075354 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2019-07-08 | 442920 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0080027 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 7 | 22 | 2019-07-22 | 468464 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0080125 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2019-07-23 | 468673 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0080798 | Animal | Squirrel | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 24 | 2019-07-24 | 470475 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
19-0081934 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2019-07-28 | 473838 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0082582 | Animal | Squirrel | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2019-07-30 | 475239 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
19-0086432 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2019-08-09 | 498086 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0088033 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2019-08-14 | 511180 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0092341 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2019-08-26 | 540454 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
19-0094450 | Animal | Bird found | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2019-09-01 | 550456 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
19-0100454 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 9 | 17 | 2019-09-17 | 589069 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
19-0115003 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2019-10-23 | 677864 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
19-0128066 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2019-11-23 | 713688 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0128110 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 11 | 24 | 2019-11-24 | 713901 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0129754 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 716168 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0130220 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 11 | 27 | 2019-11-27 | 720503 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
19-0137958 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2019-12-26 | 750595 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0004913 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2020-01-03 | 754430 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0007083 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2020-01-10 | 758302 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0019287 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 784299 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0022118 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2020-02-14 | 790763 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0029076 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2020-03-05 | 832052 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0030836 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2020-03-11 | 843793 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0034183 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 858543 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0036885 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2020-03-28 | 869012 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0045755 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2020-04-29 | 904130 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0050972 | Equipment Failure/Involved | Electrical Overload | Transformer | Deteriorated | 2020 | Tier 2 - Elevated | Transformer only | 5 | 17 | 2020-05-17 | 915112 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Deteriorated
20-0057695 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2020-06-04 | 930751 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
20-0057780 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2020-06-04 | 930968 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0058844 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2020-06-08 | 934180 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0063394 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 6 | 21 | 2020-06-21 | 943621 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0063414 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 21 | 2020-06-21 | 943778 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
20-0063496 | Animal | Other | Pole-Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2020-06-22 | 944077 | Sus | Y | Animal¦Other¦PoleWood¦Deteriorated
20-0065389 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 26 | 2020-06-26 | 948019 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0078204 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2020-07-31 | 975778 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0081217 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 8 | 2020-08-08 | 984853 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0086787 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2020-08-18 | 1018797 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0091894 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1045022 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0099635 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2020-09-21 | 1085593 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0100568 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1089288 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0103740 | Vegetation | Tree - branch fell on line | Transformer | Broken | 2020 | Tier 2 - Elevated | Transformer only | 9 | 30 | 2020-09-30 | 1102819 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Broken
20-0109586 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2020-10-15 | 1119019 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0110995 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2020-10-20 | 1121970 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0117677 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2020-11-06 | 1137202 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0118387 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2020-11-08 | 1139063 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0121293 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 16 | 2020-11-16 | 1146173 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
20-0125380 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2020-11-26 | 1154748 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0131289 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2020-12-20 | 1196077 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0131926 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2020-12-27 | 1199373 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0004930 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2021-01-04 | 1204148 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0007785 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2021-01-12 | 1209073 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0010120 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214097 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
21-0011173 | Vegetation | Tree - branch fell on line | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2021-01-19 | 1216839 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦BurnedOpen
21-0011219 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1218138 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0011746 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 20 | 2021-01-20 | 1219201 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
21-0016000 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234733 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016231 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1228380 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0016730 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237063 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0017119 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1238366 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0017125 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1238518 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0018474 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2021-01-29 | 1241234 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020014 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 1 | 31 | 2021-01-31 | 1243956 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0023088 | Animal | Squirrel | Bushing | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2021-02-08 | 1250760 | Sus | N | Animal¦Squirrel¦Bushing¦Burnedflashed
21-0025991 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 2 | 16 | 2021-02-16 | 1255947 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0032959 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2021-03-05 | 1270557 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0033076 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2021-03-06 | 1271106 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
21-0033160 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2021-03-07 | 1272711 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0034638 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2021-03-10 | 1277147 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0035576 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2021-03-11 | 1279410 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0039912 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2021-03-23 | 1294133 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0041748 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 27 | 2021-03-27 | 1300254 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0041831 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2021-03-27 | 1300819 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0042474 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transmission line | 3 | 30 | 2021-03-30 | 1302960 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0045052 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2021-04-06 | 1307457 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0045452 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2021-04-06 | 1307858 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0052970 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2021-04-25 | 1333758 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0053936 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2021-04-27 | 1335549 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0057318 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 5 | 2021-05-05 | 1341697 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0059511 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2021-05-10 | 1345416 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0064113 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2021-05-20 | 1354714 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0065967 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2021-05-25 | 1358597 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0080756 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2021-06-28 | 1386419 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0084157 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2021-07-02 | 1390560 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0093968 | Company Initiated | Improper Construction | Transformer (UG) | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2021-07-23 | 1412173 | Sus | Y | CompanyInitiated¦ImproperConstruction¦Transformer(UG)¦Normal
21-0106029 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Transmission line | 8 | 17 | 2021-08-17 | 1446048 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0108006 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2021-08-22 | 1450270 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0110043 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2021-08-27 | 1455216 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0119616 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2021 | Tier 2 - Elevated | Transformer only | 9 | 19 | 2021-09-19 | 1475661 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
21-0125118 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2021-10-02 | 1485280 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0126264 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2021-10-05 | 1487415 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
21-0129330 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2021-10-11 | 1494915 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0130198 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2021-10-13 | 1496396 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
21-0134109 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2021-10-20 | 1503637 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136321 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512922 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136452 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513986 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136452 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513986 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0137063 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 25 | 2021-10-25 | 1517452 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0145725 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2021-11-15 | 1545120 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0156763 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2021-12-12 | 1564988 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0157340 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1567676 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
21-0158237 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1571628 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161081 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585652 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161165 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1586017 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0161181 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585323 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161391 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585744 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0161435 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2021 | Tier 3 - Extreme | Transformer only | 12 | 28 | 2021-12-28 | 1586694 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing
21-0161619 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1588773 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005077 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2021-12-31 | 1590333 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0008224 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2022-01-10 | 1599674 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
22-0008593 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2022-01-11 | 1600096 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0013348 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2022-01-24 | 1610211 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
22-0034319 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 3 | 15 | 2022-03-15 | 1649234 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0042269 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 4 | 4 | 2022-04-04 | 1662268 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0043953 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2022-04-07 | 1665186 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0045137 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2022-04-10 | 1667508 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0054046 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2022-04-25 | 1681005 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0054266 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2022-04-25 | 1681281 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0065622 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 5 | 24 | 2022-05-24 | 1708849 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
22-0075962 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 6 | 18 | 2022-06-18 | 1734847 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0079341 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2022-06-28 | 1744127 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0081938 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2022-07-05 | 1749375 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0085219 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2022-07-14 | 1755951 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0086039 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2022-07-15 | 1757515 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0089192 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 24 | 2022-07-24 | 1764572 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
22-0095849 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 8 | 10 | 2022-08-10 | 1777676 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0095910 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 8 | 10 | 2022-08-10 | 1777782 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0098935 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2022-08-17 | 1783890 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0111696 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1814743 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0115547 | 3rd Party | Vehicle | Pole-Wood | On Ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2022-09-27 | 1822998 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦OnGround
22-0126759 | Equipment Failure/Involved | Overhead | Booster | Arcing | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1850887 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Booster¦Arcing
22-0128806 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1856699 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0133497 | Company Initiated | Construction Activity/equip, company | Transformer | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2022-12-13 | 1888545 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Broken
22-0134230 | 3rd Party | Other | Transformer | Malfunctioning | 2022 | Tier 2 - Elevated | Transformer only | 11 | 26 | 2022-11-26 | 1869546 | Sus | Y | 3rdParty¦Other¦Transformer¦Malfunctioning
22-0136879 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 12 | 5 | 2022-12-05 | 1876888 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0137109 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 12 | 6 | 2022-12-06 | 1877419 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0137609 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2022-12-08 | 1878836 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0137906 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 9 | 2022-12-09 | 1879739 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
22-0138206 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880900 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0139398 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2022-12-12 | 1887803 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
22-0139590 | Animal | Squirrel | Transformer (OH) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2022-12-13 | 1888738 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦Normal
23-0004231 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1906641 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
15-0006396 | Equipment Failure/Involved | Other | Conductor, Underground | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2015-01-22 | 1167314 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorUnderground¦Broken
15-0009796 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1173072 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0009812 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1173257 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0011564 | Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2015-02-07 | 1181235 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonground
15-0012065 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1185343 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0032376 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230406 | Sus | Y | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken
15-0032746 | Environmental/External | Lightning | Transformer | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2015-05-07 | 1231137 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦Deteriorated
15-0037449 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 30 | 2015-05-30 | 1241554 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0042328 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2015-06-21 | 1254062 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
15-0043174 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 6 | 24 | 2015-06-24 | 1256095 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0043829 | Animal | Bird found | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2015-06-28 | 1258073 | Sus | Y | Animal¦Birdfound¦Fuse¦Normal
15-0044519 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2015-07-01 | 1260130 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0049260 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2015-07-20 | 1274059 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0053694 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2015 | Tier 3 - Extreme | Transformer only | 8 | 7 | 2015-08-07 | 1284776 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
15-0054076 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2015 | Tier 3 - Extreme | Transformer only | 8 | 10 | 2015-08-10 | 1285795 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
15-0058275 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 30 | 2015-08-30 | 1297310 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
15-0062171 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2015-09-18 | 1308106 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
15-0071271 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324232 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0073249 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2015-10-25 | 1329055 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0073441 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 26 | 2015-10-26 | 1329452 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0075338 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2015-11-03 | 1334666 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0075375 | Environmental/External | Lightning |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 11 | 3 | 2015-11-03 | 1334832 | Sus | Y | EnvironmentalExternal¦Lightning¦¦FailedFaulted
15-0076574 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2015-11-09 | 1337668 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0077897 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1341744 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0084519 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Transmission line | 12 | 13 | 2015-12-13 | 1359891 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0084959 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1362355 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0087837 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2015-12-30 | 1374637 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
16-0004765 | Equipment Failure/Involved | Overhead | Transformer |  | 2016 | Tier 2 - Elevated | Transformer only | 1 | 12 | 2016-01-12 | 1382076 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦
16-0005995 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2016-01-18 | 1385849 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0006949 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 1 | 20 | 2016-01-20 | 1388741 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0013837 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408124 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
16-0015724 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2016-02-25 | 1412352 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017839 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418826 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018117 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420097 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018467 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421242 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
16-0018726 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2016-03-07 | 1423216 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018919 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1420885 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0021338 | Vegetation | Tree - branch fell on line | Secondary | Broken | 2016 | Tier 3 - Extreme | Transformer only | 3 | 14 | 2016-03-14 | 1431125 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Broken
16-0021504 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2016-03-15 | 1431658 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0023005 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2016-03-21 | 1435331 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0024297 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2016-03-28 | 1439554 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0029695 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 19 | 2016-04-19 | 1453747 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0030054 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 20 | 2016-04-20 | 1454388 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0032101 | Environmental/External | Lightning | Elbow | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2016-04-27 | 1460457 | Sus | N | EnvironmentalExternal¦Lightning¦Elbow¦FailedFaulted
16-0032238 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2016-04-27 | 1460670 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0033051 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2016-05-01 | 1462705 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0036948 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2016-05-19 | 1472491 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0051132 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2016-07-20 | 1512997 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
16-0051304 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 20 | 2016-07-20 | 1513232 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0055523 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2016-08-06 | 1522542 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
16-0057914 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2016-08-17 | 1527813 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0059078 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2016-08-22 | 1530411 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
16-0060900 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2016-08-29 | 1534089 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0076495 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2016-10-28 | 1571974 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0077628 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2016-11-02 | 1575498 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0078737 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2016-11-08 | 1578357 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0082433 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589780 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0086899 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2016-12-24 | 1610160 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0004775 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1622117 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005446 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627686 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005487 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623733 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0005704 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627090 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0005896 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1630298 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0009350 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2017-01-16 | 1644278 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0009382 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2017-01-16 | 1644396 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0012102 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1656860 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0012823 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658628 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0013131 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658640 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013249 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1661265 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
17-0014322 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663341 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0015431 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2017-01-26 | 1668275 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
17-0016945 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2017-02-02 | 1672993 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018720 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680588 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019137 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transmission line | 2 | 8 | 2017-02-08 | 1682479 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0019374 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1682833 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0023940 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703653 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0024846 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707245 | Sus | N | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
17-0026454 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2017-02-24 | 1713020 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028717 | Animal | Squirrel | Insulator | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720909 | Sus | N | Animal¦Squirrel¦Insulator¦Burnedflashed
17-0029879 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2017-03-10 | 1723744 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0031173 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2017-03-16 | 1728180 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0032406 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2017-03-21 | 1731984 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0033727 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 25 | 2017-03-25 | 1735383 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0036953 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745205 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0040176 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 13 | 2017-04-13 | 1757458 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0040769 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 17 | 2017-04-17 | 1759226 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0040823 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 4 | 17 | 2017-04-17 | 1759180 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0043899 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 29 | 2017-04-29 | 1770446 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0045447 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2017-05-05 | 1775126 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0045730 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2017-05-06 | 1775939 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0047769 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 13 | 2017-05-13 | 1781622 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0051907 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 5 | 31 | 2017-05-31 | 1794264 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0052625 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2017-06-04 | 1796728 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0052895 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2017-06-05 | 1797677 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
17-0054564 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2017-06-11 | 1802274 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0057001 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 20 | 2017-06-20 | 1812485 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0057001 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 20 | 2017-06-20 | 1812485 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0059617 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2017-06-29 | 1821046 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0063268 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2017-07-16 | 1833016 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0063304 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2017-07-17 | 1833181 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0067490 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Transmission line | 8 | 2 | 2017-08-02 | 1844863 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
17-0067555 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 8 | 2 | 2017-08-02 | 1844912 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
17-0069906 | Animal | Bird found | Relay | Malfunctioning | 2017 | Tier 2 - Elevated | Substation - Transmission | 8 | 13 | 2017-08-13 | 1851403 | Sus | Y | Animal¦Birdfound¦Relay¦Malfunctioning
17-0077730 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2017-09-11 | 1875413 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
17-0079078 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 14 | 2017-09-14 | 1879176 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
17-0082357 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2017-09-28 | 1887216 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0085391 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893949 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0085441 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1894199 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086158 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1897935 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
17-0086845 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899530 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0089798 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2017-10-23 | 1908136 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonobject
17-0098085 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2017-11-28 | 1930926 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0099758 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2017-12-04 | 1935770 | Sus | N | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Broken
17-0099781 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1935661 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0100908 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 12 | 9 | 2017-12-09 | 1939375 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0004779 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2018-01-09 | 5145 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
18-0011411 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2018-02-04 | 19223 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0014105 | 3rd Party | Vehicle | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2018-02-14 | 24330 | Sus | N | 3rdParty¦Vehicle¦Fuse¦FailedFaulted
18-0018459 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2018-03-01 | 34422 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
18-0021851 | Company Initiated | Construction Activity/equip, company | Fuse | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2018-03-12 | 42383 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Normal
18-0022741 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 44086 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
18-0022741 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 44086 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
18-0025773 | Environmental/External | Lightning | Transformer (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 51195 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken
18-0026874 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2018-03-26 | 54082 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0027003 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2018-03-27 | 54226 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0027182 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2018-03-27 | 54653 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
18-0029829 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 4 | 6 | 2018-04-06 | 60658 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0030405 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2018-04-08 | 62697 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0031403 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2018-04-11 | 64784 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
18-0035737 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2018-04-26 | 74137 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0036123 | Equipment Failure/Involved | Substation | Relay | Malfunctioning | 2018 | Tier 2 - Elevated | Substation - Transmission | 4 | 27 | 2018-04-27 | 75009 | Sus | N | EquipmentFailureInvolved¦Substation¦Relay¦Malfunctioning
18-0037435 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2018-05-01 | 77764 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
18-0051538 | Equipment Failure/Involved | Overhead | Jumper | Deteriorated | 2018 | Tier 3 - Extreme | Transformer only | 6 | 15 | 2018-06-15 | 110411 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Deteriorated
18-0053614 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2018-06-22 | 115520 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
18-0055490 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2018 | Tier 2 - Elevated | Transformer only | 6 | 28 | 2018-06-28 | 120370 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
18-0058056 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2018-07-09 | 127241 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0063742 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 25 | 2018-07-25 | 140078 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0063810 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 140585 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
18-0064573 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on object | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2018-07-28 | 142285 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject
18-0068630 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2018-08-10 | 152793 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
18-0068798 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2018-08-10 | 152960 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0069681 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2018-08-14 | 155119 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0073995 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 27 | 2018-08-27 | 163326 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0077324 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2018-09-06 | 169583 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
18-0082304 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2018-09-21 | 179155 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0095245 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2018-10-29 | 204456 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0098444 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 211920 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0100803 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217812 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101452 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219050 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102417 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2018-11-22 | 222324 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0102667 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2018-11-23 | 223081 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0103204 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 224347 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0109176 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 239864 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0110455 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2018-12-24 | 246159 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0110765 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 12 | 26 | 2018-12-26 | 247651 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0111213 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2018-12-31 | 250317 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
19-0005263 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255929 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009368 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 266439 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010058 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 267167 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0012676 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2019-01-20 | 277624 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0017042 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286526 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0017197 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287519 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
19-0017427 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2019-02-03 | 288310 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0017549 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2019-02-03 | 288611 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
19-0019358 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294759 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020161 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2019-02-06 | 294940 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020305 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2019-02-09 | 296368 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020563 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298046 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020574 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298041 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020954 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298267 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0022479 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 2 | 12 | 2019-02-12 | 301089 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
19-0022859 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 306937 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0023502 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 309339 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024218 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 312725 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0024389 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Transmission line | 2 | 16 | 2019-02-16 | 313323 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0024488 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 313760 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0024552 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314382 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025565 | Animal | Other | Insulator | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2019-02-18 | 317367 | Sus | N | Animal¦Other¦Insulator¦Burnedflashed
19-0026115 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 19 | 2019-02-19 | 318938 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0026966 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2019-02-21 | 320670 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed
19-0029047 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326969 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0029388 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2019-02-28 | 327739 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0030218 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2019-03-03 | 329951 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0032433 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2019-03-10 | 335616 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0038532 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2019-03-30 | 350944 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0041100 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2019-04-09 | 357091 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0042332 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 4 | 14 | 2019-04-14 | 360570 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0043627 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2019-04-17 | 362692 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0058965 | Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2019-05-29 | 392524 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated
19-0061729 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2019-06-03 | 396063 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0063669 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2019-06-06 | 399537 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0064912 | Vegetation | Tree - fell into line | Anchor or Guy | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2019-06-09 | 402804 | Sus | Y | Vegetation¦Treefellintoline¦AnchororGuy¦Normal
19-0065856 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2019-06-11 | 405350 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0086431 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2019-08-10 | 498422 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
19-0087568 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2019-08-13 | 507803 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0087906 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2019-08-14 | 510473 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0088785 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2019-08-16 | 517156 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0091797 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2019-08-24 | 536753 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0092053 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 8 | 26 | 2019-08-26 | 538608 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0120417 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2019-11-02 | 698288 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0129673 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 717305 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130224 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 721292 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0136582 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2019-12-14 | 739802 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
20-0005121 | 3rd Party | Gun Shot | Regulator | Leaking | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2020-01-04 | 754620 | Sus | N | 3rdParty¦GunShot¦Regulator¦Leaking
20-0007311 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2020-01-10 | 758757 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0009587 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on object | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 762227 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonobject
20-0011154 | Vegetation | Tree - fell into line | Service conductor | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2020-01-19 | 766061 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
20-0013591 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2020-01-24 | 769688 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0019109 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 781017 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0022743 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2020-02-17 | 792379 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0024961 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2020-02-22 | 800832 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0032356 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852298 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0032943 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852681 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
20-0033410 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Transmission line | 3 | 17 | 2020-03-17 | 856798 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0033510 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2020-03-17 | 856571 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033572 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2020-03-17 | 857307 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0033876 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 18 | 2020-03-18 | 858279 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0034931 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2020-03-21 | 860197 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0035981 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 25 | 2020-03-25 | 864527 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0039037 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2020-04-06 | 886258 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
20-0040253 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2020-04-10 | 893283 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0048472 | Vegetation | Tree - fell into line | Cutout, fuse holder | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2020-05-08 | 909549 | Sus | Y | Vegetation¦Treefellintoline¦Cutoutfuseholder¦FailedFaulted
20-0048717 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 8 | 2020-05-08 | 909878 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0051013 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2020-05-17 | 915191 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0052039 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2020-05-19 | 917706 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0052076 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 5 | 19 | 2020-05-19 | 917675 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0055090 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2020-05-28 | 924085 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0062046 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2020-06-17 | 940811 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0063826 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 944888 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0066559 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 30 | 2020-06-30 | 954447 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0078014 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2020-07-30 | 975549 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0082911 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2020-08-13 | 994710 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0084663 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1010226 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0084678 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1010437 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0090476 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033379 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0094141 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 9 | 7 | 2020-09-07 | 1058186 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0094750 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2020-09-08 | 1060436 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Fuse¦Normal
20-0096099 | Environmental/External | Fire, Forest/Grass | Transformer | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 19 | 2020-08-19 | 1063640 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal
20-0100175 | Company Initiated | Personnel, company | Relay | Malfunctioning | 2020 | Tier 2 - Elevated | Substation - Transmission | 9 | 22 | 2020-09-22 | 1087179 | Sus | Y | CompanyInitiated¦Personnelcompany¦Relay¦Malfunctioning
20-0102542 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2020-09-28 | 1096879 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0102940 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2020-09-28 | 1099133 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0106797 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2020-10-09 | 1114173 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0110052 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 10 | 17 | 2020-10-17 | 1120040 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0113707 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2020-10-27 | 1129677 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0115605 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1132521 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0119882 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2020-11-11 | 1142156 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
20-0124832 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 11 | 24 | 2020-11-24 | 1154158 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
20-0125732 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2020-11-29 | 1155853 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0126433 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2020-12-01 | 1157526 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0127031 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2020 | Tier 3 - Extreme | Transformer only | 12 | 2 | 2020-12-02 | 1159627 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0004423 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2021-01-03 | 1202742 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0006753 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2021-01-08 | 1207026 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0009478 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1213699 | Sus | N | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0011024 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1217712 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0015917 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234435 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020597 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2021-02-01 | 1245346 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020905 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2021-02-02 | 1246001 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0024373 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2021-02-11 | 1252752 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0024970 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2021-02-12 | 1253512 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0029434 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261703 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0029591 | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261508 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦BurnedOpen
21-0030227 | Equipment Failure/Involved | Underground | Service conductor | Broken | 2021 | Tier 2 - Elevated | Transformer only | 2 | 27 | 2021-02-27 | 1263411 | Sus | N | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Broken
21-0035323 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2021-03-11 | 1278695 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0039397 | Equipment Failure/Involved | Overhead | Service conductor | Broken | 2021 | Tier 2 - Elevated | Transformer only | 3 | 22 | 2021-03-22 | 1292043 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken
21-0039822 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 23 | 2021-03-23 | 1293792 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0041834 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2021-03-27 | 1301509 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonground
21-0045701 | Equipment Failure/Involved | Overhead | Crossarm, Steel | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2021-04-07 | 1308774 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Broken
21-0047724 | Animal | Squirrel | Footings, Tower or Pole | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2021-04-13 | 1313991 | Sus | N | Animal¦Squirrel¦FootingsTowerorPole¦Burnedflashed
21-0048881 | 3rd Party | Customer Equipment | Secondary | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2021-04-15 | 1317776 | Sus | N | 3rdParty¦CustomerEquipment¦Secondary¦Broken
21-0060486 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2021-05-12 | 1347296 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0061852 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2021-05-15 | 1349770 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0066711 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 5 | 27 | 2021-05-27 | 1359632 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0070561 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Transformer only | 6 | 6 | 2021-06-06 | 1366775 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0076666 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 6 | 19 | 2021-06-19 | 1379535 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0079367 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2021-06-24 | 1384293 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0084869 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 5 | 2021-07-05 | 1392164 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0091570 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2021-07-19 | 1407783 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0092544 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 7 | 20 | 2021-07-20 | 1409314 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0098240 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 1 | 2021-08-01 | 1428128 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0099237 | Vegetation | Tree - bark fell into line | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2021-08-03 | 1429850 | Sus | Y | Vegetation¦Treebarkfellintoline¦CrossarmWood¦Broken
21-0106468 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2021-08-18 | 1446725 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
21-0113787 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2021-09-05 | 1462623 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
21-0117434 | Equipment Failure/Involved | Overhead | Service conductor | Broken | 2021 | Tier 2 - Elevated | Transformer only | 9 | 14 | 2021-09-14 | 1471628 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken
21-0126211 | 3rd Party | Other | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2021-10-05 | 1487721 | Sus | Y | 3rdParty¦Other¦ConductorOverhead¦Normal
21-0130152 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 10 | 12 | 2021-10-12 | 1496278 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0135813 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508812 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0139116 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 27 | 2021-10-27 | 1523715 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0140746 | Equipment Failure/Involved | Overhead | Other | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2021-11-01 | 1527436 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Together
21-0149208 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 21 | 2021-11-21 | 1552540 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0155054 | Animal | Squirrel | Fuse | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 5 | 2021-12-05 | 1559713 | Sus | N | Animal¦Squirrel¦Fuse¦Normal
21-0158407 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1571513 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158732 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1574049 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0159537 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2021-12-18 | 1576726 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0159556 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2021 | Tier 3 - Extreme | Transformer only | 12 | 18 | 2021-12-18 | 1576720 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
21-0160586 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581408 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
21-0160655 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581756 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0160848 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582982 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161354 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2021-12-28 | 1586764 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0161369 | Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1587183 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground
21-0161564 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1587744 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161597 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585803 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161643 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1588871 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0161704 | Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1589056 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal
21-0161991 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1590734 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0005090 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2021-12-31 | 1591807 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005126 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591960 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0005726 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2022-01-03 | 1594138 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0005832 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1594631 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0006169 | Vegetation | Tree - fell into line | Transformer | Normal | 2022 | Tier 3 - Extreme | Transformer only | 1 | 3 | 2022-01-03 | 1594740 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Normal
22-0006618 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 1 | 5 | 2022-01-05 | 1595968 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0007738 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2022-01-09 | 1598636 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0018595 | Company Initiated | Personnel, company | Fuse | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2022-02-04 | 1621102 | Sus | N | CompanyInitiated¦Personnelcompany¦Fuse¦Normal
22-0022276 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2022-02-15 | 1627500 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
22-0031911 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2022-03-09 | 1645569 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0033344 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2022-03-13 | 1647710 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0033668 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2022 | Tier 3 - Extreme | Transformer only | 3 | 14 | 2022-03-14 | 1648272 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
22-0047796 | 3rd Party | Vehicle | Transformer (UG) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2022-04-13 | 1672072 | Sus | N | 3rdParty¦Vehicle¦Transformer(UG)¦Normal
22-0065786 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 5 | 24 | 2022-05-24 | 1708903 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
22-0067386 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 5 | 27 | 2022-05-27 | 1712319 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083461 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2022-07-08 | 1751873 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0084833 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2022-07-13 | 1755471 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0092291 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 3 - Extreme | Transformer only | 8 | 1 | 2022-08-01 | 1770539 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0111924 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2022-09-19 | 1815678 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0112914 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2022-09-21 | 1818034 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0117008 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2022-10-02 | 1826046 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
22-0126494 | 3rd Party | Customer Equipment | Switch (OH) | Arcing | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1850128 | Sus | Y | 3rdParty¦CustomerEquipment¦Switch(OH)¦Arcing
22-0127258 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2022-11-02 | 1852066 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0133285 | Vegetation | Tree - fell into line | Cutout, fuse holder | Broken | 2022 | Tier 3 - Extreme | Transformer only | 11 | 21 | 2022-11-21 | 1867352 | Sus | Y | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken
22-0136143 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 2022 | Tier 3 - Extreme | Transformer only | 12 | 2 | 2022-12-02 | 1874313 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal
22-0136330 | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2022-12-03 | 1875311 | Sus | N | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Burnedflashed
22-0138488 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1883004 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139010 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 12 | 10 | 2022-12-10 | 1884488 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
22-0141420 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1897952 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0141628 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned/flashed | 2022 | Tier 3 - Extreme | Transformer only | 12 | 27 | 2022-12-27 | 1898694 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Burnedflashed
22-0141780 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2022-12-26 | 1897611 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0142609 | Vegetation | Tree - grew into line | Conductor, Overhead | Arcing | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903712 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Arcing
15-0010839 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1178217 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0010991 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2015-02-07 | 1179963 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0015504 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 2 | 24 | 2015-02-24 | 1195369 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0029378 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 4 | 24 | 2015-04-24 | 1224395 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0032764 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2015-05-07 | 1231228 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0033421 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 11 | 2015-05-11 | 1232873 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0035120 | Animal | Squirrel | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2015-05-19 | 1236766 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0037697 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 1 | 2015-06-01 | 1242280 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0046561 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2015-07-09 | 1265531 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0046900 | Animal | Other | Conductor, Overhead | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2015-07-10 | 1266372 | Sus | Y | Animal¦Other¦ConductorOverhead¦FailedFaulted
15-0048918 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 20 | 2015-07-20 | 1273202 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0049295 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 20 | 2015-07-20 | 1274121 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0049441 | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2015-07-21 | 1274499 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Deteriorated
15-0050401 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 24 | 2015-07-24 | 1276696 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0051924 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 31 | 2015-07-31 | 1280816 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0052610 | Animal | Squirrel | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 8 | 4 | 2015-08-04 | 1282420 | Sus | Y | Animal¦Squirrel¦Transformer¦FailedFaulted
15-0056656 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2015-08-21 | 1292758 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0059473 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2015-09-05 | 1300464 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0061809 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 9 | 16 | 2015-09-16 | 1307243 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0062818 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1310579 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
15-0073937 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 28 | 2015-10-28 | 1330703 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0075232 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2015-11-02 | 1334108 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0075385 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 11 | 3 | 2015-11-03 | 1334868 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0081595 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 11 | 29 | 2015-11-29 | 1350178 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0082940 | Animal | Squirrel | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2015-12-05 | 1354294 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
15-0084772 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361230 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0086446 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2015-12-21 | 1367733 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0087515 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2015-12-27 | 1372577 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0006365 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2016-01-19 | 1387003 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017118 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 3 | 4 | 2016-03-04 | 1415541 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0018099 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418164 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018258 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1419598 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0018358 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421279 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0020449 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427656 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0022719 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2016-03-20 | 1434483 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0024668 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 29 | 2016-03-29 | 1440647 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0025430 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Transformer only | 3 | 31 | 2016-03-31 | 1442495 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0025760 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 3 | 2016-04-03 | 1443513 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0028408 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2016-04-13 | 1450180 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0034676 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2016-05-07 | 1466560 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0037269 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2016-05-19 | 1473238 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0038918 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 27 | 2016-05-27 | 1477985 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0041057 | 3rd Party | Vehicle | Connector or Splice (OH) | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2016-06-04 | 1482782 | Sus | Y | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Broken
16-0041819 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 8 | 2016-06-08 | 1485070 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0043088 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2016-06-14 | 1488639 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0047727 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 4 | 2016-07-04 | 1500741 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
16-0048348 | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2016-07-07 | 1502208 | Sus | Y | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Burnedflashed
16-0048647 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2016-07-08 | 1502825 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
16-0050756 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2016-07-18 | 1512246 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0052097 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 24 | 2016-07-24 | 1515038 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal
16-0053452 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 7 | 28 | 2016-07-28 | 1518100 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0054807 | Equipment Failure/Involved | Underground | Transformer | Leaking | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2016-08-03 | 1521063 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦Leaking
16-0058270 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2016-08-18 | 1528472 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0066279 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2016 | Tier 2 - Elevated | Transformer only | 9 | 21 | 2016-09-21 | 1545479 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
16-0073326 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2016-10-17 | 1564561 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0076828 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2016-10-30 | 1573362 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject
16-0078158 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 4 | 2016-11-04 | 1576865 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0078850 | Company Initiated | Return Circuit Normal | Conductor, Underground | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2016-12-02 | 1593441 | Sus | N | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Broken
16-0084472 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2016-12-08 | 1596629 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0086167 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2016-12-17 | 1605603 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0003222 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1616540 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0003596 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1617931 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005148 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625138 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006218 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 9 | 2017-01-09 | 1631254 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0007650 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638181 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007765 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639249 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0008350 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 12 | 2017-01-12 | 1640930 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0011369 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653184 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011873 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on object | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655395 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonobject
17-0012750 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658395 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013629 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662910 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
17-0014643 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2017-01-25 | 1666913 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0014796 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2017-01-25 | 1667084 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0014842 | Equipment Failure/Involved | Overhead | Switch (OH) | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2017-01-25 | 1666895 | Sus | N | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Normal
17-0017346 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2017-02-03 | 1674237 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0017397 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2017-02-03 | 1674289 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0017630 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2017-02-05 | 1675559 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017935 | Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2017-02-06 | 1676974 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted
17-0018731 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680705 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018738 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680919 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0019877 | Vegetation | Tree - fell into line | Anchor or Guy | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2017-02-10 | 1684847 | Sus | N | Vegetation¦Treefellintoline¦AnchororGuy¦Broken
17-0022193 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1693463 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0022640 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698372 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0024348 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705997 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject
17-0024897 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704503 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0025118 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1708599 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0027587 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2017-03-01 | 1716711 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
17-0027994 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2017-03-02 | 1718007 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028643 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720604 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0030075 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2017-03-10 | 1724352 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0034945 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2017-03-30 | 1738920 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0035298 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2017-03-30 | 1740223 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0036899 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745134 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0037801 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1750325 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0037801 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1750325 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0038479 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2017-04-09 | 1753659 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0040098 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757212 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
17-0045862 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2017-05-06 | 1776624 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0050012 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2017-05-23 | 1788866 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0054377 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2017-06-11 | 1802236 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0057782 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2017-06-22 | 1814993 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0060827 | Company Initiated | Dig in, company | Conductor, Underground | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2017-07-06 | 1824514 | Sus | Y | CompanyInitiated¦Digincompany¦ConductorUnderground¦Broken
17-0063180 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2017-07-15 | 1832554 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0064950 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 24 | 2017-07-24 | 1838484 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0067193 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2017-08-01 | 1844236 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0067866 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2017-08-04 | 1846133 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
17-0082666 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2017-09-28 | 1887693 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0083231 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 2 | 2017-10-02 | 1889036 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0085770 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1896863 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0087542 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2017-10-15 | 1901360 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
17-0090228 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 10 | 25 | 2017-10-25 | 1909194 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
17-0092473 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 11 | 3 | 2017-11-03 | 1915138 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0092655 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 4 | 2017-11-04 | 1916072 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0093186 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2017-11-07 | 1917460 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦Normal
17-0094533 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 11 | 12 | 2017-11-12 | 1920931 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0099870 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2017-12-05 | 1936214 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0100617 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 12 | 7 | 2017-12-07 | 1938324 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
18-0004382 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2018-01-09 | 4876 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0005927 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2018-01-13 | 7651 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0007718 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2018-01-21 | 11725 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0018062 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2018-02-28 | 33410 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
18-0021781 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2018-03-12 | 42138 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0028011 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2018-03-30 | 56634 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0033463 | Equipment Failure/Involved | Overhead | Transformer | Malfunctioning | 2018 | Tier 2 - Elevated | Transformer only | 4 | 18 | 2018-04-18 | 69216 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Malfunctioning
18-0034104 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2018-04-20 | 70717 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0039216 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2018-05-08 | 81576 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0040666 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 14 | 2018-05-14 | 85467 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0043229 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2018-05-22 | 91929 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0044769 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2018-05-27 | 94947 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
18-0056037 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2018-06-30 | 122028 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
18-0062890 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 7 | 23 | 2018-07-23 | 138579 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
18-0066244 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2018-08-02 | 147758 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
18-0066707 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2018-08-04 | 148726 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0066899 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2018-08-05 | 149344 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0080296 | Animal | Other | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 9 | 17 | 2018-09-17 | 175536 | Sus | Y | Animal¦Other¦Transformer¦FailedFaulted
18-0084013 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2018-09-27 | 182237 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0086532 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2018-10-03 | 187812 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0088292 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2018-10-08 | 191033 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0089352 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2018-10-11 | 192997 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦¦
18-0097704 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2018-11-07 | 210202 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0098912 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2018-11-11 | 213364 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0099085 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2018-11-11 | 213559 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0101457 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219069 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0105398 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on object | 2018 | Tier 2 - Elevated | Transformer only | 11 | 29 | 2018-11-29 | 229087 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonobject
18-0106605 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2018-12-03 | 232986 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0109938 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2018 | Tier 2 - Elevated | Transformer only | 12 | 18 | 2018-12-18 | 243336 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
18-0110470 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2018-12-24 | 246294 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0110545 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2018-12-24 | 246730 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0110580 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2018-12-24 | 246799 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0004558 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2019-01-04 | 253292 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0010970 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 270207 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0015362 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2019-01-29 | 283094 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0017622 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2019-02-03 | 288888 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018163 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 291114 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019034 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294031 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019657 | Vegetation | Tree - grew into line | Conductor, Overhead | Arcing | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2019-02-07 | 295204 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Arcing
19-0019687 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2019-02-07 | 295278 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
19-0019758 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2019-02-07 | 295576 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020879 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298066 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
19-0022553 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303780 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0023305 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 309444 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0023398 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 308757 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023750 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 311045 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Burnedflashed
19-0023898 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 311721 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024133 | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2019-02-15 | 312427 | Sus | N | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal
19-0024150 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 312465 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0024469 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2019-02-16 | 313472 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0025274 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 16 | 2019-02-16 | 316519 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0025367 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 316743 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0026090 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 316490 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0026201 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 319138 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028730 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2019-02-27 | 326378 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028980 | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Bent or Twisted | 2019 | Tier 3 - Extreme | Transformer only | 2 | 27 | 2019-02-27 | 326250 | Sus | N | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦BentorTwisted
19-0029354 | Equipment Failure/Involved | Overhead | Service conductor | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 2 | 28 | 2019-02-28 | 327982 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Deteriorated
19-0030278 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2019-03-03 | 330133 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0031428 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 332915 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0036276 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2019-03-23 | 345713 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
19-0036572 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2019-03-25 | 346563 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0037776 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2019-03-28 | 349166 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0039456 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 3 | 2019-04-03 | 353217 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0041049 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2019-04-09 | 356809 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0042058 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 12 | 2019-04-12 | 359819 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
19-0049780 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2019-05-07 | 375833 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0050182 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2019-05-08 | 376672 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0052254 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 15 | 2019-05-15 | 381124 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0053129 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 17 | 2019-05-17 | 383243 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0053998 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2019-05-19 | 385142 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0058532 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2019-05-28 | 391908 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
19-0058584 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2019-05-28 | 391978 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0066899 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2019-06-12 | 408103 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦FailedFaulted
19-0067134 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2019-06-13 | 408626 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0068594 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Transformer only | 6 | 17 | 2019-06-17 | 417552 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0072069 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 26 | 2019-06-26 | 429208 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0072667 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 27 | 2019-06-27 | 430814 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0074653 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 4 | 2019-07-04 | 441086 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0078241 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 17 | 2019-07-17 | 455041 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0081746 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 27 | 2019-07-27 | 473008 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0083906 | 3rd Party | Other | Metering Equipment | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 2 | 2019-08-02 | 478354 | Sus | Y | 3rdParty¦Other¦MeteringEquipment¦FailedFaulted
19-0086470 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2019-08-10 | 498647 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0086566 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2019-08-10 | 498672 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
19-0087018 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 12 | 2019-08-12 | 503584 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0095955 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2019-09-06 | 556970 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0099056 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2019-09-13 | 579701 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
19-0099373 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2019-09-16 | 583801 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0113165 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2019-10-17 | 667261 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0114878 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2019-10-22 | 677143 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0114970 | Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2019-10-23 | 677734 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Recloser¦Normal
19-0115397 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2019-10-24 | 679332 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0121052 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2019 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2019-11-04 | 699526 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
19-0129512 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 717925 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0132125 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2019-12-01 | 726730 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0132771 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2019-12-03 | 728199 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0138275 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2019-12-31 | 752920 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0010538 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2020-01-17 | 763774 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0010980 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 765214 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
20-0016625 | Animal | Squirrel | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2020-02-03 | 776431 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
20-0019504 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 783772 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
20-0021788 | Animal | Bird found | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2020-02-13 | 790058 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
20-0022900 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2020-02-17 | 792655 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031592 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2020-03-12 | 848357 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0032725 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 16 | 2020-03-16 | 853816 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0033491 | Vegetation | Tree - fell into line | Conductor, Overhead | Contaminated | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2020-03-17 | 856929 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Contaminated
20-0033539 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2020 | Tier 3 - Extreme | Transformer only | 3 | 16 | 2020-03-16 | 857117 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
20-0036322 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2020-03-26 | 866253 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0036594 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2020-03-27 | 868114 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0038456 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 4 | 2020-04-04 | 882500 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0041062 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Transformer only | 4 | 13 | 2020-04-13 | 894735 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken
20-0050778 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 15 | 2020-05-15 | 914426 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0055724 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2020-05-29 | 925561 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0064599 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2020-06-24 | 946511 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0069461 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2020-07-08 | 959920 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0071158 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2020-07-13 | 963303 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0079895 | Animal | Squirrel | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2020-08-05 | 979089 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
20-0084784 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1011241 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0087027 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2020-08-18 | 1021028 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
20-0090711 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2020-08-27 | 1034326 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0091438 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1041112 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0099091 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 9 | 18 | 2020-09-18 | 1081475 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0099818 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086124 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100051 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2020 | Tier 2 - Elevated | Transformer only | 9 | 22 | 2020-09-22 | 1086862 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
20-0104996 | Equipment Failure/Involved | Overhead |  | Broken | 2020 | Tier 2 - Elevated | Transformer only | 10 | 4 | 2020-10-04 | 1110980 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦Broken
20-0110480 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2020 | Tier 2 - Elevated | Transformer only | 10 | 19 | 2020-10-19 | 1121163 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
20-0112580 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1124348 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0113888 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2020-10-27 | 1129958 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0115883 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2020-11-02 | 1133609 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0121082 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2020-11-15 | 1145556 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
20-0128308 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2020-12-06 | 1167109 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0130079 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2020-12-13 | 1182300 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0131855 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2020-12-26 | 1198949 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0009660 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1212262 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011575 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1218925 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0013778 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224095 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0014165 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1225119 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0016129 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232234 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0019988 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1243874 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020981 | Animal | Bird found | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2021-02-02 | 1246116 | Sus | N | Animal¦Birdfound¦Fuse¦BurnedOpen
21-0020994 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2021-02-02 | 1246295 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
21-0022147 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2021-02-04 | 1248303 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken
21-0029480 | Animal | Squirrel | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 2 | 25 | 2021-02-25 | 1261976 | Sus | N | Animal¦Squirrel¦Fuse¦BurnedOpen
21-0033170 | Equipment Failure/Involved | Overhead | Transformer | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 3 | 7 | 2021-03-07 | 1272756 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground
21-0034432 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2021-03-10 | 1276856 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0037382 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 16 | 2021-03-16 | 1285572 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0038283 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2021-03-18 | 1288240 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
21-0038728 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2021-03-19 | 1288929 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0039089 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2021-03-20 | 1290630 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0040270 | Animal | Bird found | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2021-03-24 | 1295012 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
21-0041805 | Animal | Squirrel | Jumper |  | 2021 | Tier 2 - Elevated | Transformer only | 3 | 27 | 2021-03-27 | 1300533 | Sus | N | Animal¦Squirrel¦Jumper¦
21-0041933 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 28 | 2021-03-28 | 1302014 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0051673 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2021-04-22 | 1327876 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0052768 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2021-04-24 | 1332516 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0054257 | Equipment Failure/Involved | Electrical Overload | Fuse | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 28 | 2021-04-28 | 1336122 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦FailedFaulted
21-0055666 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 30 | 2021-04-30 | 1338099 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0063578 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2021-05-19 | 1353948 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0074285 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2021-06-15 | 1373637 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0075853 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 6 | 17 | 2021-06-17 | 1376665 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0075992 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2021-06-18 | 1377182 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0077234 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 6 | 21 | 2021-06-21 | 1381583 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0094666 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 25 | 2021-07-25 | 1414226 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0097878 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 31 | 2021-07-31 | 1424437 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0098154 | Equipment Failure/Involved | Fire, pole | Pole - Tower, steel | Normal | 2021 | Tier 3 - Extreme | Transmission line | 8 | 1 | 2021-08-01 | 1427939 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleTowersteel¦Normal
21-0099544 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 2021 | Tier 3 - Extreme | Transformer only | 8 | 4 | 2021-08-04 | 1433523 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal
21-0106533 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2021-08-18 | 1446834 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0121724 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2021-09-23 | 1479020 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Broken
21-0131998 | Animal | Squirrel | Recloser | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499386 | Sus | Y | Animal¦Squirrel¦Recloser¦Normal
21-0134137 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2021-10-20 | 1503698 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
21-0134150 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 10 | 20 | 2021-10-20 | 1503836 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137584 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1519506 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
21-0138316 | Vegetation | Tree - fell into line | Secondary | Broken | 2021 | Tier 3 - Extreme | Transformer only | 10 | 26 | 2021-10-26 | 1521600 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Broken
21-0139670 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2021-10-29 | 1525013 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0142007 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2021 | Tier 2 - Elevated | Transformer only | 11 | 3 | 2021-11-03 | 1534207 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
21-0154976 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2021-12-04 | 1559327 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
21-0154978 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2021-12-04 | 1559339 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0157333 | Equipment Failure/Involved | Overhead | Transformer | Arcing | 2021 | Tier 2 - Elevated | Transformer only | 12 | 13 | 2021-12-13 | 1567539 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Arcing
21-0157345 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1567506 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0157958 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569195 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0159860 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 12 | 20 | 2021-12-20 | 1577973 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
21-0161583 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588552 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0162016 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1590860 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0007584 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2022-01-08 | 1598069 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0012566 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 1 | 21 | 2022-01-21 | 1607374 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0016142 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 1 | 30 | 2022-01-30 | 1616549 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
22-0031453 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2022-03-08 | 1645013 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0046136 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1670053 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0046785 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 12 | 2022-04-12 | 1670664 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0051158 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 18 | 2022-04-18 | 1676031 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0059431 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2022-05-08 | 1691209 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0065666 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2022-05-24 | 1708944 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0068027 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2022-05-30 | 1713861 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0069078 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 6 | 1 | 2022-06-01 | 1716192 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0074036 | Company Initiated | Personnel, company | Recloser | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 14 | 2022-06-14 | 1730998 | Sus | Y | CompanyInitiated¦Personnelcompany¦Recloser¦Normal
22-0074499 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2022-06-15 | 1732130 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
22-0081064 | Equipment Failure/Involved | Substation | Other | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2022-07-01 | 1747042 | Sus | Y | EquipmentFailureInvolved¦Substation¦Other¦FailedFaulted
22-0084931 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2022-07-13 | 1755612 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0087714 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2022-07-20 | 1761419 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
22-0089321 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 25 | 2022-07-25 | 1764893 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
22-0102524 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 26 | 2022-08-26 | 1792438 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0108156 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2022-09-08 | 1806521 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0111421 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 17 | 2022-09-17 | 1813017 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0112695 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2022-09-20 | 1817516 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0112892 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2022-09-21 | 1817964 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0114421 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2022-09-23 | 1820390 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0118831 | 3rd Party | Dig in, 3rd party | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 10 | 6 | 2022-10-06 | 1830728 | Sus | Y | 3rdParty¦Digin3rdparty¦Secondary¦Broken
22-0119426 | Animal | Squirrel | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 10 | 8 | 2022-10-08 | 1831990 | Sus | Y | Animal¦Squirrel¦Transformer¦FailedFaulted
22-0123906 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2022-10-22 | 1842879 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0125684 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2022-10-28 | 1847688 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0127270 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2022-11-03 | 1852126 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0132711 | Equipment Failure/Involved | Overhead | Other | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865725 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
22-0135535 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2022-12-01 | 1872788 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
22-0135567 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2022-12-01 | 1873087 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
22-0138515 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882771 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
22-0138847 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880602 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0139257 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 12 | 12 | 2022-12-12 | 1887188 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0141015 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2022-12-22 | 1895974 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Burnedflashed
22-0141157 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 12 | 23 | 2022-12-23 | 1896619 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0141408 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1897853 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
22-0141449 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898031 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
23-0004709 | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1909866 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround
15-0002488 | Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2015-01-05 | 1159456 | Sus | N | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
15-0010222 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1174757 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
15-0011331 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Transformer only | 2 | 7 | 2015-02-07 | 1180430 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0011917 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2015-02-08 | 1185248 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
15-0016412 | Equipment Failure/Involved | Other | Transformer | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 2 | 28 | 2015-02-28 | 1197551 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Deteriorated
15-0026032 | Equipment Failure/Involved | Other | Cutout, fuse holder | Broken | 2015 | Tier 2 - Elevated | Transformer only | 4 | 11 | 2015-04-11 | 1217422 | Sus | N | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Broken
15-0035578 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2015-05-20 | 1237691 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0040026 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Transformer only | 6 | 10 | 2015-06-10 | 1248347 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0045334 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 3 | 2015-07-03 | 1262321 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
15-0048838 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1273012 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0053843 | Vegetation | Tree - fell into line | Secondary | Together | 2015 | Tier 3 - Extreme | Transformer only | 8 | 8 | 2015-08-08 | 1285189 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Together
15-0057082 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2015-08-24 | 1294014 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0061119 | Animal | Bird found | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2015-09-13 | 1305132 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
15-0061783 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2015-09-16 | 1307079 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0062922 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2015 | Tier 3 - Extreme | Transformer only | 9 | 23 | 2015-09-23 | 1310772 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
15-0067258 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2015-10-01 | 1315008 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0068456 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 6 | 2015-10-06 | 1317954 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
15-0068619 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2015-10-07 | 1318217 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0069125 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2015-10-09 | 1319078 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0071337 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324369 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0071713 | Environmental/External | Lightning | Transformer (OH) | Deteriorated | 2015 | Tier 3 - Extreme | Transformer only | 10 | 18 | 2015-10-18 | 1325567 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Deteriorated
15-0074463 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2015-10-31 | 1332042 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0078391 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2015-11-16 | 1343429 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0082131 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2015-12-02 | 1351870 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0082504 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352825 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0086544 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned/flashed | 2015 | Tier 3 - Extreme | Transformer only | 12 | 21 | 2015-12-21 | 1368240 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Burnedflashed
16-0003450 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378207 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0003462 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378540 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0005718 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2016 | Tier 2 - Elevated | Transformer only | 1 | 15 | 2016-01-15 | 1384694 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
16-0012998 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1404689 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0013310 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1405869 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
16-0013714 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 2 | 18 | 2016-02-18 | 1407820 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
16-0013819 | Equipment Failure/Involved | Overhead | PT/CCVT | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408422 | Sus | N | EquipmentFailureInvolved¦Overhead¦PTCCVT¦FailedFaulted
16-0013819 | Equipment Failure/Involved | Overhead | PT/CCVT | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408422 | Sus | N | EquipmentFailureInvolved¦Overhead¦PTCCVT¦FailedFaulted
16-0015796 | Animal | Other | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2016-02-26 | 1412494 | Sus | N | Animal¦Other¦PoleWood¦Broken
16-0015925 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 2 | 26 | 2016-02-26 | 1412726 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0017460 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416580 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0020704 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1428983 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0030956 | Environmental/External | Lightning | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 4 | 23 | 2016-04-23 | 1456753 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken
16-0032229 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 4 | 27 | 2016-04-27 | 1460610 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0034372 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 6 | 2016-05-06 | 1465716 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
16-0037658 | Animal | Squirrel | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2016-05-22 | 1474652 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
16-0039627 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2016-05-29 | 1478975 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0042709 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 12 | 2016-06-12 | 1487479 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0051085 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2016 | Tier 2 - Elevated | Transformer only | 7 | 20 | 2016-07-20 | 1512845 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
16-0054033 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2016-08-01 | 1519597 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0056320 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2016-08-10 | 1524364 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0063684 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2016-09-10 | 1539224 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0067003 | 3rd Party | Vehicle | Pole-Wood | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 23 | 2016-09-23 | 1546593 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
16-0071641 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2016-10-13 | 1557424 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
16-0075193 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2016-10-24 | 1569133 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0075209 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2016-10-24 | 1569100 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0076533 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 28 | 2016-10-28 | 1572140 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0077275 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2016-10-31 | 1574691 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0083957 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2016-12-05 | 1594858 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
16-0084691 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2016-12-08 | 1597315 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0084926 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2016-12-10 | 1598360 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0084940 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on object | 2016 | Tier 2 - Elevated | Transformer only | 12 | 10 | 2016-12-10 | 1598426 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonobject
17-0003317 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1617172 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005289 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625670 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0006102 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627004 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0008400 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 12 | 2017-01-12 | 1641307 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0008844 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2017-01-13 | 1642822 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0009272 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2017-01-15 | 1643932 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0009396 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 16 | 2017-01-16 | 1644623 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0011236 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652353 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011972 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1656308 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0012005 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655895 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
17-0012538 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1657663 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013852 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 22 | 2017-01-22 | 1662141 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0013880 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1660496 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0014347 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 24 | 2017-01-24 | 1665383 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
17-0014454 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1662565 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0017448 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2017-02-04 | 1674685 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017478 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2017-02-04 | 1674962 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0018129 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677711 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018612 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1678657 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0019128 | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682310 | Sus | N | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Broken
17-0023285 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2017-02-18 | 1700907 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023949 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1702805 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
17-0024673 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706240 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0024913 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707678 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0025982 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2017-02-23 | 1711963 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0028769 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720929 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0029042 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2017-03-07 | 1721732 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0030084 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2017-03-10 | 1724375 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0030566 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2017-03-14 | 1726568 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0031531 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2017-03-17 | 1729193 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
17-0032504 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 3 | 21 | 2017-03-21 | 1731655 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
17-0037411 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748585 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0037454 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1746312 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0039860 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2017-04-13 | 1756893 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0040085 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757338 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0040107 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757117 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0041427 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 19 | 2017-04-19 | 1761098 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0042570 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2017-04-24 | 1766108 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0044009 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 30 | 2017-04-30 | 1771097 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0047653 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2017-05-12 | 1781049 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0051494 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2017-05-30 | 1793257 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0051688 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 5 | 31 | 2017-05-31 | 1793713 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
17-0052791 | Equipment Failure/Involved | Overhead | Insulator | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2017-06-05 | 1797328 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Normal
17-0060238 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2017 | Tier 3 - Extreme | Transformer only | 7 | 3 | 2017-07-03 | 1822777 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
17-0062814 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2017-07-14 | 1831159 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0063103 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2017-07-15 | 1832065 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0065184 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Transmission line | 7 | 25 | 2017-07-25 | 1839251 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0066467 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2017-07-29 | 1842166 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0067853 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 3 | 2017-08-03 | 1846027 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0070108 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2017-08-14 | 1852096 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0071612 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2017-08-20 | 1855865 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0074954 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2017-09-01 | 1865475 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
17-0083879 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2017-10-03 | 1890243 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0085359 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893943 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0085994 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2017-10-10 | 1897527 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0087555 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1901384 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Normal
17-0088404 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1903576 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0088841 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1904804 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0089163 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1905098 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0090724 | Vegetation | Tree - fell into line | Fuse | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2017-10-27 | 1910526 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦Normal
17-0090994 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2017-10-28 | 1911255 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
17-0094579 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 12 | 2017-11-12 | 1921061 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0096069 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2017-11-17 | 1925203 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken
17-0096710 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2017-11-21 | 1927010 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
17-0102258 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2017-12-16 | 1945971 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0003372 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2018-01-03 | 1364 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0009959 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2018-01-29 | 16071 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0010079 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 30 | 2018-01-30 | 16345 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
18-0013123 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2018-02-10 | 22471 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0019033 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 35953 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
18-0023609 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2018-03-16 | 46140 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023618 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46308 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
18-0023887 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2018-03-18 | 47308 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0023893 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 18 | 2018-03-18 | 47315 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0025857 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 22 | 2018-03-22 | 51448 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
18-0026813 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Transformer only | 3 | 26 | 2018-03-26 | 53816 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0034735 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 23 | 2018-04-23 | 72289 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0035995 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2018-04-26 | 74590 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0036092 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2018-04-27 | 74778 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0044588 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2018-05-25 | 94291 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0048378 | Animal | Squirrel | Cutout, fuse holder | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 7 | 2018-06-07 | 103555 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
18-0053270 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 21 | 2018-06-21 | 114682 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
18-0057904 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2018-07-09 | 126797 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0059660 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2018-07-13 | 130734 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0062842 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on object | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2018-07-23 | 138405 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonobject
18-0063774 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 25 | 2018-07-25 | 140386 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
18-0067450 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2018-08-07 | 150686 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075948 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2018-09-03 | 167343 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0081858 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2018-09-21 | 178479 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0082091 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2018-09-21 | 178782 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0088855 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2018-10-09 | 192143 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
18-0101251 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218622 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102658 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2018-11-23 | 223164 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0103937 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2018-11-27 | 225745 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
18-0107966 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2018-12-07 | 235964 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109585 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2018-12-16 | 241738 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0110112 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | On Ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 20 | 2018-12-20 | 244329 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦OnGround
19-0005084 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255170 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0005519 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 258347 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0010284 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 270517 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0012874 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2019-01-21 | 278240 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0013255 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 1 | 22 | 2019-01-22 | 279214 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0017385 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 288182 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017765 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 289591 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018736 | Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 292907 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed
19-0020467 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2019-02-09 | 297450 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
19-0020625 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298482 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0020787 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2019-02-10 | 298964 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0020877 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 299472 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0022591 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 305719 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
19-0023144 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 308686 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0023586 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 308470 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0023980 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 15 | 2019-02-15 | 311594 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0024546 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314355 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0026604 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2019-02-20 | 319766 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0027574 | Vegetation | Other ground vegetation | Other | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2019-02-24 | 322406 | Sus | N | Vegetation¦Othergroundvegetation¦Other¦Normal
19-0028226 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324183 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
19-0030138 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2019-03-02 | 329828 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030211 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2019-03-02 | 329877 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0031943 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 8 | 2019-03-08 | 334138 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0033913 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 3 | 14 | 2019-03-14 | 339329 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0038938 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 1 | 2019-04-01 | 352023 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
19-0039569 | Company Initiated | Construction Activity/equip, company | Anchor or Guy | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2019-04-06 | 354784 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦AnchororGuy¦Deteriorated
19-0041006 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2019-04-09 | 356832 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0042521 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2019-04-15 | 361049 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
19-0042727 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2019-04-16 | 361477 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
19-0042948 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2019-04-16 | 361857 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
19-0045749 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2019-04-24 | 367246 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0052690 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2019-05-21 | 386724 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0053357 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Transformer only | 5 | 17 | 2019-05-17 | 383718 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0056528 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 23 | 2019-05-23 | 389065 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0057586 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2019-05-25 | 390085 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0057838 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 26 | 2019-05-26 | 390870 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0061097 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 6 | 1 | 2019-06-01 | 394968 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0063925 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 3 - Extreme | Transformer only | 6 | 6 | 2019-06-06 | 400131 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0068319 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 16 | 2019-06-16 | 417139 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0068480 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2019-06-17 | 417295 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0073518 | Animal | Squirrel | Transformer (OH) | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2019-07-01 | 438423 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
19-0074900 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2019-07-06 | 441677 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0076959 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2019-07-12 | 447757 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0082539 | Animal | Squirrel | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2019-07-30 | 475476 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
19-0086584 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2019-08-10 | 501675 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
19-0095358 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2019-09-04 | 553367 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0097965 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2019-09-11 | 572453 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0099234 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 15 | 2019-09-15 | 583270 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0100661 | 3rd Party | Tree - cutting, 3rd party | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 9 | 18 | 2019-09-18 | 590433 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Transformer¦Burnedflashed
19-0101486 | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 19 | 2019-09-19 | 595700 | Sus | Y | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Broken
19-0105739 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2019-10-01 | 633516 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0106874 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 10 | 3 | 2019-10-03 | 638912 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
19-0107857 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 10 | 5 | 2019-10-05 | 644225 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
19-0112567 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2019-10-16 | 663195 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0118804 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2019-10-29 | 694094 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦FailedFaulted
19-0124290 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2019-11-13 | 706109 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0125308 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2019-11-15 | 707887 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0126925 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 11 | 20 | 2019-11-20 | 711709 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
19-0128064 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2019-11-23 | 713695 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0129212 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 716125 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0129501 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 718027 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0130029 | 3rd Party | Vandalism | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 720654 | Sus | Y | 3rdParty¦Vandalism¦PoleWood¦Broken
19-0130786 | Animal | Bird found | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2019-11-28 | 722628 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
19-0131671 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724544 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0132128 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2019-12-01 | 726742 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0134888 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2019-12-07 | 733148 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0136149 | Animal | Bird found | Bus | Burned/flashed | 2019 | Tier 2 - Elevated | Substation - Distribution | 12 | 12 | 2019-12-12 | 737384 | Sus | N | Animal¦Birdfound¦Bus¦Burnedflashed
19-0136394 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2019-12-13 | 738435 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0137783 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2019-12-23 | 749728 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0137823 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2019-12-24 | 749856 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0009650 | Company Initiated | Improper Construction | Conductor, Underground | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2020-02-08 | 780592 | Sus | N | CompanyInitiated¦ImproperConstruction¦ConductorUnderground¦Normal
20-0013696 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2020-01-25 | 770132 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0020221 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 781747 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0027529 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2020-03-01 | 820797 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0029798 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2020-03-07 | 838315 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0030578 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2020-03-10 | 843201 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0032464 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2020-03-15 | 853008 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0032485 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 853317 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0032537 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853764 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0037265 | Animal | Squirrel | Cutout, fuse holder | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2020-03-30 | 870697 | Sus | N | Animal¦Squirrel¦Cutoutfuseholder¦Normal
20-0038616 | Environmental/External | Ice or snow | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 5 | 2020-04-05 | 882971 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Together
20-0039014 | 3rd Party | Customer Equipment | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2020-04-06 | 886133 | Sus | N | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal
20-0039373 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2020-04-08 | 890795 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
20-0041589 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2020-04-15 | 895772 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0043246 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2020-04-21 | 898787 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
20-0044517 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2020-04-25 | 901262 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0048367 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2020-05-08 | 909332 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0056088 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2020-05-31 | 926768 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0056448 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2020-06-02 | 927993 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0056846 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2020 | Tier 3 - Extreme | Transformer only | 6 | 3 | 2020-06-03 | 929052 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
20-0059257 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2020-06-09 | 935185 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0059865 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 6 | 10 | 2020-06-10 | 936239 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
20-0063508 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 22 | 2020-06-22 | 944135 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0066351 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2020-06-29 | 953970 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0068275 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2020-07-03 | 957452 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0069812 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2020-07-08 | 960520 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0071759 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2020 | Tier 3 - Extreme | Transformer only | 7 | 14 | 2020-07-14 | 964552 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
20-0073744 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 20 | 2020-07-20 | 968470 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0074036 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2020-07-21 | 969082 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0076514 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2020-07-27 | 973166 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0084464 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2020-08-15 | 1009273 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
20-0084499 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2020-08-15 | 1005054 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0084980 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 16 | 2020-08-16 | 1012721 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0086339 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2020-08-17 | 1017741 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0088349 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 20 | 2020-08-20 | 1025964 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0090839 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2020-08-27 | 1035359 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0093908 | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2020-09-06 | 1057033 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦BurnedOpen
20-0099795 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086080 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0103798 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2020-10-01 | 1102961 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0109944 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2020-10-17 | 1119813 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0110429 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2020-10-19 | 1121054 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0111566 | 3rd Party | Customer Equipment | Metering Equipment | Malfunctioning | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2020-10-22 | 1123354 | Sus | Y | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Malfunctioning
20-0112261 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 10 | 23 | 2020-10-23 | 1124112 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0113692 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2020-10-27 | 1129663 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0123691 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2020-11-20 | 1150474 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0130147 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 12 | 13 | 2020-12-13 | 1182558 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0131018 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Transformer only | 12 | 17 | 2020-12-17 | 1193145 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
21-0010361 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1215627 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0011381 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2021-01-20 | 1218554 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0011820 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1219387 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0014406 | Vegetation | Tree - fell into line | Insulator | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224752 | Sus | N | Vegetation¦Treefellintoline¦Insulator¦Broken
21-0015760 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232512 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0015791 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1232679 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0016063 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233434 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016460 | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234048 | Sus | N | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Normal
21-0017284 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1238626 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020618 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2021-02-01 | 1245467 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
21-0021445 | 3rd Party | Tree - cutting, 3rd party | Fuse | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2021-02-23 | 1260129 | Sus | N | 3rdParty¦Treecutting3rdparty¦Fuse¦Normal
21-0022295 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2021-02-05 | 1248715 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
21-0033809 | Equipment Failure/Involved | Electrical Overload | Jumper | Burned Open | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2021-04-15 | 1317616 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Jumper¦BurnedOpen
21-0034206 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2021-03-09 | 1276313 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0038906 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2021-03-20 | 1289527 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0047209 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 10 | 2021-04-10 | 1312833 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0051089 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2021-04-20 | 1325932 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0054777 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 29 | 2021-04-29 | 1336974 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0058449 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2021-05-07 | 1343292 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0062542 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2021-05-18 | 1351953 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0063032 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 18 | 2021-05-18 | 1352847 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0065368 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 24 | 2021-05-24 | 1357763 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0067403 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2021-05-28 | 1360711 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0077290 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2021-06-22 | 1381705 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0082940 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2021-06-30 | 1389192 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0084476 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2021-07-02 | 1390950 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0084773 | Animal | Squirrel | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 4 | 2021-07-04 | 1391580 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
21-0092834 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 7 | 21 | 2021-07-21 | 1409871 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0107355 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2021-08-20 | 1448686 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
21-0107978 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2021-08-22 | 1450177 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0110872 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 8 | 30 | 2021-08-30 | 1457837 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
21-0111260 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2021-08-30 | 1458415 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
21-0111721 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 31 | 2021-08-31 | 1459230 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0113685 | Animal | Other | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2021-09-04 | 1462153 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
21-0116391 | Animal | Squirrel | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2021-09-11 | 1468940 | Sus | Y | Animal¦Squirrel¦Fuse¦BurnedOpen
21-0135336 | Vegetation | Tree - fell into line | Service conductor | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2021-10-22 | 1506288 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
21-0136227 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511710 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0136500 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514261 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0136500 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514261 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0136545 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1513822 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137339 | Vegetation | Tree - fell into line | Pole-Wood | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509719 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Normal
21-0137496 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1518800 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
21-0137579 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 10 | 25 | 2021-10-25 | 1519192 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0143004 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2021-11-06 | 1536239 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0143117 | Animal | Squirrel | Switch | Normal | 2021 | Tier 2 - Elevated | Substation - Distribution | 11 | 7 | 2021-11-07 | 1536747 | Sus | Y | Animal¦Squirrel¦Switch¦Normal
21-0154143 | Company Initiated | Construction Activity/equip, company |  | Normal | 2021 | Tier 2 - Elevated | Transformer only | 12 | 2 | 2021-12-02 | 1557861 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦¦Normal
21-0156009 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2021-12-08 | 1562071 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157235 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1567053 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
21-0157658 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568800 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0157919 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1570177 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158891 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574227 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158895 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573945 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0158956 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1575034 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0159312 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574666 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0160222 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2021-12-23 | 1579544 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0160222 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2021-12-23 | 1579544 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0160708 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582120 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0161222 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585784 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
21-0161448 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1587546 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0161970 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2021-12-31 | 1590610 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
22-0005023 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2021-12-31 | 1590946 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0005362 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 2 - Elevated | Transformer only | 1 | 3 | 2022-01-03 | 1593150 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0007005 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2022-01-05 | 1596162 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0008235 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2022-01-11 | 1599705 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
22-0008350 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2022-01-11 | 1599872 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0009606 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2022-01-13 | 1601389 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
22-0010387 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2022-01-16 | 1603718 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0011169 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | 2022 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2022-01-19 | 1605095 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken
22-0013013 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2022-01-22 | 1608923 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0013168 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2022-01-23 | 1609841 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0014278 | 3rd Party | Fire, house or bldg. | Customer Equipment | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 1 | 25 | 2022-01-25 | 1612058 | Sus | N | 3rdParty¦Firehouseorbldg¦CustomerEquipment¦Burnedflashed
22-0017357 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2022-02-02 | 1618803 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0018586 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2022-02-04 | 1621079 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0019579 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2022-02-07 | 1622977 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0020860 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2022-02-10 | 1624535 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0036631 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transmission line | 3 | 22 | 2022-03-22 | 1653049 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0038265 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2022-03-24 | 1655423 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0044808 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2022-04-09 | 1666544 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0045145 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2022 | Tier 3 - Extreme | Transformer only | 4 | 10 | 2022-04-10 | 1667476 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
22-0054579 | 3rd Party | Customer Equipment | Secondary | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2022-04-26 | 1681734 | Sus | N | 3rdParty¦CustomerEquipment¦Secondary¦Burnedflashed
22-0056946 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2022-05-02 | 1686514 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0060383 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 10 | 2022-05-10 | 1693104 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0064969 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 22 | 2022-05-22 | 1707393 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0067257 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 26 | 2022-05-26 | 1712126 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0070211 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2022-06-04 | 1719129 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0070297 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2022-06-05 | 1719439 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0070358 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 5 | 2022-06-05 | 1719661 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
22-0071194 | 3rd Party | Customer Equipment | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2022-06-07 | 1721668 | Sus | Y | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal
22-0073699 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2022-06-13 | 1730233 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0080676 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 3 - Extreme | Transformer only | 6 | 30 | 2022-06-30 | 1746582 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0083535 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2022-07-09 | 1752143 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
22-0087336 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2022-07-19 | 1760700 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0089573 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2022-07-25 | 1765430 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0091597 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2022-07-30 | 1768711 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0100986 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2022-08-23 | 1788386 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0111388 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 9 | 16 | 2022-09-16 | 1812922 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0121753 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2022-10-15 | 1837741 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
22-0122528 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 10 | 18 | 2022-10-18 | 1839775 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0130651 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2022-11-13 | 1861521 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0135460 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2022-12-01 | 1872871 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138713 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882691 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0142478 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903197 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0004677 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 1 | 14 | 2015-01-14 | 1163864 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0010436 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1175008 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
15-0010629 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1178126 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0011297 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2015-02-07 | 1181473 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0011361 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2015-02-07 | 1180503 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0013523 | Equipment Failure/Involved | Other | Transformer | Broken | 2015 | Tier 2 - Elevated | Transformer only | 2 | 16 | 2015-02-16 | 1190868 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Broken
15-0032590 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230713 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0039118 | Animal | Squirrel | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2015-06-07 | 1245053 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0042011 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2015-06-18 | 1253084 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0042219 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 19 | 2015-06-19 | 1253498 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
15-0045997 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2015-07-07 | 1264264 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0048067 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2015-07-16 | 1269312 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0048774 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1272638 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0048778 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 19 | 2015-07-19 | 1272594 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0051541 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2015-07-30 | 1280025 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed
15-0052165 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2015-08-02 | 1281566 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0056803 | Animal | Squirrel | Transformer (OH) | Normal | 2015 | Tier 2 - Elevated | Transformer only | 8 | 23 | 2015-08-23 | 1293162 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
15-0059935 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2015-09-08 | 1301972 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
15-0062011 | Animal | Squirrel | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 17 | 2015-09-17 | 1307783 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
15-0070600 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2015-10-15 | 1322662 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0076899 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 10 | 2015-11-10 | 1338563 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦Normal
15-0076902 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 10 | 2015-11-10 | 1338565 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0078317 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2015-11-16 | 1343114 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0078414 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2015-11-16 | 1343511 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0082560 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352853 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0083700 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 9 | 2015-12-09 | 1356560 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
15-0083891 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357326 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0087295 | Vegetation | Tree - fell into line | Recloser | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2015-12-25 | 1371747 | Sus | N | Vegetation¦Treefellintoline¦Recloser¦Normal
15-0087949 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 12 | 31 | 2015-12-31 | 1375317 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0003628 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2016-01-06 | 1379007 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0006076 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2016-01-18 | 1385975 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0010219 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2016-02-02 | 1397389 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0011000 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2016-02-05 | 1399060 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0011049 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2016-02-06 | 1399337 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0014326 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 19 | 2016-02-19 | 1409557 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0015055 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 23 | 2016-02-23 | 1410946 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0018666 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2016-03-07 | 1423014 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0023079 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2016-03-21 | 1435399 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0023350 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2016-03-22 | 1436236 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0026081 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 4 | 2016-04-04 | 1444420 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0027865 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2016-04-11 | 1448988 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
16-0030432 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2016-04-22 | 1455419 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0036043 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2016-05-14 | 1469711 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0041139 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2016-06-05 | 1483201 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0046612 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 29 | 2016-06-29 | 1498220 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0048746 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2016-07-08 | 1503110 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0054900 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2016-08-03 | 1521156 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0055470 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 5 | 2016-08-05 | 1522337 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0063725 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 10 | 2016-09-10 | 1539400 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0066464 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Transformer only | 9 | 22 | 2016-09-22 | 1545775 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0068885 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2016-10-01 | 1550857 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0069689 | Animal | Bird found | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2016-10-04 | 1552813 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
16-0070706 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 10 | 2016-10-10 | 1555586 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072603 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561624 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0072925 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562942 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0073525 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 18 | 2016-10-18 | 1564933 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0075488 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 25 | 2016-10-25 | 1569880 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
16-0079773 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2016-11-14 | 1580801 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0085992 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2016-12-16 | 1604177 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0087463 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2016-12-31 | 1613692 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0003679 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1618517 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0004031 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1619317 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0004759 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1621961 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005267 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625954 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
17-0005720 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625993 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005850 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627213 | Sus | N | Vegetation¦Treebranchfellonline¦LightningArrestor¦Normal
17-0006707 | Vegetation | Tree - fell into line | Secondary | Broken | 2017 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2017-01-10 | 1632274 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Broken
17-0007158 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1636648 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
17-0011470 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653110 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0011976 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1656113 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0017034 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 2 | 2 | 2017-02-02 | 1673171 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0017226 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673895 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0018332 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679273 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0018576 | Equipment Failure/Involved | Other | Cutout, fuse holder | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679947 | Sus | N | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Broken
17-0018732 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680887 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0019149 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682456 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0023638 | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1702303 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground
17-0024796 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1707124 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025236 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1708897 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0025855 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2017-02-22 | 1711126 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0027668 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2017-03-01 | 1716897 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0028877 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720754 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0029467 | Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2017-03-08 | 1722727 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal
17-0032540 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2017-03-21 | 1732446 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0032551 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2017-03-21 | 1732366 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0033495 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2017-03-24 | 1734741 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0034366 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2017-03-28 | 1737340 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0035862 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2017-04-02 | 1742439 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038217 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2017-04-08 | 1752314 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0038429 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2017-04-09 | 1753424 | Sus | N | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
17-0039986 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757070 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0040103 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757279 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0043498 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2017-04-27 | 1768803 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0047691 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 13 | 2017-05-13 | 1781219 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0051873 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2017-05-31 | 1794086 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0054873 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 13 | 2017-06-13 | 1803340 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0056034 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2017-06-17 | 1807323 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0062804 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2017-07-14 | 1831155 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
17-0075617 | Environmental/External | Lightning | Secondary | Burned/flashed | 2017 | Tier 2 - Elevated | Transformer only | 9 | 3 | 2017-09-03 | 1868656 | Sus | Y | EnvironmentalExternal¦Lightning¦Secondary¦Burnedflashed
17-0077284 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 10 | 2017-09-10 | 1874171 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0083565 | Equipment Failure/Involved | Overhead | Secondary | On Ground | 2017 | Tier 2 - Elevated | Transformer only | 10 | 2 | 2017-10-02 | 1889713 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦OnGround
17-0086444 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1898756 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0086758 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2017-10-12 | 1899237 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0088813 | Vegetation | Tree - branch fell on line | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2017-10-19 | 1904644 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦FailedFaulted
17-0098232 | Animal | Squirrel | Pole-Wood | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2017-11-28 | 1931370 | Sus | Y | Animal¦Squirrel¦PoleWood¦Normal
17-0099849 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1936041 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0102941 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2017-12-21 | 1949476 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0103257 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2017-12-25 | 1951048 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0103504 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2017-12-28 | 1952496 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0004048 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 1 | 6 | 2018-01-06 | 3226 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0004312 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2018-01-08 | 3858 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0004505 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2018-01-08 | 4414 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0009337 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2018-01-26 | 14623 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
18-0013157 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2018-02-10 | 22579 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0017192 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2018-02-26 | 31632 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
18-0019065 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 35957 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0020461 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 6 | 2018-03-06 | 39519 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0022547 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 43769 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023482 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 16 | 2018-03-16 | 45958 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
18-0023594 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 45464 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0024318 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2018-03-20 | 48301 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0027875 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2018-03-29 | 56297 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0030296 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2018-04-07 | 62135 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0030770 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2018-04-10 | 63581 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0033064 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 4 | 17 | 2018-04-17 | 68634 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
18-0044921 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2018-05-28 | 95396 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0045432 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 5 | 29 | 2018-05-29 | 96441 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0045890 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2018-05-31 | 97649 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
18-0051881 | Animal | Squirrel | Transformer (OH) | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2018-06-18 | 111799 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
18-0054438 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2018-06-25 | 118183 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0059908 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2018-07-14 | 131936 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0062212 | Animal | Other | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 7 | 21 | 2018-07-21 | 136854 | Sus | Y | Animal¦Other¦Transformer¦FailedFaulted
18-0064616 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2018-07-28 | 142676 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0066094 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | On Ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2018-07-29 | 147384 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦OnGround
18-0070845 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2018-08-16 | 156652 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0071303 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2018-08-18 | 157433 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0072774 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2018-08-23 | 160837 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
18-0075066 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 30 | 2018-08-30 | 165369 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
18-0078121 | Animal | Bird found | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 10 | 2018-09-10 | 171457 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦FailedFaulted
18-0084910 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 29 | 2018-09-29 | 184240 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0085529 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 2 | 2018-10-02 | 185525 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0088057 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2018-10-08 | 190523 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0090193 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2018-10-14 | 194784 | Sus | Y | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
18-0098245 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 211438 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0100799 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217802 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0103317 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2018-11-26 | 224714 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
18-0104799 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2018-11-29 | 227529 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0105240 | Equipment Failure/Involved | Overhead | Stepdown | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 11 | 29 | 2018-11-29 | 229299 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Stepdown¦FailedFaulted
18-0105284 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2018-11-29 | 229208 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
18-0106628 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2018-12-03 | 232773 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
18-0107482 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2018-12-05 | 234602 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0108776 | Animal | Squirrel | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2018-12-12 | 238435 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦Normal
18-0109845 | Equipment Failure/Involved | Overhead | Woodpin | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2018-12-18 | 242960 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Brokenwireonground
19-0006467 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2019-01-08 | 260847 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0009291 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2019-01-15 | 265985 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0011376 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 267626 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0013885 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2019-01-24 | 280107 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0016851 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 285892 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0017397 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 288290 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017635 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2019-02-03 | 289223 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0017803 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289666 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018656 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292672 | Sus | N | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
19-0021023 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 299839 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0022154 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 302941 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0022799 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 306504 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0022966 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 305588 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024077 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 312216 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024493 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 310634 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0024651 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2019-02-15 | 314703 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024710 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 314930 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025132 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315820 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025195 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315911 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028483 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324324 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0032653 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2019-03-11 | 336294 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0033173 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2019-03-12 | 337472 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0033617 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2019-03-13 | 338768 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
19-0034318 | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2019-03-16 | 340600 | Sus | N | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted
19-0039181 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2019-04-02 | 352516 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0042250 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2019-04-13 | 360419 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0043810 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2019-04-17 | 362763 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0044509 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2019-04-19 | 364068 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0048900 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 4 | 2019-05-04 | 373766 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
19-0050938 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2019-05-10 | 378248 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0052474 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 15 | 2019-05-15 | 381423 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0052589 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2019-05-16 | 382130 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0057644 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 25 | 2019-05-25 | 390290 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0060281 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2019-05-30 | 393828 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0061054 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 31 | 2019-05-31 | 394861 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0063895 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2019-06-06 | 400061 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0064515 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 8 | 2019-06-08 | 401169 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0069092 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 6 | 18 | 2019-06-18 | 418635 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
19-0071400 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2019-06-24 | 427462 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0075866 | Vegetation | Tree - fell into line | Secondary | Bent or Twisted | 2019 | Tier 3 - Extreme | Transformer only | 7 | 10 | 2019-07-10 | 444061 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦BentorTwisted
19-0079964 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2019-07-22 | 468034 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0085780 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2019-08-08 | 492808 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0089783 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2019-08-20 | 524248 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0094117 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 30 | 2019-08-30 | 548873 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0096470 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2019 | Tier 2 - Elevated | Transformer only | 9 | 7 | 2019-09-07 | 562129 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
19-0101604 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2019-09-20 | 595926 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0102260 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2019-09-22 | 604106 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing
19-0107036 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2019-10-03 | 638978 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0119399 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2019-10-30 | 696279 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
19-0122199 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2019-11-06 | 701179 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0130001 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 720545 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0130797 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722558 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131058 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2019-11-29 | 723469 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0134927 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2019-12-07 | 733237 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0010579 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 764754 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0015874 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 1 | 31 | 2020-01-31 | 774226 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0019425 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 785070 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0025242 | Animal | Other |  | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 2 | 24 | 2020-02-24 | 801374 | Sus | N | Animal¦Other¦¦FailedFaulted
20-0027249 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2020-02-28 | 819454 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0028626 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2020-03-04 | 829209 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
20-0029685 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2020-03-06 | 837709 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031912 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2020-03-13 | 850677 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032754 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 854457 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0034545 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2020-03-20 | 859408 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0036318 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2020-03-26 | 866257 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0039450 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2020-04-07 | 890322 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0053573 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2020-05-22 | 920100 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0054902 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 27 | 2020-05-27 | 923570 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0058311 | Animal | Bird found |  | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 6 | 5 | 2020-06-05 | 932208 | Sus | Y | Animal¦Birdfound¦¦FailedFaulted
20-0061029 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2020-06-14 | 938915 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0063952 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 6 | 23 | 2020-06-23 | 945196 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0076097 | Vegetation | Tree - branch fell on line | Woodpin | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2020-07-26 | 972261 | Sus | Y | Vegetation¦Treebranchfellonline¦Woodpin¦Broken
20-0077931 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2020-07-30 | 975447 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
20-0080827 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2020-08-07 | 982895 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0082977 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2020-08-13 | 994815 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
20-0085659 | Environmental/External | Lightning | Switch | Normal | 2020 | Tier 2 - Elevated | Transmission line | 8 | 17 | 2020-08-17 | 1015944 | Sus | Y | EnvironmentalExternal¦Lightning¦Switch¦Normal
20-0086202 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2020-08-17 | 1017503 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0088587 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2020-08-21 | 1026466 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091322 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2020-08-29 | 1040493 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
20-0092029 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2020-09-01 | 1045196 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0096787 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Transformer only | 9 | 12 | 2020-09-12 | 1065438 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0098419 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 17 | 2020-09-17 | 1077066 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0101920 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1095500 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0109143 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2020-10-15 | 1118483 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0113958 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Transformer only | 10 | 27 | 2020-10-27 | 1130063 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0116175 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Transformer only | 11 | 2 | 2020-11-02 | 1134419 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0118481 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2020-11-08 | 1139473 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0121012 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Transformer only | 11 | 14 | 2020-11-14 | 1145317 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0121077 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2020-11-15 | 1145610 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0124053 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2020-11-23 | 1152964 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0128462 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1168133 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0010716 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216314 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0014839 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1227167 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0015935 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1227801 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0017613 | Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | 2021 | Tier 3 - Extreme | Substation - Transmission | 6 | 25 | 2021-06-25 | 1385275 | Sus | Y | CompanyInitiated¦ReturnCircuitNormal¦CircuitBreaker¦Normal
21-0019999 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 31 | 2021-01-31 | 1243902 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0020509 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1245237 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0021840 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2021-02-04 | 1247957 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
21-0023194 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Transformer only | 2 | 8 | 2021-02-08 | 1250888 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0027139 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 2 | 18 | 2021-02-18 | 1257585 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0027623 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2021-02-20 | 1258338 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0030176 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 2 | 26 | 2021-02-26 | 1263286 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0033903 | Vegetation | Tree - fell into line | Conductor, Underground | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2021-03-09 | 1274916 | Sus | N | Vegetation¦Treefellintoline¦ConductorUnderground¦Normal
21-0034287 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2021-03-10 | 1276649 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0046138 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2021-04-08 | 1310311 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
21-0049896 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 4 | 17 | 2021-04-17 | 1320760 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
21-0055142 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 29 | 2021-04-29 | 1337452 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0061978 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2021-05-16 | 1350674 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0061984 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 16 | 2021-05-16 | 1350767 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0068623 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2021-06-01 | 1363421 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
21-0073509 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2021-06-12 | 1371476 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0077728 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2021-06-22 | 1382536 | Sus | Y | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken
21-0079062 | Animal | Squirrel | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2021-06-24 | 1384081 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
21-0080246 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 26 | 2021-06-26 | 1385434 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
21-0087689 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 11 | 2021-07-11 | 1399190 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0087778 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2021-07-11 | 1399788 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0089232 | 3rd Party | Customer Equipment | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 13 | 2021-07-13 | 1403766 | Sus | Y | 3rdParty¦CustomerEquipment¦Transformer¦FailedFaulted
21-0091307 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 17 | 2021-07-17 | 1407122 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0092295 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 7 | 20 | 2021-07-20 | 1408764 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0100834 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2021-08-06 | 1435538 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0101648 | Vegetation | Tree - fell into line | Conductor, Underground | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2021-08-08 | 1437116 | Sus | Y | Vegetation¦Treefellintoline¦ConductorUnderground¦Broken
21-0109867 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 8 | 26 | 2021-08-26 | 1454676 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0113871 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 6 | 2021-09-06 | 1463027 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0122756 | Animal | Squirrel | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2021-09-27 | 1481279 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
21-0136441 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513915 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136477 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1513400 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
21-0136634 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513525 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0140399 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2021-11-01 | 1526857 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0140399 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2021-11-01 | 1526857 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0140861 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2021-11-01 | 1527554 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0145776 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2021-11-15 | 1545424 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0156524 | Company Initiated | Personnel, company | Lightning Arrestor | Burned/flashed | 2021 | Tier 2 - Elevated | Transformer only | 12 | 10 | 2021-12-10 | 1563528 | Sus | N | CompanyInitiated¦Personnelcompany¦LightningArrestor¦Burnedflashed
21-0158929 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1574939 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0158955 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1575030 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0159334 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Transmission line | 12 | 17 | 2021-12-17 | 1575869 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0160727 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1582189 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0161040 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582944 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0005053 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1591631 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0005587 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2022-01-03 | 1593795 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0007070 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2022-01-06 | 1596865 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0012760 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607741 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0017359 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2022-02-02 | 1618811 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0037606 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2022-03-23 | 1654565 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0043977 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2022-04-07 | 1665141 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0044976 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2022-04-09 | 1666975 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0045755 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669235 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0048488 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 14 | 2022-04-14 | 1672847 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0050708 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 4 | 17 | 2022-04-17 | 1675133 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0053014 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 21 | 2022-04-21 | 1678659 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0057743 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 4 | 2022-05-04 | 1687884 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0058116 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2022-05-05 | 1688765 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
22-0059429 | Animal | Bird found | Metering Equipment | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2022-05-08 | 1691189 | Sus | Y | Animal¦Birdfound¦MeteringEquipment¦Normal
22-0060425 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 10 | 2022-05-10 | 1693403 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0065626 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 24 | 2022-05-24 | 1708576 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0068075 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 30 | 2022-05-30 | 1714098 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
22-0069363 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 2 | 2022-06-02 | 1716660 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0074393 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2022-06-15 | 1731691 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0076066 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2022-06-19 | 1735476 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0078026 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2022-06-24 | 1740775 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0078196 | Animal | Squirrel | Fuse | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2022-06-24 | 1741230 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
22-0080824 | Vegetation | Tree - fell into line | Service conductor | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 30 | 2022-06-30 | 1746738 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
22-0097766 | Company Initiated | Personnel, company | Recloser | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2022-08-15 | 1781619 | Sus | Y | CompanyInitiated¦Personnelcompany¦Recloser¦Normal
22-0114660 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 9 | 25 | 2022-09-25 | 1821396 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0115154 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2022-09-27 | 1822290 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0116933 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 3 - Extreme | Transformer only | 10 | 1 | 2022-10-01 | 1825652 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0121711 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2022-10-14 | 1837455 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0125886 | Animal | Other | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2022-10-29 | 1848108 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
22-0126029 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 10 | 30 | 2022-10-30 | 1848808 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
22-0126143 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 31 | 2022-10-31 | 1849171 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0126810 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 1 | 2022-11-01 | 1850940 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0127327 | Company Initiated | Coordination failure | Recloser | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2022-11-03 | 1852274 | Sus | Y | CompanyInitiated¦Coordinationfailure¦Recloser¦Normal
22-0129406 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2022-11-08 | 1858299 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
22-0129942 | Environmental/External | Flood/Erosion | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 10 | 2022-11-10 | 1859799 | Sus | Y | EnvironmentalExternal¦FloodErosion¦Transformer¦FailedFaulted
22-0132783 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 11 | 19 | 2022-11-19 | 1865865 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0135770 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2022-12-01 | 1873511 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
22-0136216 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 12 | 2 | 2022-12-02 | 1874744 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0139888 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1889176 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0140992 | Animal | Squirrel | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2022-12-22 | 1895671 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦Broken
22-0142228 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2022-12-30 | 1902140 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
22-0142908 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1906510 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0003591 | Equipment Failure/Involved | Other | Transformer | Leaking | 2015 | Tier 2 - Elevated | Transformer only | 1 | 9 | 2015-01-09 | 1161572 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Leaking
15-0017809 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2015-03-06 | 1200117 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0026417 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2015-04-13 | 1218878 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0029600 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2015-04-25 | 1225104 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0032332 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2015-05-06 | 1230138 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0032939 | 3rd Party | Vehicle | Pole-Wood | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2015-05-08 | 1231688 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
15-0045605 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2015-07-05 | 1263380 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0048394 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2015-07-18 | 1270334 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0048908 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1273028 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0053041 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2015-08-05 | 1283276 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0059085 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2015-09-03 | 1299641 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
15-0059819 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2015-09-08 | 1301696 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0060295 | Vegetation | Tree - fell into line | Service conductor | Broken | 2015 | Tier 3 - Extreme | Transformer only | 9 | 9 | 2015-09-09 | 1302564 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
15-0060557 | 3rd Party | Fire, house or bldg. | Transformer (OH) | Normal | 2015 | Tier 2 - Elevated | Transformer only | 9 | 10 | 2015-09-10 | 1303412 | Sus | Y | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Normal
15-0066928 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 30 | 2015-09-30 | 1314404 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
15-0069598 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2015-10-12 | 1320383 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0074743 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2015-11-02 | 1332874 | Sus | Y | Vegetation¦Treebranchfellonline¦LightningArrestor¦Normal
15-0076481 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2015-11-08 | 1337538 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0076674 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2015-11-09 | 1337970 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0080616 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on object | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 24 | 2015-11-24 | 1348068 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject
15-0084371 | Animal | Squirrel |  | Burned Open | 2015 | Tier 2 - Elevated | Transformer only | 12 | 12 | 2015-12-12 | 1359307 | Sus | N | Animal¦Squirrel¦¦BurnedOpen
15-0085329 | Animal | Other | Transformer (UG) | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2015-12-14 | 1363601 | Sus | N | Animal¦Other¦Transformer(UG)¦Burnedflashed
15-0085347 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2015-12-14 | 1363651 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0085372 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2015-12-14 | 1363559 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0003888 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2016-01-07 | 1379678 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0003949 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 1 | 7 | 2016-01-07 | 1379995 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0009621 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2016-02-01 | 1395853 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0011266 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2016-02-08 | 1400022 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
16-0013240 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1405570 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
16-0014896 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2016-02-22 | 1410716 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0015243 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2016-02-24 | 1411482 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0020514 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2016-03-11 | 1428098 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0020756 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2016-03-12 | 1429279 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0020937 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430058 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0021758 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2016-03-15 | 1432227 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0022648 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2016-03-19 | 1434110 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0023162 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2016-03-22 | 1435917 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0023962 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2016-03-25 | 1438406 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
16-0028196 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2016-04-13 | 1449776 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0029189 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2016-04-17 | 1452331 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
16-0033069 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2016-05-01 | 1462791 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0034684 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2016-05-08 | 1466571 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0036608 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2016-05-17 | 1471394 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0041281 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 6 | 2016-06-06 | 1483775 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
16-0046177 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2016-06-28 | 1497242 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0050308 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 15 | 2016-07-15 | 1510875 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0050422 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2016-07-16 | 1511327 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
16-0054758 | Equipment Failure/Involved | Substation | Bushing | Failed/Faulted | 2016 | Zone 1 - HHZ | Generation | 8 | 3 | 2016-08-03 | 1521007 | Sus | Y | EquipmentFailureInvolved¦Substation¦Bushing¦FailedFaulted
16-0062855 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2016-09-07 | 1537654 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0065861 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2016-09-20 | 1544496 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0066934 | Animal | Bird found | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2016-09-23 | 1546561 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
16-0068229 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2016-09-28 | 1549434 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0069068 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2016-10-02 | 1551444 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
16-0069470 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 4 | 2016-10-04 | 1552432 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0072973 | Vegetation | Tree - grew into line | Transformer | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 10 | 16 | 2016-10-16 | 1562899 | Sus | Y | Vegetation¦Treegrewintoline¦Transformer¦Brokenwireonground
16-0073213 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2016-10-17 | 1564297 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0076811 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2016 | Tier 3 - Extreme | Transformer only | 10 | 30 | 2016-10-30 | 1573222 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
16-0078112 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2016-11-04 | 1576379 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0079352 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2016-11-11 | 1579668 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0082439 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589643 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0084859 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 9 | 2016-12-09 | 1598126 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0003336 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1616778 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005292 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626432 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005303 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transmission line | 1 | 8 | 2017-01-08 | 1626533 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005342 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625935 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0005445 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627304 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006278 | Vegetation | Tree - fell into line | Jumper | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1631953 | Sus | N | Vegetation¦Treefellintoline¦Jumper¦Burnedflashed
17-0007643 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638684 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0008210 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640829 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0008417 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638902 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011080 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2017-01-19 | 1651747 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0012847 | Vegetation | Tree - fell into line | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 22 | 2017-01-22 | 1658566 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Broken
17-0013392 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1662245 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013815 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662893 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0015741 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2017-01-27 | 1668873 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
17-0016128 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2017-01-30 | 1670566 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018042 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677300 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018694 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 7 | 2017-02-07 | 1680537 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0019017 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1681844 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019200 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 8 | 2017-02-08 | 1682637 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0024649 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706294 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024745 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706127 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025199 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707859 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025315 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1709301 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028313 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2017-03-04 | 1719240 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0029240 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2017-03-07 | 1722156 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0032913 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 22 | 2017-03-22 | 1733205 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0037490 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Transformer only | 4 | 6 | 2017-04-06 | 1748620 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0038194 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2017-04-08 | 1752260 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0044300 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2017-05-01 | 1771630 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0045988 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 6 | 2017-05-06 | 1776309 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0047167 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2017-05-11 | 1779863 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
17-0051136 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2017-05-27 | 1791775 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
17-0051866 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2017-05-31 | 1794083 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Deteriorated
17-0057737 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2017-06-22 | 1814867 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0060323 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 3 | 2017-07-03 | 1823018 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0061871 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2017-07-10 |  | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
17-0063193 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2017-07-16 | 1832619 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0067376 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2017-08-02 | 1844648 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦Normal
17-0067862 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2017-08-04 | 1846102 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0072435 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2017-08-23 | 1857953 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0072674 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2017-08-24 | 1858649 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0072909 | Animal | Bird found | Transformer (OH) | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2017-08-25 | 1859282 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
17-0079228 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 15 | 2017-09-15 | 1879341 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0089799 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2017-10-23 | 1908211 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Deteriorated
17-0093520 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2017-11-08 | 1918299 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0095320 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2017-11-15 | 1923219 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0099237 | Animal | Bird found | Fuse | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2017-12-02 | 1933855 | Sus | N | Animal¦Birdfound¦Fuse¦Normal
17-0099682 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1934964 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0100644 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2017-12-07 | 1938617 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0103276 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2017-12-25 | 1951093 | Sus | N | 3rdParty¦Vehicle¦AnchororGuy¦Broken
18-0005026 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2018-01-10 | 5953 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
18-0005394 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 1 | 11 | 2018-01-11 | 6696 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0005932 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 13 | 2018-01-13 | 7720 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
18-0007874 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2018-01-22 | 11974 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
18-0017102 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2018-02-26 | 31345 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0019470 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2018-03-03 | 37314 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0022855 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 44390 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
18-0023374 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 45567 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0023545 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 45960 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0024485 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2018-03-20 | 48632 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0024618 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2018-03-20 | 48992 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0027623 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2018-03-29 | 55652 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0029582 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2018-05-02 | 78288 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Together
18-0032303 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2018-04-14 | 67034 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0036569 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2018-04-29 | 76091 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0039354 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 5 | 8 | 2018-05-08 | 81805 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0040158 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2018-05-11 | 83637 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0040520 | 3rd Party | Metallic Balloon | Fuse | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2018-05-12 | 84929 | Sus | Y | 3rdParty¦MetallicBalloon¦Fuse¦Normal
18-0043472 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Transformer only | 5 | 23 | 2018-05-23 | 92352 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0049192 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2018-06-09 | 104994 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0050731 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2018-06-13 | 108506 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0051354 | 3rd Party | Tree - cutting, 3rd party | Transformer (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2018-06-15 | 110017 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Transformer(OH)¦Broken
18-0066790 | 3rd Party | Fire, house or bldg. | Jumper | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2018-08-04 | 149046 | Sus | Y | 3rdParty¦Firehouseorbldg¦Jumper¦Normal
18-0068121 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2018-08-09 | 151925 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075870 | Animal | Other | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2018-09-02 | 167068 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
18-0076917 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2018-09-05 | 168797 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0085704 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2018 | Tier 2 - Elevated | Transformer only | 10 | 2 | 2018-10-02 | 185655 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
18-0087957 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 7 | 2018-10-07 | 190256 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0090236 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2018-10-14 | 195156 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Other¦Normal
18-0093599 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2018-10-24 | 201186 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
18-0101683 | 3rd Party | Gun Shot | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2018-11-21 | 219464 | Sus | Y | 3rdParty¦GunShot¦ConductorOverhead¦Brokenwireonground
18-0102566 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2018-11-23 | 222874 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
18-0103320 | Vegetation | Tree - grew into line | Fuse | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2018-11-26 | 224855 | Sus | Y | Vegetation¦Treegrewintoline¦Fuse¦Normal
18-0103738 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 225437 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0105028 | Vegetation | Tree - fell into line | Transformer | Broken | 2018 | Tier 3 - Extreme | Transformer only | 11 | 29 | 2018-11-29 | 228108 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Broken
18-0109515 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2018-12-16 | 241649 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0005591 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 256855 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0006071 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2019-01-08 | 260069 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
19-0009780 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 267126 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009948 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 266846 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0011010 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 268967 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0011240 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 270302 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0011545 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 273926 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0012154 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2019-01-19 | 276532 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0017199 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286967 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0017318 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 287952 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0017969 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 4 | 2019-02-04 | 290392 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0018169 | Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 2 | 4 | 2019-02-04 | 291122 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonground
19-0019079 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 294151 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019115 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 291789 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0019977 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 296079 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020121 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2019-02-08 | 296428 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020852 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 299361 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
19-0022364 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 304969 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0022438 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 305197 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0023087 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 307269 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024723 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2019-02-16 | 314922 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0025115 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 315723 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0025601 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 317458 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025746 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 318175 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0025889 | Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 318449 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground
19-0029873 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2019-03-01 | 329235 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0030118 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2019-03-02 | 329790 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0030118 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2019-03-02 | 329790 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0031012 | Equipment Failure/Involved | Overhead | Pole-Wood | On Ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2019-03-05 | 331971 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦OnGround
19-0031087 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 332157 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0033017 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2019-03-12 | 337169 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0034005 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 3 | 14 | 2019-03-14 | 339670 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0035079 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2019-03-19 | 342942 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0036109 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2019-03-22 | 345367 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0037682 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348990 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0038625 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2019-03-31 | 351255 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0045849 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2019-04-24 | 367657 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0046559 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2019-04-26 | 368806 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0047748 | Animal | Other | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2019-05-01 | 371329 | Sus | Y | Animal¦Other¦Fuse¦FailedFaulted
19-0050444 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 2 - Elevated | Transformer only | 5 | 9 | 2019-05-09 | 377103 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0053105 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2019-05-16 | 383109 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0055980 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 22 | 2019-05-22 | 388375 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0057590 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 5 | 24 | 2019-05-24 | 390094 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0059045 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Transformer only | 5 | 29 | 2019-05-29 | 392633 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0062771 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2019-06-04 | 397932 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
19-0066965 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 6 | 12 | 2019-06-12 | 408325 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0068075 | Animal | Squirrel | Conductor, Overhead | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2019-06-15 | 414053 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Deteriorated
19-0077633 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2019-07-15 | 452796 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0078759 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 7 | 18 | 2019-07-18 | 458097 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0089314 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2019-08-19 | 521993 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0094428 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2019-09-01 | 550268 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0115687 | Wildfire Mitigation | Public Safety Power Shut-off | Generator | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 31 | 2019-10-31 | 697210 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Generator¦Normal
19-0119422 | Animal | Bird found | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2019-10-31 | 696350 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
19-0127901 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2019-11-23 | 713296 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0128851 | Equipment Failure/Involved | Overhead | Metering Equipment | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 715240 | Sus | Y | EquipmentFailureInvolved¦Overhead¦MeteringEquipment¦Burnedflashed
19-0129341 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 715879 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0129816 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 717055 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130815 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722796 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130935 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722523 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0132692 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2019-12-03 | 728201 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0132755 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2019-12-03 | 728257 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0138234 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2019-12-30 | 752653 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0009819 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 762496 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0013014 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2020-01-23 | 768943 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0025045 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2020-02-23 | 801060 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0025055 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2020-02-23 | 801109 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0029346 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2020-03-06 | 834693 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031780 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2020-03-13 | 849613 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0033003 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855001 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033055 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855168 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033518 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855543 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0034913 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2020-03-21 | 860231 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0037025 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 29 | 2020-03-29 | 869391 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0039987 | 3rd Party | Dig in, 3rd party | Transformer | Arcing | 2020 | Tier 2 - Elevated | Transformer only | 4 | 9 | 2020-04-09 | 892817 | Sus | N | 3rdParty¦Digin3rdparty¦Transformer¦Arcing
20-0041015 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 4 | 13 | 2020-04-13 | 894696 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0058579 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2020-06-07 | 933348 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0066096 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2020-06-29 | 952004 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0069319 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2020-07-07 | 959635 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0077191 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 7 | 28 | 2020-07-28 | 974019 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0081206 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2020-08-08 | 984375 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
20-0081225 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2020-08-08 | 985236 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0085948 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 8 | 16 | 2020-08-16 | 1010426 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0087025 | Environmental/External | Lightning | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 8 | 18 | 2020-08-18 | 1020514 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken
20-0088767 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2020-08-18 | 1026788 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090482 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033386 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0096218 | Environmental/External | Fire, Forest/Grass | Transformer | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 19 | 2020-08-19 | 1063992 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal
20-0099278 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2020-09-20 | 1083208 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0112056 | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2020-10-23 | 1123981 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed
20-0113154 | 3rd Party | Vehicle | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 10 | 25 | 2020-10-25 | 1126249 | Sus | Y | 3rdParty¦Vehicle¦Transformer(OH)¦Broken
20-0116279 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1134778 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0117649 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2020-11-06 | 1137115 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0119701 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2020-11-11 | 1141623 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0120701 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2020-11-13 | 1143578 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
20-0129532 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transformer only | 12 | 10 | 2020-12-10 | 1176209 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0131784 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2020-12-25 | 1198661 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0132074 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 3 - Extreme | Transformer only | 12 | 28 | 2020-12-28 | 1200280 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0007394 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2021-01-11 | 1208468 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal
21-0012189 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2021-01-20 | 1218786 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013305 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 23 | 2021-01-23 | 1221821 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0013563 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223068 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016033 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1228505 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0018014 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2021-01-28 | 1240477 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0018373 | Vegetation | Tree - fell into line | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Transformer only | 1 | 29 | 2021-01-29 | 1241524 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦Normal
21-0018649 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2021-01-29 | 1242403 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0020872 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2021-02-02 | 1245812 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0024077 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2021-02-10 | 1252137 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0024406 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2021-02-11 | 1252862 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0034995 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2021-03-10 | 1278183 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0039269 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2021-03-22 | 1291100 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0040521 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2021-03-24 | 1296072 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0044477 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 3 | 2021-04-03 | 1306395 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0050107 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2021-04-18 | 1322339 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0061919 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2021-05-15 | 1350234 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
21-0071402 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2021-06-08 | 1368436 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0099000 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2021-08-03 | 1429600 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0100703 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 8 | 5 | 2021-08-05 | 1435212 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0101590 | Animal | Squirrel | Switch (OH) | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2021-08-07 | 1436726 | Sus | Y | Animal¦Squirrel¦Switch(OH)¦Normal
21-0101908 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 9 | 2021-08-09 | 1438029 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0102899 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 11 | 2021-08-11 | 1439817 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0105899 | Equipment Failure/Involved | Overhead | Sectionalizer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2021-08-17 | 1445221 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Broken
21-0115978 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 9 | 10 | 2021-09-10 | 1467820 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0118200 | Animal | Bird found | Fuse | Burned Open | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2021-09-16 | 1472893 | Sus | Y | Animal¦Birdfound¦Fuse¦BurnedOpen
21-0118656 | 3rd Party | Tree - cutting, 3rd party | Fuse | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2021-09-16 | 1473452 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦Normal
21-0122326 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2021-09-25 | 1480209 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
21-0127134 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2021-10-07 | 1489360 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0129700 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2021-10-12 | 1495575 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0131972 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499149 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0137107 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2021-10-25 | 1517000 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137125 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512543 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137238 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1517362 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137500 | Vegetation | Tree - branch fell on line | Transformer | Normal | 2021 | Tier 3 - Extreme | Transformer only | 10 | 25 | 2021-10-25 | 1518531 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Normal
21-0137804 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1517142 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137978 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511933 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0138103 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1521387 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0138247 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2021-10-26 | 1521875 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0142975 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 5 | 2021-11-05 | 1535998 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0158005 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569500 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0158388 | Environmental/External | Water | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2021-12-15 | 1572243 | Sus | N | EnvironmentalExternal¦Water¦Transformer¦FailedFaulted
21-0160860 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582980 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0161249 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1586307 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0161708 | Vegetation | Tree - fell into line | Secondary | Together | 2021 | Tier 2 - Elevated | Transformer only | 12 | 29 | 2021-12-29 | 1589125 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Together
21-0161780 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2021-12-30 | 1589611 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0006806 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1596546 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0010067 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 1 | 14 | 2022-01-14 | 1602359 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
22-0022233 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2022-02-14 | 1627358 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0030290 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2022-03-05 | 1642904 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0033296 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2022-03-13 | 1647575 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0044255 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2022-04-07 | 1665435 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0044428 | Animal | Squirrel | Pole-Wood | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2022-04-08 | 1665867 | Sus | N | Animal¦Squirrel¦PoleWood¦Normal
22-0045752 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669340 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0052927 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 4 | 21 | 2022-04-21 | 1678632 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0053504 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2022-04-22 | 1679539 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
22-0059025 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2022-05-06 | 1690002 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0059214 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2022-05-07 | 1690362 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0065060 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2022-05-23 | 1707529 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0067738 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2022-05-28 | 1712927 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0074003 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2022-06-14 | 1730930 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
22-0084769 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2022-07-13 | 1755420 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
22-0086742 | Company Initiated | Operating error | Recloser | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2022-07-18 | 1759424 | Sus | Y | CompanyInitiated¦Operatingerror¦Recloser¦Normal
22-0090504 | Equipment Failure/Involved | Overhead | Jumper | Arcing | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 27 | 2022-07-27 | 1766798 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing
22-0097339 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2022-08-14 | 1780769 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0104285 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2022-08-31 | 1796172 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0113510 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2022-09-22 | 1818838 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0113568 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2022-09-22 | 1818909 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0121070 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2022-10-13 | 1836466 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0129674 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1858463 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
22-0129923 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2022-11-10 | 1859687 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0130142 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1860202 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0134002 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 24 | 2022-11-24 | 1868706 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0136340 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2022-12-03 | 1875288 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0138764 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882263 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0138901 | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1884096 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround
22-0141907 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2022-12-28 | 1900303 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0141938 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2022 | Tier 2 - Elevated | Transformer only | 12 | 27 | 2022-12-27 | 1899268 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
22-0142069 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2022-12-29 | 1901444 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
22-0142187 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2022-12-30 | 1901880 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
15-0033431 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2015-05-11 | 1232933 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0033693 | Equipment Failure/Involved | Overhead | Other | Broken | 2015 | Tier 2 - Elevated | Transformer only | 5 | 12 | 2015-05-12 | 1233526 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
15-0035708 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2015-05-21 | 1238011 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
15-0036180 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2015-05-23 | 1238865 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0037419 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2015-05-30 | 1241399 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0044430 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 30 | 2015-06-30 | 1259816 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0045385 | Vegetation | Tree - fell into line | Transformer | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 7 | 3 | 2015-07-03 | 1262422 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Deteriorated
15-0046114 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2015-07-07 | 1264463 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0047572 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2015-07-15 | 1268452 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
15-0050927 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Transformer only | 7 | 28 | 2015-07-28 | 1278537 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
15-0053710 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2015-08-07 | 1284324 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0055276 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2015-08-16 | 1289034 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
15-0062274 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2015-09-12 | 1308543 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
15-0066169 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2015-09-28 | 1313236 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0067753 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 4 | 2015-10-04 | 1316494 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0071351 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324427 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0072097 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2015-10-20 | 1326565 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
15-0074422 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2015-10-31 | 1331896 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0077754 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2015-11-14 | 1340963 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0078011 | Environmental/External | Lightning | Conductor, Underground | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342352 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorUnderground¦Burnedflashed
15-0083455 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2015-12-08 | 1355892 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083780 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357058 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0086447 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2015-12-21 | 1367822 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0002916 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2016-01-05 | 1377096 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0003379 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378051 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0005469 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 14 | 2016-01-14 | 1384125 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0006227 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2016-01-19 | 1386870 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0008728 | Animal | Squirrel | Transformer (OH) | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2016-01-27 | 1393046 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦Normal
16-0012200 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2016-02-11 |  | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0012595 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2016-02-14 | 1403369 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
16-0019826 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2016-03-10 | 1426198 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0020801 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 3 | 12 | 2016-03-12 | 1429403 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0032201 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2016-04-27 | 1460614 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0034717 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2016-05-08 | 1466690 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0036319 | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2016-05-16 | 1470665 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Burnedflashed
16-0036398 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2016-05-17 | 1470872 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
16-0045326 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 23 | 2016-06-23 | 1494530 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
16-0045825 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 26 | 2016-06-26 | 1496003 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0046127 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 27 | 2016-06-27 | 1497034 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0048278 | Animal | Bird found | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2016-07-06 | 1502118 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
16-0052490 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2016 | Tier 2 - Elevated | Transformer only | 7 | 26 | 2016-07-26 | 1516054 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
16-0056119 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2016-08-10 | 1524052 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
16-0060013 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 25 | 2016-08-25 | 1532138 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0061247 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2016-08-31 | 1534721 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0065429 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2016-09-18 | 1543491 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0076649 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2016-10-29 | 1572458 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0079087 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2016-11-09 | 1579122 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0081190 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2016-11-19 | 1585409 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0085643 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602238 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0086024 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2016-12-16 | 1604496 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0086758 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 22 | 2016-12-22 | 1609310 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0005153 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624053 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0006114 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1631232 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0006508 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632898 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007461 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1635312 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0007918 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638245 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007939 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639214 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0010578 | Equipment Failure/Involved | Underground | Elbow | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2017-01-19 | 1649215 | Sus | N | EquipmentFailureInvolved¦Underground¦Elbow¦Normal
17-0010608 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648728 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0012163 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655622 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0012704 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658576 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0013627 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663095 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0013910 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663076 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0017235 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673916 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
17-0017896 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2017-02-06 | 1676830 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
17-0023950 | Environmental/External | Flood/Erosion | Pole-Wood | On Ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704479 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦OnGround
17-0024889 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707440 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025210 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Contaminated | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704633 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Contaminated
17-0025666 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 3 - Extreme | Transformer only | 2 | 22 | 2017-02-22 | 1710841 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0028417 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2017-03-05 | 1719697 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0029360 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 8 | 2017-03-08 | 1722480 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0034658 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 29 | 2017-03-29 | 1738172 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
17-0035058 | Vegetation | Tree - branch fell on line | Secondary | Together | 2017 | Tier 3 - Extreme | Transformer only | 3 | 30 | 2017-03-30 | 1739034 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Together
17-0035802 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 4 | 1 | 2017-04-01 | 1742157 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0036313 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 4 | 4 | 2017-04-04 | 1743594 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
17-0037761 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1749774 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0043991 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 30 | 2017-04-30 | 1770915 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0047995 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2017-05-15 | 1782350 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0050356 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2017-05-24 | 1789639 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0054121 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2017-06-09 | 1800783 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0061009 | Animal | Bird found | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2017-07-06 | 1824782 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Together
17-0064684 | 3rd Party | Customer Equipment | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2017-07-22 | 1837439 | Sus | Y | 3rdParty¦CustomerEquipment¦ConductorOverhead¦OnGround
17-0076707 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2017-09-07 | 1872462 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
17-0079206 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 14 | 2017-09-14 | 1879298 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0084666 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2017-10-06 | 1891866 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0084884 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 10 | 6 | 2017-10-06 | 1892266 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0086365 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2017-10-11 | 1898059 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0087533 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1901343 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0089715 | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2017-10-23 | 1907767 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Malfunctioning
17-0090610 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Transformer only | 10 | 26 | 2017-10-26 | 1910079 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0091291 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 10 | 30 | 2017-10-30 | 1911902 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0095466 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2017-11-16 | 1923519 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0096799 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2017 | Tier 2 - Elevated | Transformer only | 11 | 21 | 2017-11-21 | 1927032 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
17-0098730 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2017-11-30 | 1932950 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
17-0100408 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2017-12-07 | 1937866 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0102914 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2017-12-21 | 1949231 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0102946 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2017-12-21 | 1949616 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0003814 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 1 | 5 | 2018-01-05 | 2460 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0006883 | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2018-01-17 | 9983 | Sus | N | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted
18-0009225 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2018-01-26 | 14327 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0013595 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2018-02-12 | 23575 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
18-0015213 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2018-02-18 | 26607 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0019549 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 4 | 2018-03-04 | 37867 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
18-0023448 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2018 | Tier 3 - Extreme | Transformer only | 3 | 16 | 2018-03-16 | 45954 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
18-0023800 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46981 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0029039 | Vegetation | Tree - grew into line | Secondary | Burned/flashed | 2018 | Tier 3 - Extreme | Transformer only | 4 | 3 | 2018-04-03 | 59068 | Sus | N | Vegetation¦Treegrewintoline¦Secondary¦Burnedflashed
18-0029135 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 4 | 2018-04-04 | 59466 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Normal
18-0042668 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2018-05-20 | 90290 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0044849 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2018-05-28 | 94999 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0049599 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 6 | 11 | 2018-06-11 | 106213 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0052795 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 20 | 2018-06-20 | 113705 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0058798 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2018-07-11 | 129013 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0065554 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 31 | 2018-07-31 | 146234 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
18-0067219 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 150078 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0069477 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2018-08-13 | 154826 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0073576 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2018-08-26 | 162594 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0074023 | 3rd Party | Vehicle | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2018-08-27 | 163363 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Broken
18-0075290 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 8 | 30 | 2018-08-30 | 165949 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0081255 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2018-09-19 | 177510 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
18-0087499 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 10 | 5 | 2018-10-05 | 189297 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0088004 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2018 | Tier 2 - Elevated | Transformer only | 10 | 7 | 2018-10-07 | 190451 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
18-0093676 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2018-11-01 | 207070 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦¦
18-0097661 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2018-11-07 | 210229 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0101243 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218606 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102229 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2018-11-22 | 221397 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0102407 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2018-11-22 | 222352 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0102471 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2018-11-23 | 222557 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
18-0104848 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 227677 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
18-0105076 | Vegetation | Tree - branch fell on line | Transformer | Broken | 2018 | Tier 3 - Extreme | Transformer only | 11 | 29 | 2018-11-29 | 228540 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Broken
18-0108867 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2018-12-12 | 238897 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0109479 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2018-12-16 | 241384 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109651 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2018-12-16 | 241729 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0110718 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2018-12-26 | 247401 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0111112 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2018-12-30 | 249645 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0003684 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 1 | 2 | 2019-01-02 | 252036 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0004944 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 254664 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009350 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2019-01-15 | 266396 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
19-0011167 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 272718 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0011293 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 269763 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
19-0011745 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2019-01-18 | 275325 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0012152 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2019-01-19 | 276817 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0016241 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 31 | 2019-01-31 | 284658 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0017191 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287496 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0017396 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 2 | 2019-02-02 | 287917 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0018769 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2019-02-05 | 293713 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
19-0019345 | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 2 | 6 | 2019-02-06 | 294703 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground
19-0020051 | Environmental/External | Ice or snow | Conductor, Overhead | Bent or Twisted | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2019-02-08 | 296266 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦BentorTwisted
19-0020622 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298189 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020632 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298358 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0021208 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Transformer only | 2 | 11 | 2019-02-11 | 299965 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0021801 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 302481 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0021963 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2019-02-12 | 301585 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0022604 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 305593 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0024240 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 312797 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024624 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 314631 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025713 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 317969 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025865 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 19 | 2019-02-19 | 317537 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0028881 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325471 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
19-0028929 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326674 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
19-0029374 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 328025 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
19-0034069 | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 3 | 15 | 2019-03-15 | 339853 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground
19-0034539 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2019-03-18 | 341661 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
19-0041128 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2019-04-09 | 357285 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0055090 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2019-05-21 | 387464 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0056929 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Transformer only | 5 | 24 | 2019-05-24 | 389612 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0058412 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2019-05-28 | 391482 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0059225 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2019-05-29 | 392908 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0062465 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 3 - Extreme | Transformer only | 6 | 4 | 2019-06-04 | 397265 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0064599 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2019-06-08 | 401514 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0066070 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 11 | 2019-06-11 | 405958 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0071766 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 25 | 2019-06-25 | 428308 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0073789 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2019-07-01 | 439247 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0075014 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2019-07-07 | 442129 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0075891 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Transmission line | 7 | 10 | 2019-07-10 | 444165 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0082322 | Environmental/External | Fire, Forest/Grass | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2019-07-29 | 474919 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal
19-0082748 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2019-07-30 | 475873 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0095512 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2019 | Tier 3 - Extreme | Transformer only | 9 | 5 | 2019-09-05 | 554616 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
19-0099061 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 14 | 2019-09-14 | 579725 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0099752 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2019-09-16 | 585282 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0102258 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2019-09-22 | 604083 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0102551 | Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2019-09-23 | 607716 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦CircuitBreaker¦Normal
19-0103372 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2019-09-25 | 612845 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0109091 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Zone 1 - HHZ | Distribution Circuit | 10 | 9 | 2019-10-09 | 649578 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0115581 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2019-10-24 | 679400 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0115796 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2019-10-24 | 679947 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0119843 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 11 | 1 | 2019-11-01 | 697267 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0129161 | Equipment Failure/Involved | Overhead | Customer Equipment | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 715811 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CustomerEquipment¦Burnedflashed
19-0129445 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 716004 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0130223 | Environmental/External | Ice or snow | Service conductor | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 720747 | Sus | Y | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦Brokenwireonground
19-0136168 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2019-12-12 | 737533 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
19-0136376 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Transformer only | 12 | 13 | 2019-12-13 | 738403 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0137893 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Transformer only | 12 | 25 | 2019-12-25 | 750211 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0016920 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2020-02-03 | 777307 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0018997 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 780902 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
20-0019762 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2020-02-10 | 786940 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken
20-0020483 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2020-02-11 | 788556 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject
20-0025877 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 2 | 26 | 2020-02-26 | 810305 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0029662 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2020-03-06 | 836576 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031192 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2020-03-11 | 844913 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0032343 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2020-03-15 | 852381 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken
20-0033053 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855654 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0038906 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2020-04-06 | 884453 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0040033 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2020-04-09 | 892971 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0040093 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2020-04-09 | 893070 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0056034 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2020-05-31 | 926726 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0056253 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2020-06-01 | 927447 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0058977 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2020-06-08 | 934447 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0063489 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2020-06-22 | 944011 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0069832 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2020-07-09 | 960539 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0080738 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2020-08-06 | 982235 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0081404 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2020 | Tier 2 - Elevated | Transformer only | 8 | 9 | 2020-08-09 | 987362 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
20-0085535 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2020-08-17 | 1015219 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0086321 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2020-08-17 | 1017535 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
20-0090327 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033071 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090491 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033395 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0095191 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2020-09-08 | 1061375 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0096028 | Environmental/External | Fire, Forest/Grass | Transformer | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 20 | 2020-08-20 | 1063502 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal
20-0104277 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 2 | 2020-10-02 | 1106082 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
20-0109712 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2020-10-16 | 1119343 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0110803 | Animal | Squirrel | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2020-10-20 | 1121651 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
20-0113039 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1127269 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0116194 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 2 | 2020-11-02 | 1134598 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0118223 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2020-11-07 | 1138045 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0120494 | 3rd Party | Customer Equipment | Circuit Breaker | Malfunctioning | 2020 | Tier 2 - Elevated | Transformer only | 11 | 13 | 2020-11-13 | 1143348 | Sus | Y | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Malfunctioning
20-0123908 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2020-11-22 | 1152650 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0130070 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2020-12-13 | 1182228 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0130472 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2020-12-15 | 1185970 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0004899 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2021-01-04 | 1204077 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
21-0004955 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 4 | 2021-01-04 | 1204192 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0012217 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1220083 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0017402 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1238579 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0019241 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1242969 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0025677 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 2 | 15 | 2021-02-15 | 1255367 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0029001 | Company Initiated | Improper Construction | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 2 | 24 | 2021-02-24 | 1261066 | Sus | N | CompanyInitiated¦ImproperConstruction¦Transformer(OH)¦Broken
21-0036030 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 13 | 2021-03-13 | 1280655 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
21-0036138 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2021-03-13 | 1281148 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0036268 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 3 | 14 | 2021-03-14 | 1282108 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0038598 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2021-03-19 | 1288873 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0041955 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2021-03-28 | 1302077 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0043049 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2021-03-30 | 1303880 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0048901 | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | 2021 | Tier 2 - Elevated | Transformer only | 4 | 15 | 2021-04-15 | 1317295 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Burnedflashed
21-0054049 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2021-04-27 | 1335774 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0057489 | Equipment Failure/Involved | Overhead | Regulator | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2021-05-05 | 1341878 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Regulator¦Burnedflashed
21-0073815 | Company Initiated | Operating error | Fuse | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2021-06-14 | 1372528 | Sus | Y | CompanyInitiated¦Operatingerror¦Fuse¦Normal
21-0075516 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 6 | 17 | 2021-06-17 | 1375980 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0085010 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2021-07-05 | 1392411 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0087428 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2021-07-10 | 1396772 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0090012 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 15 | 2021-07-15 | 1405099 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0091366 | Animal | Bird found | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2021-07-18 | 1407260 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Together
21-0096129 | Animal | Squirrel | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2021-07-28 | 1417244 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
21-0099419 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2021-08-03 | 1433264 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
21-0102376 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2021-08-10 | 1438914 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
21-0110375 | Environmental/External | Fire, Forest/Grass | Fuse | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2021-08-27 | 1455809 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal
21-0113714 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 5 | 2021-09-05 | 1462281 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0115845 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2021-09-10 | 1467603 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0118195 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2021-09-16 | 1472829 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0122545 | Animal | Other | Transformer Power | Normal | 2021 | Tier 2 - Elevated | Generation | 9 | 27 | 2021-09-27 | 1481095 | Sus | Y | Animal¦Other¦TransformerPower¦Normal
21-0123285 | Vegetation | Tree - branch fell on line | Jumper | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2021-09-28 | 1482650 | Sus | Y | Vegetation¦Treebranchfellonline¦Jumper¦Broken
21-0123431 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2021-09-28 | 1482773 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Broken
21-0134594 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 10 | 21 | 2021-10-21 | 1504495 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135914 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509810 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135935 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1510016 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0135977 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508323 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0136049 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509238 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0136584 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514581 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
21-0136836 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2021 | Tier 3 - Extreme | Transformer only | 10 | 24 | 2021-10-24 | 1515181 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
21-0138232 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512868 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0140341 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2021-10-31 | 1526495 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0140341 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2021-10-31 | 1526495 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0142937 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 5 | 2021-11-05 | 1535897 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0142937 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 5 | 2021-11-05 | 1535897 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0143245 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1537118 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0145892 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2021-11-15 | 1545647 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0146669 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2021-11-16 | 1547255 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0151357 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 26 | 2021-11-26 | 1554695 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0154839 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2021-12-03 | 1558963 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
21-0157705 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1569045 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157806 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569546 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0157861 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 12 | 14 | 2021-12-14 | 1569809 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0158063 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transmission line | 12 | 14 | 2021-12-14 | 1571043 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0158129 | 3rd Party | Vehicle | Pole-Wood | Normal | 2021 | Tier 2 - Elevated | Transformer only | 12 | 14 | 2021-12-14 | 1571450 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Normal
21-0158209 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 12 | 14 | 2021-12-14 | 1570913 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
21-0158731 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2021-12-15 | 1573668 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158916 | Vegetation | Tree - bark fell into line | Fuse | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574817 | Sus | N | Vegetation¦Treebarkfellintoline¦Fuse¦Normal
21-0160357 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2021-12-23 | 1580240 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161313 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2021-12-28 | 1586642 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0005559 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1593770 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
22-0005698 | Environmental/External | Ice or snow | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 12 | 30 | 2021-12-30 | 1589978 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Fuse¦BurnedOpen
22-0010273 | Animal | Other | Fuse | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2022-01-15 | 1602744 | Sus | N | Animal¦Other¦Fuse¦Normal
22-0012799 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607879 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0013063 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2022-01-22 | 1608163 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0016050 | Equipment Failure/Involved | Electrical Overload | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2022-01-29 | 1616075 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Broken
22-0022638 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2022-02-15 | 1628016 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0024279 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2022-02-18 | 1632096 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0025274 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2022-02-22 | 1634213 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0025957 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2022-02-23 | 1634911 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0026111 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2022 | Tier 3 - Extreme | Transmission line | 2 | 24 | 2022-02-24 | 1635312 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
22-0032316 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 3 | 10 | 2022-03-10 | 1646145 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0045238 | 3rd Party | Other | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1667788 | Sus | N | 3rdParty¦Other¦ConductorOverhead¦Broken
22-0047316 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2022-04-13 | 1671364 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0053215 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 22 | 2022-04-22 | 1679095 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0056560 | 3rd Party | Customer Equipment | Generator | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2022-05-01 | 1685699 | Sus | Y | 3rdParty¦CustomerEquipment¦Generator¦Normal
22-0057475 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2022-05-03 | 1687614 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0059826 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 9 | 2022-05-09 | 1692025 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0061426 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2022-05-12 | 1694832 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0065426 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2022-05-23 | 1708375 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0065746 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2022-05-24 | 1709024 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0074887 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 15 | 2022-06-15 | 1732701 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0081421 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2022-07-02 | 1747899 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0094592 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2022-08-06 | 1774933 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0102809 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2022-08-28 | 1793454 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
22-0103819 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 30 | 2022-08-30 | 1795325 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0108884 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2022-09-10 | 1808128 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
22-0110490 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 15 | 2022-09-15 | 1811554 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0116756 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 30 | 2022-09-30 | 1824718 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
22-0119392 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2022-10-08 | 1831864 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138652 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882086 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0138753 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1884461 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0141689 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898959 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0142016 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 12 | 29 | 2022-12-29 | 1900836 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
23-0004679 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1907501 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0003183 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2015-01-07 | 1160773 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0011431 | Equipment Failure/Involved | Other | Insulator | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2015-02-08 | 1182011 | Sus | N | EquipmentFailureInvolved¦Other¦Insulator¦Broken
15-0011726 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2015-02-08 | 1183478 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0027880 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 20 | 2015-04-20 | 1222018 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
15-0039036 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 6 | 2015-06-06 | 1244786 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0039999 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2015-06-10 | 1248315 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0040045 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2015-06-10 | 1248487 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0042268 | Animal | Squirrel | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 20 | 2015-06-20 | 1253690 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0046065 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2015-07-07 | 1264359 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0048598 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1271489 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0048788 | Vegetation | Tree - fell into line | Crossarm, Steel | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1272827 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmSteel¦Broken
15-0049828 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 7 | 22 | 2015-07-22 | 1275162 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0050720 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 27 | 2015-07-27 | 1277813 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0053930 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 9 | 2015-08-09 | 1285564 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0058128 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2015-08-29 | 1296576 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0061348 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1305761 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062041 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2015-09-12 | 1307896 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0063050 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 9 | 24 | 2015-09-24 | 1311121 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0067106 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2015-10-01 | 1314871 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0069469 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2015-10-11 | 1320134 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0081370 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2015-11-27 | 1349383 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0083632 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 9 | 2015-12-09 | 1356306 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0083697 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 9 | 2015-12-09 | 1356631 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0086717 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369230 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0087071 | 3rd Party | Customer Equipment | Customer Equipment | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2015-12-24 | 1370820 | Sus | N | 3rdParty¦CustomerEquipment¦CustomerEquipment¦FailedFaulted
15-0087434 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2015-12-26 | 1372034 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0002716 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2016-01-04 | 1376620 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0004208 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2016-01-09 | 1380720 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0009616 | Unknown Cause | Patrol - not conducted | Transformer | Malfunctioning | 2016 | Tier 3 - Extreme | Transformer only | 1 | 31 | 2016-01-31 | 1395595 | Sus | N | UnknownCause¦Patrolnotconducted¦Transformer¦Malfunctioning
16-0014355 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 2 | 20 | 2016-02-20 | 1409713 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0016879 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2016-03-03 | 1414977 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0017579 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416913 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0020412 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427799 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0021010 | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430411 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground
16-0021610 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2016-03-15 | 1431738 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0024553 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2016-03-28 | 1440120 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0029640 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2016-04-19 | 1453653 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0029679 | 3rd Party | Vehicle | Transformer (UG) | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2016-04-19 | 1453661 | Sus | N | 3rdParty¦Vehicle¦Transformer(UG)¦Broken
16-0030963 | Environmental/External | Lightning |  | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 4 | 23 | 2016-04-23 | 1456696 | Sus | N | EnvironmentalExternal¦Lightning¦¦FailedFaulted
16-0036371 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 16 | 2016-05-16 | 1470749 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0038157 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2016-05-24 | 1475989 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
16-0038411 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 25 | 2016-05-25 | 1476603 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0046010 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 27 | 2016-06-27 | 1496575 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0047681 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2016-07-03 | 1500543 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0058332 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2016-08-18 | 1528579 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Together
16-0058720 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2016-08-20 | 1529463 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0059807 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Transformer only | 8 | 24 | 2016-08-24 | 1531678 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0065386 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 17 | 2016-09-17 | 1543383 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0068471 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 29 | 2016-09-29 | 1549976 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0070533 | Vegetation | Tree - grew into line | Secondary | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 10 | 8 | 2016-10-08 | 1554947 | Sus | Y | Vegetation¦Treegrewintoline¦Secondary¦Brokenwireonground
16-0071168 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2016-10-11 | 1556450 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0071846 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1558105 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0079574 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2016-11-14 | 1580649 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0083616 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2016-12-02 | 1593382 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0086632 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2016-12-21 | 1608474 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0087127 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 12 | 27 | 2016-12-27 | 1611347 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0004957 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2017-01-08 | 1623047 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0005345 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625697 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0005584 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626785 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007348 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638230 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0007870 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640373 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0011563 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653882 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0011564 | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1654124 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground
17-0012042 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1656548 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013362 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1660450 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0019143 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682517 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0019926 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 10 | 2017-02-10 | 1684936 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
17-0022631 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1697694 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0023808 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703277 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0023895 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703304 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
17-0023930 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704223 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025396 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704443 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0033006 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2017-03-23 | 1733481 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0033119 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 23 | 2017-03-23 | 1733550 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0039523 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2017-04-12 | 1755976 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0041754 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 20 | 2017-04-20 | 1761954 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0047779 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2017-05-14 | 1781689 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0051748 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2017-05-31 | 1793833 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0054145 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 9 | 2017-06-09 | 1800879 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0056724 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 19 | 2017-06-19 | 1811135 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0060046 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2017-07-02 | 1822264 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0062821 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2017-07-14 | 1831199 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0075882 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 9 | 4 | 2017-09-04 | 1869969 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0077714 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 9 | 11 | 2017-09-11 | 1875259 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0077860 | Environmental/External | Lightning | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2017-09-11 | 1875982 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Brokenwireonground
17-0077908 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2017-09-11 | 1875701 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0080828 | 3rd Party | Fire, house or bldg. | Secondary | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2017-09-21 | 1883655 | Sus | Y | 3rdParty¦Firehouseorbldg¦Secondary¦Together
17-0083022 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2017-09-30 | 1888475 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0083081 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2017-09-30 | 1888730 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0085312 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893977 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
17-0088407 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1903598 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0089520 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2017 | Tier 2 - Elevated | Transformer only | 10 | 22 | 2017-10-22 | 1907146 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
17-0093155 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2017-11-07 | 1917261 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0100396 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2017-12-06 | 1937777 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0101971 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2017-12-16 | 1944192 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0004907 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2018-01-09 | 5556 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
18-0014437 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2018-02-15 | 24976 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
18-0015230 | Vegetation | Tree - fell into line | Conductor, Underground | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2018-02-18 | 26680 | Sus | N | Vegetation¦Treefellintoline¦ConductorUnderground¦Brokenwireonground
18-0018385 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 34208 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0019232 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 36507 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0019316 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2018-03-03 | 37085 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0023725 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2018-03-17 | 46425 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0024869 | 3rd Party | Customer Equipment | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2018-03-21 | 49330 | Sus | N | 3rdParty¦CustomerEquipment¦Fuse¦FailedFaulted
18-0026340 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Transformer only | 3 | 24 | 2018-03-24 | 52838 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0031951 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2018-04-13 | 66023 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
18-0032261 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 4 | 14 | 2018-04-14 | 66832 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0041044 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 14 | 2018-05-14 | 86209 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0046738 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2018-06-03 | 99924 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0049327 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2018-06-09 | 105526 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0052462 | Animal | Other | Transformer (UG) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2018-06-19 | 113259 | Sus | Y | Animal¦Other¦Transformer(UG)¦Normal
18-0056489 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 2 | 2018-07-02 | 123283 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
18-0057617 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2018-07-06 | 125781 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0058127 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2018-07-09 | 127663 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0058915 | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 11 | 2018-07-11 | 129256 | Sus | Y | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Normal
18-0066781 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2018-08-04 | 148981 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
18-0072114 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2018-08-21 | 159347 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075381 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2018-08-31 | 166276 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
18-0077327 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2018-09-06 | 169571 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0079615 | Equipment Failure/Involved | Underground | Other | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 14 | 2018-09-14 | 174088 | Sus | Y | EquipmentFailureInvolved¦Underground¦Other¦Normal
18-0079960 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 15 | 2018-09-15 | 174755 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
18-0086165 | Company Initiated | Other Circuits | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2018-10-03 | 187248 | Sus | Y | CompanyInitiated¦OtherCircuits¦CrossarmWood¦Broken
18-0090299 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2018-10-14 | 195022 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0090334 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2018-10-14 | 195169 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
18-0092626 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2018-10-21 | 199728 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0096712 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2018-11-02 | 207784 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦¦
18-0102492 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 222652 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104624 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2018-11-28 | 226993 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
18-0104767 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 227701 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
18-0105252 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228032 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0106961 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2018-12-04 | 233558 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Burnedflashed
18-0107823 | Environmental/External | Fire, Forest/Grass | Pole-Wood | On Ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 235575 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦OnGround
18-0109499 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2018-12-16 | 241599 | Sus | N | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Normal
18-0110929 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2018-12-28 | 248544 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0111195 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2018-12-31 | 250018 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0003401 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 1 | 2019-01-01 | 251314 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0003712 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 2 | 2019-01-02 | 251803 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0005472 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 256340 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0008700 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 14 | 2019-01-14 | 264639 | Sus | N | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonground
19-0011023 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 274009 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0011638 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2019-01-18 | 275247 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
19-0011754 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2019-01-18 | 275679 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0012754 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2019-01-20 | 277705 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0014940 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2019-01-28 | 282383 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0017688 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289396 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0017712 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 289550 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0018145 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 4 | 2019-02-04 | 290910 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0019779 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2019-02-07 | 295705 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0021190 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 300175 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0022034 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303130 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022139 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303453 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024018 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 310431 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025261 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315826 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025677 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 317926 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
19-0025736 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 318057 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0025829 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2019-02-18 | 318268 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0026489 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2019-02-20 | 319748 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
19-0027511 | Equipment Failure/Involved | Overhead | Stepdown | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 23 | 2019-02-23 | 321942 | Sus | N | EquipmentFailureInvolved¦Overhead¦Stepdown¦FailedFaulted
19-0027945 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2019-02-25 | 323333 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0029304 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 327697 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0030289 | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2019-03-03 | 330325 | Sus | N | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Burnedflashed
19-0031164 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2019-03-06 | 332249 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0034346 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2019-03-16 | 340629 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0035104 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2019-03-19 | 343033 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0035688 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2019-03-21 | 344441 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0037560 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348609 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0037719 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348947 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0037736 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2019-03-28 | 349119 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0040262 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2019-04-06 | 354844 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0041464 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2019-04-10 | 358486 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0052159 | Equipment Failure/Involved | Overhead | PGs, Kearneys | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2019-05-15 | 380943 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Brokenwireonground
19-0058286 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2019-05-27 | 391402 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0058286 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2019-05-27 | 391402 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0061188 | 3rd Party | Vehicle | Anchor or Guy | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 1 | 2019-06-01 | 395269 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Normal
19-0081381 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 25 | 2019-07-25 | 472115 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonobject
19-0087080 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2019-08-12 | 504678 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0095450 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2019-09-05 | 554001 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0102719 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 3 - Extreme | Transformer only | 9 | 23 | 2019-09-23 | 606756 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject
19-0128663 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2019 | Tier 3 - Extreme | Transformer only | 11 | 25 | 2019-11-25 | 714367 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
19-0129653 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Transmission line | 11 | 26 | 2019-11-26 | 718672 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
19-0130126 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 720327 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0130609 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 719768 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0136636 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 12 | 14 | 2019-12-14 | 739748 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
19-0137155 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2019-12-18 | 745595 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0137566 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2019-12-22 | 748114 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0010900 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 765102 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0019962 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 787416 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0022276 | Vegetation | Tree - cutting, PG&E contractor | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2020-02-14 | 791072 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦CrossarmWood¦Brokenwireonground
20-0030682 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2020-03-10 | 843229 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0032512 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 853541 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0032959 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855444 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
20-0033035 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855519 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0033417 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853779 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0033627 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855807 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0034178 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2020-03-19 | 858800 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
20-0044596 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2020-04-25 | 901575 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
20-0048268 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2020-05-07 | 909140 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
20-0049666 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 12 | 2020-05-12 | 912847 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0054084 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2020-05-26 | 921357 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0054504 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2020-05-27 | 922785 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0069376 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 7 | 8 | 2020-07-08 | 959751 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0071103 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2020-07-13 | 963143 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0071481 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2020-07-13 | 963989 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0073427 | Animal | Bird found | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2020-07-19 | 967684 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
20-0076959 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2020-07-28 | 973709 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0081809 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2020-08-10 | 991010 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0085393 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 16 | 2020-08-16 | 1014405 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0085597 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Transmission line | 8 | 17 | 2020-08-17 | 1015439 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
20-0085865 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1009843 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0090411 | Environmental/External | Fire, Forest/Grass | Fuse | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033282 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal
20-0090457 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033345 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0098744 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 17 | 2020-09-17 | 1079560 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0101521 | Animal | Squirrel | Cutout, fuse holder | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2020-09-25 | 1092408 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
20-0104166 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2020 | Tier 2 - Elevated | Transformer only | 10 | 1 | 2020-10-01 | 1105766 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
20-0106423 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2020-10-08 | 1113313 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0107976 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2020-10-13 | 1116358 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0108438 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2020-10-15 | 1118814 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
20-0111191 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2020-10-22 | 1122835 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0113072 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm, Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1127612 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦CrossarmWood¦Deteriorated
20-0113107 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2020-10-25 | 1125266 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0117398 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 5 | 2020-11-05 | 1136508 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
20-0117727 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2020-11-06 | 1137135 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
20-0121917 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2020-11-17 | 1147227 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
20-0123709 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2020-11-21 | 1150528 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0125705 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2020-11-29 | 1155790 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0128363 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167272 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0129011 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Transformer only | 12 | 8 | 2020-12-08 | 1172976 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0131439 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2020-12-22 | 1196923 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0132335 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2020-12-31 | 1201658 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0010533 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214992 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0012694 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2021-01-22 | 1221099 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0013248 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2021-01-23 | 1221761 | Sus | N | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦FailedFaulted
21-0013598 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223019 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0014127 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1225106 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0014236 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1225427 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0015778 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232391 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016193 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232405 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0017135 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1238557 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0018199 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2021-01-29 | 1241067 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0022173 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2021-02-05 | 1248369 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0022401 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2021-02-05 | 1248779 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0023107 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2021-02-08 | 1250787 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0028920 | Environmental/External | Flood/Erosion | Pole-Wood | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2021-02-24 | 1260967 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Normal
21-0050058 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 4 | 18 | 2021-04-18 | 1321936 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0051885 | Equipment Failure/Involved | Overhead | Transformer | Normal | 2021 | Tier 2 - Elevated | Transformer only | 4 | 22 | 2021-04-22 | 1328646 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Normal
21-0052950 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 25 | 2021-04-25 | 1333732 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0055439 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 30 | 2021-04-30 | 1337850 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0057496 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2021-05-05 | 1341822 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0058133 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2021-05-06 | 1342716 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0061939 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 15 | 2021-05-15 | 1350560 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0069239 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2021-06-03 | 1364519 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0071006 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 6 | 7 | 2021-06-07 | 1367510 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
21-0078603 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2021-06-24 | 1383397 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0085778 | Animal | Bird found | Transformer (OH) | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2021-07-07 | 1393519 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
21-0085878 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2021-07-07 | 1393737 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
21-0091274 | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2021-07-17 | 1406978 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Deteriorated
21-0100213 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2021-08-05 | 1434586 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0101044 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2021-08-06 | 1435839 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0106212 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2021-08-18 | 1446518 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0113701 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2021-09-04 | 1462233 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0113939 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2021-09-06 | 1463266 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0114970 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2021-09-08 | 1465100 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0116336 | Animal | Squirrel | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2021-09-11 | 1468740 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
21-0116603 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2021-09-13 | 1470358 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0120007 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2021-09-20 | 1476511 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal
21-0120506 | Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 9 | 21 | 2021-09-21 | 1477297 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonground
21-0122843 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2021-09-27 | 1481680 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0132101 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499768 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0132296 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2021-10-17 | 1500021 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0134942 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2021-10-22 | 1505652 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0135694 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508276 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0135817 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1507455 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135988 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1509366 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
21-0136368 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511514 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0136913 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514991 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0137706 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1517629 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0140314 | Animal | Bird found | Transformer (OH) | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2021-10-30 | 1526280 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
21-0143606 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1537808 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0152312 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2021-11-28 | 1555272 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0156040 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 12 | 8 | 2021-12-08 | 1562094 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0157508 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568395 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0158754 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 15 | 2021-12-15 | 1573888 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0158799 | Equipment Failure/Involved | Overhead | Secondary | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574396 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Together
21-0158958 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1574351 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0160569 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581257 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161821 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585483 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161954 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585042 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0005245 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1592672 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0006218 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2022-01-04 | 1595256 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
22-0007069 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1596859 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
22-0021120 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2022-02-10 | 1625209 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0021120 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2022-02-10 | 1625209 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0022719 | Vegetation | Tree - fell into line | Insulator | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2022-02-15 | 1628216 | Sus | N | Vegetation¦Treefellintoline¦Insulator¦Broken
22-0022961 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2022-02-16 | 1628882 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0023876 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2022-02-17 | 1631622 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0024704 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2022-02-21 | 1633166 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0030943 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2022-03-07 | 1644350 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0035496 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2022-03-18 | 1650785 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0049742 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2022-04-15 | 1673722 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0051807 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2022-04-20 | 1676931 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0053598 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 23 | 2022-04-23 | 1679737 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0053945 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2022-04-25 | 1680904 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0055314 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2022-04-27 | 1683372 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0056434 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 30 | 2022-04-30 | 1685139 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0058974 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2022-05-06 | 1690015 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
22-0059743 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2022-05-09 | 1692130 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0068879 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2022-06-01 | 1715644 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0074263 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 14 | 2022-06-14 | 1731281 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0080130 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 29 | 2022-06-29 | 1745572 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0084250 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2022-07-12 | 1754303 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0088005 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2022-07-21 | 1762147 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0093695 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2022-08-04 | 1773131 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0094883 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2022-08-08 | 1775597 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0100238 | Vegetation | Tree - fell into line | Cutout, fuse holder | Normal | 2022 | Tier 2 - Elevated | Transformer only | 8 | 21 | 2022-08-21 | 1786735 | Sus | Y | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Normal
22-0101037 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 8 | 23 | 2022-08-23 | 1788224 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0102812 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 3 - Extreme | Transformer only | 8 | 28 | 2022-08-28 | 1793465 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0118650 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 6 | 2022-10-06 | 1830313 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0124982 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2022-10-26 | 1845856 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
22-0129219 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857350 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0129234 | Vegetation | Tree - fell into line | Transformer | Broken | 2022 | Tier 3 - Extreme | Transformer only | 11 | 8 | 2022-11-08 | 1857612 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Broken
22-0132325 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Transformer only | 11 | 17 | 2022-11-17 | 1865013 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0132339 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865040 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0134207 | Animal | Squirrel | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2022-11-26 | 1869436 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
22-0135765 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2022-12-01 | 1873453 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0138032 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880153 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138744 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1884127 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139844 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2022-12-14 | 1888913 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0140995 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | 2022 | Tier 3 - Extreme | Transformer only | 12 | 22 | 2022-12-22 | 1895753 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken
22-0141296 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2022-12-26 | 1897377 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0005455 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2015-01-17 | 1165293 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0005637 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 1 | 20 | 2015-01-20 | 1165915 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0011751 | Equipment Failure/Involved | Other | Conductor, Overhead | Together | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2015-02-08 | 1183734 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Together
15-0012086 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Transformer only | 2 | 9 | 2015-02-09 | 1186049 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0014687 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2015-02-20 | 1193215 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0015258 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2015-02-23 | 1195011 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0025133 | Equipment Failure/Involved | Lightning | Fuse | Arcing | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2015-04-07 | 1215471 | Sus | N | EquipmentFailureInvolved¦Lightning¦Fuse¦Arcing
15-0032496 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230557 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0038971 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 5 | 2015-06-05 | 1244409 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0041435 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2015-06-16 | 1251802 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0042218 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 19 | 2015-06-19 | 1253466 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0042257 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 20 | 2015-06-20 | 1253676 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0042387 | Animal | Bird found | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2015-06-21 | 1254301 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
15-0046669 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 7 | 9 | 2015-07-09 | 1265721 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0046968 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2015-07-11 | 1266744 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0059488 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2015-09-05 | 1300497 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0060600 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1303640 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0062607 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2015-09-21 | 1309662 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0063087 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2015-09-12 | 1311305 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0063557 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2015-09-12 | 1311881 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0065059 | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2015-09-26 | 1312365 | Sus | Y | 3rdParty¦Treecutting3rdparty¦PoleWood¦Broken
15-0066190 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2015-09-28 | 1313341 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0071161 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2015-10-16 | 1323719 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0071308 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324253 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0077091 | Equipment Failure/Involved | Electrical Overload | Insulator | Arcing | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2015-11-10 | 1339244 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Insulator¦Arcing
15-0085678 | Equipment Failure/Involved | Underground | Transformer | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2015-12-16 | 1365155 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦Deteriorated
16-0002917 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2016-01-05 | 1377157 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0004965 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 13 | 2016-01-13 | 1382579 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0005949 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385723 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0005992 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2016-01-18 | 1385867 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0006367 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2016-01-19 | 1387281 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0011460 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 2 | 8 | 2016-02-08 | 1400478 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0013219 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1405530 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0014356 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2016-02-20 | 1409769 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0020186 | Environmental/External | Flood/Erosion | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427017 | Sus | N | EnvironmentalExternal¦FloodErosion¦CrossarmWood¦Broken
16-0020266 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427182 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0035574 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2016-05-12 | 1468597 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
16-0037491 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2016-05-20 | 1473779 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0039949 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2016-05-31 | 1479788 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0044088 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2016-06-17 | 1491423 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0048755 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2016-07-09 | 1503161 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0050432 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 17 | 2016-07-17 | 1511362 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0051816 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 22 | 2016-07-22 | 1514126 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
16-0055983 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2016-08-09 | 1523617 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0058369 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 8 | 18 | 2016-08-18 | 1528676 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed
16-0060366 | Vegetation | Tree - grew into line | Fuse | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2016-08-26 | 1532695 | Sus | Y | Vegetation¦Treegrewintoline¦Fuse¦Normal
16-0061462 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2016-08-31 | 1535027 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0063760 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2016-09-11 | 1539524 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0066771 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 9 | 22 | 2016-09-22 | 1546205 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0072014 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1558537 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
16-0072452 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2016-10-15 | 1560791 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0072854 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562769 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0075149 | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2016-10-24 | 1568820 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted
16-0077738 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2016-11-03 | 1575673 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0078493 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 7 | 2016-11-07 | 1577844 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0080811 | Animal | Squirrel |  | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 11 | 18 | 2016-11-18 | 1583832 | Sus | Y | Animal¦Squirrel¦¦FailedFaulted
16-0082747 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 11 | 28 | 2016-11-28 | 1590707 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0085979 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2016-12-16 | 1604144 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0003167 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Transformer only | 1 | 3 | 2017-01-03 | 1616173 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0003779 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2017-01-04 | 1618735 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0005200 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622793 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005366 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627166 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005447 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625288 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0005624 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626779 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006090 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2017-01-08 | 1631099 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
17-0008592 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2017-01-12 | 1642076 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0010319 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648361 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0010926 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2017-01-19 | 1651126 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0011637 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653491 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0013324 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1661890 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013590 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1662588 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013871 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662929 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0015706 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2017-01-27 | 1668850 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
17-0017908 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2017-02-06 | 1676849 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0018292 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1678185 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018725 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680766 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0019274 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1682860 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
17-0019879 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2017-02-10 | 1684638 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0023910 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703838 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024752 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Transmission line | 2 | 21 | 2017-02-21 | 1706798 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0024788 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 20 | 2017-02-20 | 1706638 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0025079 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705338 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0026849 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 26 | 2017-02-26 | 1714241 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0032813 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2017-03-22 | 1733022 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0034895 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2017-03-29 | 1738775 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0039320 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2017-04-11 | 1755604 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0040912 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 17 | 2017-04-17 | 1759704 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0041745 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2017-04-20 | 1761643 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0045448 | Equipment Failure/Involved | Underground | Switch (UG) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2017-05-05 | 1775120 | Sus | Y | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Broken
17-0045813 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2017-05-06 | 1776498 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0048032 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2017-05-15 | 1782293 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0049347 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2017-05-20 | 1786109 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
17-0052187 | Vegetation | Tree - fell into line | Anchor or Guy | Broken | 2017 | Tier 3 - Extreme | Transformer only | 6 | 1 | 2017-06-01 | 1795207 | Sus | Y | Vegetation¦Treefellintoline¦AnchororGuy¦Broken
17-0065747 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 7 | 26 | 2017-07-26 | 1840406 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
17-0071850 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Transmission line | 8 | 21 | 2017-08-21 | 1856643 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0073370 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2017-08-28 | 1861156 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0076502 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2017-09-06 | 1871967 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0077695 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 11 | 2017-09-11 | 1875184 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0081199 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 9 | 23 | 2017-09-23 | 1884559 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0083532 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2017-10-02 | 1889592 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086445 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1898761 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0090691 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2017-10-26 | 1910381 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0091046 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 10 | 28 | 2017-10-28 | 1911642 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0093616 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2017-11-08 | 1918499 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0094395 | Animal | Squirrel | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 11 | 11 | 2017-11-11 | 1920515 | Sus | Y | Animal¦Squirrel¦Transformer¦FailedFaulted
17-0094813 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2017-11-14 | 1921846 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0095469 | Equipment Failure/Involved | Overhead | Jumper | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 11 | 16 | 2017-11-16 | 1923655 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Deteriorated
17-0097699 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2017-11-27 | 1929647 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0101861 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2017-12-15 | 1943877 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0019042 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 35980 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0019424 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2018-03-02 | 36933 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023707 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46144 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0030373 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2018-04-08 | 62548 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0035792 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2018-04-26 | 74175 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0042585 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2018-05-19 | 89837 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0046428 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 6 | 1 | 2018-06-01 | 98857 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0047106 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2018-06-04 | 100919 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
18-0066279 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 147844 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0066776 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 148997 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0071369 | 3rd Party | Other | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2018-08-18 | 157696 | Sus | Y | 3rdParty¦Other¦ConductorOverhead¦Normal
18-0071896 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2018-08-20 | 159062 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0081884 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2018-09-21 | 178504 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0085377 | Animal | Squirrel | Cutout, fuse holder | Broken | 2018 | Tier 2 - Elevated | Transformer only | 10 | 1 | 2018-10-01 | 185230 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Broken
18-0086322 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2018-10-03 | 187369 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
18-0087425 | Animal | Squirrel | Cutout, fuse holder | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 5 | 2018-10-05 | 189176 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
18-0088084 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2018-10-08 | 190649 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0090124 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2018-10-13 | 194270 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0094673 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2018-10-26 | 203089 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0101508 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219178 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102297 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 11 | 21 | 2018-11-21 | 221217 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0102642 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2018-11-23 | 223035 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0103698 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2018-11-27 | 225449 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0103917 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2018-11-27 | 225514 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
18-0104308 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2018-11-28 | 226483 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0105134 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228316 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0107971 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2018-12-07 | 235965 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
18-0110549 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2018-12-24 | 246677 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0006010 | Animal | Bird found | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 1 | 7 | 2019-01-07 | 259600 | Sus | N | Animal¦Birdfound¦Transformer¦Burnedflashed
19-0006485 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2019-01-08 | 260854 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦Normal
19-0009907 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 267150 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010026 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 268230 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0010112 | Equipment Failure/Involved | Substation | Other | Normal | 2019 | Tier 2 - Elevated | Transmission line | 1 | 16 | 2019-01-16 | 269959 | Sus | N | EquipmentFailureInvolved¦Substation¦Other¦Normal
19-0010638 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 272838 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0017309 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287673 | Sus | N | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
19-0017325 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 288040 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017450 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 288015 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0019212 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 294394 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0020331 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2019-02-09 | 296959 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0021680 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301568 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0023403 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 309788 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0024020 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 306650 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024623 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314627 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0024754 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 315043 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0028109 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 323939 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028372 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324446 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0029205 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 327621 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030587 | Animal | Other | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 4 | 2019-03-04 | 330995 | Sus | N | Animal¦Other¦PoleWood¦Broken
19-0031316 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 332667 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0031380 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on object | 2019 | Tier 2 - Elevated | Transformer only | 3 | 6 | 2019-03-06 | 332984 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonobject
19-0035122 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2019-03-19 | 343073 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0039612 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 3 | 2019-04-03 | 353547 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0040680 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2019-04-08 | 356137 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0040680 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2019-04-08 | 356137 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0041027 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2019-04-09 | 356962 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0042946 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2019-04-16 | 361916 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0044711 | 3rd Party | Vehicle | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 21 | 2019-04-21 | 365040 | Sus | N | 3rdParty¦Vehicle¦CrossarmWood¦Broken
19-0046279 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2019-04-25 | 368253 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
19-0048248 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2019-05-02 | 372441 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0048844 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 4 | 2019-05-04 | 373550 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0049065 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 2 - Elevated | Transformer only | 5 | 5 | 2019-05-05 | 374146 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0049084 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2019-05-05 | 374282 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0050731 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 10 | 2019-05-10 | 377622 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0053164 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2019-05-17 | 383336 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0053889 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2019-05-19 | 385032 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0055431 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 5 | 22 | 2019-05-22 | 387723 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0059868 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2019-05-30 | 393175 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0061520 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 2 - Elevated | Transformer only | 6 | 2 | 2019-06-02 | 395751 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0061883 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2019-06-03 | 396481 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
19-0063552 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2019-06-06 | 399345 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0066490 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2019-06-12 | 407189 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
19-0072155 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 26 | 2019-06-26 | 429437 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0073296 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2019-06-29 | 435213 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦PoleWood¦Deteriorated
19-0074422 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2019-07-03 | 440696 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0079594 | 3rd Party | Tree - cutting, 3rd party | Transformer | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 7 | 21 | 2019-07-21 | 465022 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Transformer¦Deteriorated
19-0093318 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2019-08-29 | 545959 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0095283 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2019 | Tier 3 - Extreme | Transformer only | 9 | 4 | 2019-09-04 | 553193 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
19-0096133 | 3rd Party | Vehicle | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 6 | 2019-09-06 | 558195 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Broken
19-0099918 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2019-09-16 | 585464 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0105011 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2019-09-28 | 628045 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0105125 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 29 | 2019-09-29 | 628485 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0106787 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2019-10-02 | 638837 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0114631 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2019-10-22 | 677023 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0119094 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2019 | Tier 2 - Elevated | Transformer only | 10 | 30 | 2019-10-30 | 695748 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
19-0126158 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 2019 | Tier 3 - Extreme | Transformer only | 11 | 19 | 2019-11-19 | 709991 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal
19-0131038 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2019-11-29 | 723358 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
20-0004520 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2020-01-02 | 753858 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0010572 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 763727 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0029360 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2020-03-06 | 834503 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032152 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 14 | 2020-03-14 | 851545 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0032237 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2020-03-15 | 852061 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0033079 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855911 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0038740 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2020-04-05 | 883432 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0053241 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2020-05-22 | 919429 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0055655 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2020-05-29 | 924965 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0058722 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 8 | 2020-06-08 | 933832 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0059453 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2020-06-09 | 935584 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0062648 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2020-06-18 | 941947 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
20-0069732 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Transformer only | 7 | 8 | 2020-07-08 | 960428 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0082995 | 3rd Party | Customer Equipment | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 13 | 2020-08-13 | 994983 | Sus | Y | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal
20-0084798 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1011794 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0090382 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1033227 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090401 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1033266 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091319 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2020-08-29 | 1040574 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
20-0092486 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 2 | 2020-09-02 | 1047993 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Burnedflashed
20-0094693 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2020-09-08 | 1060338 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0094724 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2020-09-08 | 1060148 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0096192 | 3rd Party | Fire, house or bldg. | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2020-09-10 | 1063901 | Sus | Y | 3rdParty¦Firehouseorbldg¦PoleWood¦Burnedflashed
20-0103864 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2020-10-01 | 1103618 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0112016 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2020-10-23 | 1123862 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0115794 | Animal | Squirrel | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 11 | 1 | 2020-11-01 | 1133370 | Sus | Y | Animal¦Squirrel¦Transformer¦FailedFaulted
20-0118268 | 3rd Party | Customer Equipment | Customer Equipment | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 7 | 2020-11-07 | 1138717 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Broken
20-0121538 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2020-11-16 | 1146510 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Burnedflashed
20-0122186 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2020-11-17 | 1147977 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
20-0123009 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2020-11-19 | 1149583 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0126581 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2020-12-01 | 1157521 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0132009 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2020-12-27 | 1199653 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0004226 | 3rd Party | Vehicle | Anchor or Guy | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2021-01-01 | 1202095 | Sus | N | 3rdParty¦Vehicle¦AnchororGuy¦Normal
21-0009495 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2021-01-17 | 1211832 | Sus | N | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
21-0010854 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1217291 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011724 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1219211 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
21-0011729 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1218771 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0015978 | Vegetation | Tree - fell into line | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1230670 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦FailedFaulted
21-0016706 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1236525 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0019928 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2021-01-30 | 1243586 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0021507 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2021-02-03 | 1247337 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0029710 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 2 | 25 | 2021-02-25 | 1262449 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0031073 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 2 | 2021-03-02 | 1265218 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0040930 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 25 | 2021-03-25 | 1297330 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0041874 | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2021-03-28 | 1301829 | Sus | N | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Brokenwireonground
21-0044354 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2021-04-02 | 1306078 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0047340 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2021-04-11 | 1313130 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0053906 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2021-04-27 | 1335450 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0054034 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2021-04-27 | 1335384 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0073638 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2021-06-13 | 1372291 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0076635 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 6 | 19 | 2021-06-19 | 1379078 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0081655 | Animal | Bird found | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Transformer only | 6 | 29 | 2021-06-29 | 1388217 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
21-0085478 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2021-07-06 | 1393077 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0087723 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2021-07-11 | 1399459 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
21-0089261 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2021-07-14 | 1403861 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0090846 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on object | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2021-07-16 | 1406142 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonobject
21-0098159 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2021-08-01 | 1427877 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0100683 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 3 - Extreme | Transformer only | 8 | 5 | 2021-08-05 | 1435061 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0100704 | Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2021-08-05 | 1434900 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Regulator¦Malfunctioning
21-0104329 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2021-08-13 | 1442058 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0105911 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445236 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0106037 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1446130 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0108260 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2021 | Tier 3 - Extreme | Transformer only | 8 | 23 | 2021-08-23 | 1450698 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
21-0110534 | Equipment Failure/Involved | Overhead | Anchor or Guy | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2021-08-28 | 1456102 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Normal
21-0110779 | 3rd Party | Gun Shot | Pothead(Riser Termination) | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2021-08-29 | 1457517 | Sus | Y | 3rdParty¦GunShot¦Pothead(RiserTermination)¦Burnedflashed
21-0111247 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2021-08-30 | 1458372 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
21-0117485 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 14 | 2021-09-14 | 1471767 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0123429 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2021-09-28 | 1482730 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0135253 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 10 | 22 | 2021-10-22 | 1506080 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135770 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508185 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0135872 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508518 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0137226 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2021 | Tier 3 - Extreme | Transformer only | 10 | 24 | 2021-10-24 | 1518478 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
21-0138769 | Vegetation | Tree - fell into line | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1523033 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Broken
21-0141155 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2021-11-02 | 1531249 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0143604 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1537882 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0143633 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2021-11-08 | 1538057 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
21-0144381 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2021-11-10 | 1539832 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0149003 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 20 | 2021-11-20 | 1551040 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0157486 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1565720 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0157674 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1567443 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158917 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1574891 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0158931 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573961 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
21-0159974 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2021-12-21 | 1578559 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161316 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1586649 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0161560 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588462 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
21-0161953 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2021-12-30 | 1590221 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0162011 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1590839 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0162012 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2021-12-31 | 1590847 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0005056 | 3rd Party | Other | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591654 | Sus | N | 3rdParty¦Other¦ConductorOverhead¦Normal
22-0005064 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Transformer only | 1 | 1 | 2022-01-01 | 1591530 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
22-0006008 | 3rd Party | Customer Equipment | Transformer | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 1 | 3 | 2022-01-03 | 1593724 | Sus | N | 3rdParty¦CustomerEquipment¦Transformer¦FailedFaulted
22-0006753 | 3rd Party | Customer Equipment | Fuse | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2022-01-06 | 1596386 | Sus | N | 3rdParty¦CustomerEquipment¦Fuse¦Normal
22-0019009 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2022-02-05 | 1621834 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0019112 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2022-02-06 | 1622287 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0024555 | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2022-02-20 | 1632767 | Sus | N | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonground
22-0024800 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2022-02-21 | 1633318 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0025000 | Vegetation | Tree - fell into line | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2022-02-22 | 1633500 | Sus | N | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken
22-0025262 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2022-02-22 | 1634135 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0031902 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2022-03-09 | 1645559 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0036542 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2022-03-21 | 1652905 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
22-0045648 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669345 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
22-0053535 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 22 | 2022-04-22 | 1679580 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0057125 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 3 | 2022-05-03 | 1686876 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0057496 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2022-05-03 | 1687557 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
22-0064297 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 20 | 2022-05-20 | 1705312 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0070305 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2022-06-05 | 1719502 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
22-0077670 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2022-06-23 | 1739944 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonground
22-0078558 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 25 | 2022-06-25 | 1742154 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
22-0079277 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2022-06-28 | 1743956 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0079974 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2022-06-29 | 1745467 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0080342 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2022-06-30 | 1746042 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0081417 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2022-07-02 | 1747913 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
22-0089327 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2022-07-25 | 1764944 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
22-0094618 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2022 | Tier 3 - Extreme | Transformer only | 8 | 6 | 2022-08-06 | 1774968 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
22-0098110 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 3 - Extreme | Transformer only | 8 | 16 | 2022-08-16 | 1782144 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0104207 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 3 - Extreme | Transformer only | 8 | 31 | 2022-08-31 | 1796136 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0105820 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2022-09-05 | 1799378 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0112303 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 19 | 2022-09-19 | 1816474 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0112375 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Transmission line | 9 | 19 | 2022-09-19 | 1816809 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
22-0112375 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Transmission line | 9 | 19 | 2022-09-19 | 1816809 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
22-0112429 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 19 | 2022-09-19 | 1815895 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0112525 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2022-09-20 | 1817189 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
22-0113035 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2022-09-21 | 1818294 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0113100 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2022-09-21 | 1818298 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0117305 | Animal | Squirrel | Fuse | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2022-10-03 | 1826984 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
22-0128490 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2022 | Tier 2 - Elevated | Transformer only | 11 | 7 | 2022-11-07 | 1855653 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
22-0129409 | Equipment Failure/Involved | Overhead | Secondary | Burned Open | 2022 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2022-11-09 | 1858517 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen
22-0129876 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 10 | 2022-11-10 | 1859672 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0129876 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 10 | 2022-11-10 | 1859672 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0130366 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 11 | 11 | 2022-11-11 | 1860618 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0130667 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2022-11-11 | 1860785 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0132653 | Animal | Squirrel | Fuse | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865603 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
22-0138843 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2022-12-11 | 1884858 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0139555 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2022-12-13 | 1888550 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0140054 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 12 | 14 | 2022-12-14 | 1889784 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0140544 | Company Initiated | Other Circuits | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2022-12-18 | 1892058 | Sus | N | CompanyInitiated¦OtherCircuits¦PoleWood¦Deteriorated
22-0141939 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2022-12-28 | 1900416 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0010663 | Equipment Failure/Involved | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1177615 | Sus | N | EquipmentFailureInvolved¦Lightning¦Transformer¦FailedFaulted
15-0011111 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2015-02-07 | 1180494 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0027531 | Animal | Squirrel | Cutout, Fused, Distribution | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2015-04-17 | 1221054 | Sus | N | Animal¦Squirrel¦CutoutFusedDistribution¦FailedFaulted
15-0029536 | Equipment Failure/Involved | Other | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2015-04-25 | 1224924 | Sus | N | EquipmentFailureInvolved¦Other¦PoleWood¦Burnedflashed
15-0032718 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2015-05-07 | 1231140 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
15-0036867 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2015-05-28 | 1240413 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0044760 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2015-07-01 | 1260717 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0045316 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 3 | 2015-07-03 | 1262357 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0050175 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2015-07-23 | 1276260 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0050217 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 24 | 2015-07-24 | 1276434 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0050580 | Vegetation | Tree - fell into line | Secondary | Broken, wire on object | 2015 | Tier 2 - Elevated | Transformer only | 7 | 26 | 2015-07-26 | 1277596 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonobject
15-0056416 | 3rd Party | Vehicle | Conductor, Overhead | Together | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2015-08-20 | 1292190 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Together
15-0062108 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2015-09-18 | 1308035 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0066434 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Transformer only | 9 | 29 | 2015-09-29 | 1313900 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0071312 | Environmental/External | Lightning | Transformer (UG) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324344 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(UG)¦FailedFaulted
15-0071476 | Environmental/External | Lightning | Pothead(Riser Termination) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 18 | 2015-10-18 | 1324504 | Sus | Y | EnvironmentalExternal¦Lightning¦Pothead(RiserTermination)¦FailedFaulted
15-0074184 | Vegetation | Tree - fell into line | Transformer | Leaking | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2015-10-29 | 1331335 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Leaking
15-0075154 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2015-11-02 | 1334030 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0078322 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2015-11-16 | 1343217 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0082518 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352965 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0083653 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 9 | 2015-12-09 | 1356424 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083905 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357353 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084081 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1358076 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084257 | Environmental/External | Lightning | Transformer (OH) | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2015-12-11 | 1358683 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal
15-0084839 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361152 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0084946 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361461 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084952 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1362560 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0086708 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369004 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0002827 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2016-01-04 | 1376904 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0003184 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2016-01-05 | 1377391 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0003732 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2016-01-07 | 1379312 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0011170 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2016 | Tier 3 - Extreme | Transformer only | 2 | 7 | 2016-02-07 | 1399822 | Sus | N | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
16-0013410 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406580 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
16-0013521 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407634 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0018979 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 7 | 2016-03-07 | 1424269 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0021793 | 3rd Party | Vehicle | Cutout, fuse holder | Broken | 2016 | Tier 3 - Extreme | Transformer only | 3 | 16 | 2016-03-16 | 1432278 | Sus | N | 3rdParty¦Vehicle¦Cutoutfuseholder¦Broken
16-0025530 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 1 | 2016-04-01 | 1442666 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0025724 | Animal | Squirrel | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2016-04-02 | 1443328 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
16-0028402 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2016-04-13 | 1450196 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
16-0031023 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457036 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0031106 | Animal | Other | Recloser | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457674 | Sus | N | Animal¦Other¦Recloser¦Burnedflashed
16-0031168 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2016-04-25 | 1457766 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0031756 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2016-04-26 | 1459717 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0032075 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2016-04-27 | 1460379 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
16-0035451 | 3rd Party | Dig in, 3rd party | Service conductor | Bent or Twisted | 2016 | Tier 3 - Extreme | Transformer only | 5 | 11 | 2016-05-11 | 1468320 | Sus | Y | 3rdParty¦Digin3rdparty¦Serviceconductor¦BentorTwisted
16-0036911 | Vegetation | Tree - fell into line | Crossarm, Steel | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2016-05-18 | 1472326 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmSteel¦Brokenwireonground
16-0037945 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2016-05-24 | 1475640 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0038854 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 26 | 2016-05-26 | 1477820 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0039700 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 30 | 2016-05-30 | 1479199 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0041809 | Animal | Bird found | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2016-06-08 | 1485046 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
16-0041917 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2016-06-08 | 1485327 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0044341 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2016-06-19 | 1492373 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
16-0047250 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2016-07-01 | 1499253 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0048725 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2016-07-08 | 1502985 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0049442 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2016-07-12 | 1509028 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
16-0055524 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2016-08-06 | 1522554 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0057291 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2016-08-15 | 1526608 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
16-0059182 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2016-08-22 | 1530552 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
16-0064995 | Company Initiated | Personnel, company | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 15 | 2016-09-15 | 1542505 | Sus | Y | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Normal
16-0066400 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2016-09-21 | 1545678 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0067610 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2016-09-26 | 1547983 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0070811 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 10 | 2016-10-10 | 1555749 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0071519 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2016-10-13 | 1557274 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072503 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2016-10-15 | 1560943 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0074959 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2016-10-24 | 1568428 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0075012 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2016-10-24 | 1568621 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0079530 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2016-11-13 | 1580490 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
16-0080333 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2016-11-16 | 1582354 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0080929 | Equipment Failure/Involved | Overhead | Stepdown | Deteriorated | 2016 | Tier 3 - Extreme | Transformer only | 11 | 18 | 2016-11-18 | 1584112 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Stepdown¦Deteriorated
16-0081079 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2016-11-19 | 1584777 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0084221 | Unknown Cause | Patrol - found nothing | Recloser | Malfunctioning | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2016-12-06 | 1595646 | Sus | N | UnknownCause¦Patrolfoundnothing¦Recloser¦Malfunctioning
16-0084902 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2016-12-10 | 1598230 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0085857 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1603357 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0086780 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2016-12-23 | 1609381 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0087355 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2016-12-29 | 1613057 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0002783 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 2 | 2017-01-02 | 1614635 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0005034 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623292 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0005314 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623161 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0005314 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623161 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0005426 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627010 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0005855 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1629962 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007266 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637179 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0007557 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639537 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0007601 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638794 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007859 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640472 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0007912 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640681 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0009137 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 14 | 2017-01-14 | 1643589 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0010121 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1646895 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0010566 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1649065 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0013103 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660839 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0014681 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2017-01-25 | 1666700 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0016163 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2017-01-30 | 1670820 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0017282 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673887 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0019110 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682080 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0019391 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683059 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019549 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683806 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0020035 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2017-02-10 | 1685602 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0021757 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2017-02-16 | 1690731 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023034 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2017-02-18 | 1699766 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0023476 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2017-02-19 | 1701728 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
17-0023918 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704064 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0024025 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703988 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024683 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704787 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0027158 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2017-02-27 | 1715315 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
17-0028324 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 4 | 2017-03-04 | 1719230 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0028395 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 4 | 2017-03-04 | 1719472 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0028527 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2017-03-05 | 1720272 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0030721 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 14 | 2017-03-14 | 1726989 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0031592 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2017-03-17 | 1729391 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0035270 | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2017-03-30 | 1740212 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround
17-0037182 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745722 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0044402 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 2 | 2017-05-02 | 1772139 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0048096 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2017-05-15 | 1782596 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0052493 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2017-06-03 | 1796012 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0054287 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 11 | 2017-06-11 | 1801594 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0059751 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2017-06-30 | 1821399 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
17-0066578 | Vegetation | Tree - fell into line | Fuse | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2017-07-30 | 1842773 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦Normal
17-0066586 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2017-07-30 | 1842777 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0067079 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2017-08-01 | 1843929 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0072733 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 25 | 2017-08-25 | 1858912 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0073944 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2017-08-29 | 1862788 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0085204 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893744 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0085376 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1894816 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0086840 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899525 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0088846 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2017-10-19 | 1904753 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0090681 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2017-10-26 | 1910451 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0100640 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2017-12-07 | 1938588 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0103653 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2017-12-30 | 1953283 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0003245 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2018-01-03 | 1007 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0003335 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2018-01-03 | 1310 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0005917 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 13 | 2018-01-13 | 7662 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0008170 | Animal | Squirrel | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 1 | 23 | 2018-01-23 | 12528 | Sus | N | Animal¦Squirrel¦Transformer¦FailedFaulted
18-0017120 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2018-02-26 | 31388 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0018441 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Transformer only | 3 | 1 | 2018-03-01 | 34298 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0018542 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2018-03-01 | 34681 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0018542 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2018-03-01 | 34681 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0020089 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 5 | 2018-03-05 | 38659 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0022027 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2018-03-12 | 42801 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0029761 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2018-04-06 | 60566 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0033227 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2018-04-17 | 69076 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0035655 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2018-04-25 | 73955 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0044988 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2018-05-29 | 95650 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0046246 | Environmental/External | Fire, Forest/Grass | Transformer | Burned/flashed | 2018 | Tier 3 - Extreme | Transformer only | 6 | 1 | 2018-06-01 | 98402 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Burnedflashed
18-0046711 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 2 | 2018-06-02 | 99739 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0046782 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2018-06-03 | 100235 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0048743 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2018-06-08 | 104051 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0048743 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2018-06-08 | 104051 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0049379 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2018-06-10 | 105648 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0055203 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 27 | 2018-06-27 | 119749 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0065451 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2018-07-31 | 146057 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0068704 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2018-08-10 | 152883 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
18-0073262 | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2018-08-24 | 161668 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted
18-0076013 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2018-09-03 | 167554 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
18-0077710 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 9 | 7 | 2018-09-07 | 170218 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0102190 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2018-11-22 | 221289 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0105442 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 229566 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0106316 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 12 | 2 | 2018-12-02 | 231952 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0109292 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Transformer only | 12 | 14 | 2018-12-14 | 240571 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
18-0109382 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2018-12-15 | 241056 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed
19-0004529 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2019-01-04 | 253096 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0005192 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255403 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0005258 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 256345 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0010710 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 269516 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0014712 | Animal | Squirrel | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2019-01-26 | 281736 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
19-0017307 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287402 | Sus | N | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
19-0017624 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2019-02-03 | 289218 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0018122 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 290566 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0020226 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2019-02-08 | 296653 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020273 | Animal | Bird found | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2019-02-09 | 296767 | Sus | N | Animal¦Birdfound¦Transformer(OH)¦FailedFaulted
19-0020934 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2019-02-11 | 299544 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0021582 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2019-02-12 | 301000 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0021817 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 302511 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022934 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 307670 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0023322 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 307332 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0024631 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314649 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025080 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315323 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0025121 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 315558 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0026132 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 318969 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0027493 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2019-02-23 | 321966 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0030019 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2019-03-02 | 329436 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0031067 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 332094 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0036470 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2019-03-24 | 346315 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0036882 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2019-03-26 | 347329 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0038987 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2019-04-02 | 352158 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0043052 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2019-04-16 | 362029 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0049759 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2019-05-07 | 375841 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0051018 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 5 | 11 | 2019-05-11 | 378297 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0052455 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2019-05-15 | 381516 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0057091 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2019-05-24 | 389844 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
19-0060309 | Environmental/External | Lightning | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2019-05-30 | 393869 | Sus | Y | EnvironmentalExternal¦Lightning¦LightningArrestor¦FailedFaulted
19-0066173 | Equipment Failure/Involved | Electrical Overload | Generator | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2019-06-11 | 406335 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Generator¦Normal
19-0067072 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2019-06-13 | 408495 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0067667 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2019-06-14 | 410953 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0068071 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 15 | 2019-06-15 | 414473 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0069727 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2019-06-19 | 421372 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0071744 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 25 | 2019-06-25 | 428179 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0077043 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2019-07-13 | 447988 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0082366 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2019-07-29 | 475000 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0085091 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2019-08-07 | 487833 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0098606 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 13 | 2019-09-13 | 576727 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0106241 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Transformer only | 10 | 1 | 2019-10-01 | 634865 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0112456 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Transformer only | 10 | 16 | 2019-10-16 | 662364 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0114985 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2019-10-23 | 677365 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0116292 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 686186 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0119863 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2019-11-01 | 697282 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0123430 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2019-11-10 | 704093 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
19-0124300 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 13 | 2019-11-13 | 705964 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
19-0129482 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 717841 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0129537 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 717202 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0130375 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 721356 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0130836 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2019-11-28 | 722826 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0131442 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 30 | 2019-11-30 | 724460 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0132797 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2019-12-03 | 728509 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
19-0133684 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2019-12-04 | 730171 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0134509 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2019-12-06 | 731691 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0138021 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2019-12-27 | 751108 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
20-0009773 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 762704 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
20-0012158 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2020-01-22 | 767673 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0019284 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 782224 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0020198 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 787142 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0028527 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2020-03-04 | 828062 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0028615 | Animal | Squirrel | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2020-03-04 | 829196 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Brokenwireonground
20-0033008 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855617 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033024 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855680 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033039 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855612 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0033104 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855931 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0038639 | Equipment Failure/Involved | Fire, pole | Other | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2020-04-05 | 883302 | Sus | N | EquipmentFailureInvolved¦Firepole¦Other¦Broken
20-0039019 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2020-04-06 | 886175 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0039019 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2020-04-06 | 886175 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0039179 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2020-04-07 | 886993 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0040642 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2020-04-12 | 894020 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0043770 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2020-04-22 | 899455 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0056843 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2020-06-03 | 929034 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0070879 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2020-07-11 | 962529 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0077715 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 7 | 30 | 2020-07-30 | 975009 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0084453 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2020-08-15 | 1004949 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0084664 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1010361 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0085802 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1016775 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
20-0087798 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2020-08-20 | 1024041 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0088746 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2020-08-21 | 1026647 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0090168 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1032155 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090275 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1032636 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091335 | Environmental/External | Fire, Forest/Grass | Other | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2020-08-18 | 1040801 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Other¦Burnedflashed
20-0099821 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086129 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100153 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 22 | 2020-09-22 | 1087655 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0100722 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | On Ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2020-08-19 | 1090484 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦OnGround
20-0101334 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2020-09-25 | 1091952 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0105865 | Company Initiated | Construction Activity/equip, company | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2020-10-06 | 1112340 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConnectororSplice(OH)¦Broken
20-0109923 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2020-10-17 | 1119728 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0112526 | Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1125820 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Recloser¦Normal
20-0119166 | Animal | Squirrel | Fuse | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2020-11-10 | 1140962 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
20-0127765 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2020-12-04 | 1162429 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Broken
20-0129960 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2020-12-12 | 1181190 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0131212 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 12 | 19 | 2020-12-19 | 1195719 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0131678 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2020-12-24 | 1198165 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0004278 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 1 | 2021-01-01 | 1202271 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0010974 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2021-01-19 | 1215807 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011043 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1217767 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0013170 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2021-01-22 | 1221530 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0013429 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2021-01-24 | 1222369 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0014732 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226384 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0014996 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226984 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0015411 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1230531 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
21-0015951 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1232023 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0015995 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232045 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0016105 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1227753 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016194 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234170 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016625 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232768 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016785 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237019 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0021629 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 2 | 3 | 2021-02-03 | 1247537 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0029905 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 2 | 26 | 2021-02-26 | 1262737 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0037704 | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2021-03-17 | 1286891 | Sus | N | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted
21-0041670 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2021 | Tier 3 - Extreme | Transformer only | 3 | 26 | 2021-03-26 | 1300013 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
21-0043005 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2021-03-30 | 1303887 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0043556 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 1 | 2021-04-01 | 1304826 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0052259 | Animal | Bird found | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 23 | 2021-04-23 | 1329372 | Sus | N | Animal¦Birdfound¦Fuse¦BurnedOpen
21-0061926 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 15 | 2021-05-15 | 1350262 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0062732 | Animal | Bird found | Bushing | Arcing | 2021 | Tier 2 - Elevated | Transformer only | 5 | 18 | 2021-05-18 | 1352254 | Sus | Y | Animal¦Birdfound¦Bushing¦Arcing
21-0066084 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2021-05-25 | 1358776 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0071761 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Transformer only | 6 | 8 | 2021-06-08 | 1368845 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
21-0074482 | Animal | Squirrel |  | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 6 | 15 | 2021-06-15 | 1374305 | Sus | Y | Animal¦Squirrel¦¦FailedFaulted
21-0086761 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 7 | 8 | 2021-07-08 | 1394865 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0092175 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 20 | 2021-07-20 | 1408713 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
21-0099402 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2021-08-03 | 1433243 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
21-0101117 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 6 | 2021-08-06 | 1435772 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
21-0104440 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2021-08-13 | 1442307 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0105221 | 3rd Party | Vehicle | Pole-Wood | Normal | 2021 | Tier 3 - Extreme | Transformer only | 8 | 16 | 2021-08-16 | 1444124 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
21-0128898 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2021-10-11 | 1493339 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0129259 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1494504 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0132052 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499645 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0136649 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514379 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137420 | Vegetation | Tree - fell into line | Secondary | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1516934 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Broken
21-0138060 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2021-10-25 | 1521246 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0138076 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2021-10-26 | 1521306 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0139593 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2021-10-28 | 1524877 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0142531 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 4 | 2021-11-04 | 1535044 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0145890 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 11 | 15 | 2021-11-15 | 1545579 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0156576 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2021-12-10 | 1563891 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0157300 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1567427 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0158794 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574325 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0160088 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2021-12-22 | 1578961 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160260 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2021-12-23 | 1579790 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0160408 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2021-12-24 | 1580497 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160623 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581711 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0160745 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581715 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0160948 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1583853 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0160960 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1583368 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0161041 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585335 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161047 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585345 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161800 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Transformer only | 12 | 30 | 2021-12-30 | 1589749 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0161990 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1590732 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005251 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 1 | 1 | 2022-01-01 | 1591941 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
22-0007094 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2022-01-06 | 1596941 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0012812 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607939 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0013198 | Environmental/External | Water | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Transformer only | 1 | 22 | 2022-01-22 | 1608565 | Sus | N | EnvironmentalExternal¦Water¦CrossarmWood¦Broken
22-0017327 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2022-02-02 | 1618792 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0022531 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2022-02-15 | 1627954 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0033255 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2022-03-12 | 1647455 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0036560 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2022-03-21 | 1652837 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0037043 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 3 | 22 | 2022-03-22 | 1653661 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0039227 | Animal | Other | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2022-03-28 | 1657455 | Sus | N | Animal¦Other¦ConductorOverhead¦Normal
22-0043274 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2022-04-06 | 1663955 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0046618 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 12 | 2022-04-12 | 1670164 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0052844 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2022-04-21 | 1678414 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0060947 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2022-05-11 | 1694179 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0062832 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 17 | 2022-05-17 | 1698882 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0065898 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 24 | 2022-05-24 | 1709239 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0072919 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2022-06-10 | 1727417 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
22-0078341 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2022-06-24 | 1741513 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0084380 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2022-07-12 | 1754538 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0086073 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 7 | 15 | 2022-07-15 | 1757526 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0097235 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Transformer only | 8 | 13 | 2022-08-13 | 1780285 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
22-0097917 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2022-08-16 | 1782007 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0099646 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2022-08-19 | 1784979 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0106018 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2022-09-05 | 1800415 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0109350 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 3 - Extreme | Transformer only | 9 | 12 | 2022-09-12 | 1809237 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0119338 | Environmental/External | Fire, Forest/Grass | Service conductor | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 10 | 7 | 2022-10-07 | 1831696 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦Burnedflashed
22-0124132 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2022-10-23 | 1843804 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0126437 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1849973 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0129831 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2022-11-09 | 1859429 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0130293 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 10 | 2022-11-10 | 1860356 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0135358 | 3rd Party | Vehicle | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2022-11-30 | 1872513 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Broken
22-0138151 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880466 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0138398 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882393 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0138844 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885299 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0138941 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885598 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0139326 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2022 | Tier 3 - Extreme | Transformer only | 12 | 11 | 2022-12-11 | 1887268 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
22-0141726 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899439 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0141737 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899355 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0141737 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899355 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0142318 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2022-12-30 | 1902722 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0142869 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1905783 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0007400 | Equipment Failure/Involved | Other | Insulator | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2015-01-27 | 1168980 | Sus | N | EquipmentFailureInvolved¦Other¦Insulator¦FailedFaulted
15-0010216 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1175486 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
15-0010532 | Vegetation | Tree - fell into line | Conductor, Underground | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1175598 | Sus | N | Vegetation¦Treefellintoline¦ConductorUnderground¦Brokenwireonground
15-0010956 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1180028 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0016417 | Equipment Failure/Involved | Lightning | Transformer | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 2 | 28 | 2015-02-28 | 1197530 | Sus | N | EquipmentFailureInvolved¦Lightning¦Transformer¦Burnedflashed
15-0026732 | Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2015-04-14 | 1219528 | Sus | N | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
15-0033896 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 13 | 2015-05-13 | 1233878 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0038574 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 6 | 4 | 2015-06-04 | 1243725 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0038690 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2015-06-05 | 1243979 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0039390 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 8 | 2015-06-08 | 1245697 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0041882 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2015-06-18 | 1252796 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0044086 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2015-06-29 | 1258849 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0047075 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2015-07-13 | 1267129 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0055233 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2015-08-15 | 1288715 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0055927 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2015-08-18 | 1291077 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0058503 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2015-09-01 | 1298092 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
15-0061025 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2015-09-12 | 1304676 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0071334 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324257 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0071762 | Equipment Failure/Involved | Underground | Transformer | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2015-10-19 | 1325851 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦Broken
15-0071873 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 19 | 2015-10-19 | 1325929 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0074006 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2015-10-29 | 1330855 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0078015 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 11 | 15 | 2015-11-15 | 1342502 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0079870 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 11 | 21 | 2015-11-21 | 1346429 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0081277 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 11 | 26 | 2015-11-26 | 1349088 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
15-0081396 | 3rd Party | Other | Other | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2015-11-27 | 1349518 | Sus | Y | 3rdParty¦Other¦Other¦Normal
15-0083411 | 3rd Party | Other | Insulator | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2015-12-08 | 1355716 | Sus | N | 3rdParty¦Other¦Insulator¦Broken
15-0083767 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357008 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084143 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 12 | 10 | 2015-12-10 | 1358310 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0084673 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1360307 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0084740 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361545 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0085489 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2015-12-15 | 1364190 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed
15-0086817 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369612 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0003130 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2016-01-05 | 1377585 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0004916 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2016-01-12 | 1382412 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0006029 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2016-01-18 | 1385992 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0008991 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2016-01-28 | 1393694 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0009289 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 1 | 30 | 2016-01-30 | 1394458 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0013540 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407670 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0015079 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2016-02-23 | 1411000 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0015135 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 23 | 2016-02-23 | 1411200 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0017495 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416662 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
16-0017558 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416920 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017769 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417769 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017990 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417183 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0018404 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421846 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0020396 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427230 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
16-0024857 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 29 | 2016-03-29 | 1441082 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0029382 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 18 | 2016-04-18 | 1452893 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0032138 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2016-04-27 | 1460451 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0032861 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 30 | 2016-04-30 | 1462173 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0038550 | Environmental/External | Lightning |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 25 | 2016-05-25 | 1477232 | Sus | Y | EnvironmentalExternal¦Lightning¦¦FailedFaulted
16-0042588 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2016-06-11 | 1487126 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
16-0049403 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2016-07-12 | 1508960 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0050426 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Transformer only | 7 | 16 | 2016-07-16 | 1511329 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0058819 | Equipment Failure/Involved | Underground | Elbow | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2016-08-21 | 1529713 | Sus | Y | EquipmentFailureInvolved¦Underground¦Elbow¦Deteriorated
16-0059180 | Unknown Cause | Patrol - not conducted |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2016-08-22 | 1530505 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦FailedFaulted
16-0066281 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2016-09-21 | 1545485 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
16-0068705 | Animal | Squirrel | Transformer (OH) | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2016-09-30 | 1550361 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
16-0070577 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2016-10-08 | 1555067 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0072709 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561449 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0073074 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1563225 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0073259 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562937 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0075144 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2016-10-24 | 1568874 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0079937 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2016-11-15 | 1581604 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0086971 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2016-12-24 | 1610589 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0087002 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2016-12-25 | 1610807 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
17-0004629 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1620893 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
17-0005480 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627536 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0006240 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2017-01-09 | 1631569 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006339 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1632328 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006395 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632529 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006501 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632559 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0008280 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 1 | 12 | 2017-01-12 | 1640961 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0010357 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1647381 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011762 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1655055 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013624 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1663014 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0018803 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680704 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0022437 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1696186 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0022632 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698213 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0025699 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2017-02-22 | 1710847 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0027982 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2017-03-02 | 1717977 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0029422 | Equipment Failure/Involved | Underground | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 8 | 2017-03-08 | 1722614 | Sus | N | EquipmentFailureInvolved¦Underground¦Fuse¦FailedFaulted
17-0030666 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2017-03-14 | 1726876 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0031767 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | 2017 | Tier 2 - Elevated | Transformer only | 3 | 19 | 2017-03-19 | 1730100 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed
17-0032709 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2017-03-22 | 1732736 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0037474 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748425 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0037800 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1750502 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0038129 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1751916 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0039312 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 4 | 11 | 2017-04-11 | 1755537 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0040689 | Vegetation | Tree - fell into line | Cutout, fuse holder | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 16 | 2017-04-16 | 1759073 | Sus | N | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken
17-0042133 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2017-04-22 | 1764852 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0051282 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2017-05-29 | 1792536 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0051487 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 5 | 30 | 2017-05-30 | 1793204 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
17-0052520 | Equipment Failure/Involved | Overhead | Regulator | Arcing | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2017-06-03 | 1796244 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Regulator¦Arcing
17-0056105 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2017 | Tier 2 - Elevated | Transformer only | 6 | 18 | 2017-06-18 | 1807748 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
17-0059825 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2017-06-30 | 1821457 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0061288 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2017-07-07 | 1825609 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
17-0063119 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2017 | Tier 3 - Extreme | Transformer only | 7 | 15 | 2017-07-15 | 1831966 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
17-0064727 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 7 | 22 | 2017-07-22 | 1837622 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
17-0075893 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 4 | 2017-09-04 | 1870064 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0076915 | 3rd Party | Other | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2017-09-08 | 1873179 | Sus | Y | 3rdParty¦Other¦ConductorOverhead¦Normal
17-0081338 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2017-09-24 | 1885047 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0081910 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2017-09-26 | 1886291 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0084615 | Animal | Bird found | Cutout, fuse holder | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2017-10-06 | 1891745 | Sus | Y | Animal¦Birdfound¦Cutoutfuseholder¦FailedFaulted
17-0091303 | Equipment Failure/Involved | Overhead | Transformer | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 10 | 30 | 2017-10-30 | 1912226 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground
17-0091559 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2017-10-31 | 1913129 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0091620 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2017-10-31 | 1913229 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0094896 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2017-11-14 | 1922074 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0098434 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2017-11-29 | 1932042 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
17-0099816 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1936065 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0099875 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 5 | 2017-12-05 | 1936184 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0102585 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 19 | 2017-12-19 | 1947874 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0103139 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 12 | 23 | 2017-12-23 | 1950685 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0103589 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2017-12-29 | 1952963 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0103664 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 12 | 30 | 2017-12-30 | 1953339 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0004760 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2018-01-09 | 5169 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
18-0004901 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2018-01-09 | 5546 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0005173 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2018-01-10 | 6272 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0012643 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2018-02-08 | 21636 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0014806 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2018-02-16 | 25688 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
18-0019561 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2018-03-04 | 37927 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0026269 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Arcing | 2018 | Tier 3 - Extreme | Transformer only | 3 | 24 | 2018-03-24 | 52543 | Sus | N | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Arcing
18-0029888 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2018-04-06 | 60825 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0031656 | 3rd Party | Customer Equipment | Other | Burned/flashed | 2018 | Tier 2 - Elevated | Transformer only | 4 | 12 | 2018-04-12 | 65513 | Sus | N | 3rdParty¦CustomerEquipment¦Other¦Burnedflashed
18-0033762 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2018 | Tier 2 - Elevated | Transformer only | 4 | 19 | 2018-04-19 | 70003 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
18-0037450 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2018-05-01 | 77868 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0052796 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2018 | Tier 3 - Extreme | Transformer only | 6 | 20 | 2018-06-20 | 113694 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
18-0057640 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2018-07-07 | 125946 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0059460 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2018-07-13 | 130489 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0065074 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2018-07-26 | 145196 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0066748 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2018-08-04 | 148897 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0068868 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2018-08-10 | 153064 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0075810 | Animal | Bird found | Transformer (OH) | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2018-09-01 | 166697 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
18-0080751 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2018-09-18 | 176283 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0089960 | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2018-10-12 | 194032 | Sus | Y | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Brokenwireonground
18-0089960 | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2018-10-12 | 194032 | Sus | Y | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Brokenwireonground
18-0090767 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2018-10-16 | 196161 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦¦
18-0098071 | Company Initiated | Personnel, company | Generator | Malfunctioning | 2018 | Tier 2 - Elevated | Substation - Distribution | 11 | 8 | 2018-11-08 | 210971 | Sus | Y | CompanyInitiated¦Personnelcompany¦Generator¦Malfunctioning
18-0098610 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2018-11-09 | 212322 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0098832 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2018 | Tier 3 - Extreme | Transformer only | 11 | 10 | 2018-11-10 | 212994 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
18-0099240 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2018-11-13 | 214106 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0100890 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217956 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101770 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219833 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104666 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2018-11-28 | 227115 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0109183 | Vegetation | Other ground vegetation | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 239965 | Sus | N | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Broken
18-0110757 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2018-12-26 | 247453 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0003446 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2019-01-01 | 251420 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0003456 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2019-01-01 | 251521 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0004933 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2019-01-05 | 254462 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0008183 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2019-01-12 | 263649 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009175 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2019-01-15 | 265585 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009753 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 267148 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011763 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 273476 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0012174 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2019-01-19 | 276992 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0016950 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 286622 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0016950 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 286622 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0017186 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 286849 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0018156 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 4 | 2019-02-04 | 290537 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0018977 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 293662 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020132 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2019-02-08 | 296385 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
19-0020572 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298148 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020604 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298092 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020604 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298092 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020688 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298411 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0020703 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298919 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
19-0022552 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 305424 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024037 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 312121 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0024090 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2019-02-15 | 311334 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0028978 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325506 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0033338 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2019-03-13 | 338257 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0037554 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2019-03-27 | 348589 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0038493 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2019-03-30 | 350781 | Sus | N | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦FailedFaulted
19-0038493 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2019-03-30 | 350781 | Sus | N | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦FailedFaulted
19-0041078 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2019-04-09 | 356941 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0041433 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2019-04-10 | 358294 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
19-0042140 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 4 | 13 | 2019-04-13 | 360023 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0053629 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2019-05-18 | 384135 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
19-0053961 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2019-05-19 | 385306 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0054925 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 21 | 2019-05-21 | 387058 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0055407 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 22 | 2019-05-22 | 387820 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0059237 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2019-05-29 | 392919 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
19-0064337 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Transformer only | 6 | 7 | 2019-06-07 | 400957 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0064905 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2019-06-09 | 402828 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal
19-0069736 | Animal | Bird found | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 19 | 2019-06-19 | 421220 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
19-0070576 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2019-06-21 | 425350 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0073625 | Vegetation | Tree - fell into line | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2019-07-01 | 438441 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Broken
19-0077742 | Vegetation | Tree - branch fell on line | Secondary | Broken | 2019 | Tier 3 - Extreme | Transformer only | 7 | 16 | 2019-07-16 | 453271 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Broken
19-0084082 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2019-08-03 | 482204 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0095609 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 5 | 2019-09-05 | 555293 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0099293 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 15 | 2019-09-15 | 583479 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0101153 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 9 | 19 | 2019-09-19 | 593017 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0101168 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 19 | 2019-09-19 | 593613 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0104976 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2019-09-28 | 627439 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0111681 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2019 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2019-10-15 | 658968 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
19-0112508 | Equipment Failure/Involved | Underground | Secondary | Broken | 2019 | Tier 3 - Extreme | Transformer only | 10 | 16 | 2019-10-16 | 662753 | Sus | Y | EquipmentFailureInvolved¦Underground¦Secondary¦Broken
19-0116019 | Animal | Squirrel | Pole-Wood | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2019-10-25 | 680249 | Sus | Y | Animal¦Squirrel¦PoleWood¦Normal
19-0120301 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2019-11-01 | 697935 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0123838 | Animal | Squirrel | Lightning Arrestor | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 12 | 2019-11-12 | 704801 | Sus | Y | Animal¦Squirrel¦LightningArrestor¦FailedFaulted
19-0126565 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 20 | 2019-11-20 | 710926 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0127475 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2019-11-22 | 712619 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0129737 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 719325 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
19-0129737 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 719325 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
19-0129837 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 718073 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0132130 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2019-12-01 | 726761 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0132431 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2019-12-02 | 727643 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0133123 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2019-12-04 | 729235 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0134720 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 732311 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0135851 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 12 | 11 | 2019-12-11 | 736251 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0136311 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2019-12-12 | 737990 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137104 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2019-12-18 | 745375 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0137281 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2019 | Tier 2 - Elevated | Transformer only | 12 | 19 | 2019-12-19 | 746705 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
19-0137853 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2019-12-24 | 750057 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137877 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2019-12-25 | 750163 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137977 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2019-12-26 | 750824 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0005294 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2020-01-05 | 755148 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0009638 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 762422 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0010566 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2020-01-17 | 764658 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0011151 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2020-01-19 | 765988 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0017822 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2020-02-05 | 778760 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0019811 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 782461 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
20-0020208 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2020-02-10 | 787849 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
20-0020317 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2020 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2020-02-09 | 784993 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
20-0032376 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852221 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0032719 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853719 | Sus | N | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
20-0033555 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 16 | 2020-03-16 | 856796 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0033915 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 858438 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0034377 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 859182 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0039060 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2020-04-06 | 885737 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0041666 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2020-04-15 | 896001 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
20-0043099 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2020-04-21 | 898518 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0044745 | Animal | Squirrel | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2020-04-27 | 901980 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
20-0044973 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2020-04-27 | 902550 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0051616 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 18 | 2020-05-18 | 917257 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
20-0056571 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2020-06-02 | 928326 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0057940 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2020-06-05 | 931356 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0059884 | 3rd Party | Other | Cutout, fuse holder | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2020-06-10 | 936352 | Sus | Y | 3rdParty¦Other¦Cutoutfuseholder¦Normal
20-0062808 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2020-06-18 | 942143 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0064011 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 944900 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0065404 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 26 | 2020-06-26 | 948081 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0071991 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2020-07-14 | 964842 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0073197 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2020-07-17 | 966871 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0083196 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 13 | 2020-08-13 | 996636 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0089081 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 23 | 2020-08-23 | 1027802 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
20-0089718 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2020-08-25 | 1029046 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0090369 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1033215 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090423 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033300 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0091839 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 31 | 2020-08-31 | 1044116 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0096052 | Environmental/External | Fire, Forest/Grass | Transformer | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 20 | 2020-08-20 | 1063547 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal
20-0110108 | Equipment Failure/Involved | Overhead | Service conductor | Burned Open | 2020 | Tier 3 - Extreme | Transformer only | 10 | 18 | 2020-10-18 | 1120426 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦BurnedOpen
20-0111952 | Animal | Squirrel | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 10 | 22 | 2020-10-22 | 1123736 | Sus | Y | Animal¦Squirrel¦Transformer¦FailedFaulted
20-0116355 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2020-11-03 | 1134894 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0118796 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2020-11-09 | 1140371 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0121776 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2020-11-17 | 1146726 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0124352 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 11 | 23 | 2020-11-23 | 1153423 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0131077 | Animal | Squirrel | Transformer | Malfunctioning | 2020 | Tier 3 - Extreme | Transformer only | 12 | 18 | 2020-12-18 | 1193735 | Sus | N | Animal¦Squirrel¦Transformer¦Malfunctioning
21-0005093 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2021-01-05 | 1204294 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0008021 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2021-01-13 | 1209431 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0009564 | Animal | Other | Anchor or Guy | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2021-01-18 | 1212101 | Sus | N | Animal¦Other¦AnchororGuy¦Normal
21-0009967 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1213706 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0010216 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214923 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0010756 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Bent or Twisted | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216759 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted
21-0010997 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214855 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011616 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1218989 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0014031 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2021 | Tier 3 - Extreme | Transformer only | 1 | 25 | 2021-01-25 | 1224534 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
21-0014108 | 3rd Party | Customer Equipment | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224614 | Sus | N | 3rdParty¦CustomerEquipment¦PoleWood¦Broken
21-0016196 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234876 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016443 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226620 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016673 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1231976 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0018140 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 1 | 28 | 2021-01-28 | 1240706 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0019311 | Environmental/External | Ice or snow | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2021-01-29 | 1241384 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Together
21-0034475 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2021-03-10 | 1276954 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0051116 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 20 | 2021-04-20 | 1326059 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
21-0051336 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2021 | Tier 2 - Elevated | Transmission line | 4 | 22 | 2021-04-22 | 1329153 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
21-0060941 | Equipment Failure/Involved | Underground | Conductor, Underground | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 13 | 2021-05-13 | 1348616 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Normal
21-0063001 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 18 | 2021-05-18 | 1352348 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0063060 | Animal | Bird found | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Transformer only | 5 | 18 | 2021-05-18 | 1352884 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
21-0069688 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 6 | 3 | 2021-06-03 | 1364992 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0073399 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2021-06-11 | 1371255 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0079272 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2021-06-24 | 1384133 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
21-0082946 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 30 | 2021-06-30 | 1389389 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0085004 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 5 | 2021-07-05 | 1392419 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0091013 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2021-07-16 | 1406292 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
21-0097048 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 7 | 29 | 2021-07-29 | 1420262 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0104514 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2021-08-14 | 1442458 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0106902 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2021-08-19 | 1447274 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0108114 | Animal | Squirrel | Pole-Wood | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2021-08-23 | 1450440 | Sus | Y | Animal¦Squirrel¦PoleWood¦Normal
21-0123171 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2021-09-28 | 1482378 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0127607 | Animal | Other | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2021-10-08 | 1490218 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
21-0128465 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2021-10-11 | 1491928 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
21-0129640 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2021-10-12 | 1495489 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0130324 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2021-10-13 | 1496541 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136699 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513233 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136743 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1515938 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0136796 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1515454 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0140350 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2021-10-31 | 1526372 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0141409 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2021-11-02 | 1532601 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0144125 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2021 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2021-11-09 | 1539104 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
21-0144315 | Animal | Squirrel | Transformer (OH) | Leaking | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2021-11-10 | 1539414 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Leaking
21-0147423 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2021-11-17 | 1548569 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
21-0150051 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2021-11-23 | 1553541 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0158046 | Equipment Failure/Involved | Overhead | Crossarm, Steel | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1570823 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmSteel¦Broken
21-0160526 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581085 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160919 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1583403 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161099 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584298 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161215 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1586181 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161331 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585304 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161401 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2021-12-28 | 1587314 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
21-0161810 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2021-12-30 | 1589806 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0005646 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2022-01-03 | 1593813 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0006237 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2022-01-04 | 1595326 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0006240 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2022-01-04 | 1595289 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
22-0006915 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2021-12-31 | 1596675 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0012687 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 1 | 21 | 2022-01-21 | 1607537 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0016488 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 31 | 2022-01-31 | 1617256 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0019507 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2022-02-07 | 1622900 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0031148 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2022-03-08 | 1644419 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0038260 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2022-03-24 | 1655290 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0038948 | Animal | Squirrel | Fuse | Burned Open | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2022-03-26 | 1656496 | Sus | N | Animal¦Squirrel¦Fuse¦BurnedOpen
22-0041765 | Company Initiated | Construction Activity/equip, company | Cutout, fuse holder | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2022-04-13 | 1671413 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦Cutoutfuseholder¦Normal
22-0050837 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2022-04-18 | 1675458 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0052297 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 2 - Elevated | Transformer only | 4 | 20 | 2022-04-20 | 1677855 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0052901 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2022-04-21 | 1678616 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0056466 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 30 | 2022-04-30 | 1685308 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0061443 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 5 | 12 | 2022-05-12 | 1694679 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0063807 | Animal | Bird found | Transformer (OH) | Burned/flashed | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2022-05-19 | 1702807 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Burnedflashed
22-0064897 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 5 | 21 | 2022-05-21 | 1707072 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0075381 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 16 | 2022-06-16 | 1733509 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0087351 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 19 | 2022-07-19 | 1760729 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0089191 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 24 | 2022-07-24 | 1764570 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
22-0091863 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 7 | 31 | 2022-07-31 | 1769746 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0111730 | Animal | Other | Conductor, Overhead | Burned/flashed | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2022-09-18 | 1815068 | Sus | Y | Animal¦Other¦ConductorOverhead¦Burnedflashed
22-0112305 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 9 | 19 | 2022-09-19 | 1816490 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
22-0114435 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2022-09-23 | 1820378 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0114655 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2022-09-25 | 1821338 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0130582 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 12 | 2022-11-12 | 1861155 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0131409 | Equipment Failure/Involved | Underground | Elbow | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2022-11-15 | 1863453 | Sus | Y | EquipmentFailureInvolved¦Underground¦Elbow¦Broken
22-0132896 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Transformer only | 11 | 19 | 2022-11-19 | 1866298 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0136888 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2022-12-06 | 1876923 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138380 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882028 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0138839 | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885133 | Sus | N | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Normal
22-0138953 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882607 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0140113 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2022-12-15 | 1890140 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Normal
22-0141531 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898355 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0002064 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2015-01-01 | 1157787 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0009903 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1173540 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0011415 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2015-02-07 | 1181937 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0011995 | Equipment Failure/Involved | Rock/mud slide | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2015-02-09 | 1185595 | Sus | N | EquipmentFailureInvolved¦Rockmudslide¦PoleWood¦Brokenwireonground
15-0012314 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2015-02-09 | 1185861 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0013800 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2015-02-17 | 1191640 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0030287 | Equipment Failure/Involved | Other | Conductor, Underground | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 28 | 2015-04-28 | 1226582 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorUnderground¦Broken
15-0037852 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 6 | 2 | 2015-06-02 | 1242595 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
15-0041343 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2015-06-16 | 1251645 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0041764 | Vegetation | Tree - fell into line | Secondary | Normal | 2015 | Tier 3 - Extreme | Transformer only | 6 | 17 | 2015-06-17 | 1252477 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Normal
15-0050041 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 7 | 23 | 2015-07-23 | 1275948 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0051821 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2015-07-31 | 1280642 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0053873 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 2 - Elevated | Transformer only | 8 | 8 | 2015-08-08 | 1285209 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0060298 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2015-09-09 | 1302835 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0060526 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 9 | 10 | 2015-09-10 | 1303317 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0060698 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2015-09-11 | 1303890 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
15-0061082 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1304966 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0063502 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2015-09-25 | 1311764 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0067582 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2015 | Tier 3 - Extreme | Transformer only | 10 | 3 | 2015-10-03 | 1315790 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing
15-0070161 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2015 | Tier 2 - Elevated | Transformer only | 10 | 14 | 2015-10-14 | 1321641 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
15-0070569 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2015-10-15 | 1322606 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0071188 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2015-10-17 | 1323839 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
15-0073330 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2015-10-26 | 1329271 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0075931 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Together | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 5 | 2015-11-05 | 1336226 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together
15-0076413 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 2 - Elevated | Transformer only | 11 | 7 | 2015-11-07 | 1337174 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0082338 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352192 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0082576 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352942 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083819 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357180 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084047 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1358012 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0084190 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2015-12-11 | 1358399 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084315 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2015-12-11 | 1358947 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
15-0084796 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361067 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0085217 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2015-12-14 | 1363107 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
15-0087120 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2015-12-24 | 1371037 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0002583 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2016-01-03 | 1376245 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
16-0006061 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2016-01-18 | 1386111 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0009298 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 30 | 2016-01-30 | 1394524 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0009518 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 31 | 2016-01-31 | 1395422 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0013393 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1405873 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013554 | Vegetation | Tree - fell into line | Insulator | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406789 | Sus | N | Vegetation¦Treefellintoline¦Insulator¦Broken
16-0013633 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2016-02-18 | 1407892 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0018489 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421612 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0018670 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2016-03-07 | 1423044 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0020761 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2016-03-12 | 1429178 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
16-0020925 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430107 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0021226 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430494 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0022762 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2016-03-20 | 1434724 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken
16-0024589 | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2016-03-28 | 1440344 | Sus | N | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal
16-0027191 | Vegetation | Tree - fell into line | Secondary | Normal | 2016 | Tier 2 - Elevated | Transformer only | 4 | 8 | 2016-04-08 | 1446947 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Normal
16-0029651 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 19 | 2016-04-19 | 1453657 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0032111 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2016-04-27 | 1460503 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0033853 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 4 | 2016-05-04 | 1464643 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0036840 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Transformer only | 5 | 18 | 2016-05-18 | 1472134 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0039996 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2016-05-31 | 1479944 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0044339 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2016-06-19 | 1492350 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0048510 | Company Initiated | Improper Construction | Jumper | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2016-07-07 | 1502550 | Sus | Y | CompanyInitiated¦ImproperConstruction¦Jumper¦Normal
16-0048874 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 10 | 2016-07-10 | 1507735 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0049460 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 12 | 2016-07-12 | 1509108 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0059871 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 8 | 25 | 2016-08-25 | 1531828 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0060429 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 8 | 26 | 2016-08-26 | 1532840 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0064797 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2016-09-14 | 1541885 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0065102 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2016-09-16 | 1542633 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0067566 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2016-09-26 | 1547890 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0069028 | Equipment Failure/Involved | Overhead | Jumper | Bent or Twisted | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2016-10-02 | 1551341 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BentorTwisted
16-0076061 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 27 | 2016-10-27 | 1570877 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0084600 | Equipment Failure/Involved | Overhead |  | Normal | 2016 | Tier 3 - Extreme | Transformer only | 12 | 8 | 2016-12-08 | 1596992 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦Normal
16-0084630 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2016-12-08 | 1596971 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0086137 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 17 | 2016-12-17 | 1605335 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0002696 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 1 | 1 | 2017-01-01 | 1614197 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0005456 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627312 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0005608 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627577 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0009112 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 14 | 2017-01-14 | 1643289 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0009238 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 14 | 2017-01-14 | 1643854 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0010978 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2017-01-19 | 1651182 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0012511 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1657158 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0012935 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1659422 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0013783 | Environmental/External | Lightning | Transformer (OH) | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663523 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal
17-0013891 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664367 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0014348 | Company Initiated | Return Circuit Normal | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2017-01-24 | 1665604 | Sus | N | CompanyInitiated¦ReturnCircuitNormal¦ConductorOverhead¦Normal
17-0016600 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2017-02-01 | 1671921 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018236 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1678158 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019470 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683477 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019496 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1682943 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0022725 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1696259 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023884 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703005 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0024404 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704367 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0024793 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706301 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025729 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1709648 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0027758 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2017-03-02 | 1717302 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0027851 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2017-03-02 | 1717805 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0032273 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2017-03-21 | 1731602 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0035600 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2017-03-31 | 1740901 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0035647 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2017-03-31 | 1741480 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0036832 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2017-04-05 | 1744854 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038308 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 4 | 8 | 2017-04-08 | 1752728 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0040930 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2017-04-17 | 1759816 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0042738 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2017-04-25 | 1766714 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0043903 | Vegetation | Tree - fell into line | Secondary | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2017-04-29 | 1770503 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Broken
17-0047073 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2017-05-10 | 1779674 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0048431 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2017-05-16 | 1783646 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0058764 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 26 | 2017-06-26 | 1818720 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0066731 | 3rd Party | Tree - cutting, 3rd party | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 7 | 31 | 2017-07-31 | 1843089 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Transformer¦Broken
17-0071151 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2017-08-17 | 1854429 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0074628 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2017-09-01 | 1864452 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0075112 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 2 | 2017-09-02 | 1866076 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0077299 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 10 | 2017-09-10 | 1874223 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0085394 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1895664 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground
17-0086839 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1894286 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0087429 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2017-10-14 | 1901035 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0090131 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2017-10-24 | 1909071 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0090131 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2017-10-24 | 1909071 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0093598 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2017-11-08 | 1918467 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0094386 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2017-11-11 | 1920421 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0096843 | 3rd Party | Vehicle | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 11 | 21 | 2017-11-21 | 1927315 | Sus | Y | 3rdParty¦Vehicle¦CrossarmWood¦Brokenwireonground
17-0099614 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1934837 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0103754 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2017-12-31 | 1953692 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0018506 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 34616 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
18-0018660 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 34385 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0019402 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2018-03-03 | 37358 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
18-0024603 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2018-03-20 | 48955 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0030358 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2018-04-08 | 62477 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0030358 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2018-04-08 | 62477 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0033650 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2018-04-19 | 69868 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0034767 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2018-04-23 | 72486 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0039246 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2018-05-08 | 81533 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0053468 | 3rd Party | Customer Equipment | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 6 | 22 | 2018-06-22 | 115106 | Sus | Y | 3rdParty¦CustomerEquipment¦Transformer¦FailedFaulted
18-0054129 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2018-06-24 | 117250 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0065886 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2018-07-23 | 146873 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0066274 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 147840 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0067639 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2018-08-07 | 150992 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0068317 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2018-08-09 | 152142 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0071998 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2018-08-21 | 159105 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075960 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2018-09-03 | 167393 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0078558 | 3rd Party | Customer Equipment | Customer Equipment | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2018-09-11 | 172364 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Normal
18-0082772 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2018 | Tier 2 - Elevated | Transformer only | 9 | 24 | 2018-09-24 | 180266 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
18-0084428 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2018-09-28 | 183114 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0086190 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2018-10-03 | 187138 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0088316 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2018-10-08 | 191065 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0090131 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2018-10-13 | 194502 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
18-0092544 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2018-10-21 | 199537 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0094379 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2018-10-29 | 204599 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Together
18-0094484 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2018-10-26 | 202863 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦FailedFaulted
18-0095696 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2018-10-30 | 205724 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0099398 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 13 | 2018-11-13 | 214543 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0101384 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2018-11-20 | 218872 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0101384 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2018-11-20 | 218872 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0102513 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 222719 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102556 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2018-11-23 | 222769 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0102664 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2018-11-23 | 223194 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0103621 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2018-11-26 | 225182 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
18-0106528 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2018-12-03 | 232741 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0109180 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 240146 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0109220 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 240275 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109385 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2018-12-15 | 240993 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0110454 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2018-12-24 | 246154 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0110601 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2018-12-25 | 246921 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0003576 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2019-01-02 | 251782 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0004491 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2019 | Tier 2 - Elevated | Transformer only | 1 | 4 | 2019-01-04 | 253093 | Sus | N | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
19-0005490 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 257393 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0006590 | Equipment Failure/Involved | Overhead | Secondary | Arcing | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2019-01-08 | 260978 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Arcing
19-0009997 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 267899 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010085 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 268867 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010750 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 272956 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0010922 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 273676 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011180 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 272010 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0011302 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 272650 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0014807 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2019-01-27 | 282144 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
19-0017228 | Environmental/External | Lightning | Circuit Breaker | Normal | 2019 | Tier 3 - Extreme | Generation | 2 | 2 | 2019-02-02 | 287634 | Sus | N | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Normal
19-0018743 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292021 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020671 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298410 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0021342 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 300382 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023263 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 308451 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0024249 | Environmental/External | Ice or snow | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 312830 | Sus | N | EnvironmentalExternal¦Iceorsnow¦CrossarmWood¦Broken
19-0025760 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 318083 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0026224 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 319182 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
19-0028177 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324080 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0031014 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2019-03-05 | 331678 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0031752 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 3 | 7 | 2019-03-07 | 333744 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
19-0032637 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2019-03-11 | 336283 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0036243 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2019-03-22 | 345608 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
19-0038286 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2019 | Tier 3 - Extreme | Transformer only | 3 | 29 | 2019-03-29 | 350273 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
19-0040229 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 4 | 5 | 2019-04-05 | 354657 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0040356 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2019-04-07 | 355089 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0041605 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2019-04-11 | 358815 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0041718 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2019-04-11 | 359033 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0041759 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2019-04-11 | 359127 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0043871 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2019-04-18 | 362848 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0043895 | 3rd Party | Vehicle | Pole-Wood | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2019-04-18 | 362891 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Burnedflashed
19-0045792 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2019-04-24 | 367411 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
19-0049851 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2019-05-07 | 376046 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0055299 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 22 | 2019-05-22 | 387752 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0071589 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2019-06-24 | 427855 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0073006 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2019-06-28 | 433141 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0081356 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2019-07-25 | 472016 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0081771 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Transmission line | 7 | 27 | 2019-07-27 | 473079 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0087911 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2019-08-14 | 510676 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0091279 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2019-08-23 | 533039 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0095470 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 5 | 2019-09-05 | 554004 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0104850 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2019-09-28 | 624162 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0114317 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2019-10-22 | 676816 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0116288 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2019-10-26 | 684937 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
19-0116561 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2019-10-26 | 688066 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Secondary¦Brokenwireonground
19-0122298 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2019-11-07 | 701671 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0129904 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 719928 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130552 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 721689 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0134618 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2019-12-06 | 731862 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0135958 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2019-12-11 | 736561 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137168 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 18 | 2019-12-18 | 745727 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0010565 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2020-01-17 | 763831 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0015078 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2020-01-29 | 772674 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
20-0018955 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 781231 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
20-0019162 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 782850 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken
20-0020231 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 787909 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
20-0022803 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2020-02-17 | 792574 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0025836 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2020-02-25 | 810143 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0027615 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2020-03-02 | 821134 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0027647 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2020-03-02 | 821159 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031397 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2020-03-12 | 846013 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0033050 | Vegetation | Tree - branch fell on line | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855665 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦FailedFaulted
20-0033405 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 856782 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0034296 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2020-03-19 | 858652 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0034353 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2020-03-19 | 858858 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0038690 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2020-04-05 | 883514 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0039938 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2020-04-09 | 892725 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0044469 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Transmission line | 4 | 24 | 2020-04-24 | 900962 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0044659 | Equipment Failure/Involved | Overhead | Other | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 26 | 2020-04-26 | 901785 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
20-0050909 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2020-05-16 | 914882 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0051059 | Company Initiated | Construction Activity/equip, company | Jumper | Arcing | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 17 | 2020-05-17 | 915480 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Arcing
20-0062413 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Transformer only | 6 | 17 | 2020-06-17 | 941498 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0062816 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Transformer only | 6 | 18 | 2020-06-18 | 942164 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0066084 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2020-06-29 | 950029 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0068333 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 4 | 2020-07-04 | 957671 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0071915 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2020 | Tier 2 - Elevated | Transformer only | 7 | 14 | 2020-07-14 | 964723 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
20-0073231 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 17 | 2020-07-17 | 966945 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0073925 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2020-07-20 | 968808 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0081194 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 7 | 2020-08-07 | 984334 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
20-0083366 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 13 | 2020-08-13 | 997114 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
20-0085206 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1013814 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
20-0086090 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 8 | 17 | 2020-08-17 | 1017232 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0089986 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Transformer only | 8 | 25 | 2020-08-25 | 1030711 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0090252 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1032556 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090413 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033284 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091529 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2020-08-31 | 1041222 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
20-0097167 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 14 | 2020-09-14 | 1068941 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0098537 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1078253 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0098569 | 3rd Party | Vehicle | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 17 | 2020-09-17 | 1078196 | Sus | Y | 3rdParty¦Vehicle¦Fuse¦FailedFaulted
20-0099785 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086065 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0104932 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2020-10-04 | 1110731 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0109029 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2020-10-15 | 1118314 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0123201 | Animal | Squirrel | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 20 | 2020-11-20 | 1149911 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
20-0128361 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167257 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0128400 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167263 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0130229 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2020-12-14 | 1182932 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0130278 | Equipment Failure/Involved | Underground | Service conductor | Broken | 2020 | Tier 2 - Elevated | Transformer only | 12 | 14 | 2020-12-14 | 1183748 | Sus | N | EquipmentFailureInvolved¦Underground¦Serviceconductor¦Broken
20-0131748 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2020-12-25 | 1198441 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0010539 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216245 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011519 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214533 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0012847 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1221364 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0016132 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 27 | 2021-01-27 | 1234090 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken
21-0016562 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1236314 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0017039 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237167 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0021377 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2021-02-03 | 1247063 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
21-0022537 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2021-02-05 | 1249104 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0028951 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2021-02-23 | 1260984 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0034261 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 9 | 2021-03-09 | 1276453 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0051710 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2021-04-22 | 1328122 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0051710 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2021-04-22 | 1328122 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0069740 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2021-06-03 | 1365258 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0077568 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2021-06-22 | 1382363 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0078287 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 23 | 2021-06-23 | 1383301 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0078940 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 6 | 24 | 2021-06-24 | 1383790 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0080121 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2021-06-25 | 1385321 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0085241 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2021-07-06 | 1392870 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0092978 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 21 | 2021-07-21 | 1409906 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
21-0098271 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2021-08-01 | 1428319 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0102154 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 8 | 9 | 2021-08-09 | 1438277 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0102294 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2021-08-10 | 1438725 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0106801 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2021-08-19 | 1447298 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
21-0112374 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2021-09-01 | 1460353 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0112734 | Equipment Failure/Involved | Overhead | Secondary | Normal | 2021 | Tier 2 - Elevated | Transformer only | 9 | 2 | 2021-09-02 | 1461108 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal
21-0113017 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2021-09-02 | 1461291 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0113801 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 5 | 2021-09-05 | 1462670 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0118156 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2021 | Tier 2 - Elevated | Transformer only | 9 | 15 | 2021-09-15 | 1472791 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
21-0123801 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 29 | 2021-09-29 | 1483399 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0126426 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2021-10-06 | 1488203 | Sus | Y | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
21-0126679 | 3rd Party | Kite | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2021-10-06 | 1488758 | Sus | Y | 3rdParty¦Kite¦ConductorOverhead¦Normal
21-0128454 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492081 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0131740 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2021-10-15 | 1498463 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136211 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508487 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
21-0136681 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514781 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0137002 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2021-10-25 | 1517676 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137473 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1518981 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0141612 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2021-11-03 | 1533724 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0150376 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 11 | 23 | 2021-11-23 | 1553847 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0158222 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1570315 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0161056 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584188 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0161378 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1587212 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0161529 | Environmental/External | Ice or snow | Service conductor | Bent or Twisted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 29 | 2021-12-29 | 1587995 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦BentorTwisted
21-0161536 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1588332 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161768 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2021-12-30 | 1589403 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161826 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2021-12-29 | 1589878 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0005352 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 3 - Extreme | Transformer only | 1 | 3 | 2022-01-03 | 1593115 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0006215 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1595246 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0009021 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2022-01-12 | 1601009 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0010527 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2022-01-17 | 1604079 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
22-0013756 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 1 | 24 | 2022-01-24 | 1611279 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0014088 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2022-01-25 | 1611669 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0015454 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 1 | 27 | 2022-01-27 | 1614754 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0017343 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2022-02-02 | 1618793 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0026232 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2022 | Tier 3 - Extreme | Transformer only | 2 | 23 | 2022-02-23 | 1635163 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
22-0026922 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2022 | Tier 3 - Extreme | Transformer only | 2 | 25 | 2022-02-25 | 1637654 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
22-0033325 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2022-03-13 | 1647647 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0036093 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2022-03-20 | 1651997 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0050550 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 16 | 2022-04-16 | 1674205 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0060426 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 10 | 2022-05-10 | 1693368 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0060840 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2022-05-11 | 1693841 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
22-0072454 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2022-06-09 | 1726753 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0073959 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2022-06-14 | 1730771 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0078659 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Transformer only | 6 | 25 | 2022-06-25 | 1742352 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
22-0080865 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2022-07-01 | 1746837 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0084510 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2022-07-12 | 1754725 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0086021 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2022-07-15 | 1757433 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0086253 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 7 | 17 | 2022-07-17 | 1758284 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0094350 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2022-08-05 | 1774272 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100001 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2022-08-19 | 1785651 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0107900 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 8 | 2022-09-08 | 1805753 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0111728 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1815112 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0115975 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2022-09-28 | 1823801 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0117028 | Animal | Squirrel | Cutout, fuse holder | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2022-10-02 | 1826174 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
22-0119689 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2022-10-10 | 1834015 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0121000 | Equipment Failure/Involved | Overhead | Secondary | Normal | 2022 | Tier 3 - Extreme | Transformer only | 10 | 13 | 2022-10-13 | 1836391 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal
22-0121863 | Animal | Other | Jumper | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2022-10-16 | 1838247 | Sus | Y | Animal¦Other¦Jumper¦Broken
22-0126773 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 1 | 2022-11-01 | 1850517 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0130592 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Transformer only | 11 | 12 | 2022-11-12 | 1861063 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0132595 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Transmission line | 11 | 18 | 2022-11-18 | 1865505 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0136264 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2022-12-03 | 1874922 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0137667 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2022-12-08 | 1878970 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0142183 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2022-12-30 | 1901943 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0142709 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1904230 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0018988 | Animal | Bird found | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2015-03-11 | 1202367 | Sus | N | Animal¦Birdfound¦Transformer¦FailedFaulted
15-0018997 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2015-03-11 | 1202381 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0019168 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2015-03-12 | 1202644 | Sus | N | EquipmentFailureInvolved¦Other¦PotheadRiserTermination¦Burnedflashed
15-0033073 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 9 | 2015-05-09 | 1231967 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
15-0034925 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2015-05-18 | 1236389 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0038584 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2015-06-04 | 1243768 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0039494 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 8 | 2015-06-08 | 1245979 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
15-0044459 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 1 | 2015-07-01 | 1260032 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0046639 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2015-07-09 | 1265774 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
15-0047094 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 13 | 2015-07-13 | 1267221 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0048599 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1271797 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0048923 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Transformer only | 7 | 19 | 2015-07-19 | 1271834 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0049305 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 20 | 2015-07-20 | 1273695 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0050594 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 27 | 2015-07-27 | 1277621 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0055629 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2015-08-17 | 1290375 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
15-0055700 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2015-08-17 | 1290663 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0059138 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2015-09-03 | 1299613 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
15-0059189 | Animal | Squirrel | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2015-09-03 | 1299790 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
15-0061090 | Vegetation | Tree - branch fell on line | Bushing | Broken | 2015 | Tier 2 - Elevated | Transformer only | 9 | 13 | 2015-09-13 | 1304995 | Sus | Y | Vegetation¦Treebranchfellonline¦Bushing¦Broken
15-0061338 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1305730 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062278 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 19 | 2015-09-19 | 1308513 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0067708 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2015-10-03 | 1316255 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0070254 | 3rd Party | Vehicle | Transformer | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2015-10-14 | 1321829 | Sus | Y | 3rdParty¦Vehicle¦Transformer¦Broken
15-0074470 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 31 | 2015-10-31 | 1332139 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0077247 | Animal | Squirrel | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2015-11-11 | 1339575 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
15-0077708 | Animal | Squirrel | Cutout, fuse holder | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2015-11-13 | 1340814 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Burnedflashed
15-0078046 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342570 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0081059 | Unknown Cause | Patrol - not conducted | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 25 | 2015-11-25 | 1348434 | Sus | Y | UnknownCause¦Patrolnotconducted¦Transformer¦FailedFaulted
15-0086083 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 18 | 2015-12-18 | 1366012 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0087452 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2015-12-26 | 1372186 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
16-0003371 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378236 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0003840 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2016-01-07 | 1379531 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0006724 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2016-01-20 | 1388327 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0012637 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2016-02-15 | 1403601 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013415 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406454 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0017591 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416905 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018342 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421070 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018668 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 7 | 2016-03-07 | 1423016 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0019228 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2016-03-08 | 1425095 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
16-0032098 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2016-04-27 | 1460344 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0032347 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 28 | 2016-04-28 | 1460877 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0036540 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2016-05-17 | 1471281 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
16-0044875 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 6 | 21 | 2016-06-21 | 1493414 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0045502 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2016-06-24 | 1495010 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0049398 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2016-07-12 | 1508893 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0053862 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2016-07-30 | 1519103 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0054589 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 2 | 2016-08-02 | 1520710 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0059569 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2016-08-24 | 1531225 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0064887 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 9 | 15 | 2016-09-15 | 1542048 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0067391 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2016-09-26 | 1547614 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0072450 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2016-10-15 | 1560713 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0072589 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561326 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0074498 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2016-10-21 | 1566891 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
16-0075166 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2016-10-24 | 1569007 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0076428 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2016-10-28 | 1571895 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0076641 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2016-10-29 | 1572479 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0077631 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2016-11-02 | 1575463 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0078310 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2016-11-06 | 1577437 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
16-0083522 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2016-12-02 | 1593130 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0086073 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2016-12-16 | 1604913 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0086705 | Animal | Bird found | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2016-12-22 | 1609065 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0002804 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2017-01-02 | 1614742 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0003187 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1616374 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0003883 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2017-01-05 | 1619112 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0004163 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2017-01-06 | 1620015 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0005604 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627933 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006004 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1629610 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007424 | Environmental/External | Flood/Erosion | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638477 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Normal
17-0007681 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1639913 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0007773 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1638075 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0010370 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648599 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011077 | Environmental/External | Flood/Erosion | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2017-01-19 | 1651782 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦OnGround
17-0013047 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660473 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0013127 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660681 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017005 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2017-02-02 | 1673071 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0017633 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transmission line | 2 | 5 | 2017-02-05 | 1675736 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017763 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2017-02-06 |  | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground
17-0017763 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2017-02-06 |  | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground
17-0020785 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2017-02-13 | 1687735 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0022997 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2017-02-18 | 1699250 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0023008 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2017-02-18 | 1699415 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023194 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2017-02-18 | 1700439 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0024098 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704729 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0024820 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706735 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0025191 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1707572 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing
17-0028245 | 3rd Party | Customer Equipment | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2017-03-03 | 1718905 | Sus | N | 3rdParty¦CustomerEquipment¦Fuse¦FailedFaulted
17-0028450 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2017-03-05 | 1719803 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0029926 | 3rd Party | Customer Equipment | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2017-03-10 | 1723896 | Sus | N | 3rdParty¦CustomerEquipment¦Fuse¦FailedFaulted
17-0032022 | Equipment Failure/Involved | Underground | Secondary | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 3 | 20 | 2017-03-20 | 1730829 | Sus | N | EquipmentFailureInvolved¦Underground¦Secondary¦Deteriorated
17-0033411 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2017-03-24 | 1734396 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0037169 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745590 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
17-0037727 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1749185 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0037931 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2017 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2017-04-07 | 1750634 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
17-0037960 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1748958 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0038259 | Equipment Failure/Involved | Electrical Overload | Secondary | Arcing | 2017 | Tier 2 - Elevated | Transformer only | 4 | 8 | 2017-04-08 | 1752557 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Arcing
17-0038437 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2017-04-09 | 1753350 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0046826 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 10 | 2017-05-10 | 1779123 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
17-0048427 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2017-05-16 | 1783627 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0050605 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2017-05-25 | 1790284 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0055701 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2017-06-16 | 1805603 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0068605 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2017-08-07 | 1848180 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0070260 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 14 | 2017-08-14 | 1852555 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0072181 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2017-08-22 | 1857355 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0075229 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 2 | 2017-09-02 | 1866774 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0075505 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2017-09-03 | 1867889 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0078672 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 9 | 13 | 2017-09-13 | 1878205 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0083822 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2017-10-03 | 1890174 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0087854 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1902240 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0093397 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2017-11-08 | 1917964 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
17-0093726 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2017-11-08 | 1918865 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0004461 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2018-01-08 | 4260 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0007358 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2018-01-19 | 10708 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0011746 | Company Initiated | Other Circuits |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2018-02-06 | 19958 | Sus | N | CompanyInitiated¦OtherCircuits¦¦
18-0021738 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2018-03-12 | 42097 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0034046 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 4 | 20 | 2018-04-20 | 70537 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0038783 | 3rd Party | Tree - cutting, 3rd party | Fuse | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2018-05-07 | 80692 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦Normal
18-0042421 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2018 | Tier 2 - Elevated | Transmission line | 5 | 18 | 2018-05-18 | 89328 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
18-0050077 | 3rd Party | Vehicle | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2018-06-12 | 107210 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Together
18-0060095 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2018-07-16 | 132492 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0066271 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 147837 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0067236 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2018-08-06 | 150113 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
18-0075181 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2018-08-30 | 165659 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075939 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2018-09-03 | 167322 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
18-0079203 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2018-09-13 | 173394 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed
18-0080700 | Animal | Other | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2018-09-18 | 176248 | Sus | Y | Animal¦Other¦Transformer(OH)¦Normal
18-0083524 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2018 | Tier 2 - Elevated | Transformer only | 9 | 25 | 2018-09-25 | 181355 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
18-0086013 | Company Initiated | Personnel, company |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2018-10-15 | 195576 | Sus | Y | CompanyInitiated¦Personnelcompany¦¦
18-0089371 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2018-10-11 | 192938 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0090195 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Transformer only | 10 | 14 | 2018-10-14 | 194702 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0090220 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2018-10-14 | 195074 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
18-0091198 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2018-10-17 | 197059 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0093326 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2018-10-23 | 200840 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0094868 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2018-10-28 | 203682 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0099437 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 214585 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal
18-0100504 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2018-11-16 | 217023 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
18-0102786 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 24 | 2018-11-24 | 223637 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
18-0110974 | Equipment Failure/Involved | Overhead | Service conductor | Broken | 2018 | Tier 2 - Elevated | Transformer only | 12 | 28 | 2018-12-28 | 248616 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken
19-0005657 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 258783 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
19-0010097 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 268681 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
19-0011076 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 274115 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0013529 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 1 | 23 | 2019-01-23 | 279628 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0014005 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 1 | 24 | 2019-01-24 | 280157 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
19-0020813 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298619 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0021684 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301580 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
19-0021976 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 302875 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0023123 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 307665 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024261 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Transformer only | 2 | 14 | 2019-02-14 | 312895 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken
19-0024613 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 314601 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
19-0025306 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 316716 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0025315 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 316780 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0025593 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 316557 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025688 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 317956 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0031056 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 332117 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0031282 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2019-03-06 | 332352 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0034955 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2019-03-19 | 342771 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0035283 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2019-03-20 | 343473 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0036857 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 25 | 2019-03-25 | 347217 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0045760 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2019-04-24 | 367288 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0046097 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2019-04-25 | 368097 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0049603 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2019-05-07 | 375234 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0049902 | Equipment Failure/Involved | Overhead | Pole-Wood | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2019-05-08 | 376133 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦OnGround
19-0050688 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2019-05-10 | 377590 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0053149 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2019-05-17 | 383277 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
19-0053901 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2019-05-19 | 385075 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0060313 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2019-05-30 | 393889 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0063149 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2019-06-05 | 398342 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0063160 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2019-06-05 | 398446 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0063628 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2019-06-06 | 399532 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0064808 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2019-06-09 | 402419 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0067154 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2019-06-13 | 408661 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0069824 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2019-06-19 | 421684 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0077156 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2019-07-14 | 450060 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0080133 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 7 | 23 | 2019-07-23 | 468828 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
19-0088648 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2019-08-16 | 515076 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0090038 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2019-08-20 | 525911 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0090657 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2019-08-21 | 529553 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0094686 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2019-08-30 | 551181 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
19-0099455 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2019-09-16 | 584067 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0102785 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 23 | 2019-09-23 | 608006 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0104117 | Equipment Failure/Involved | Overhead | Switch | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 9 | 26 | 2019-09-26 | 617720 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Switch¦FailedFaulted
19-0104342 | Equipment Failure/Involved | Overhead | Transformer | Together | 2019 | Tier 2 - Elevated | Transformer only | 9 | 26 | 2019-09-26 | 619834 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Together
19-0105013 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2019-09-28 | 627974 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0113793 | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2019-10-20 | 674701 | Sus | Y | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted
19-0118857 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2019-10-30 | 694822 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0120093 | Animal | Squirrel | Recloser | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2019-11-01 | 697662 | Sus | Y | Animal¦Squirrel¦Recloser¦Burnedflashed
19-0120308 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 3 - Extreme | Transformer only | 11 | 1 | 2019-11-01 | 697919 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0123610 | Animal | Bird found | Conductor, Underground | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2019-11-11 | 704413 | Sus | Y | Animal¦Birdfound¦ConductorUnderground¦Normal
19-0129968 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 719747 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0131533 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 725012 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing
19-0131908 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 725386 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0133694 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2019-12-05 | 730198 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0136310 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2019-12-12 | 737977 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
20-0012196 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2020 | Tier 2 - Elevated | Transformer only | 1 | 22 | 2020-01-22 | 767875 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
20-0019874 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Bent or Twisted | 2020 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2020-02-10 | 787292 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted
20-0019916 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 785170 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0024566 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 2 | 21 | 2020-02-21 | 797753 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0026388 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2020-02-27 | 814365 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032250 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2020-03-15 | 851917 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0032436 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852800 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032655 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 854155 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0032941 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 853408 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0036176 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 25 | 2020-03-25 | 865613 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0038280 | Company Initiated | Improper Construction | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 3 | 2020-04-03 | 881357 | Sus | N | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Normal
20-0060097 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2020-06-11 | 936485 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0060481 | Animal | Squirrel | Switch (OH) | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2020-06-12 | 937470 | Sus | Y | Animal¦Squirrel¦Switch(OH)¦Normal
20-0062009 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 16 | 2020-06-16 | 940474 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0065770 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2020-06-28 | 949173 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0068271 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2020-07-03 | 957393 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0076362 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2020-07-27 | 972987 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed
20-0077166 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 7 | 28 | 2020-07-28 | 973848 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0079990 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 5 | 2020-08-05 | 979394 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0090162 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1032136 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091459 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1041135 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091530 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2020-08-31 | 1042573 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0094030 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 6 | 2020-09-06 | 1057207 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0097448 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2020-09-14 | 1070492 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
20-0099178 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2020-09-19 | 1082157 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0099966 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086473 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0102103 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2020-09-27 | 1095169 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0104190 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2020-10-01 | 1105839 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
20-0108654 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Arcing | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2020-10-14 | 1117993 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Arcing
20-0113885 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 10 | 27 | 2020-10-27 | 1129764 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0114611 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2020-10-29 | 1131212 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0115452 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 10 | 30 | 2020-10-30 | 1132284 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
20-0117189 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 4 | 2020-11-04 | 1136174 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0121188 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2020-11-16 | 1145913 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0122943 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 19 | 2020-11-19 | 1149339 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0124566 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 24 | 2020-11-24 | 1153777 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0125118 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 25 | 2020-11-25 | 1154474 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0125545 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2020-11-28 | 1155402 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0125545 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2020-11-28 | 1155402 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0125598 | Animal | Squirrel | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2020-11-28 | 1155485 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Broken
20-0126532 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2020-12-02 | 1159723 | Sus | N | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0127034 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2020-12-02 | 1159693 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0128121 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 5 | 2020-12-05 | 1164184 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0128402 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167259 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
20-0131033 | 3rd Party | Customer Equipment | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2020-12-18 | 1193202 | Sus | N | 3rdParty¦CustomerEquipment¦CrossarmWood¦Broken
21-0005768 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 6 | 2021-01-06 | 1205419 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken
21-0009166 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 15 | 2021-01-15 | 1211103 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0009744 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1212392 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0014145 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224849 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0015743 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233019 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
21-0017474 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233329 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0018527 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1241260 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0019192 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2021-01-30 | 1242839 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0024826 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2021-02-11 | 1253454 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
21-0027885 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2021-02-21 | 1259026 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0030412 | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2021-02-28 | 1264102 | Sus | N | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Broken
21-0036569 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2021-03-15 | 1282953 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0037235 | Vegetation | Tree - branch fell on line | Insulator | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2021-03-16 | 1285211 | Sus | N | Vegetation¦Treebranchfellonline¦Insulator¦Broken
21-0048963 | 3rd Party | Dig in, 3rd party | Secondary | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2021-04-15 | 1318026 | Sus | N | 3rdParty¦Digin3rdparty¦Secondary¦Broken
21-0051479 | Equipment Failure/Involved | Overhead |  | Broken | 2021 | Tier 3 - Extreme | Transformer only | 4 | 21 | 2021-04-21 | 1327069 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦Broken
21-0051604 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 21 | 2021-04-21 | 1327241 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0060792 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 13 | 2021-05-13 | 1347671 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0064127 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2021-05-20 | 1354976 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
21-0064772 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 5 | 22 | 2021-05-22 | 1356514 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0067986 | Vegetation | Tree - bark fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2021-05-31 | 1362159 | Sus | Y | Vegetation¦Treebarkfellintoline¦PoleWood¦Brokenwireonground
21-0071762 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 6 | 8 | 2021-06-08 | 1368797 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0083653 | 3rd Party | Dig in, 3rd party | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2021-07-01 | 1390087 | Sus | Y | 3rdParty¦Digin3rdparty¦Transformer(OH)¦FailedFaulted
21-0084768 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 4 | 2021-07-04 | 1391560 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0087507 | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2021-07-10 | 1398517 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Normal
21-0089824 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2021-07-14 | 1404995 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0096456 | Vegetation | Tree - branch fell on line | Transformer (OH) | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2021-07-28 | 1418008 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Burnedflashed
21-0114262 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 7 | 2021-09-07 | 1463721 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0120260 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2021-09-21 | 1476834 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0120752 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2021-09-22 | 1477688 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0121885 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2021-09-24 | 1479423 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0122656 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2021 | Tier 3 - Extreme | Transformer only | 9 | 27 | 2021-09-27 | 1481419 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0128134 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2021-10-11 | 1494449 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0128380 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 10 | 10 | 2021-10-10 | 1491519 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0135876 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509527 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0141605 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2021-11-03 | 1533532 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0143592 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1537908 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0143828 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2021-11-09 | 1538485 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0157651 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568567 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157689 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1568495 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0158029 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569339 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160397 | Animal | Bird found | Fuse | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2021-12-24 | 1580443 | Sus | N | Animal¦Birdfound¦Fuse¦Normal
21-0160492 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2021-12-24 | 1580972 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0160953 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1583773 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0161064 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585175 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0161143 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585379 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0161585 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588558 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161848 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1589956 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005759 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1594305 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0006633 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1596209 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0008015 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2022-01-10 | 1599358 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0013622 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2022-01-24 | 1610844 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0029774 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2022 | Tier 3 - Extreme | Transformer only | 3 | 4 | 2022-03-04 | 1642016 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
22-0039080 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2022-03-27 | 1657238 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0051229 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 19 | 2022-04-19 | 1676171 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0051490 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2022-04-19 | 1676470 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0055751 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 28 | 2022-04-28 | 1684142 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0056436 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 30 | 2022-04-30 | 1685237 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0059954 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 9 | 2022-05-09 | 1692450 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0060384 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2022 | Tier 2 - Elevated | Transmission line | 5 | 10 | 2022-05-10 | 1693122 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
22-0085585 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Transformer only | 7 | 14 | 2022-07-14 | 1756637 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0087283 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 7 | 19 | 2022-07-19 | 1760477 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0095073 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2022-08-08 | 1776195 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0099274 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2022-08-18 | 1784459 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0099905 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 8 | 19 | 2022-08-19 | 1785363 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0105744 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2022-09-04 | 1799018 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0116240 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 29 | 2022-09-29 | 1824307 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0117198 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2022-10-03 | 1826755 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0118501 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2022-10-06 | 1830004 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0121925 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2022-10-16 | 1838448 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0123002 | Company Initiated | Personnel, company | Recloser | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2022-10-19 | 1840753 | Sus | Y | CompanyInitiated¦Personnelcompany¦Recloser¦Normal
22-0123189 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2022-10-20 | 1841362 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
22-0128141 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 5 | 2022-11-05 | 1854393 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0128924 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1856930 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
22-0129344 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1858430 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0129843 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2022-11-09 | 1859527 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0131431 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2022-11-15 | 1863579 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139105 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1886438 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0140891 | Environmental/External | Earthquake | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2022-12-21 | 1894774 | Sus | N | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Together
22-0141649 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898289 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0142227 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2022-12-30 | 1902207 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0142916 | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1905050 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground
23-0004440 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1908674 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0011265 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2015-02-07 | 1181025 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0013391 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 3 - Extreme | Transformer only | 2 | 14 | 2015-02-14 | 1190265 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0017061 | Equipment Failure/Involved | Other | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2015-03-03 | 1198914 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Normal
15-0034013 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2015-05-14 | 1234233 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
15-0038578 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 6 | 4 | 2015-06-04 | 1243734 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0047491 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2015-07-14 | 1268180 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0052209 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 3 | 2015-08-03 | 1281756 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
15-0053762 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 7 | 2015-08-07 | 1285009 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0054926 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2015-08-13 | 1288043 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
15-0057335 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Transformer only | 8 | 25 | 2015-08-25 | 1294487 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0060950 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2015-09-11 | 1304292 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0062433 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1309149 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0070013 | 3rd Party | Customer Equipment |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 13 | 2015-10-13 | 1321207 | Sus | Y | 3rdParty¦CustomerEquipment¦¦FailedFaulted
15-0070135 | Animal | Other | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2015-10-14 | 1321582 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
15-0077236 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2015-11-11 | 1339448 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0080713 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 24 | 2015-11-24 | 1348152 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0084485 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1359797 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0084980 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361797 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0085364 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2015-12-14 | 1363094 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0086483 | Vegetation | Tree - fell into line | Secondary | Normal | 2015 | Tier 2 - Elevated | Transformer only | 12 | 21 | 2015-12-21 | 1367993 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Normal
15-0086677 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2015-12-22 | 1368853 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0086794 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2015 | Tier 3 - Extreme | Transformer only | 12 | 22 | 2015-12-22 | 1369349 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
15-0086999 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2015-12-23 | 1370403 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0003915 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 1 | 7 | 2016-01-07 | 1379789 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0005497 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2016-01-15 | 1384264 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0005925 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385588 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0013461 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407199 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0014631 | Vegetation | Tree - fell into line | Cutout, fuse holder | Broken | 2016 | Tier 3 - Extreme | Transformer only | 2 | 22 | 2016-02-22 | 1410201 | Sus | N | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken
16-0017498 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416774 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017498 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416774 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017696 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417818 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017975 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420157 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0019511 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2016-03-09 | 1425576 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0019732 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2016-03-09 | 1426059 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
16-0019732 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2016-03-09 | 1426059 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
16-0020329 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427278 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0020718 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2016-03-12 | 1429027 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0028216 | 3rd Party | Vehicle | Transformer (UG) | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2016-04-13 | 1449820 | Sus | N | 3rdParty¦Vehicle¦Transformer(UG)¦Broken
16-0038305 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2016-05-25 | 1476406 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0040088 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 1 | 2016-06-01 | 1480442 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0045711 | Equipment Failure/Involved | Overhead | Transformer | Burned Open | 2016 | Tier 3 - Extreme | Transformer only | 6 | 25 | 2016-06-25 | 1495553 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦BurnedOpen
16-0048394 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2016-07-07 | 1502330 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
16-0050006 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2016-07-14 | 1510277 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0052096 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 24 | 2016-07-24 | 1515054 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0058381 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2016-08-18 | 1528707 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0064921 | Vegetation | Tree - branch fell on line |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 9 | 15 | 2016-09-15 | 1542191 | Sus | Y | Vegetation¦Treebranchfellonline¦¦FailedFaulted
16-0065405 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2016-09-18 | 1543424 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0065807 | 3rd Party | Vehicle | Secondary | Burned/flashed | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2016-09-19 | 1544266 | Sus | Y | 3rdParty¦Vehicle¦Secondary¦Burnedflashed
16-0069405 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2016 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2016-10-03 | 1552286 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
16-0070901 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 10 | 2016-10-10 | 1555836 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0082418 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589707 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0085152 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2016-12-11 | 1599999 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
16-0085711 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 |  | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0085779 | Vegetation | Tree - fell into line | Secondary | Arcing | 2016 | Tier 3 - Extreme | Transformer only | 12 | 15 | 2016-12-15 | 1602946 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Arcing
16-0086116 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2016-12-16 | 1604342 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0002870 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2017-01-02 | 1615223 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0003278 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1616721 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0003450 | Environmental/External | Ice or snow | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1617771 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Insulator¦Broken
17-0004546 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1620816 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0005145 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624016 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
17-0007831 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 11 | 2017-01-11 | 1638184 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
17-0009364 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2017-01-16 | 1644336 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0009731 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 18 | 2017-01-18 | 1645668 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0009964 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1646286 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0009979 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1646317 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0010587 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1649303 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0010942 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648330 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0010998 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2017-01-19 | 1650912 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011458 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653773 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0013088 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660737 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0013331 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1661953 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
17-0013485 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1662238 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013821 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663391 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013869 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664315 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
17-0014444 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2017-01-24 | 1665775 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017768 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 6 | 2017-02-06 | 1676000 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0019598 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2017-02-09 | 1683831 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0021733 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Burned/flashed | 2017 | Tier 2 - Elevated | Transformer only | 2 | 16 | 2017-02-16 | 1690578 | Sus | N | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Burnedflashed
17-0023210 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2017-02-18 | 1699622 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0027447 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2017-02-28 | 1716291 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028956 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2017-03-07 | 1721492 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0037871 | Vegetation | Tree - fell into line | Crossarm, Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1750832 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Burnedflashed
17-0038092 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1751740 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0040897 | Vegetation | Tree - fell into line | Transformer | Broken | 2017 | Tier 2 - Elevated | Transformer only | 4 | 17 | 2017-04-17 | 1759559 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Broken
17-0042793 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2017-04-25 | 1766832 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0051300 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2017-05-29 | 1792649 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0060090 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 3 - Extreme | Transformer only | 7 | 2 | 2017-07-02 | 1822422 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0062429 | Environmental/External | Fire, Forest/Grass | Secondary | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2017-07-12 | 1830151 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Secondary¦Broken
17-0075903 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 4 | 2017-09-04 | 1870078 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0076791 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2017-09-07 | 1872725 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0078356 | Environmental/External | Lightning | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Transformer only | 9 | 12 | 2017-09-12 | 1876972 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken
17-0092519 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2017-11-03 | 1915228 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0101292 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2017-12-12 | 1941136 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0009964 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2018-01-29 | 16033 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0013139 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2018-02-10 | 22522 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0013241 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2018-02-11 | 22733 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
18-0013471 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2018-02-12 | 23346 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0017247 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2018-02-26 | 31510 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0017971 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2018-02-28 | 33200 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0018840 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2018-03-01 | 35222 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0019342 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2018-03-03 | 36997 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0019975 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2018-03-05 | 38621 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0023409 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2018-03-16 | 45549 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0025152 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2018-03-21 | 49639 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
18-0025259 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2018-03-22 | 50078 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0025259 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2018-03-22 | 50078 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0026913 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2018-03-27 | 54118 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0028971 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 3 | 2018-04-03 | 58962 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
18-0037415 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 5 | 1 | 2018-05-01 | 77776 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
18-0037448 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2018-05-01 | 77849 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0044614 | Animal | Bird found | Transformer | Burned/flashed | 2018 | Tier 2 - Elevated | Transformer only | 5 | 26 | 2018-05-26 | 94364 | Sus | Y | Animal¦Birdfound¦Transformer¦Burnedflashed
18-0061600 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Transformer only | 7 | 19 | 2018-07-19 | 135717 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0062044 | 3rd Party | Other | Conductor, Overhead | Bent or Twisted | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2018-07-20 | 136559 | Sus | Y | 3rdParty¦Other¦ConductorOverhead¦BentorTwisted
18-0072245 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2018-08-21 | 159815 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0082588 | Environmental/External | Fire, Forest/Grass | Regulator | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2018-09-23 | 179868 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Regulator¦Burnedflashed
18-0086365 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 10 | 3 | 2018-10-03 | 187375 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0086660 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2018-10-04 | 187974 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0087096 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2018-10-04 | 188587 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0088660 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2018-10-09 | 191824 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0090147 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2018-10-13 | 194602 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
18-0095402 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2018-10-29 | 204799 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
18-0098099 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Transmission line | 11 | 8 | 2018-11-08 | 211205 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0100887 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217952 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102349 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2018-11-22 | 222004 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0107747 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2018-12-06 | 235365 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0111305 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2018-12-31 | 250801 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0004384 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 1 | 4 | 2019-01-04 | 252932 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0005112 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255293 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0008129 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2019-01-11 | 263401 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017485 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 287105 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017714 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 289541 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
19-0017832 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289722 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018776 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292910 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0019126 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294209 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0019131 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294231 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020072 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2019-02-08 | 296091 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0022172 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 303957 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022191 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 2 | 13 | 2019-02-13 | 302966 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0022908 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 307636 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022964 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Transmission line | 2 | 14 | 2019-02-14 | 307883 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0023248 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 309175 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0023272 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 305723 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024310 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2019-02-15 | 313033 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024425 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2019-02-16 | 313527 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025016 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 315198 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025210 | Vegetation | Tree - fell into line | Cutout, fuse holder | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 17 | 2019-02-17 | 315597 | Sus | N | Vegetation¦Treefellintoline¦Cutoutfuseholder¦Broken
19-0025404 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 317066 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025881 | 3rd Party | Customer Equipment | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 19 | 2019-02-19 | 318432 | Sus | N | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Brokenwireonground
19-0028121 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324052 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028783 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 325896 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0029296 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 28 | 2019-02-28 | 327809 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0030032 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2019-03-02 | 329501 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030530 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2019-03-04 | 330891 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0032567 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2019-03-11 | 336100 | Sus | N | 3rdParty¦Vehicle¦AnchororGuy¦Broken
19-0035207 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2019-03-19 | 343262 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
19-0035435 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2019-03-20 | 343803 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0037667 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348683 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0037705 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 349073 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0037945 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2019-03-28 | 349463 | Sus | N | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
19-0039008 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2019-04-02 | 352137 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
19-0048971 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2019-05-07 | 375295 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
19-0049660 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2019-05-07 | 375942 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0050826 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 5 | 10 | 2019-05-10 | 378026 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
19-0054036 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 19 | 2019-05-19 | 385594 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0054861 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 21 | 2019-05-21 | 386878 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0058855 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2019-05-29 | 392245 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
19-0062629 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 6 | 4 | 2019-06-04 | 397488 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0074995 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 7 | 7 | 2019-07-07 | 442063 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
19-0079546 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 21 | 2019-07-21 | 464947 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0082054 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2019-07-29 | 474284 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0090305 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2019-08-21 | 526981 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0090961 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2019-08-22 | 531555 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0099151 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 2 - Elevated | Transformer only | 9 | 14 | 2019-09-14 | 582414 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0105166 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 29 | 2019-09-29 | 628942 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0108234 | Company Initiated | Construction Activity/equip, company | Jumper | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2019-10-07 | 646012 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Broken
19-0110751 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2019-10-11 | 654932 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
19-0116766 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2019-10-26 | 681284 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Brokenwireonground
19-0126614 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2019-11-20 | 710632 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
19-0130143 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 718165 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130265 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 720388 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130443 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 721039 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130819 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722549 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0136870 | Equipment Failure/Involved | Underground | Service conductor | Burned Open | 2019 | Tier 2 - Elevated | Transformer only | 12 | 16 | 2019-12-16 | 743825 | Sus | N | EquipmentFailureInvolved¦Underground¦Serviceconductor¦BurnedOpen
20-0007006 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2020-01-09 | 758133 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0010057 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 763086 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0019148 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782604 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0021174 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2020-02-12 | 789642 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0022948 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2020-02-17 | 792788 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0025395 | Animal | Bird found | Transformer (UG) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2020-02-24 | 804747 | Sus | N | Animal¦Birdfound¦Transformer(UG)¦FailedFaulted
20-0028906 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2020-03-05 | 831251 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0029742 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2020-03-07 | 837999 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033119 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 856114 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0033726 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 857772 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
20-0034547 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2020 | Tier 3 - Extreme | Transformer only | 3 | 15 | 2020-03-15 | 859433 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
20-0038949 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2020-04-06 | 885293 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0039129 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2020 | Tier 3 - Extreme | Transformer only | 4 | 6 | 2020-04-06 | 886570 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
20-0039888 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2020-04-08 | 892606 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0043281 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2020-04-21 | 898818 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0045697 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2020-04-29 | 903942 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
20-0046699 | Animal | Bird found | Conductor, Overhead | Annealed | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2020-05-03 | 906191 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Annealed
20-0049564 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2020-05-12 | 912193 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0051595 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2020-05-18 | 917236 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0060898 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 13 | 2020-06-13 | 938444 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0077773 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2020-07-30 | 975135 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0082843 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 12 | 2020-08-12 | 994619 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0085436 | Environmental/External | Lightning | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Transmission line | 8 | 17 | 2020-08-17 | 1014597 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Brokenwireonground
20-0088816 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2020-08-22 | 1026875 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090467 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033358 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091432 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1041105 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0093640 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2020-09-04 | 1055463 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0094401 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1059861 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0096037 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 20 | 2020-08-20 | 1063513 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Normal
20-0096817 | Animal | Bird found | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2020-09-12 | 1065533 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦FailedFaulted
20-0097375 | Environmental/External | Fire, Forest/Grass | Fuse | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2020-09-11 | 1070358 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal
20-0097487 | Equipment Failure/Involved | Overhead | Sectionalizer | Malfunctioning | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2020-09-14 | 1070609 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Sectionalizer¦Malfunctioning
20-0099446 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2020-09-21 | 1083734 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0100066 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1087013 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0101622 | Company Initiated | Construction Activity/equip, company | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2020-09-25 | 1092873 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Normal
20-0101622 | Company Initiated | Construction Activity/equip, company | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2020-09-25 | 1092873 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer(OH)¦Normal
20-0103155 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 29 | 2020-09-29 | 1100742 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0110473 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2020 | Tier 2 - Elevated | Transformer only | 10 | 19 | 2020-10-19 | 1120661 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
20-0112628 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2020-10-24 | 1124398 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0113907 | Vegetation | Tree - branch fell on line | Secondary | Together | 2020 | Tier 3 - Extreme | Transformer only | 10 | 26 | 2020-10-26 | 1129746 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Together
20-0121729 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2020-11-17 | 1146936 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0122139 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Transformer only | 11 | 17 | 2020-11-17 | 1147949 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
20-0129624 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 3 - Extreme | Transformer only | 12 | 11 | 2020-12-11 | 1178088 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0131445 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2020-12-22 | 1196954 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0132192 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2020-12-29 | 1200940 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0010010 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1213504 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
21-0012256 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2021 | Tier 3 - Extreme | Transformer only | 1 | 21 | 2021-01-21 | 1220052 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
21-0013261 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2021-01-22 | 1221773 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0015601 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232541 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0015753 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1230078 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0017914 | Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1240507 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground
21-0018683 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1240019 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
21-0022228 | 3rd Party | Other | Recloser | Normal | 2021 | Tier 3 - Extreme | Substation - Distribution | 2 | 5 | 2021-02-05 | 1248538 | Sus | N | 3rdParty¦Other¦Recloser¦Normal
21-0024259 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2021-02-10 | 1252655 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0028100 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2021-02-22 | 1259419 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0032811 | Animal | Squirrel | Bushing | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2021-03-05 | 1270288 | Sus | N | Animal¦Squirrel¦Bushing¦Burnedflashed
21-0039199 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 21 | 2021-03-21 | 1290906 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0041422 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2021-03-26 | 1299339 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
21-0041754 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2021-03-27 | 1300172 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0046233 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2021-04-08 | 1310336 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0047059 | Equipment Failure/Involved | Fire, pole | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2021-04-10 | 1312444 | Sus | N | EquipmentFailureInvolved¦Firepole¦Transformer(OH)¦FailedFaulted
21-0047809 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 4 | 13 | 2021-04-13 | 1314258 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0062807 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2021-05-18 | 1352433 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0064721 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2021-05-22 | 1356308 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0073933 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 6 | 14 | 2021-06-14 | 1372708 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0075328 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 6 | 17 | 2021-06-17 | 1375490 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
21-0083567 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 1 | 2021-07-01 | 1390271 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
21-0083997 | Animal | Squirrel | Cutout, fuse holder | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 2 | 2021-07-02 | 1390335 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
21-0104792 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2021-08-15 | 1443355 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0105466 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1444523 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0105865 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445863 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0113986 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2021-09-07 | 1463391 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0114630 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 9 | 8 | 2021-09-08 | 1464372 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0117132 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2021-09-14 | 1471300 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0117135 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 14 | 2021-09-14 | 1471274 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0119829 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transmission line | 9 | 20 | 2021-09-20 | 1476162 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0124898 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2021-10-01 | 1484934 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0127428 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 10 | 7 | 2021-10-07 | 1489796 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
21-0127728 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2021-10-08 | 1490324 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0128321 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1491994 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0130241 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 10 | 13 | 2021-10-13 | 1496487 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0133435 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2021-10-20 | 1502593 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0133874 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2021-10-20 | 1503250 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0134236 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) |  | 2021 | Tier 2 - Elevated | Transformer only | 10 | 21 | 2021-10-21 | 1504070 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦
21-0135812 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1507762 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0136039 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1510041 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136068 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508688 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
21-0136623 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513000 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0137820 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513238 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0140388 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 3 - Extreme | Transformer only | 10 | 31 | 2021-10-31 | 1526770 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0154351 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2021-12-02 | 1558141 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0156129 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2021-12-08 | 1562464 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
21-0157626 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568433 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0158408 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 15 | 2021-12-15 | 1572336 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
21-0159733 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 19 | 2021-12-19 | 1577298 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0160771 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 26 | 2021-12-26 | 1582422 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0161398 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582920 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0161430 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 12 | 28 | 2021-12-28 | 1587290 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken
21-0162019 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2021-12-31 | 1590739 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0005783 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2022-01-03 | 1594346 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005920 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 3 - Extreme | Transformer only | 1 | 4 | 2022-01-04 | 1594652 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0007721 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1598569 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0007778 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1598790 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0013064 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2022-01-22 | 1609446 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0018995 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 3 - Extreme | Transformer only | 2 | 4 | 2022-02-04 | 1621500 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0019004 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2022-02-05 | 1621794 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0025463 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2022-02-23 | 1634480 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0028425 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2022-03-01 | 1640132 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0030221 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2022-03-04 | 1642609 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
22-0037056 | Equipment Failure/Involved | Overhead | Other | Broken, wire on object | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2022-03-22 | 1653742 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Brokenwireonobject
22-0041996 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2022-04-02 | 1661577 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0045754 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669515 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0052217 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 20 | 2022-04-20 | 1677469 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0052309 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2022-04-21 | 1677902 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0053743 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 24 | 2022-04-24 | 1680176 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0056918 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2022-05-02 | 1686511 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0059604 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2022-05-09 | 1691639 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0060041 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2022-05-10 | 1692550 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0064004 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2022-05-19 | 1704473 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0076989 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2022-06-22 | 1738246 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0087298 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 19 | 2022-07-19 | 1760570 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0092293 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 1 | 2022-08-01 | 1770581 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0097209 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 13 | 2022-08-13 | 1780240 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0108126 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2022 | Tier 3 - Extreme | Transmission line | 9 | 9 | 2022-09-09 | 1807262 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
22-0114677 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2022-09-25 | 1821456 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0118843 | Equipment Failure/Involved | Overhead | Switch (OH) | Arcing | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2022-10-06 | 1830778 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Arcing
22-0123068 | 3rd Party | Fire, house or bldg. | Service conductor | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2022-10-19 | 1841011 | Sus | Y | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Brokenwireonground
22-0129125 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857401 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0136328 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2022-12-03 | 1875334 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139117 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2022-12-12 | 1886572 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139336 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2022-12-12 | 1887561 | Sus | N | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
22-0142315 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2022-12-30 | 1902635 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0002074 | Equipment Failure/Involved | Other | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2015-01-01 | 1157816 | Sus | N | EquipmentFailureInvolved¦Other¦CrossarmWood¦Broken
15-0002741 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 1 | 6 | 2015-01-06 | 1159899 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0008553 | Equipment Failure/Involved | Other | Transformer | Broken | 2015 | Tier 2 - Elevated | Transformer only | 2 | 1 | 2015-02-01 | 1170855 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Broken
15-0012310 | Equipment Failure/Involved | Lightning | Transformer | Broken | 2015 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2015-02-09 | 1186961 | Sus | N | EquipmentFailureInvolved¦Lightning¦Transformer¦Broken
15-0014060 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2015-02-18 | 1192172 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0018816 | Equipment Failure/Involved | Other | Cutout, fuse holder | Broken | 2015 | Tier 2 - Elevated | Transformer only | 3 | 11 | 2015-03-11 | 1202022 | Sus | N | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Broken
15-0020850 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2015-03-20 | 1205803 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0022042 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2015-03-25 | 1207949 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0025988 | Equipment Failure/Involved | Other | Transformer | Deteriorated | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2015-04-11 | 1217318 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Deteriorated
15-0033164 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 10 | 2015-05-10 | 1232318 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
15-0033671 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2015 | Tier 2 - Elevated | Transformer only | 5 | 12 | 2015-05-12 | 1233460 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
15-0037358 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 2 - Elevated | Transformer only | 5 | 29 | 2015-05-29 | 1241191 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0039865 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2015-06-09 | 1247926 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
15-0039901 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 9 | 2015-06-09 | 1248093 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0046151 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2015-07-07 | 1264516 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0048469 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2015-07-18 | 1270265 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0048766 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2015-07-18 | 1271319 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0054765 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2015-08-13 | 1287741 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0055005 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2015-08-14 | 1288157 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0056332 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2015-08-20 | 1292008 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0056598 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2015-08-21 | 1292532 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0076862 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2015-11-09 | 1338485 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0077943 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342125 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0081036 | Equipment Failure/Involved | Overhead | Insulator | Arcing | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 25 | 2015-11-25 | 1348473 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Arcing
15-0083739 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1356943 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground
15-0085955 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 12 | 17 | 2015-12-17 | 1365609 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
15-0087173 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2015-12-24 | 1370826 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0087976 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2015-12-31 | 1375433 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0002690 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2016-01-04 | 1376495 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
16-0003444 | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378454 | Sus | N | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted
16-0008046 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2016-01-25 | 1391756 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017840 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418253 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018466 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421854 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0018592 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1422689 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0019977 | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2016-03-10 | 1426498 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Burnedflashed
16-0020384 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427704 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0023441 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2016-03-23 | 1436753 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0025150 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2016-03-30 | 1441908 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0029487 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 4 | 18 | 2016-04-18 | 1453187 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
16-0031445 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2016-04-25 | 1458896 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0038538 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 5 | 25 | 2016-05-25 | 1476734 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
16-0043342 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2016-06-15 | 1489287 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0044173 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2016-06-17 | 1491650 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0058579 | Animal | Squirrel |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 8 | 19 | 2016-08-19 | 1529039 | Sus | Y | Animal¦Squirrel¦¦FailedFaulted
16-0067317 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Transformer only | 9 | 25 | 2016-09-25 | 1547274 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0069834 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2016-10-05 | 1553320 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0070336 | Animal | Squirrel | Cutout, fuse holder | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2016-10-07 | 1554472 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Broken
16-0072182 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1559625 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
16-0072640 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561852 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0072986 | Vegetation | Tree - fell into line | Service conductor | Broken | 2016 | Tier 3 - Extreme | Transformer only | 10 | 16 | 2016-10-16 | 1563389 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
16-0079533 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 11 | 13 | 2016-11-13 | 1580496 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0082438 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589848 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
17-0004799 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2017-01-07 | 1622202 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0005121 | Environmental/External | Ice or snow | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624937 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Together
17-0005572 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628478 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006347 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628522 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0007236 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1636753 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007396 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1635853 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007774 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638401 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
17-0008230 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1639207 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0008252 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640835 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0008472 | Vegetation | Tree - fell into line | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 11 | 2017-01-11 | 1639482 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Broken
17-0011446 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2017 | Tier 2 - Elevated | Transformer only | 1 | 20 | 2017-01-20 | 1653399 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
17-0012814 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1657905 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0013045 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660466 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0013385 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655680 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013755 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663756 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0015329 | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2017-01-26 | 1667872 | Sus | N | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Normal
17-0017667 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2017-02-06 | 1675846 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018070 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2017-02-06 | 1677203 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018428 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677812 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018743 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680508 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0019561 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683733 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0021729 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 2 | 16 | 2017-02-16 | 1690560 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0021742 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 16 | 2017-02-16 | 1690702 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0022204 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transmission line | 2 | 17 | 2017-02-17 | 1695236 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023757 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703044 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
17-0023781 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1702959 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0024011 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703807 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024109 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705156 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken
17-0027173 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2017-02-27 | 1715548 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028887 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1721019 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0033890 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2017-03-26 | 1736090 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038192 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1752105 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0039742 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2017 | Tier 2 - Elevated | Transformer only | 4 | 12 | 2017-04-12 | 1756513 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
17-0040038 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757179 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
17-0053690 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 8 | 2017-06-08 | 1799537 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0054105 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2017-06-09 | 1800688 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0056081 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2017-06-18 | 1807475 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0058218 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 23 | 2017-06-23 | 1816771 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0059307 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2017-06-28 | 1820066 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0062727 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 7 | 13 | 2017-07-13 | 1830801 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
17-0063108 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 15 | 2017-07-15 | 1832092 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0063298 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2017-07-16 | 1833198 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0064383 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2017-07-20 | 1836692 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0065145 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 24 | 2017-07-24 | 1839110 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground
17-0066463 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2017-07-29 | 1842145 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0069952 | 3rd Party | Vehicle | Secondary | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2017-08-13 | 1851717 | Sus | Y | 3rdParty¦Vehicle¦Secondary¦Burnedflashed
17-0070746 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2017-08-16 | 1853548 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0080702 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2017-09-21 | 1883311 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonobject
17-0080785 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2017-09-21 | 1883489 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0081230 | Animal | Squirrel | Fuse | Burned Open | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 23 | 2017-09-23 | 1884725 | Sus | Y | Animal¦Squirrel¦Fuse¦BurnedOpen
17-0082872 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 9 | 29 | 2017-09-29 | 1888133 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
17-0084179 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2017-10-04 | 1890861 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0085499 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Transformer only | 10 | 9 | 2017-10-09 | 1895945 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0085658 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1896601 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0086666 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1896669 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0086766 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 12 | 2017-10-12 | 1899326 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0093729 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2017-11-09 | 1918935 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0100919 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 9 | 2017-12-09 | 1939405 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0101018 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2017-12-10 | 1940026 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0004044 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2018-01-06 | 3235 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0006863 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2018-01-17 | 9956 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0015246 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Transformer only | 2 | 18 | 2018-02-18 | 26766 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0020806 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 3 | 7 | 2018-03-07 | 40139 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0022676 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 43988 | Sus | N | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
18-0026905 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2018-03-27 | 54117 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0028349 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2018-04-02 | 57638 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0032180 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2018-04-13 | 66340 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0036484 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 28 | 2018-04-28 | 75933 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0042450 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 18 | 2018-05-18 | 89431 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
18-0046677 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 2 | 2018-06-02 | 99667 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0049297 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Transformer only | 6 | 9 | 2018-06-09 | 105324 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
18-0049492 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2018-06-11 | 106020 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
18-0059918 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 15 | 2018-07-15 | 132059 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0071001 | Equipment Failure/Involved | Electrical Overload | Transformer | Leaking | 2018 | Tier 3 - Extreme | Transformer only | 8 | 17 | 2018-08-17 | 156971 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Leaking
18-0078442 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2018-09-11 | 172124 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
18-0079446 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2018-09-13 | 173746 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0087678 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2018-10-06 | 189810 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0088923 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 10 | 2018-10-10 | 192186 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0090051 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2018-10-13 | 194240 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0096263 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | 2018 | Tier 3 - Extreme | Transformer only | 11 | 1 | 2018-11-01 | 206916 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦¦
18-0100802 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217811 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0100886 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217951 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101233 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218582 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102305 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 11 | 22 | 2018-11-22 | 221916 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
18-0102326 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2018-11-21 | 220371 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0103778 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 225545 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0106563 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2018-12-03 | 232805 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
18-0109213 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2018-12-14 | 240240 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0109970 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 19 | 2018-12-19 | 243681 | Sus | N | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0111055 | Equipment Failure/Involved | Overhead | Other | Broken | 2018 | Tier 2 - Elevated | Transformer only | 12 | 29 | 2018-12-29 | 249342 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
19-0005408 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 257734 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0005996 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2019-01-07 | 259685 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0007374 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2019-01-10 | 262237 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0010007 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 268571 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010356 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 271351 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0010480 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 272234 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0014189 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2019-01-24 | 280637 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing
19-0018760 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 293696 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0020802 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2019-02-10 | 299218 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0021064 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2019-02-11 | 299759 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0021687 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2019-02-12 | 301620 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0022122 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303948 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0023477 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 310109 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024175 | Vegetation | Tree - bark fell into line | Service conductor | Normal | 2019 | Tier 2 - Elevated | Transformer only | 2 | 15 | 2019-02-15 | 311909 | Sus | N | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Normal
19-0024196 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 312643 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
19-0025284 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 316532 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0026298 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 19 | 2019-02-19 | 319105 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0026617 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2019-02-20 | 320057 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0028522 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 325090 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028945 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 325509 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0028962 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 325930 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0029004 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326234 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0030373 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2019-03-04 | 330422 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0031021 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2019-03-05 | 331991 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0037074 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2019-03-26 | 347775 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0038566 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2019-03-31 | 351095 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0039118 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2019-04-02 | 352411 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0040261 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2019-04-06 | 354735 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0040949 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2019-04-09 | 356681 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
19-0049607 | Company Initiated | Construction Activity/equip, company | Insulator | Burned/flashed | 2019 | Tier 3 - Extreme | Transmission line | 5 | 7 | 2019-05-07 | 375509 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Burnedflashed
19-0052651 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2019-05-16 | 382251 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0053638 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 18 | 2019-05-18 | 384193 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0053925 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2019-05-19 | 385162 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0058959 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 29 | 2019-05-29 | 392416 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0061788 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2019-06-03 | 396251 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
19-0065901 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2019-06-11 | 405002 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0067423 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2019 | Tier 2 - Elevated | Transformer only | 6 | 13 | 2019-06-13 | 409347 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
19-0079952 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2019-07-22 | 467956 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0080778 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 24 | 2019-07-24 | 470139 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0082726 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2019-07-30 | 475697 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0084466 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2019-08-05 | 485057 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0085086 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2019-08-07 | 487641 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
19-0099339 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2019-09-16 | 583594 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0103096 | Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2019-09-25 | 612805 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦CircuitBreaker¦Normal
19-0105699 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 30 | 2019-09-30 | 633444 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0124325 | Animal | Squirrel | Transformer (OH) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2019-11-13 | 706101 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Broken
19-0129519 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 715885 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0129715 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 716720 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130659 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 720532 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0134882 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 733179 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
19-0136633 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2019-12-15 | 740090 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0137109 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 18 | 2019-12-18 | 745454 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0137599 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2019-12-22 | 748260 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0137663 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 12 | 22 | 2019-12-22 | 748488 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
19-0137787 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 12 | 23 | 2019-12-23 | 749701 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0004285 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2020-01-02 | 753512 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0011665 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2020-01-21 | 767186 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0012047 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 1 | 21 | 2020-01-21 | 767554 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0019777 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782250 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0020011 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2020-02-09 | 783442 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0022674 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 2 | 16 | 2020-02-16 | 792101 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0024981 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2020-02-22 | 800864 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
20-0027557 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2020-03-01 | 821006 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
20-0030441 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2020-03-10 | 842123 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0030949 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 11 | 2020-03-11 | 844164 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
20-0031743 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 13 | 2020-03-13 | 848656 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0031936 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2020-03-13 | 850173 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0032106 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2020-03-14 | 851323 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032308 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852311 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0032531 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 853808 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0033070 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 854043 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0033766 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2020 | Tier 2 - Elevated | Transformer only | 3 | 18 | 2020-03-18 | 857919 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
20-0037778 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 1 | 2020-04-01 | 877736 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0039228 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2020-04-07 | 887637 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
20-0041003 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2020-04-13 | 894627 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0042440 | 3rd Party | Other | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 17 | 2020-04-17 | 897148 | Sus | N | 3rdParty¦Other¦Fuse¦FailedFaulted
20-0043492 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 22 | 2020-04-22 | 899109 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0047862 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2020-05-06 | 908277 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0050827 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2020-05-16 | 914601 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
20-0055946 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2020-05-30 | 926118 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0067303 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 7 | 1 | 2020-07-01 | 955876 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0078745 | 3rd Party | Vehicle | Pole-Wood | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2020-08-01 | 976777 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
20-0078849 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2020-08-02 | 977083 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0083800 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 14 | 2020-08-14 | 999438 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
20-0083950 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2020-08-14 | 999214 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0086878 | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2020-08-18 | 1015566 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground
20-0088478 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2020-08-21 | 1026173 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground
20-0088802 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2020 | Tier 2 - Elevated | Transformer only | 8 | 21 | 2020-08-21 | 1026799 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
20-0094519 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1058687 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
20-0097180 | Environmental/External | Fire, Forest/Grass | Secondary | Burned/flashed | 2020 | Tier 3 - Extreme | Transformer only | 8 | 19 | 2020-08-19 | 1068980 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Secondary¦Burnedflashed
20-0099168 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 19 | 2020-09-19 | 1082092 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0099976 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2020-09-22 | 1086635 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
20-0103309 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 30 | 2020-09-30 | 1101256 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0103812 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 1 | 2020-10-01 | 1103281 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
20-0104946 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 10 | 4 | 2020-10-04 | 1110813 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0105141 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2020-10-05 | 1111148 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0109889 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2020-10-16 | 1119533 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0110089 | 3rd Party | Vehicle | Lightning Arrestor | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 18 | 2020-10-18 | 1120260 | Sus | Y | 3rdParty¦Vehicle¦LightningArrestor¦FailedFaulted
20-0117632 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2020-11-06 | 1137096 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0117703 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2020-11-06 | 1137142 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0128178 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2020-12-05 | 1165959 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0128270 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2020-12-06 | 1166394 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0128399 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167291 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0130985 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2020-12-17 | 1193008 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
20-0131782 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2020-12-25 | 1198505 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
21-0010556 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214838 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0013581 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223084 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013917 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223911 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0013993 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223115 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0014796 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226631 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0024382 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Transformer only | 2 | 11 | 2021-02-11 | 1252816 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0025239 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2021-02-13 | 1254145 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0029306 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261693 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0030979 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2021-03-01 | 1265091 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0033107 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2021-03-06 | 1272611 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0040941 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2021-03-25 | 1297449 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0041747 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2021-03-27 | 1300148 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0045359 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 4 | 6 | 2021-04-06 | 1308036 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0046098 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2021-04-08 | 1310290 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0053550 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2021-04-26 | 1334896 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0058201 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2021-05-07 | 1342937 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0063971 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 20 | 2021-05-20 | 1354683 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0064475 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 5 | 21 | 2021-05-21 | 1355594 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0067711 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 5 | 29 | 2021-05-29 | 1361095 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0094178 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 23 | 2021-07-23 | 1412485 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0094178 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 23 | 2021-07-23 | 1412485 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0094362 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 24 | 2021-07-24 | 1412895 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
21-0097310 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 2 - Elevated | Transformer only | 7 | 30 | 2021-07-30 | 1421586 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0106575 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2021-08-18 | 1446905 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0110762 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 8 | 29 | 2021-08-29 | 1457486 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0117599 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2021-09-14 | 1471977 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed
21-0119421 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2021-09-18 | 1474864 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0119805 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2021-09-20 | 1475973 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0124613 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2021-09-30 | 1484493 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0125166 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2021 | Tier 2 - Elevated | Transformer only | 10 | 2 | 2021-10-02 | 1485455 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
21-0134885 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2021-10-22 | 1505384 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0135525 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 10 | 23 | 2021-10-23 | 1506956 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0136185 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511435 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136345 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512950 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0136459 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1510355 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0136929 | 3rd Party | Other | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1517291 | Sus | Y | 3rdParty¦Other¦ConductorOverhead¦Normal
21-0138138 | Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2021-10-26 | 1521563 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed
21-0142157 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 4 | 2021-11-04 | 1534402 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0142264 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2021-11-04 | 1534413 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0143638 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1538146 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0144021 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 11 | 9 | 2021-11-09 | 1538862 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0145185 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 12 | 2021-11-12 | 1542101 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
21-0146113 | Animal | Squirrel | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2021-11-16 | 1546416 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
21-0157966 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1570642 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0158045 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1571005 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158988 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1575228 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0160462 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2021-12-24 | 1580624 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161449 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584540 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0162047 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1590999 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0004974 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2021-12-31 | 1591175 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0005061 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1591692 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005678 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1593967 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005728 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2022 | Tier 3 - Extreme | Transformer only | 1 | 1 | 2022-01-01 | 1591860 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
22-0006599 | Environmental/External | Ice or snow | Pole-Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2022-01-04 | 1596026 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Brokenwireonground
22-0007752 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2022-01-09 | 1598673 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0019037 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2022-02-05 | 1621927 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0019702 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2022-02-08 | 1623026 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0036116 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 3 | 20 | 2022-03-20 | 1652011 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0039249 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2022-03-27 | 1657226 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0043102 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2022-04-05 | 1663596 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0044602 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2022-04-08 | 1666050 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Normal
22-0045908 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669896 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0050539 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 16 | 2022-04-16 | 1674211 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0050640 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 16 | 2022-04-16 | 1674654 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0051475 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2022-04-19 | 1676477 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0052458 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 4 | 21 | 2022-04-21 | 1678078 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0070254 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 6 | 4 | 2022-06-04 | 1719169 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0075309 | Company Initiated | Contact with High Voltage, company | Transformer | Broken | 2022 | Tier 3 - Extreme | Transformer only | 6 | 16 | 2022-06-16 | 1733346 | Sus | Y | CompanyInitiated¦ContactwithHighVoltagecompany¦Transformer¦Broken
22-0078699 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 26 | 2022-06-26 | 1742458 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083486 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2022-07-09 | 1751993 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083502 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2022-07-09 | 1752084 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083607 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2022-07-09 | 1752359 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0097886 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2022-08-16 | 1781917 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0109243 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2022-09-12 | 1809030 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0114557 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 24 | 2022-09-24 | 1820951 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
22-0126019 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2022-10-30 | 1848762 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0126717 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 11 | 1 | 2022-11-01 | 1850440 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
22-0127467 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2022-11-03 | 1852639 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
22-0127645 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2022-11-03 | 1852923 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0128550 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2022-11-07 | 1855936 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0129015 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857253 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
22-0129332 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2022-11-08 | 1858155 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0129519 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2022-11-08 | 1859011 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0133649 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2022-11-22 | 1868032 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0137260 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2022-12-07 | 1877785 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0137784 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2022-12-08 | 1879282 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0138408 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882470 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0139060 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1886182 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
22-0139167 | Environmental/External | Water | Transformer | Broken | 2022 | Tier 3 - Extreme | Transformer only | 12 | 12 | 2022-12-12 | 1886847 | Sus | N | EnvironmentalExternal¦Water¦Transformer¦Broken
22-0141728 | Vegetation | Tree - bark fell into line | Service conductor | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 12 | 27 | 2022-12-27 | 1899258 | Sus | N | Vegetation¦Treebarkfellintoline¦Serviceconductor¦Brokenwireonground
22-0142642 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1904370 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0005459 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2015-01-17 | 1165326 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0012148 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1185773 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0024877 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2015-04-07 | 1214914 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
15-0027022 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Transformer only | 4 | 15 | 2015-04-15 | 1220154 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0034613 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2015-05-16 | 1235500 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0038897 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2015-06-05 | 1244345 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0040945 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2015-06-14 | 1250819 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0048878 | Environmental/External | Lightning | Transformer (OH) | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1272451 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Deteriorated
15-0053518 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2015-08-07 | 1284237 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
15-0053641 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 8 | 7 | 2015-08-07 | 1284583 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0056262 | Animal | Bird found | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2015-08-20 | 1291877 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
15-0059258 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2015-09-04 | 1299953 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
15-0061023 | Vegetation | Tree - bark fell into line | Secondary | On Ground | 2015 | Tier 3 - Extreme | Transformer only | 9 | 12 | 2015-09-12 | 1304620 | Sus | Y | Vegetation¦Treebarkfellintoline¦Secondary¦OnGround
15-0062397 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2015-09-20 | 1309014 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062718 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 22 | 2015-09-22 | 1309952 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0067739 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2015-10-03 | 1316356 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0074050 | Equipment Failure/Involved | Overhead | Transformer | Arcing | 2015 | Tier 2 - Elevated | Transformer only | 10 | 29 | 2015-10-29 | 1331075 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Arcing
15-0075302 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 11 | 3 | 2015-11-03 | 1334577 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0075388 | Environmental/External | Lightning |  | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 11 | 3 | 2015-11-03 | 1334847 | Sus | Y | EnvironmentalExternal¦Lightning¦¦FailedFaulted
15-0077863 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1341539 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0077917 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 2 - Elevated | Transformer only | 11 | 15 | 2015-11-15 | 1341747 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0080537 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 24 | 2015-11-24 | 1347824 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0082621 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2015-12-03 | 1353130 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
15-0082886 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 4 | 2015-12-04 | 1354023 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
15-0083833 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357002 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084217 | Environmental/External | Lightning | Transformer (OH) | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2015-12-11 | 1358491 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal
15-0084873 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361981 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
15-0085359 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2015-12-14 | 1363685 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0086157 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 19 | 2015-12-19 | 1366441 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0087645 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2015-12-28 | 1373174 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0003330 | Equipment Failure/Involved | Overhead | Secondary | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378245 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Together
16-0005875 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Transformer only | 1 | 17 | 2016-01-17 | 1385341 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0005878 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken, wire on object | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385401 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Brokenwireonobject
16-0007326 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2016-01-22 | 1389699 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0007529 | Equipment Failure/Involved | Overhead | Fuse | Arcing | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2016-01-22 | 1390147 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Arcing
16-0014054 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2016-02-19 | 1409029 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017972 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418650 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018045 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417174 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
16-0018111 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1420859 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0018468 | Unknown Cause | Patrol - not conducted | Transformer | Malfunctioning | 2016 | Tier 2 - Elevated | Transformer only | 3 | 6 | 2016-03-06 | 1421986 | Sus | N | UnknownCause¦Patrolnotconducted¦Transformer¦Malfunctioning
16-0020187 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427009 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0023897 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2016-03-24 | 1438204 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0024358 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2016-03-28 | 1439720 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0031102 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457666 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0031102 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457666 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0036252 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2016-05-16 | 1470298 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0042935 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2016-06-13 | 1488193 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0043476 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2016-06-15 | 1489479 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0047227 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 6 | 30 | 2016-06-30 | 1499119 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
16-0051942 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 22 | 2016-07-22 | 1514517 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0052645 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2016-07-26 | 1516269 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0059795 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2016-08-24 | 1531601 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0060715 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2016-08-29 | 1533673 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0065949 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 20 | 2016-09-20 | 1544661 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
16-0067641 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 26 | 2016-09-26 | 1548073 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0069960 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2016-10-05 | 1553596 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0071927 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1558460 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0072764 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562195 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0074078 | 3rd Party | Vehicle | Conductor, Overhead | Bent or Twisted | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2016-10-19 | 1566117 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦BentorTwisted
16-0075797 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2016-10-27 | 1570541 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing
16-0078290 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2016-11-06 | 1577316 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0079442 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 12 | 2016-11-12 | 1580113 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0084798 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 9 | 2016-12-09 | 1597835 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
16-0085010 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2016-12-10 | 1599122 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0085681 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602465 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0086770 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2016-12-23 | 1609457 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
16-0086895 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2016-12-24 | 1610181 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground
17-0002803 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Transformer only | 1 | 2 | 2017-01-02 | 1614836 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0003927 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2017-01-05 | 1619230 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005922 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628980 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006268 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1631848 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0006778 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634078 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006882 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1633397 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007187 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634610 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007580 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637575 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0007896 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639005 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0008851 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2017-01-13 | 1642833 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0010478 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648917 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0010597 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Transmission line | 1 | 19 | 2017-01-19 | 1649722 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0012600 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658095 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013243 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1661429 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013702 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1662164 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
17-0014732 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2017-01-25 | 1666774 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0015666 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 27 | 2017-01-27 | 1668733 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
17-0016347 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 31 | 2017-01-31 | 1671257 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0022767 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698618 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0024044 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705093 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0025015 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1707263 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0026497 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2017-02-24 | 1713007 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028430 | Animal | Bird found | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2017-03-05 | 1719794 | Sus | N | Animal¦Birdfound¦PoleWood¦Broken
17-0028513 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2017-03-05 | 1720233 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0029888 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2017-03-10 | 1723747 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0032491 | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2017-03-21 | 1732296 | Sus | N | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted
17-0032991 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2017 | Tier 2 - Elevated | Transformer only | 3 | 22 | 2017-03-22 | 1733444 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
17-0033649 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 3 | 24 | 2017-03-24 | 1735058 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0033916 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2017-03-26 | 1736084 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038219 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 8 | 2017-04-08 | 1752306 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0038901 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 10 | 2017-04-10 | 1754135 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0040921 | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 17 | 2017-04-17 | 1759781 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground
17-0045764 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 6 | 2017-05-06 | 1776053 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0049911 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2017-05-23 | 1788553 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0057441 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 21 | 2017-06-21 | 1814149 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0066507 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 7 | 29 | 2017-07-29 | 1842396 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0072573 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2017-08-24 | 1858429 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
17-0080409 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2017-09-21 |  | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0083595 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2017-10-03 | 1889762 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0086697 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899218 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Broken
17-0087348 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2017-10-14 | 1900683 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0087924 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2017-10-17 | 1902420 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
17-0089164 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 10 | 20 | 2017-10-20 | 1906003 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0090554 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2017-10-26 | 1910069 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0091066 | Animal | Squirrel | Transformer (OH) | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 28 | 2017-10-28 | 1911650 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
17-0092419 | Equipment Failure/Involved | Overhead | Recloser | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2017-11-03 | 1915118 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Normal
17-0095295 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2017-11-15 | 1923144 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0099364 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2017-12-03 | 1934295 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0103326 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 12 | 26 | 2017-12-26 | 1951373 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0005678 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2018-01-12 | 7221 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0015413 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2018-02-19 | 27108 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
18-0016852 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2018-02-23 | 30447 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
18-0018424 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 34735 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0020773 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2018-03-07 | 40035 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0022751 | Animal | Other | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 43759 | Sus | N | Animal¦Other¦Transformer(OH)¦Normal
18-0023746 | Vegetation | Tree - fell into line | Secondary | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2018-03-17 | 46456 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Broken
18-0024209 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2018-03-20 | 48290 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
18-0025506 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 50622 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0026060 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2018-03-23 | 51970 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0036366 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2018 | Tier 3 - Extreme | Transformer only | 4 | 27 | 2018-04-27 | 75550 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
18-0038559 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2018-05-05 | 80028 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0044947 | Vegetation | Tree - fell into line | Secondary | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2018-05-28 | 95447 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Normal
18-0046518 | 3rd Party | Vehicle | Cutout, fuse holder | Broken | 2018 | Tier 2 - Elevated | Transformer only | 6 | 1 | 2018-06-01 | 99118 | Sus | Y | 3rdParty¦Vehicle¦Cutoutfuseholder¦Broken
18-0051671 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2018-06-16 | 111030 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0052878 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 6 | 20 | 2018-06-20 | 113785 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
18-0056061 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2018-07-01 | 122186 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0057823 | Animal | Bird found | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2018-07-09 | 126725 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
18-0079281 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2018-09-13 | 173431 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0084040 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 9 | 27 | 2018-09-27 | 182298 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0090330 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2018-10-14 | 195705 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
18-0094712 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 27 | 2018-10-27 | 203220 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0098052 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 210930 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0098440 | Environmental/External | Fire, Forest/Grass | Pole-Wood | On Ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 211957 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦OnGround
18-0099318 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2018-11-13 | 214305 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0099356 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 214435 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal
18-0100952 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2018-11-19 | 218070 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0101149 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218433 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101446 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219046 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101783 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2018-11-21 | 219710 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0102028 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2018-11-21 | 220566 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0103354 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2018-11-26 | 224873 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0105802 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2018-12-01 | 230724 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0106601 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2018-12-03 | 232925 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109575 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2018-12-17 | 241775 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0110581 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2018-12-24 | 246551 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0003618 | Equipment Failure/Involved | Overhead | Other | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 2 | 2019-01-02 | 251909 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
19-0003882 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2019-01-02 | 252223 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0005441 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 257501 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0010041 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 268214 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010118 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transmission line | 1 | 16 | 2019-01-16 | 269818 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010311 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 271283 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010809 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 270490 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0010847 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 268899 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0017079 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 287163 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0017178 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287507 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0018259 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 291658 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0018302 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 291874 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019351 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292632 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0020408 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2019-02-09 | 297376 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020675 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298816 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0021959 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 13 | 2019-02-13 | 302227 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0022011 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301161 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0024348 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 15 | 2019-02-15 | 312785 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0024762 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314381 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025569 | Equipment Failure/Involved | Overhead | Service conductor | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 317385 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken
19-0026182 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 315939 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0028705 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326008 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028721 | Vegetation | Tree - fell into line | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325815 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦FailedFaulted
19-0029445 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 328167 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0031256 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 332655 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0035867 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2019-03-21 | 344889 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0035889 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2019-03-21 | 344822 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0037574 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2019-03-27 | 348697 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0038407 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 29 | 2019-03-29 | 350439 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0046198 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2019-04-25 | 368152 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0048292 | Environmental/External | Ice or snow | Service conductor | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2019-05-02 | 372439 | Sus | Y | EnvironmentalExternal¦Iceorsnow¦Serviceconductor¦Brokenwireonground
19-0048761 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2019-05-03 | 373349 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0048845 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 5 | 4 | 2019-05-04 | 373572 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0049722 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2019-05-07 | 375724 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0050326 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2019-05-09 | 376987 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0051802 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 14 | 2019-05-14 | 380358 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
19-0052552 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2019-05-16 | 381764 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0053836 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2019-05-19 | 384725 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0054364 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2019-05-20 | 385877 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0057546 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 25 | 2019-05-25 | 389891 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0059369 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2019-05-29 | 393085 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0071334 | Animal | Bird found | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2019-06-23 | 427180 | Sus | Y | Animal¦Birdfound¦LightningArrestor¦FailedFaulted
19-0071655 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2019-06-24 | 428025 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0072290 | Vegetation | Tree - cutting, PG&E contractor | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 26 | 2019-06-26 | 429784 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦CrossarmWood¦Brokenwireonground
19-0080268 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 23 | 2019-07-23 | 469036 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
19-0082206 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2019-07-29 | 474308 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0082571 | Company Initiated | Personnel, company | Conductor, Underground | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2019-08-07 | 489996 | Sus | Y | CompanyInitiated¦Personnelcompany¦ConductorUnderground¦Burnedflashed
19-0084780 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2019-08-06 | 487194 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0092754 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2019-08-27 | 542960 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0096478 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2019-09-07 | 562199 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0107405 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2019-10-04 | 642248 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0109345 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2019-10-09 | 648323 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0110748 | 3rd Party | Fire, house or bldg. | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2019-10-11 | 654902 | Sus | Y | 3rdParty¦Firehouseorbldg¦ConductorOverhead¦Normal
19-0110802 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Transformer only | 10 | 12 | 2019-10-12 | 655113 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0112116 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2019-10-15 | 659994 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0114715 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2019-10-23 | 677776 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
19-0114948 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2019-10-23 | 677835 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0123743 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 12 | 2019-11-12 | 704689 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0126453 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2019-11-19 | 710346 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0127692 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2019-11-22 | 712859 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0129766 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 719339 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0129999 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 719619 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130177 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 720759 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0130186 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 719177 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0130299 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 718293 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131024 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722795 | Sus | Y | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
19-0131499 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 30 | 2019-11-30 | 724446 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0134977 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 732878 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0136079 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2019-12-12 | 737080 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
20-0005325 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2020-01-06 | 755207 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0007596 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2020-01-10 | 759133 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0017247 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2020-02-04 | 777794 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0018880 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2020-02-08 | 780845 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
20-0019000 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 781294 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0019472 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 784029 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0019624 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 783965 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0021953 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2020 | Tier 3 - Extreme | Transformer only | 2 | 13 | 2020-02-13 | 790510 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
20-0027532 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2020-03-01 | 820897 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0032511 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853382 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0033288 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2020-03-17 | 856272 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033408 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 853688 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0033869 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2020-03-18 | 858216 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0034825 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2020-03-20 | 859617 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0035116 | Animal | Bird found | Fuse | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2020-03-22 | 861541 | Sus | N | Animal¦Birdfound¦Fuse¦Normal
20-0036842 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2020-03-27 | 868833 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0038644 | Vegetation | Tree - fell into line | Anchor or Guy | Broken, wire on ground | 2020 | Tier 2 - Elevated | Transformer only | 4 | 5 | 2020-04-05 | 883280 | Sus | N | Vegetation¦Treefellintoline¦AnchororGuy¦Brokenwireonground
20-0038686 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2020-04-05 | 883371 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0041817 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Transformer only | 4 | 15 | 2020-04-15 | 896165 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0045729 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2020-04-29 | 903991 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0049273 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 12 | 2020-05-12 | 911735 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
20-0053861 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 25 | 2020-05-25 | 921076 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0059868 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2020-06-10 | 936254 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0060395 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 11 | 2020-06-11 | 937181 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
20-0063011 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2020-06-19 | 942513 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0065779 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2020-06-28 | 949198 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0074904 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2020-07-22 | 970210 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
20-0085160 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1013115 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0086913 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2020-08-18 | 1020178 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
20-0088117 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2020-08-20 | 1025709 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0088181 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1025752 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0089339 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 24 | 2020-08-24 | 1028177 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0093842 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2020-09-06 | 1056804 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0095348 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2020-09-09 | 1061739 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0097503 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 15 | 2020-09-15 | 1070692 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
20-0098856 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Normal | 2020 | Tier 3 - Extreme | Transformer only | 9 | 18 | 2020-09-18 | 1079937 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Normal
20-0099902 | Animal | Squirrel | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2020-09-21 | 1086224 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
20-0102367 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2020-09-28 | 1096258 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0104652 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 10 | 2 | 2020-10-02 | 1107359 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
20-0110527 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 10 | 19 | 2020-10-19 | 1121160 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0110974 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 10 | 20 | 2020-10-20 | 1121905 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0112855 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1126101 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0113033 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1127276 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0114073 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2020-10-25 | 1130381 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Fuse¦Normal
20-0119635 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 11 | 2020-11-11 | 1141725 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0128417 | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 2020 | Tier 2 - Elevated | Transformer only | 12 | 7 | 2020-12-07 | 1167337 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground
20-0131814 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2020-12-25 | 1198761 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0005170 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2021-01-05 | 1204624 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0010244 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1215047 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011014 | Vegetation | Tree - fell into line | Other | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216708 | Sus | N | Vegetation¦Treefellintoline¦Other¦Broken
21-0013869 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223441 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0014163 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224778 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0014959 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226679 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0015642 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232478 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0016219 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1227593 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0016378 | Equipment Failure/Involved | Overhead | Other | Malfunctioning | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1235867 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Malfunctioning
21-0016834 | Vegetation | Tree - fell into line | Secondary | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237096 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Broken
21-0017434 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2021-01-28 | 1239473 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0019989 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1243875 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020775 | Animal | Squirrel | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2021-02-02 | 1245718 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
21-0021719 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2021-02-04 | 1247773 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0030542 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2021-03-01 | 1264372 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0034664 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 3 - Extreme | Transformer only | 3 | 10 | 2021-03-10 | 1276772 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0035731 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2021-03-12 | 1280070 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0035949 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2021-03-12 | 1280382 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0036191 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2021-03-14 | 1281742 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0049243 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2021-04-15 | 1318557 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing
21-0050597 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 19 | 2021-04-19 | 1324239 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0050754 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 20 | 2021-04-20 | 1324742 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0057033 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 5 | 2021-05-05 | 1341167 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0058980 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2021-05-09 | 1344312 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0059044 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2021-05-10 | 1344598 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0060025 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2021-05-11 | 1346323 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0060129 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 12 | 2021-05-12 | 1346778 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
21-0064725 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 22 | 2021-05-22 | 1356350 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0065662 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2021-05-25 | 1358146 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0070282 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2021-06-04 | 1365533 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0070355 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2021-06-04 | 1366040 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0080914 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2021-06-28 | 1387096 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0086251 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2021-07-08 | 1394427 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
21-0095233 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2021-07-26 | 1415308 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0100957 | Equipment Failure/Involved | Overhead | Secondary | Together | 2021 | Tier 2 - Elevated | Transformer only | 8 | 6 | 2021-08-06 | 1435643 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Together
21-0110510 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2021-08-28 | 1456119 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0113910 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 6 | 2021-09-06 | 1463165 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0114905 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 8 | 2021-09-08 | 1464889 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
21-0115022 | 3rd Party | Fire, house or bldg. | Service conductor | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2021-09-09 | 1465187 | Sus | Y | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Burnedflashed
21-0126018 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 5 | 2021-10-05 | 1487218 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0131200 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2021-10-14 | 1497703 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0131327 | 3rd Party | Customer Equipment | Fuse | Burned Open | 2021 | Tier 3 - Extreme | Transformer only | 10 | 14 | 2021-10-14 | 1497843 | Sus | Y | 3rdParty¦CustomerEquipment¦Fuse¦BurnedOpen
21-0131981 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499188 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0131982 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499251 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Normal
21-0136750 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1516052 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0137604 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512255 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0137843 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2021-10-26 | 1520734 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
21-0160391 | Vegetation | Tree - fell into line | Service conductor | On Ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2021-12-24 | 1580420 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦OnGround
21-0161074 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584410 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161467 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1587657 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0161779 | Vegetation | Tree - fell into line | Secondary | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2021-12-28 | 1589638 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Broken
22-0006453 | Vegetation | Tree - fell into line | Transformer (OH) | On Ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2022-01-05 | 1595816 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦OnGround
22-0006963 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2021-12-31 | 1590840 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
22-0007765 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2022-01-09 | 1598573 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0008602 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1600339 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0017150 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2022-02-01 | 1618292 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0047714 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2022-04-13 | 1671982 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
22-0050778 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 17 | 2022-04-17 | 1675328 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0058629 | Animal | Other | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Transformer only | 5 | 5 | 2022-05-05 | 1689192 | Sus | Y | Animal¦Other¦PoleWood¦Broken
22-0060918 | Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2022-05-11 | 1694108 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Brokenwireonground
22-0062642 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2022-05-16 | 1697586 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0073412 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2022-06-12 | 1729410 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0073808 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2022-06-13 | 1730386 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0076722 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2022-06-21 | 1737432 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0079242 | Equipment Failure/Involved | Overhead | Other | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 27 | 2022-06-27 | 1743654 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
22-0082795 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 7 | 7 | 2022-07-07 | 1750634 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0092815 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2022-08-02 | 1771389 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0098961 | Equipment Failure/Involved | Fire, pole | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2022-08-17 | 1783951 | Sus | Y | EquipmentFailureInvolved¦Firepole¦Transformer¦FailedFaulted
22-0102328 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2022-08-26 | 1792202 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0105486 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Transformer only | 9 | 3 | 2022-09-03 | 1798338 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0108646 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 9 | 9 | 2022-09-09 | 1807289 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0115033 | Animal | Squirrel | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 9 | 26 | 2022-09-26 | 1822118 | Sus | Y | Animal¦Squirrel¦Transformer¦FailedFaulted
22-0121388 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2022-10-14 | 1836984 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0123923 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2022-10-22 | 1842982 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0126137 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2022-10-31 | 1849125 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0128198 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Transformer only | 11 | 5 | 2022-11-05 | 1854465 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0129844 | Environmental/External | Ice or snow | Transformer | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2022-11-09 | 1859563 | Sus | Y | EnvironmentalExternal¦Iceorsnow¦Transformer¦FailedFaulted
22-0130355 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 11 | 2022-11-11 | 1860622 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0132687 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865683 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
22-0133893 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2022-11-23 | 1868475 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0136589 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2022-12-05 | 1876221 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0138095 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880401 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138343 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880253 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
22-0138458 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882703 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0138827 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1884616 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0138848 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885447 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0138849 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885452 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139011 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882741 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0141637 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899026 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0142053 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2022-12-29 | 1901216 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0142572 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903887 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
23-0004409 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903846 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0002127 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 2015 | Tier 3 - Extreme | Transformer only | 1 | 1 | 2015-01-01 | 1158118 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject
15-0003189 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Transformer only | 1 | 7 | 2015-01-07 | 1160783 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0007222 | Equipment Failure/Involved | Other | Jumper | Burned Open | 2015 | Tier 2 - Elevated | Transformer only | 1 | 26 | 2015-01-26 | 1168505 | Sus | N | EquipmentFailureInvolved¦Other¦Jumper¦BurnedOpen
15-0010355 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1175827 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0011326 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2015-02-07 | 1180221 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0012279 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1186942 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
15-0023124 | Animal | Bird found | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2015-03-31 | 1210495 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦OnGround
15-0026862 | 3rd Party | Vehicle | Other | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2015-04-15 | 1219685 | Sus | N | 3rdParty¦Vehicle¦Other¦Normal
15-0030564 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2015-04-29 | 1227052 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0032367 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230283 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
15-0032685 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2015-05-07 | 1231229 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
15-0038549 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2015-06-04 | 1243688 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0038988 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 6 | 2015-06-06 | 1244627 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0039621 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 9 | 2015-06-09 | 1247309 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
15-0040827 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2015 | Tier 2 - Elevated | Transformer only | 6 | 13 | 2015-06-13 | 1250268 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
15-0045841 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2015-07-06 | 1263796 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
15-0059419 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2015-09-04 | 1300223 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0061913 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 17 | 2015-09-17 | 1307532 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
15-0072459 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 10 | 21 | 2015-10-21 | 1327254 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0083317 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2015-12-08 | 1355420 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083954 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357614 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
15-0084208 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 12 | 10 | 2015-12-10 | 1358298 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0003965 | 3rd Party | Vehicle | Pole-Wood | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2016-01-08 | 1380061 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Normal
16-0005384 | Equipment Failure/Involved | Overhead | Other | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 14 | 2016-01-14 | 1383836 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦BurnedOpen
16-0006992 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2016-01-20 | 1388958 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0007707 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2016-01-23 | 1390547 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
16-0009455 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Burned/flashed | 2016 | Tier 3 - Extreme | Transformer only | 1 | 31 | 2016-01-31 | 1395017 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Burnedflashed
16-0010134 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2016-02-01 | 1397246 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0010400 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2016-02-03 | 1397926 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0013649 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2016-02-18 | 1407959 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0014662 | Equipment Failure/Involved | Overhead |  | Normal | 2016 | Tier 2 - Elevated | Transformer only | 2 | 22 | 2016-02-22 | 1410219 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦Normal
16-0016828 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 3 | 2 | 2016-03-02 | 1414829 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
16-0017988 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1419429 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0018091 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1420858 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0026096 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 4 | 2016-04-04 | 1444417 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0027439 | Animal | Other | Recloser | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2016-04-09 | 1447635 | Sus | N | Animal¦Other¦Recloser¦FailedFaulted
16-0035231 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 5 | 10 | 2016-05-10 | 1467538 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0039488 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2016 | Tier 2 - Elevated | Transformer only | 5 | 28 | 2016-05-28 | 1478392 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
16-0043671 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 16 | 2016-06-16 | 1489938 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0053793 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2016 | Tier 2 - Elevated | Transformer only | 7 | 30 | 2016-07-30 | 1518783 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
16-0054310 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2016-08-02 | 1520105 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0062256 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2016-09-03 | 1536369 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0062301 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2016-09-04 | 1536491 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0073747 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 18 | 2016-10-18 | 1565556 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0082405 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589626 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0083121 | Animal | Squirrel | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 30 | 2016-11-30 | 1591937 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
16-0084533 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2016-12-08 | 1596726 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0084895 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2016-12-10 | 1598212 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0084917 | Vegetation | Tree - fell into line | Pole-Wood | On Ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2016-12-10 | 1598265 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦OnGround
16-0085688 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602475 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0085783 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1603004 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0086113 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2016-12-16 | 1605187 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0087141 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2016-12-27 | 1611413 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0003077 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Transformer only | 1 | 3 | 2017-01-03 | 1615578 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
17-0005055 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623559 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007592 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634163 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
17-0008475 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2017-01-12 | 1641691 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0009418 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 16 | 2017-01-16 | 1644728 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0011421 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652965 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0013313 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 1 | 22 | 2017-01-22 | 1660289 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
17-0013829 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663345 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
17-0014121 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1665010 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0014622 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2017-01-24 | 1665670 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0015281 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2017-01-26 | 1667688 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0017436 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2017-02-04 | 1674665 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0018474 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679306 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
17-0018745 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680707 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0019753 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 2 | 9 | 2017-02-09 | 1683698 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
17-0019756 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 2 | 10 | 2017-02-10 | 1684494 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0021584 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2017-02-16 | 1690327 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0022137 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1694581 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0023587 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 19 | 2017-02-19 | 1702232 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0026980 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2017-02-27 | 1714824 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0028037 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2017-03-03 | 1718244 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0028612 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720615 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0032516 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2017-03-21 | 1732340 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0037344 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1746635 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0038298 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 4 | 8 | 2017-04-08 | 1752793 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0045726 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 5 | 2017-05-05 | 1775889 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0047799 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2017-05-14 | 1781720 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0052551 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2017-06-03 | 1796320 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0055900 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2017-06-17 | 1806555 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0057443 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 21 | 2017-06-21 | 1814241 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0062054 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2017-07-08 | 1829108 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0066423 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 7 | 29 | 2017-07-29 | 1842002 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0068093 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2017-08-04 | 1846612 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0077137 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2017-09-08 | 1873727 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0082941 | Environmental/External | Lightning | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 29 | 2017-09-29 | 1888113 | Sus | Y | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦Broken
17-0085263 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893816 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0087390 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2017-10-14 | 1900864 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0088842 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1905030 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0088842 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1905030 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0092601 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2017-11-04 | 1915693 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0094888 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 11 | 14 | 2017-11-14 | 1921995 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0096292 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2017-11-19 | 1925976 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0098919 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2017-12-01 | 1933295 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0100421 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2017-12-07 | 1937894 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0101709 | Equipment Failure/Involved | Electrical Overload | Transformer | Leaking | 2017 | Tier 3 - Extreme | Transformer only | 12 | 14 | 2017-12-14 | 1943303 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Leaking
17-0102573 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2017 | Tier 2 - Elevated | Transformer only | 12 | 19 | 2017-12-19 | 1947839 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
17-0102955 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 12 | 21 | 2017-12-21 | 1949727 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0103308 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2017-12-26 | 1951217 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0005436 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2018-01-11 | 6761 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0007226 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2018-01-19 | 10584 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0016115 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2018-02-21 | 28953 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0016568 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2018-02-22 | 29711 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0017579 | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2018-02-26 | 32445 | Sus | N | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted
18-0019440 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2018-03-02 | 36973 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0021112 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 8 | 2018-03-08 | 40619 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
18-0023120 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2018-03-15 | 44829 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
18-0028022 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2018-03-30 | 56648 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0029863 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2018-04-06 | 60796 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Broken
18-0030158 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 4 | 6 | 2018-04-06 | 61104 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0033741 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2018-04-19 | 70113 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
18-0034165 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 20 | 2018-04-20 | 70809 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0038537 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2018-05-05 | 79963 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0045881 | Equipment Failure/Involved | Overhead | Secondary | On Ground | 2018 | Tier 3 - Extreme | Transformer only | 5 | 30 | 2018-05-30 | 97605 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦OnGround
18-0045888 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 30 | 2018-05-30 | 97636 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0047077 | 3rd Party | Fire, house or bldg. | Conductor, Underground | Normal | 2018 | Tier 2 - Elevated | Transformer only | 6 | 4 | 2018-06-04 | 100886 | Sus | Y | 3rdParty¦Firehouseorbldg¦ConductorUnderground¦Normal
18-0048215 | Animal | Squirrel | Cutout, fuse holder | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 7 | 2018-06-07 | 103365 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
18-0051260 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 14 | 2018-06-14 | 109620 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0051722 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2018-06-17 | 111288 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0054013 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 6 | 24 | 2018-06-24 | 116901 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0057701 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2018-07-07 | 126246 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0061095 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 18 | 2018-07-18 | 134846 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
18-0062658 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Transformer only | 7 | 23 | 2018-07-23 | 138110 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0069937 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2018-08-14 | 155521 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0072822 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2018-08-23 | 160944 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
18-0075179 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2018-08-30 | 165631 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
18-0084334 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2018-09-27 | 182943 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0086433 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2018-10-03 | 187695 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0086729 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2018-10-04 | 188135 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0093179 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2018-10-23 | 200668 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
18-0099168 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 213863 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101260 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 218633 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101484 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219127 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0110034 | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 19 | 2018-12-19 | 244067 | Sus | N | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonground
18-0110660 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2018-12-25 | 247143 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0110924 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2018-12-27 | 248524 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0111185 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2018-12-31 | 250105 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0005793 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Transformer only | 1 | 7 | 2019-01-07 | 258824 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009938 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 268225 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010428 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 269199 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0012796 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2019-01-20 | 277644 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0017577 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2019-02-03 | 288971 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0018407 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292372 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0019036 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294032 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019298 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 294471 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020881 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2019-02-10 | 299474 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0022464 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 302623 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0022546 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 305548 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0023276 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 308405 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0023574 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 310416 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0023836 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 307821 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0024676 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 313847 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025644 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 2 | 18 | 2019-02-18 | 317345 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0025737 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 318142 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0027973 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 25 | 2019-02-25 | 323376 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028297 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324284 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0028481 | Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 324914 | Sus | N | EquipmentFailureInvolved¦Overhead¦Regulator¦Malfunctioning
19-0030611 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2019-03-04 | 331071 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0031075 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2019-03-05 | 332024 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0031263 | Equipment Failure/Involved | Fire, pole | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2019-03-06 | 332645 | Sus | N | EquipmentFailureInvolved¦Firepole¦Transformer¦FailedFaulted
19-0033246 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2019-03-12 | 338036 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
19-0033450 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2019-03-13 | 338474 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
19-0034415 | Animal | Squirrel | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2019-03-16 | 340961 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
19-0034992 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2019 | Tier 2 - Elevated | Transformer only | 3 | 19 | 2019-03-19 | 342853 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
19-0037875 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 3 | 27 | 2019-03-27 | 349087 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0040250 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2019-04-06 | 354766 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0040393 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2019-04-07 | 355320 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0041155 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2019-04-09 | 357587 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
19-0042205 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2019-04-13 | 360217 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
19-0045629 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2019-04-24 | 367037 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0048361 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2019-05-02 | 372577 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
19-0049685 | Vegetation | Tree - grew into line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2019-05-07 | 375680 | Sus | Y | Vegetation¦Treegrewintoline¦Fuse¦FailedFaulted
19-0050169 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2019-05-08 | 376633 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
19-0071237 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 23 | 2019-06-23 | 426823 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0071262 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2019-06-23 | 427030 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0075113 | Animal | Squirrel | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2019-07-08 | 442380 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
19-0084288 | Animal | Squirrel | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2019-08-05 | 483288 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
19-0089410 | Animal | Squirrel | Fuse | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2019-08-19 | 522255 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
19-0090133 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2019-08-20 | 525673 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0099167 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2019-09-14 | 582776 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0100984 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2019-09-18 | 592406 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0108071 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 10 | 6 | 2019-10-06 | 645604 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0110767 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2019-10-12 | 655026 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0113791 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2019-10-19 | 674766 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0115852 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 683411 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0120312 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2019-11-01 | 697985 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0122005 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2019-11-06 | 700953 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0122662 | 3rd Party | Other | Jumper | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2019-11-07 | 702168 | Sus | Y | 3rdParty¦Other¦Jumper¦Normal
19-0123425 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2019-11-10 | 704069 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0129084 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 715381 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130326 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 717342 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130416 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 719026 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130488 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 720041 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0130607 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 720985 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0130909 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 723089 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0131529 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724687 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0137780 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2019-12-23 | 749631 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0011590 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2020-01-21 | 766965 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0014955 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2020-01-29 | 772499 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0019537 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 2 | 9 | 2020-02-09 | 783253 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0020109 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 787333 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0027603 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2020-03-01 | 821069 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0027749 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2020-03-02 | 821777 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0031168 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2020-03-11 | 844976 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0034230 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2020-03-19 | 858905 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0038661 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2020-04-05 | 883357 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0038803 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2020-04-06 | 883576 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0038901 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2020-04-06 | 884535 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0041321 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 4 | 14 | 2020-04-14 | 895311 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0043651 | Vegetation | Tree - fell into line | Secondary | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2020-04-22 | 899383 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Broken
20-0044149 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 23 | 2020-04-23 | 900252 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0046557 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2020-05-02 | 905743 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0047641 | Equipment Failure/Involved | Overhead | Secondary | Together | 2020 | Tier 3 - Extreme | Transformer only | 5 | 5 | 2020-05-05 | 907724 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Together
20-0049052 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2020 | Tier 2 - Elevated | Transformer only | 5 | 11 | 2020-05-11 | 911114 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
20-0053813 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 25 | 2020-05-25 | 920861 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0055910 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 30 | 2020-05-30 | 926289 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0056010 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2020-05-30 | 926616 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
20-0058550 | Vegetation | Tree - branch fell on line | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 6 | 6 | 2020-06-06 | 933206 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦FailedFaulted
20-0058676 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2020-06-07 | 933725 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0059607 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2020-06-10 | 935817 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0059607 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2020-06-10 | 935817 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0060758 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2020-06-12 | 938028 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0061893 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 16 | 2020-06-16 | 940447 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0063683 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2020-06-22 | 944522 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
20-0063917 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 944927 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0064169 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 945681 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0065846 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2020-06-28 | 949407 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
20-0073861 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2020-07-20 | 968630 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
20-0085146 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1010501 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0089156 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 8 | 24 | 2020-08-24 | 1028003 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0089265 | Animal | Squirrel | Cutout, fuse holder | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2020-08-24 | 1028185 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
20-0090185 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1032293 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0090464 | Environmental/External | Fire, Forest/Grass | Cutout, fuse holder | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033356 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Cutoutfuseholder¦Normal
20-0091445 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1041121 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0092988 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2020-09-03 | 1051537 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0096952 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 9 | 13 | 2020-09-13 | 1067238 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0098687 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1079256 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0099799 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086087 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0108196 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2020-10-14 | 1117937 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0114076 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 27 | 2020-10-27 | 1130121 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0114414 | 3rd Party | Fire, house or bldg. | Secondary | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2020-10-28 | 1130861 | Sus | Y | 3rdParty¦Firehouseorbldg¦Secondary¦Brokenwireonground
20-0115030 | Vegetation | Tree - cutting, PG&E contractor | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2020-10-29 | 1131842 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦CrossarmWood¦Broken
20-0124827 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 24 | 2020-11-24 | 1153732 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0128458 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1168116 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0004811 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2021-01-04 | 1203854 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0005497 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2021-01-06 | 1205205 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0009814 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2021-01-18 | 1212875 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0009874 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2021-01-18 | 1213127 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0010621 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214706 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Broken
21-0016680 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1236838 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0019374 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1243507 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0021663 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 2 | 4 | 2021-02-04 | 1247645 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0022920 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2021-02-08 | 1250364 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0025483 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2021-02-14 | 1254890 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0031911 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2021-03-03 | 1266679 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0032365 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 3 | 4 | 2021-03-04 | 1268072 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
21-0036352 | Vegetation | Tree - branch fell on line | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2021-03-14 | 1282376 | Sus | N | Vegetation¦Treebranchfellonline¦Jumper¦BurnedOpen
21-0038979 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2021-03-20 | 1290089 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0048241 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2021-04-13 | 1315711 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
21-0052149 | Animal | Squirrel | Fuse | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2021-04-22 | 1329093 | Sus | N | Animal¦Squirrel¦Fuse¦Normal
21-0056003 | Animal | Bird found | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2021-05-03 | 1339459 | Sus | Y | Animal¦Birdfound¦Cutoutfuseholder¦Broken
21-0057917 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2021-05-06 | 1342581 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
21-0062011 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 5 | 16 | 2021-05-16 | 1350781 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0064336 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2021-05-21 | 1355313 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0071936 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2021-06-09 | 1369245 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0078398 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 23 | 2021-06-23 | 1383311 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0081068 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Transformer only | 6 | 28 | 2021-06-28 | 1387440 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0089416 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 14 | 2021-07-14 | 1404259 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0104544 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2021-08-14 | 1442453 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0107637 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Transformer only | 8 | 21 | 2021-08-21 | 1449240 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0111223 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2021-08-30 | 1458414 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0122431 | Animal | Squirrel | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2021-09-26 | 1480779 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Broken
21-0124896 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2021-10-01 | 1484972 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0126367 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 5 | 2021-10-05 | 1487973 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
21-0128074 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 8 | 2021-10-08 | 1490866 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0136384 | 3rd Party | Vehicle | Connector or Splice (UG) | Burned/flashed | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1513066 | Sus | Y | 3rdParty¦Vehicle¦ConnectororSplice(UG)¦Burnedflashed
21-0136461 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1510590 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0137481 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 10 | 25 | 2021-10-25 | 1517487 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0139601 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2021-10-29 | 1524903 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0146655 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 16 | 2021-11-16 | 1547233 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0156796 | Vegetation | Tree - branch fell on line | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 12 | 2021-12-12 | 1564964 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦FailedFaulted
21-0156809 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2021-12-12 | 1564985 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158103 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 12 | 14 | 2021-12-14 | 1570621 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken
21-0158191 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1571625 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0158434 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569350 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0158987 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1575092 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160111 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2021 | Tier 3 - Extreme | Transformer only | 12 | 22 | 2021-12-22 | 1578983 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
21-0160547 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581151 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161318 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2021-12-28 | 1586655 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161339 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585194 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161372 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2021-12-28 | 1587198 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0161635 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588076 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0161664 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588632 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0161814 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1589826 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005211 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1592532 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0007081 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1583173 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0039084 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2022-03-27 | 1657231 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0042173 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 3 | 2022-04-03 | 1662142 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0045742 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669465 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0046415 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669483 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0051639 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 19 | 2022-04-19 | 1676718 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
22-0052204 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 20 | 2022-04-20 | 1677697 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0055712 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 13 | 2022-06-13 | 1730027 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0059838 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2022-05-09 | 1692182 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0060978 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2022-05-11 | 1694165 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0064717 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2022-05-20 | 1706419 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0065923 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2022-05-24 | 1709208 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
22-0066148 | Company Initiated | Personnel, company | CT | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2022-05-25 | 1709944 | Sus | Y | CompanyInitiated¦Personnelcompany¦CT¦Normal
22-0072498 | Animal | Other | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2022-06-10 | 1726870 | Sus | Y | Animal¦Other¦PoleWood¦Deteriorated
22-0074187 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2022-06-14 | 1731307 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
22-0083626 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2022-07-10 | 1752457 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0087368 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2022-07-19 | 1760763 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0088341 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2022-07-21 | 1762586 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0090340 | Company Initiated | Personnel, company | Recloser | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2022-07-27 | 1766658 | Sus | Y | CompanyInitiated¦Personnelcompany¦Recloser¦Normal
22-0090995 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2022-07-28 | 1767529 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0092003 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 2 - Elevated | Transformer only | 8 | 1 | 2022-08-01 | 1770098 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0094664 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2022-08-07 | 1775173 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
22-0100185 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2022-08-21 | 1786489 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
22-0102114 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2022-08-25 | 1791705 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
22-0106125 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 5 | 2022-09-05 | 1800420 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0106947 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 6 | 2022-09-06 | 1803220 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
22-0107340 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2022-09-07 | 1804239 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0107995 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2022-09-08 | 1805921 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0111371 | 3rd Party | Customer Equipment | Customer Equipment | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2022-09-16 | 1812888 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Broken
22-0111654 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1814501 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0112671 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 20 | 2022-09-20 | 1817584 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0112835 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2022-09-20 | 1817805 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0119468 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2022-10-09 | 1832155 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
22-0122065 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2022-10-17 | 1838934 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0123161 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2022-10-20 | 1841686 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0124470 | Equipment Failure/Involved | Underground | Other | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2022-10-25 | 1844725 | Sus | Y | EquipmentFailureInvolved¦Underground¦Other¦Broken
22-0125171 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2022-10-26 | 1846459 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0135399 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2022-12-01 | 1872691 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0135490 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2022-12-01 | 1872949 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0138818 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885148 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
22-0140924 | Environmental/External | Earthquake | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2022-12-21 | 1895255 | Sus | N | EnvironmentalExternal¦Earthquake¦ConductorOverhead¦Normal
22-0141023 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 12 | 22 | 2022-12-22 | 1896041 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Burnedflashed
22-0141656 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Leaking | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899105 | Sus | N | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Leaking
15-0003719 | Vegetation | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2015-01-10 | 1161918 | Sus | N | Vegetation¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
15-0015517 | Equipment Failure/Involved | Other | Insulator | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2015-02-24 | 1195485 | Sus | N | EquipmentFailureInvolved¦Other¦Insulator¦Broken
15-0036224 | Animal | Bird found | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2015-05-24 | 1239007 | Sus | Y | Animal¦Birdfound¦Fuse¦Normal
15-0037342 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2015-05-29 | 1241105 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0042935 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2015-06-23 | 1255463 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0042983 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2015-06-24 | 1255596 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0043416 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 25 | 2015-06-25 | 1256524 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0044053 | Equipment Failure/Involved | Electrical Overload |  | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 6 | 29 | 2015-06-29 | 1258761 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦¦FailedFaulted
15-0044417 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2015-06-30 | 1259696 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0045531 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 4 | 2015-07-04 | 1263026 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0048937 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1272523 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0053531 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2015-08-07 | 1284278 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0055664 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2015-08-17 | 1290517 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0058549 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2015-09-01 | 1298152 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
15-0060871 | Equipment Failure/Involved | Overhead | Switch (OH) | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2015-09-11 | 1304073 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Burnedflashed
15-0061112 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1305108 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062161 | Animal | Bird found | Bushing | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2015-09-18 | 1308160 | Sus | Y | Animal¦Birdfound¦Bushing¦Burnedflashed
15-0063165 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2015-09-24 | 1311471 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
15-0065878 | Animal | Other | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2015-09-26 | 1312532 | Sus | Y | Animal¦Other¦Fuse¦FailedFaulted
15-0067843 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 4 | 2015-10-04 | 1316736 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
15-0071364 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324420 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0071898 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2015-10-19 | 1326067 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0075098 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 11 | 2 | 2015-11-02 | 1334046 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0082991 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2015-12-05 | 1354472 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0084095 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 10 | 2015-12-10 | 1358185 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0084203 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2015-12-11 | 1358361 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground
15-0084978 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361603 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0087719 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 28 | 2015-12-28 | 1373709 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0003658 | Vegetation | Tree - branch fell on line | Secondary | Arcing | 2016 | Tier 3 - Extreme | Transformer only | 1 | 6 | 2016-01-06 | 1379085 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Arcing
16-0004229 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2016-01-09 | 1380849 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0006070 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2016-01-18 | 1386145 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0006071 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2016-01-18 | 1386121 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0006488 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2016-01-19 | 1387304 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0007459 | Unknown Cause | Patrol - found nothing |  | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2016-01-22 | 1389919 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦BurnedOpen
16-0014004 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1407952 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0015412 | Equipment Failure/Involved | Underground | Transformer | Broken | 2016 | Tier 2 - Elevated | Transformer only | 2 | 24 | 2016-02-24 | 1411698 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦Broken
16-0015921 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2016-02-26 | 1412665 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0016948 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2016-03-03 | 1415089 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0017765 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418279 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0017798 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417863 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0021025 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430453 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0021710 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2016-03-15 | 1432042 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0022347 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2016-03-17 | 1433503 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0022960 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 3 | 21 | 2016-03-21 | 1435093 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0024018 | 3rd Party | Customer Equipment | Other | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2016-03-25 | 1438502 | Sus | N | 3rdParty¦CustomerEquipment¦Other¦Broken
16-0024636 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 29 | 2016-03-29 | 1440525 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0027554 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2016-04-10 | 1448046 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0028414 | 3rd Party | Tree - cutting, 3rd party | Secondary | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 4 | 13 | 2016-04-13 | 1450060 | Sus | N | 3rdParty¦Treecutting3rdparty¦Secondary¦Brokenwireonground
16-0030088 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2016-04-20 | 1454508 | Sus | N | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
16-0030147 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2016 | Tier 3 - Extreme | Transformer only | 4 | 21 | 2016-04-21 | 1454738 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
16-0031381 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2016-04-25 | 1458397 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0036675 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2016-05-18 | 1471746 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0039631 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2016-05-29 | 1478991 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0040901 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 3 | 2016-06-03 | 1482315 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
16-0042317 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2016-06-09 | 1486295 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0044364 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Transformer only | 6 | 19 | 2016-06-19 | 1492420 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0050153 | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 15 | 2016-07-15 | 1510488 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted
16-0062718 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2016-09-06 | 1537386 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
16-0064023 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2016-09-12 | 1540261 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0064571 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2016-09-14 | 1541452 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0065289 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2016-09-16 | 1542966 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0067371 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2016-09-26 | 1547547 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0067613 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2016-09-26 | 1547969 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0072990 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1563347 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0075824 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2016-10-27 | 1570583 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0080165 | Animal | Squirrel | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2016-11-16 | 1581967 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
16-0081148 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2016-11-19 | 1585229 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
16-0081582 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2016-11-22 | 1586973 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
16-0082756 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2016-11-28 | 1590867 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
16-0084471 | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2016-12-07 | 1596549 | Sus | N | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted
16-0085897 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1603724 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0005139 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625049 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0005377 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625997 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006795 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634068 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006906 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634710 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0007176 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634826 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0007277 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637779 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007763 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640160 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007827 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639194 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0008715 | Equipment Failure/Involved | Overhead | Other | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1642422 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Normal
17-0009150 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 14 | 2017-01-14 | 1643764 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0010486 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648711 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0010570 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648956 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011582 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1654327 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0013198 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655471 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0013692 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662861 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0014235 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2017-01-24 | 1665141 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0016082 | Equipment Failure/Involved | Overhead | Other | Broken | 2017 | Tier 2 - Elevated | Transformer only | 1 | 30 | 2017-01-30 | 1670514 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
17-0016399 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 31 | 2017-01-31 | 1671394 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0018601 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679559 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
17-0019112 | Animal | Other | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682239 | Sus | N | Animal¦Other¦PoleWood¦Brokenwireonground
17-0019733 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2017-02-10 | 1684383 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0019909 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2017-02-10 | 1684877 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0022361 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1696022 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0022520 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1693746 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0022901 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1696480 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023816 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 2 | 20 | 2017-02-20 | 1703310 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
17-0024857 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706251 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025042 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706181 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0025652 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2017-02-22 | 1710768 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0028550 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2017-03-05 | 1720393 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0028801 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720899 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
17-0031082 | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2017-03-15 | 1728095 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated
17-0032545 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 21 | 2017-03-21 | 1732495 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0033651 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2017-03-24 | 1735080 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0036882 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745025 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0038085 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1751492 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0040388 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2017-04-14 | 1758060 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0043306 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2017-04-27 | 1768220 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0045734 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | 2017 | Tier 3 - Extreme | Transmission line | 5 | 6 | 2017-05-06 | 1775977 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed
17-0048405 | Animal | Other | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2017-05-16 | 1783518 | Sus | Y | Animal¦Other¦Fuse¦FailedFaulted
17-0049478 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 5 | 21 | 2017-05-21 | 1786903 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0049778 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 22 | 2017-05-22 | 1787524 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0053783 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2017-06-08 | 1799838 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0057669 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2017-06-22 | 1814629 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0059342 | Vegetation | Tree - fell into line | Insulator | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2017-06-29 | 1820294 | Sus | Y | Vegetation¦Treefellintoline¦Insulator¦Brokenwireonground
17-0060155 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2017-07-03 | 1822645 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0063742 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2017-08-03 | 1845409 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
17-0063932 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 19 | 2017-07-19 | 1835738 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0070173 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2017-08-14 | 1852255 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0073928 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2017-08-29 | 1862751 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0075003 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2017-09-01 | 1865056 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0085196 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893810 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0086745 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899352 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0087486 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2017-10-15 | 1901242 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0087717 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1901817 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Broken
17-0088840 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2017-10-19 | 1904694 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Burnedflashed
17-0089249 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2017-10-20 | 1906380 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
17-0090215 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1909171 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
17-0091801 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2017-11-01 | 1913801 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
17-0092216 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 11 | 2 | 2017-11-02 | 1914566 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
17-0097367 | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 24 | 2017-11-24 | 1928595 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Brokenwireonground
17-0099692 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1935367 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0101070 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2017-12-11 | 1940233 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0102501 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2017-12-18 | 1947242 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0004986 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2018-01-10 | 5656 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0007276 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2018-01-19 | 10672 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0012349 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2018-02-07 | 21078 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0016952 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2018-02-24 | 30832 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0018195 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2018-02-28 | 33618 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0019210 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 36564 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0019416 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2018-03-03 | 37423 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0019435 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2018-03-03 | 37506 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0020396 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2018-03-06 | 39447 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0021578 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 3 | 10 | 2018-03-10 | 41531 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0022722 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 44110 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
18-0025318 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 50275 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0026876 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 27 | 2018-03-27 | 54077 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0028222 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2018-03-31 | 57303 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0028632 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2018-04-02 | 58231 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0029884 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2018-04-06 | 60833 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
18-0037073 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 30 | 2018-04-30 | 77084 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0044980 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2018-05-29 | 95569 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0049419 | Animal | Squirrel | Fuse | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2018-06-10 | 105806 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
18-0059026 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2018-07-11 | 129456 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0063313 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 24 | 2018-07-24 | 139591 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0063323 | Animal | Other | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2018-07-25 | 139625 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
18-0066890 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 149309 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0066953 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2018-08-05 | 149550 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0068412 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2018-08-09 | 152091 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0070405 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2018 | Tier 3 - Extreme | Transformer only | 8 | 15 | 2018-08-15 | 156059 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
18-0071465 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2018-08-19 | 158131 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
18-0072342 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2018-08-22 | 160075 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
18-0073107 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2018-08-24 | 161365 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
18-0076928 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2018 | Tier 2 - Elevated | Transformer only | 9 | 5 | 2018-09-05 | 168857 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
18-0080333 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 17 | 2018-09-17 | 175706 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0088625 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2018-10-09 | 191799 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0091505 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2018-10-17 | 197563 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0092913 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2018-10-22 | 200212 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0098866 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2018-11-10 | 213020 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0101338 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218782 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102382 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2018-11-22 | 222114 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0102553 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2018-11-23 | 222818 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0102665 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 11 | 23 | 2018-11-23 | 223147 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0106123 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2018-12-02 | 231655 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0107730 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Transmission line | 12 | 6 | 2018-12-06 | 235317 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0109497 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2018-12-16 | 241507 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0004795 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 253799 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0005297 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 255894 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0005466 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 256015 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009598 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Bent or Twisted | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 266825 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted
19-0010493 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 272263 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010892 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 271916 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0011065 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 274086 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0011372 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 274873 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
19-0012514 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2019-01-20 | 277101 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0018954 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2019-02-06 | 293828 | Sus | N | 3rdParty¦Vehicle¦AnchororGuy¦Broken
19-0019328 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2019-02-06 | 294647 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020368 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2019-02-08 | 296390 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
19-0020676 | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298396 | Sus | N | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Normal
19-0020696 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298370 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0021197 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 11 | 2019-02-11 | 300134 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
19-0021317 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2019-02-12 | 300373 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0021846 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 303015 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022093 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303838 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0023427 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 309884 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0023642 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 309140 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0024692 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 314852 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025171 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315988 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025631 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 317666 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0026079 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 2 | 17 | 2019-02-17 | 318608 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
19-0028926 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326257 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0032164 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2019-03-08 | 334590 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0033093 | Vegetation | Tree - fell into line | Conductor, Overhead | Contaminated | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2019-03-12 | 337352 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Contaminated
19-0037000 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2019-03-26 | 347602 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0038155 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2019-03-29 | 349929 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0039620 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 3 | 2019-04-03 | 353545 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0046969 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2019-04-29 | 369947 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
19-0048103 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2019-05-02 | 372157 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0048551 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2019-05-03 | 373042 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0051253 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 13 | 2019-05-13 | 379149 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0052452 | Animal | Other | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2019-05-15 | 381583 | Sus | Y | Animal¦Other¦Jumper¦BurnedOpen
19-0053005 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2019-05-16 | 382954 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0053939 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2019-05-19 | 384961 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0060930 | Wildfire Mitigation | CWSP - Vegetation Removal | Other | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2019-05-31 | 394748 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦Other¦Normal
19-0062441 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2019-06-04 | 397209 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0065549 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 6 | 10 | 2019-06-10 | 404473 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
19-0065561 | Equipment Failure/Involved | Electrical Overload | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2019-06-10 | 404604 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦FailedFaulted
19-0066574 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 6 | 12 | 2019-06-12 | 407449 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0066838 | 3rd Party | Vehicle | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 12 | 2019-06-12 | 407924 | Sus | Y | 3rdParty¦Vehicle¦CrossarmWood¦Broken
19-0066891 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2019-06-12 | 408060 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0071183 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 6 | 23 | 2019-06-23 | 426653 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
19-0073497 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2019-06-30 | 438364 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0088912 | Vegetation | Tree - cutting, PG&E contractor | Secondary | Broken | 2019 | Tier 2 - Elevated | Transformer only | 8 | 16 | 2019-08-16 | 518576 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦Secondary¦Broken
19-0090193 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2019-08-20 | 526824 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0091739 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2019-08-24 | 535126 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0094572 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2019-09-02 | 550919 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0100459 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2019-09-18 | 589099 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
19-0106791 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2019-10-02 | 638892 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0112591 | Vegetation | Tree - fell into line | Pole - Tower, steel | Burned/flashed | 2019 | Tier 2 - Elevated | Transmission line | 10 | 16 | 2019-10-16 | 663256 | Sus | Y | Vegetation¦Treefellintoline¦PoleTowersteel¦Burnedflashed
19-0114525 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2019-10-22 | 676896 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0123413 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2019-11-10 | 703984 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0129334 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 716683 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0130005 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 719839 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0131546 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724852 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0134688 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 732154 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0135020 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2019-12-08 | 733630 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0136862 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2019-12-16 | 743768 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0137507 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2019-12-22 | 748042 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0018534 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 2 | 7 | 2020-02-07 | 779839 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0019830 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 787282 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0030660 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2020-03-10 | 843296 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0031464 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2020-03-12 | 846154 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032307 | Animal | Squirrel | Transformer | Broken | 2020 | Tier 2 - Elevated | Transformer only | 3 | 15 | 2020-03-15 | 852207 | Sus | N | Animal¦Squirrel¦Transformer¦Broken
20-0032363 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852494 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0033331 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 854505 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0033920 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 858455 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0034122 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2020 | Tier 2 - Elevated | Transformer only | 3 | 19 | 2020-03-19 | 858667 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
20-0038154 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 3 | 2020-04-03 | 880022 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0040762 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2020-04-13 | 894433 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
20-0041047 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2020-04-13 | 894808 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0041792 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2020-04-15 | 896145 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0045044 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 4 | 28 | 2020-04-28 | 902643 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
20-0053850 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 25 | 2020-05-25 | 921049 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0054709 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 27 | 2020-05-27 | 923269 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0055482 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2020-05-29 | 924905 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0064033 | Equipment Failure/Involved | Fire, pole | Secondary | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 945352 | Sus | Y | EquipmentFailureInvolved¦Firepole¦Secondary¦Burnedflashed
20-0064604 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2020-06-24 | 946464 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0066389 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 29 | 2020-06-29 | 954075 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0076552 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 7 | 27 | 2020-07-27 | 973121 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0078652 | Vegetation | Tree - fell into line | Insulator | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 1 | 2020-08-01 | 976408 | Sus | Y | Vegetation¦Treefellintoline¦Insulator¦Broken
20-0084787 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1011545 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0085410 | Environmental/External | Lightning | Transformer | Burned/flashed | 2020 | Tier 3 - Extreme | Transformer only | 8 | 16 | 2020-08-16 | 1014476 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦Burnedflashed
20-0086802 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2020-08-18 | 1019654 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0087295 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transmission line | 8 | 19 | 2020-08-19 | 1022079 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0094356 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1059502 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(OH)¦Normal
20-0094679 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2020-09-08 | 1060531 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0096065 | Environmental/External | Fire, Forest/Grass | Transformer | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 20 | 2020-08-20 | 1063558 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal
20-0096883 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 9 | 12 | 2020-09-12 | 1067055 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0099828 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086152 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0101291 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2020-09-24 | 1091924 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
20-0104764 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1109093 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0107853 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1116159 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
20-0109417 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2020-10-15 | 1119005 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0120025 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 12 | 2020-11-12 | 1142454 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0120651 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 13 | 2020-11-13 | 1143605 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0122367 | Environmental/External | Lightning | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2020-11-18 | 1148275 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Broken
20-0122752 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 11 | 19 | 2020-11-19 | 1149110 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0127588 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 12 | 4 | 2020-12-04 | 1162300 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0004582 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2021-01-04 | 1203095 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0008197 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2021-01-13 | 1209756 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
21-0009137 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 1 | 15 | 2021-01-15 | 1210999 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0010127 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214443 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0010182 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214552 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0011310 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1215089 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0011600 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2021-01-20 | 1218572 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
21-0011738 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2021-01-20 | 1219110 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0013595 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223373 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0015759 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233227 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0017974 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2021-01-28 | 1240676 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0017974 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2021-01-28 | 1240676 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0018698 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2021-01-29 | 1242608 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
21-0022434 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2021-02-05 | 1248799 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
21-0025672 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2021-02-15 | 1255338 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0028774 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2021-02-23 | 1260602 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0031932 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2021-03-03 | 1266755 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0039204 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2021-03-21 | 1290951 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0040170 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2021-03-23 | 1294787 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed
21-0042371 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 3 - Extreme | Transformer only | 3 | 29 | 2021-03-29 | 1302722 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0045567 | Vegetation | Tree - grew into line | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2021-04-07 | 1308455 | Sus | N | Vegetation¦Treegrewintoline¦Secondary¦Broken
21-0051916 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2021-04-22 | 1328562 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0055716 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 5 | 1 | 2021-05-01 | 1338539 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
21-0061962 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 15 | 2021-05-15 | 1350655 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0063047 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 18 | 2021-05-18 | 1352894 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0067165 | Animal | Bird found | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2021-05-28 | 1360431 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
21-0075597 | Company Initiated | Operating error | Recloser | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2021-07-14 | 1404799 | Sus | Y | CompanyInitiated¦Operatingerror¦Recloser¦Normal
21-0076870 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 21 | 2021-06-21 | 1380714 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0086237 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2021-07-07 | 1394187 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0089055 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 7 | 13 | 2021-07-13 | 1403490 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
21-0091995 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 19 | 2021-07-19 | 1408220 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0100147 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 8 | 5 | 2021-08-05 | 1434516 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
21-0103395 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 12 | 2021-08-12 | 1440638 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0103461 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2021-08-12 | 1440817 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0103485 | Animal | Squirrel | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2021-08-12 | 1440803 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
21-0123760 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 3 - Extreme | Transformer only | 9 | 29 | 2021-09-29 | 1483341 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0135522 | 3rd Party | Vehicle | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2021-10-23 | 1506972 | Sus | Y | 3rdParty¦Vehicle¦CrossarmWood¦Broken
21-0135522 | 3rd Party | Vehicle | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2021-10-23 | 1506972 | Sus | Y | 3rdParty¦Vehicle¦CrossarmWood¦Broken
21-0136085 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1507327 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0137768 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1520046 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0146726 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2021-11-17 | 1547467 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0152829 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2021-11-29 | 1555996 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0157930 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569581 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0158012 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568988 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158175 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568597 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158208 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568782 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
21-0159576 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2021-12-18 | 1577098 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0159758 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Substation - Distribution | 12 | 19 | 2021-12-19 | 1577608 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161173 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1583733 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0007925 | Environmental/External | Ice or snow | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2022-01-10 | 1599218 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Broken
22-0011686 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2022-01-20 | 1605550 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0013057 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607983 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0014335 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 1 | 25 | 2022-01-25 | 1612153 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0016702 | Animal | Squirrel | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Transformer only | 2 | 1 | 2022-02-01 | 1617578 | Sus | N | Animal¦Squirrel¦Fuse¦BurnedOpen
22-0021076 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2022-02-10 | 1625162 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0022454 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 2 | 15 | 2022-02-15 | 1627653 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0030404 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2022-03-05 | 1643227 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0030427 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2022-03-06 | 1643336 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0053185 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2022-04-22 | 1678843 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0055299 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2022 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2022-04-27 | 1683323 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
22-0055313 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2022-04-27 | 1683337 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0060972 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 11 | 2022-05-11 | 1694191 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0074386 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2022-06-15 | 1731643 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0082603 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2022-07-07 | 1750384 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083634 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2022-07-10 | 1752445 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
22-0087017 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 19 | 2022-07-19 | 1760206 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
22-0093713 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2022-08-04 | 1773099 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
22-0100692 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2022-08-22 | 1787655 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0102743 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2022-08-27 | 1793212 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
22-0106525 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 9 | 6 | 2022-09-06 | 1801741 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed
22-0110915 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 16 | 2022-09-16 | 1812218 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0114797 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 26 | 2022-09-26 | 1821791 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
22-0126535 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1849926 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0127012 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2022-11-02 | 1851485 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0128043 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2022-11-04 | 1853586 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0128406 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2022-11-07 | 1855660 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0129239 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857993 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0129293 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857518 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
22-0133442 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2022-11-22 | 1867587 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0136585 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2022-12-05 | 1876184 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0139222 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2022-12-12 | 1886627 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0139871 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Zone 1 - HHZ | Distribution Circuit | 12 | 14 | 2022-12-14 | 1888935 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0140939 | Environmental/External | Earthquake | Fuse | Normal | 2022 | Tier 2 - Elevated | Transformer only | 12 | 21 | 2022-12-21 | 1895319 | Sus | N | EnvironmentalExternal¦Earthquake¦Fuse¦Normal
22-0141418 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1897942 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
23-0004252 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1907687 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
23-0004357 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 12 | 31 | 2022-12-31 | 1904448 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0005518 | Animal | Squirrel | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2015-01-19 | 1165615 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
15-0012428 | Equipment Failure/Involved | Other | Jumper | Burned Open | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2015-02-10 | 1187751 | Sus | N | EquipmentFailureInvolved¦Other¦Jumper¦BurnedOpen
15-0013295 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2015 | Tier 3 - Extreme | Transformer only | 2 | 13 | 2015-02-13 | 1189652 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
15-0014198 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2015-02-19 | 1192426 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0024210 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 4 | 2015-04-04 | 1212674 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0032183 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2015-05-06 | 1229965 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0035693 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 5 | 21 | 2015-05-21 | 1237989 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0038707 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2015-06-05 | 1244061 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
15-0040661 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2015-06-12 | 1249752 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0046691 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 7 | 9 | 2015-07-09 | 1265810 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0048612 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 19 | 2015-07-19 | 1271795 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0053506 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2015-08-07 | 1284384 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
15-0059489 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2015-09-05 | 1300525 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0059761 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 8 | 2015-09-08 | 1301568 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0059905 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 8 | 2015-09-08 | 1301898 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0061091 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2015-09-13 | 1305000 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
15-0062334 | 3rd Party | Vehicle | Pole-Wood | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2015-09-19 | 1308779 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
15-0062485 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2015-09-21 | 1309326 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062704 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 13 | 2015-09-13 | 1310142 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0073357 | Equipment Failure/Involved | Underground | Secondary | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2015-10-26 | 1329446 | Sus | Y | EquipmentFailureInvolved¦Underground¦Secondary¦Broken
15-0074157 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2015-10-29 | 1331280 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0078050 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342595 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0082660 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1353515 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0084768 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361691 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0084843 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361394 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0086318 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2015-12-20 | 1367075 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦Normal
15-0086408 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 21 | 2015-12-21 | 1367489 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
15-0087866 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2015-12-30 | 1374840 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0002445 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 1 | 1 | 2016-01-01 | 1375699 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
16-0002549 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2016-01-03 | 1376121 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0003256 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2016-01-06 | 1377952 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0005305 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 14 | 2016-01-14 | 1383655 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
16-0013360 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406188 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0016229 | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 29 | 2016-02-29 | 1413593 | Sus | N | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal
16-0016964 | Equipment Failure/Involved | Electrical Overload | Transformer |  | 2016 | Tier 2 - Elevated | Transformer only | 3 | 3 | 2016-03-03 | 1415021 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦
16-0018630 | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 7 | 2016-03-07 | 1422985 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround
16-0019052 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Transformer only | 3 | 7 | 2016-03-07 | 1424436 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0019993 | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2016-03-10 | 1426591 | Sus | N | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted
16-0025704 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 2 | 2016-04-02 | 1443216 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
16-0025787 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 3 | 2016-04-03 | 1443500 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0028597 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 14 | 2016-04-14 | 1450689 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0031070 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Transformer only | 4 | 24 | 2016-04-24 | 1457415 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
16-0031705 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 26 | 2016-04-26 | 1459378 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0031745 | Equipment Failure/Involved | Overhead | Other | Broken | 2016 | Tier 2 - Elevated | Transformer only | 4 | 26 | 2016-04-26 | 1459553 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
16-0041042 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2016-06-04 | 1482712 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0051635 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 21 | 2016-07-21 | 1513974 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
16-0052418 | 3rd Party | Fire, house or bldg. | Jumper | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2016-07-25 | 1515913 | Sus | Y | 3rdParty¦Firehouseorbldg¦Jumper¦Broken
16-0055741 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2016-08-08 | 1523050 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0059702 | 3rd Party | Vehicle | Conductor, Overhead | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2016-08-24 | 1531506 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦OnGround
16-0063759 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2016-09-11 | 1539532 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0063850 | Equipment Failure/Involved | Overhead | Anchor or Guy | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2016-09-11 | 1539943 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Normal
16-0070201 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 6 | 2016-10-06 | 1554137 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0070324 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2016-10-07 | 1554431 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072522 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561111 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072743 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561973 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0073203 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 10 | 17 | 2016-10-17 | 1564093 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
16-0074067 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 10 | 19 | 2016-10-19 | 1566149 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
16-0081132 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2016-11-19 | 1585144 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
16-0081243 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 20 | 2016-11-20 | 1585590 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0082103 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 24 | 2016-11-24 | 1588146 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0082210 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 11 | 25 | 2016-11-25 | 1588808 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
16-0083485 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2016-12-01 | 1592991 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
16-0085208 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 12 | 2016-12-12 | 1600235 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0085480 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2016-12-14 | 1601507 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0085657 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602289 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0085808 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1603340 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0085978 | 3rd Party | Other | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2016-12-16 | 1604166 | Sus | N | 3rdParty¦Other¦ConductorOverhead¦Normal
16-0087215 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2016-12-28 | 1612007 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
17-0002967 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1615646 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground
17-0003043 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1615470 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0004937 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622544 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005039 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623241 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0005887 | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1630256 | Sus | N | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Normal
17-0006360 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632412 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007506 | Vegetation | Tree - fell into line | Secondary | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1636357 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Normal
17-0007658 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637701 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0007839 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640229 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0008415 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2017-01-12 | 1641431 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0011409 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653335 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0012742 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658743 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0014338 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663505 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0014409 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663944 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0016849 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2017-02-02 | 1672696 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017189 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673496 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0018846 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679416 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0019525 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683670 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0020359 | 3rd Party | Customer Equipment | Secondary | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2017-02-11 | 1686263 | Sus | N | 3rdParty¦CustomerEquipment¦Secondary¦Normal
17-0021884 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1692164 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0024858 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706679 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0026562 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2017-02-24 | 1713496 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0028942 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2017-03-07 | 1721466 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0031579 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2017-03-17 | 1729223 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0031700 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2017-03-18 | 1729939 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0035882 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2017-04-02 | 1742532 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0037591 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 4 | 6 | 2017-04-06 | 1748210 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0037936 | Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | 2017 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2017-04-07 | 1750868 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed
17-0046037 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2017-05-07 | 1777179 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0051079 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2017-05-26 | 1791538 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0051365 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 29 | 2017-05-29 | 1792675 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0056278 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 18 | 2017-06-18 | 1809033 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0060070 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 2 | 2017-07-02 | 1822355 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
17-0068242 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2017-08-06 | 1847211 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0074889 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 1 | 2017-09-01 | 1864876 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0077948 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 11 | 2017-09-11 | 1876464 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0079877 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 19 | 2017-09-19 | 1881455 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0083939 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2017-10-03 | 1890444 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed
17-0085779 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 10 | 9 | 2017-10-09 | 1896747 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0087194 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2017-10-13 | 1900300 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0087245 | Equipment Failure/Involved | Overhead |  | Normal | 2017 | Tier 2 - Elevated | Transformer only | 10 | 13 | 2017-10-13 | 1900342 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦Normal
17-0087359 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1900760 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0087504 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1901286 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
17-0088108 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Burned/flashed | 2017 | Tier 3 - Extreme | Transformer only | 10 | 8 | 2017-10-08 | 1902842 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed
17-0090227 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2017-10-25 | 1909193 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
17-0092788 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2017 | Tier 3 - Extreme | Transformer only | 11 | 5 | 2017-11-05 | 1916461 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
17-0099834 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1936085 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0099872 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 5 | 2017-12-05 | 1936219 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0102065 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2017-12-16 | 1944249 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0102499 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2017-12-18 | 1947249 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0102860 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2017-12-20 | 1948964 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0103193 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2017-12-24 | 1950847 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0008063 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2018-01-23 | 12311 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0013091 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2018-02-10 | 22352 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023578 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46176 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
18-0025253 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2018-03-21 | 49904 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0026437 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2018-03-25 | 53165 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0037750 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2018-05-02 | 78384 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
18-0040052 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 10 | 2018-05-10 | 83438 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0046252 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2018-06-01 | 98397 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0046574 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2018-06-02 | 99206 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0047934 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 6 | 6 | 2018-06-06 | 102637 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0060348 | Animal | Other |  | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 7 | 16 | 2018-07-16 | 133124 | Sus | Y | Animal¦Other¦¦FailedFaulted
18-0062912 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2018-07-23 | 138630 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
18-0064491 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2018-07-27 | 142134 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0064531 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2018-07-28 | 142200 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0065613 | Animal | Squirrel | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2018-08-01 | 146376 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
18-0066118 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 147455 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0067623 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 150975 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0076071 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2018-09-04 | 167718 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
18-0077464 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2018-09-07 | 169725 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0077580 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2018-09-07 | 169989 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0081509 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 9 | 19 | 2018-09-19 | 177783 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0085648 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2018-10-02 | 185849 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
18-0088290 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2018-10-08 | 191035 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
18-0090023 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2018-10-12 | 194159 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0090210 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2018-10-14 | 195065 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
18-0099146 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 12 | 2018-11-12 | 213721 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0101361 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218843 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101866 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2018-11-21 | 219860 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0105250 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 229403 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0106864 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 12 | 4 | 2018-12-04 | 233525 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
18-0107149 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2018-12-04 | 233935 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109301 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 240726 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0003409 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2019-01-01 | 251320 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0003926 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2019-01-03 | 252328 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0005369 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 256611 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0005935 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2019-01-07 | 259853 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0008115 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2019-01-11 | 263478 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017538 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2019-02-03 | 288764 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018088 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289859 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed
19-0018188 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 291125 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020460 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2019-02-09 | 297456 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0020529 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 297828 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020748 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2019-02-09 | 299064 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0021724 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 301532 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
19-0022143 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303494 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0022304 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 302951 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023054 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 306891 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0023158 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 308760 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024454 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 313804 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025165 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315675 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0025675 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2019-02-18 | 317768 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0026199 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2019-02-19 | 319129 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0026360 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2019-02-20 | 319445 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0028356 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324565 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028694 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 325687 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0028748 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 325950 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028825 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 326648 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0039312 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 3 | 2019-04-03 | 352890 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0041010 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Transformer only | 4 | 9 | 2019-04-09 | 356816 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0052309 | Vegetation | Tree - palm frond fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2019-05-15 | 381280 | Sus | Y | Vegetation¦Treepalmfrondfellintoline¦ConductorOverhead¦Normal
19-0064796 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 9 | 2019-06-09 | 402387 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0072829 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 27 | 2019-06-27 | 432256 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0074176 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2019-07-02 | 440211 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
19-0078094 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2019-07-16 | 454788 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0080036 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 7 | 22 | 2019-07-22 | 467634 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0084127 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2019-08-04 | 482304 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0084134 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2019-08-04 | 482269 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0089750 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2019-08-20 | 524215 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0092161 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 8 | 26 | 2019-08-26 | 539724 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
19-0093813 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 29 | 2019-08-29 | 547464 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0094483 | Animal | Bird found | Cutout, fuse holder | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 9 | 1 | 2019-09-01 | 550582 | Sus | Y | Animal¦Birdfound¦Cutoutfuseholder¦Burnedflashed
19-0104998 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2019-09-28 | 627653 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0107531 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Arcing | 2019 | Tier 2 - Elevated | Transformer only | 10 | 4 | 2019-10-04 | 643502 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Arcing
19-0111294 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2019 | Tier 2 - Elevated | Transformer only | 10 | 14 | 2019-10-14 | 657879 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
19-0111925 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2019-10-15 | 659281 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
19-0115792 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2019-10-24 | 679846 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
19-0118500 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2019-10-29 | 693836 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0118964 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Transformer only | 10 | 30 | 2019-10-30 | 695125 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0126536 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2019-11-20 | 711089 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0130479 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 721833 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0131864 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2019-12-01 | 725538 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0131879 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2019-12-01 | 725576 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0131901 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | 2019 | Tier 2 - Elevated | Transformer only | 12 | 1 | 2019-12-01 | 725697 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Normal
19-0132136 | 3rd Party | Vehicle | Pothead(Riser Termination) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2019-12-02 | 726830 | Sus | N | 3rdParty¦Vehicle¦Pothead(RiserTermination)¦Broken
19-0137065 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2019-12-18 | 745136 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0137165 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 12 | 18 | 2019-12-18 | 745685 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
20-0018996 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 781094 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0019430 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 785447 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0019700 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2020 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2020-02-09 | 784281 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
20-0019763 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 787066 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0021257 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2020-02-12 | 789809 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
20-0023172 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2020-02-18 | 794936 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground
20-0026558 | Vegetation | Tree - fell into line | Secondary | Broken, wire on object | 2020 | Tier 3 - Extreme | Transformer only | 2 | 27 | 2020-02-27 | 815278 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonobject
20-0032482 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853310 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0033612 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2020-03-18 | 857473 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0033868 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 858263 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0033921 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 854393 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0034239 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2020-03-19 | 858720 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0038813 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 5 | 2020-04-05 | 883507 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0040731 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2020-04-13 | 894335 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0050788 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2020-05-15 | 914558 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0053690 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 24 | 2020-05-24 | 920497 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
20-0056653 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2020-06-02 | 928471 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0063817 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 23 | 2020-06-23 | 944866 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0079976 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 8 | 5 | 2020-08-05 | 979279 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0085682 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2020-08-17 | 1015155 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0086250 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2020-08-17 | 1017773 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0088807 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 22 | 2020-08-22 | 1026846 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0093880 | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2020-09-06 | 1056911 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Fuse¦BurnedOpen
20-0094301 | 3rd Party | Other | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1058721 | Sus | Y | 3rdParty¦Other¦ConductorOverhead¦Together
20-0096061 | Environmental/External | Fire, Forest/Grass | Customer Equipment | Burned/flashed | 2020 | Tier 3 - Extreme | Transformer only | 8 | 20 | 2020-08-20 | 1063555 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦CustomerEquipment¦Burnedflashed
20-0098372 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 17 | 2020-09-17 | 1076922 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0098621 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 9 | 17 | 2020-09-17 | 1077981 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0100070 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Transformer only | 9 | 22 | 2020-09-22 | 1087053 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0100297 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1088345 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100329 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1088563 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100452 | 3rd Party | Vehicle | Transformer (UG) | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 23 | 2020-09-23 | 1088762 | Sus | Y | 3rdParty¦Vehicle¦Transformer(UG)¦Broken
20-0101048 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Transformer only | 9 | 24 | 2020-09-24 | 1091193 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0102528 | Animal | Squirrel | Transformer | Normal | 2020 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2020-09-28 | 1096878 | Sus | Y | Animal¦Squirrel¦Transformer¦Normal
20-0102701 | Equipment Failure/Involved | Overhead | Jumper | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 29 | 2020-09-29 | 1097473 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Normal
20-0111460 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2020-10-21 | 1122662 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0118521 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2020-11-08 | 1139398 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0121255 | Animal | Other | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2020-11-16 | 1146077 | Sus | Y | Animal¦Other¦PoleWood¦Broken
20-0125734 | Animal | Squirrel | Fuse | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2020-11-29 | 1155885 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
20-0129516 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2020-12-10 | 1177329 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0130310 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transformer only | 12 | 14 | 2020-12-14 | 1184095 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0130945 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 17 | 2020-12-17 | 1192707 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0131562 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2020-12-23 | 1197578 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0009883 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1212986 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0010161 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2021-01-19 | 1214192 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0010504 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216152 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011608 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1213465 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011698 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1219138 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0012890 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 1 | 22 | 2021-01-22 | 1221391 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013273 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2021-01-23 | 1221804 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0014422 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1225329 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0015873 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233902 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0016180 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1230882 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016583 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233772 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0017031 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237774 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0017453 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1239509 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0020397 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2021-02-01 | 1244921 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0025181 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2021-02-12 | 1254023 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0032189 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2021 | Tier 2 - Elevated | Transformer only | 3 | 4 | 2021-03-04 | 1267516 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
21-0033256 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2021-03-07 | 1272998 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0034499 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2021-03-10 | 1276943 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0040162 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2021-03-23 | 1294743 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0041019 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2021-03-25 | 1297701 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0043458 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2021-03-31 | 1304631 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0052974 | Environmental/External | Lightning |  | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 4 | 25 | 2021-04-25 | 1333761 | Sus | N | EnvironmentalExternal¦Lightning¦¦FailedFaulted
21-0054045 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2021-04-27 | 1335754 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0064681 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 5 | 21 | 2021-05-21 | 1356093 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0067801 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 30 | 2021-05-30 | 1361542 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0071156 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2021-06-07 | 1367874 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0075967 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2021-06-18 | 1377132 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0077118 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2021-06-21 | 1381282 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
21-0077782 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2021-06-23 | 1382620 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0085055 | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2021-07-06 | 1392543 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed
21-0087698 | 3rd Party | Vehicle | Anchor or Guy | Bent or Twisted | 2021 | Tier 2 - Elevated | Transmission line | 7 | 11 | 2021-07-11 | 1399371 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦BentorTwisted
21-0087757 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2021-07-11 | 1399635 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
21-0094095 | Equipment Failure/Involved | Overhead | Service conductor | Broken | 2021 | Tier 2 - Elevated | Transformer only | 7 | 23 | 2021-07-23 | 1412404 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken
21-0111832 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2021-08-31 | 1459347 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0114930 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2021-09-08 | 1464950 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0119388 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2021-09-18 | 1474679 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0132482 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 18 | 2021-10-18 | 1500990 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0134691 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2021-10-21 | 1504702 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0135639 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1507752 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0136215 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509622 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0138161 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2021-10-26 | 1521094 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0138529 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2021-10-27 | 1522573 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
21-0140512 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2021-11-01 | 1526893 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0140611 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2021-11-01 | 1527164 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0157623 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transmission line | 12 | 13 | 2021-12-13 | 1568889 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157707 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569255 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0158936 | Equipment Failure/Involved | Overhead | Transformer | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2021-12-15 | 1573459 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦BurnedOpen
21-0160204 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2021-12-22 | 1579423 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0160519 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581093 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0161069 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585518 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161455 | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2021-12-28 | 1587489 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Deteriorated
22-0005562 | Vegetation | Tree - fell into line | Bushing | Broken | 2021 | Tier 3 - Extreme | Transformer only | 12 | 27 | 2021-12-27 | 1593144 | Sus | N | Vegetation¦Treefellintoline¦Bushing¦Broken
22-0006031 | Vegetation | Tree - branch fell on line | Jumper | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1594950 | Sus | N | Vegetation¦Treebranchfellonline¦Jumper¦Broken
22-0006686 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1596387 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0007204 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2022-01-06 | 1596927 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0007587 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2022 | Tier 3 - Extreme | Transformer only | 1 | 8 | 2022-01-08 | 1598072 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
22-0007741 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2022-01-09 | 1598577 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0017431 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2022-02-02 | 1618868 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0021101 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2022-02-10 | 1625083 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0048565 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 14 | 2022-04-14 | 1672887 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0050916 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 18 | 2022-04-18 | 1675355 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0052228 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2022-04-20 | 1677800 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0056432 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 4 | 30 | 2022-04-30 | 1685240 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0057055 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 2 | 2022-05-02 | 1686658 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0065225 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 23 | 2022-05-23 | 1708004 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0069105 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 2 | 2022-06-02 | 1716252 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0081358 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2022-07-02 | 1747772 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0081996 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 7 | 5 | 2022-07-05 | 1749404 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0086303 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2022-07-17 | 1758698 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0089566 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 7 | 25 | 2022-07-25 | 1765298 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0100153 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2022-08-20 | 1786357 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0102754 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2022-08-28 | 1793526 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0103883 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 31 | 2022-08-31 | 1795441 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0106121 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 9 | 5 | 2022-09-05 | 1800175 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦FailedFaulted
22-0116905 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 1 | 2022-10-01 | 1825578 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0120130 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2022-10-11 | 1834773 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0123210 | Animal | Squirrel | Cutout, fuse holder | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2022-10-20 | 1841386 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
22-0125654 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 10 | 28 | 2022-10-28 | 1847590 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
22-0132767 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2022-11-19 | 1865793 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
22-0138176 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1881071 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0139141 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2022-12-12 | 1886727 | Sus | N | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
22-0139843 | Equipment Failure/Involved | Overhead | Transformer | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 12 | 14 | 2022-12-14 | 1888928 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground
22-0139958 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2022-12-14 | 1889481 | Sus | N | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
22-0141500 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898037 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0141527 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898125 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0141704 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898755 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0141921 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2022-12-28 | 1900140 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0142773 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1905534 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0003722 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2015-01-10 | 1161910 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0006769 | Equipment Failure/Involved | Other | Crossarm, Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2015-01-23 | 1167798 | Sus | N | EquipmentFailureInvolved¦Other¦CrossarmWood¦Broken
15-0028338 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2015-04-21 | 1222681 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0032437 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2015-05-07 | 1230276 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0041762 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 17 | 2015-06-17 | 1252470 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0042958 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2015-06-24 | 1255561 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0044908 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2015-07-02 | 1261561 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0045476 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 4 | 2015-07-04 | 1262833 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0046038 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2015-07-07 | 1264334 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0046547 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2015 | Tier 3 - Extreme | Transformer only | 7 | 9 | 2015-07-09 | 1265560 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
15-0047250 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 13 | 2015-07-13 | 1267549 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0049009 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2015-07-20 | 1273474 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0052107 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2015-08-01 | 1281289 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0052231 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 3 | 2015-08-03 | 1281751 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0068027 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2015-10-05 | 1317139 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0069069 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2015 | Tier 2 - Elevated | Transformer only | 10 | 8 | 2015-10-08 | 1318952 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
15-0069350 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 10 | 2015-10-10 | 1319509 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0074307 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2015-10-30 | 1331600 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0083009 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2015-12-06 | 1354564 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦Normal
15-0085619 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2015-12-16 | 1364863 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0086505 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2015-12-21 | 1368228 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086552 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2015-12-21 | 1368260 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0005977 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385780 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0011082 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2016-02-06 | 1399528 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
16-0013503 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406052 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013843 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2016-02-18 | 1407840 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0013873 | Environmental/External | Lightning | Transformer (UG) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1408288 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(UG)¦FailedFaulted
16-0013890 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2016-02-18 | 1408379 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
16-0015635 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2016-02-25 | 1412189 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018041 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on object | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418779 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonobject
16-0018107 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Transmission line | 3 | 5 | 2016-03-05 | 1420516 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0018236 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1419315 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0018499 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2016-03-06 | 1422271 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0018782 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 7 | 2016-03-07 | 1423342 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018939 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 7 | 2016-03-07 | 1424111 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0020848 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2016-03-12 | 1429747 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0021623 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2016 | Tier 2 - Elevated | Transformer only | 3 | 15 | 2016-03-15 | 1431800 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
16-0025146 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 3 | 30 | 2016-03-30 | 1441844 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0031305 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2016-04-25 | 1458260 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0031665 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Transformer only | 4 | 26 | 2016-04-26 | 1459461 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0032009 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2016-04-27 | 1460176 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
16-0034224 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 5 | 2016-05-05 | 1465416 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0035025 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2016-05-10 | 1467417 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0035588 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2016-05-12 | 1468531 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0036093 | Animal | Other | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 15 | 2016-05-15 | 1469894 | Sus | Y | Animal¦Other¦Fuse¦FailedFaulted
16-0036336 | 3rd Party | Customer Equipment | Customer Equipment | Bent or Twisted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 16 | 2016-05-16 | 1470647 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦BentorTwisted
16-0041046 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 4 | 2016-06-04 | 1482738 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
16-0043254 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2016-06-14 | 1488986 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0050004 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2016-07-14 | 1510176 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0053400 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2016-07-28 | 1518005 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
16-0057528 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2016-08-16 | 1527021 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0067233 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2016-09-24 | 1547116 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0072767 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562197 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0072983 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1563444 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0080075 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2016-11-15 | 1581793 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0080236 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2016-11-16 | 1582149 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0081530 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 11 | 21 | 2016-11-21 | 1586859 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0081866 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2016-11-23 | 1587628 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0081933 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2016-11-23 | 1587709 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0084404 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 7 | 2016-12-07 | 1596236 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0084469 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2016-12-07 | 1596575 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0002726 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2017-01-01 | 1614328 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0002796 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 2 | 2017-01-02 | 1614781 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0003462 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1617530 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0003705 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1618586 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005082 | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 8 | 2017-01-08 | 1624294 | Sus | N | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Broken
17-0005492 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626728 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0005562 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626580 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006549 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632976 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006774 | Environmental/External | Flood/Erosion | Other | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1634053 | Sus | N | EnvironmentalExternal¦FloodErosion¦Other¦Normal
17-0007342 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2017-01-10 | 1637947 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
17-0009643 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2017-01-17 | 1645386 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0010140 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1646836 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Together
17-0011400 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653271 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0011872 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655353 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0012821 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1659135 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0016200 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2017-01-30 | 1670827 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0019337 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683054 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0019643 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 2 | 9 | 2017-02-09 | 1683928 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
17-0020703 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2017-02-13 | 1687479 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023434 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1694745 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024965 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1708009 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0025759 | 3rd Party | Customer Equipment | Customer Equipment | Burned Open | 2017 | Tier 3 - Extreme | Transformer only | 2 | 22 | 2017-02-22 | 1711104 | Sus | N | 3rdParty¦CustomerEquipment¦CustomerEquipment¦BurnedOpen
17-0025872 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2017-02-23 | 1711506 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0026883 | 3rd Party | Customer Equipment | Customer Equipment | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2017-02-26 | 1714356 | Sus | N | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Broken
17-0028315 | 3rd Party | Vehicle | Anchor or Guy | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2017-03-04 | 1719290 | Sus | N | 3rdParty¦Vehicle¦AnchororGuy¦Normal
17-0032071 | Equipment Failure/Involved | Overhead | Other | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2017-03-20 | 1730850 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
17-0033898 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2017-03-26 | 1736094 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦Broken
17-0040578 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2017-04-16 | 1758787 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
17-0041074 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 4 | 18 | 2017-04-18 | 1760069 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
17-0047671 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 12 | 2017-05-12 | 1781053 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0047805 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 14 | 2017-05-14 | 1781851 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0053879 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2017-06-09 | 1800184 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0055929 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 17 | 2017-06-17 | 1806676 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0060571 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 5 | 2017-07-05 | 1823773 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0065452 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2017-07-25 | 1839786 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0068679 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 8 | 2017-08-08 | 1848263 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0069668 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 11 | 2017-08-11 | 1850701 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0069731 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 11 | 2017-08-11 | 1850718 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0071464 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2017-08-19 | 1855210 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0075863 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 4 | 2017-09-04 | 1869629 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0078314 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 12 | 2017-09-12 | 1877506 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0085020 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1892941 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0087529 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1901338 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0087662 | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Burned/flashed | 2017 | Tier 2 - Elevated | Transformer only | 10 | 8 | 2017-10-08 | 1901667 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Burnedflashed
17-0088203 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 18 | 2017-10-18 | 1903049 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0089365 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1906774 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0091543 | Environmental/External | Fire, Forest/Grass | Transformer | Broken | 2017 | Tier 2 - Elevated | Transformer only | 10 | 31 | 2017-10-31 | 1913009 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Broken
17-0091636 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transmission line | 10 | 31 | 2017-10-31 | 1913338 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0095455 | Equipment Failure/Involved | Overhead | Other | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2017-11-16 | 1923502 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
17-0096274 | 3rd Party | Customer Equipment | Secondary | Arcing | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2017-11-19 | 1926000 | Sus | Y | 3rdParty¦CustomerEquipment¦Secondary¦Arcing
17-0099278 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2017-12-02 | 1933997 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0099767 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1935768 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0103265 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2017-12-25 | 1951064 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
18-0005096 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2018-01-10 | 6084 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
18-0019310 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2018-03-03 | 37057 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0019468 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2018-03-03 | 37513 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023419 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 45876 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0024804 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2018-03-21 | 49230 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0025659 | Equipment Failure/Involved | Overhead | Switch (OH) | Arcing | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 50705 | Sus | N | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Arcing
18-0027468 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2018-03-28 | 55298 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0028425 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2018-04-02 | 58017 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
18-0030195 | Equipment Failure/Involved | Overhead | Insulator | Arcing | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2018-04-07 | 61676 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Arcing
18-0030195 | Equipment Failure/Involved | Overhead | Insulator | Arcing | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2018-04-07 | 61676 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Arcing
18-0030722 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2018-04-09 | 63379 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
18-0037469 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 5 | 1 | 2018-05-01 | 77869 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
18-0037788 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 5 | 2 | 2018-05-02 | 78448 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
18-0037973 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 3 | 2018-05-03 | 78847 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0039520 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 5 | 9 | 2018-05-09 | 82332 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0044589 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2018-05-25 | 94272 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0046145 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2018-05-31 | 98093 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0047488 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2018-06-05 | 101580 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
18-0048739 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2018-06-08 | 104024 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0049001 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2018-06-08 | 104500 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0053839 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2018-06-23 | 116038 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
18-0056098 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 1 | 2018-07-01 | 122460 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0059717 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2018-07-13 | 131290 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0081461 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2018 | Tier 2 - Elevated | Transformer only | 9 | 19 | 2018-09-19 | 177566 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
18-0090444 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2018-10-15 | 195402 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0096524 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2018-11-02 | 207304 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0097899 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2018-11-07 | 210570 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0099169 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 213865 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0099373 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 214474 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal
18-0100666 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 11 | 17 | 2018-11-17 | 217343 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0101246 | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218609 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Burnedflashed
18-0101292 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218659 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104985 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228702 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0107786 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2018-12-07 | 235442 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109728 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 17 | 2018-12-17 | 242631 | Sus | N | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0110708 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2018-12-26 | 247289 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0111118 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 12 | 30 | 2018-12-30 | 249697 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0003439 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2019 | Tier 2 - Elevated | Transformer only | 1 | 1 | 2019-01-01 | 251415 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
19-0005153 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255424 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0006220 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2019-01-08 | 260378 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
19-0007682 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2019-01-10 | 262744 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009660 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 267002 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009887 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 267449 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0010845 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 1 | 17 | 2019-01-17 | 273005 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0013037 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2019-01-22 | 278714 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0014840 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2019-01-27 | 282207 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0016901 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286221 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
19-0017632 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2019-02-03 | 288657 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018706 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292936 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0020552 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298003 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonground
19-0020697 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298739 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020709 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 2 | 10 | 2019-02-10 | 298603 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0022690 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 305833 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0023372 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 308290 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0024575 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314476 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0024684 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314678 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0024738 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314894 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025196 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 316323 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025726 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 318115 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025836 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 2 | 19 | 2019-02-19 | 318283 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0027478 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 23 | 2019-02-23 | 321866 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0029825 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2019-03-01 | 328995 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0033608 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 3 | 13 | 2019-03-13 | 338656 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0037703 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348917 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
19-0047201 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2019-04-29 | 370412 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0048993 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2019-05-05 | 374005 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0052574 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2019-05-16 | 381951 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0063896 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 6 | 2019-06-06 | 400064 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal
19-0064222 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2019-06-07 | 400674 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0065377 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2019-06-10 | 403792 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
19-0071274 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 23 | 2019-06-23 | 427157 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0075049 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2019-07-07 | 442198 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0076324 | Company Initiated | Operating error | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2019-08-15 | 511897 | Sus | Y | CompanyInitiated¦Operatingerror¦ConductorOverhead¦Normal
19-0079816 | Company Initiated | Operating error | Fuse | Normal | 2019 | Tier 3 - Extreme | Transformer only | 7 | 22 | 2019-07-22 | 466201 | Sus | Y | CompanyInitiated¦Operatingerror¦Fuse¦Normal
19-0080453 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 7 | 23 | 2019-07-23 | 469749 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
19-0084586 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 5 | 2019-08-05 | 485271 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0086593 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2019-08-10 | 501686 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0094276 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 8 | 30 | 2019-08-30 | 549287 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
19-0103779 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2019-09-25 | 615436 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0103993 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 9 | 25 | 2019-09-25 | 614923 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
19-0110938 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2019-10-13 | 655569 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
19-0116815 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2019-10-26 | 680786 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0126593 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2019-11-19 | 710522 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0128318 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 25 | 2019-11-25 | 714263 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0130032 | Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 718547 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Brokenwireonground
19-0130064 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 720442 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130821 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722801 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0132926 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2019-12-03 | 728862 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0134822 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2019-12-07 | 732646 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0134962 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2019-12-07 | 733447 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0136599 | Environmental/External | Lightning | Transformer (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2019-12-14 | 739918 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Brokenwireonground
20-0005252 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2020 | Tier 2 - Elevated | Transformer only | 1 | 5 | 2020-01-05 | 755022 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
20-0006148 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2020-01-08 | 756850 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0011908 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2020-01-21 | 767427 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0016380 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2020-02-02 | 775990 | Sus | N | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
20-0018557 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2020-02-07 | 780096 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0020304 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782305 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0027460 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 29 | 2020-02-29 | 820396 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0033041 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 14 | 2020-03-14 | 855812 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0035869 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2020-03-24 | 863973 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0044889 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2020-04-27 | 902083 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0045019 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2020-04-27 | 902580 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0045300 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 4 | 28 | 2020-04-28 | 903155 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0050003 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 13 | 2020-05-13 | 913378 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0055492 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2020-05-29 | 924915 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0063199 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2020-06-19 | 942795 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0064664 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2020 | Tier 3 - Extreme | Transformer only | 6 | 24 | 2020-06-24 | 946601 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
20-0065691 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 6 | 27 | 2020-06-27 | 948639 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0070926 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2020-07-12 | 962703 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0081667 | Equipment Failure/Involved | Overhead | Other | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2020-08-10 | 989913 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
20-0084119 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2020-08-14 | 999735 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
20-0086442 | Environmental/External | Lightning | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2020-08-17 | 1017618 | Sus | Y | EnvironmentalExternal¦Lightning¦PoleWood¦Burnedflashed
20-0087359 | 3rd Party | Customer Equipment | Customer Equipment | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2020-08-19 | 1022853 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Broken
20-0096105 | Environmental/External | Fire, Forest/Grass | Transformer | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 19 | 2020-08-19 | 1063646 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦Normal
20-0100226 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1088033 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0104851 | Equipment Failure/Involved | Overhead | Other | Malfunctioning | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2020-10-03 | 1110395 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Malfunctioning
20-0111428 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2020-10-21 | 1122473 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0112510 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1125748 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0117019 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transformer only | 11 | 4 | 2020-11-04 | 1135845 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0124949 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 25 | 2020-11-25 | 1154349 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0125152 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 25 | 2020-11-25 | 1154523 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
20-0125442 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2020-11-26 | 1155017 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0125478 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2020-11-27 | 1155083 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0125673 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 11 | 28 | 2020-11-28 | 1155701 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0126642 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2020-12-02 | 1157655 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0131457 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2020-12-22 | 1196976 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0005092 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2021-01-05 | 1204321 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0008489 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 14 | 2021-01-14 | 1210162 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011494 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2021-01-19 | 1216988 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0011783 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1219307 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0014861 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226767 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0015430 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1231553 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0015929 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234501 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016224 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233602 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0019909 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1243681 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0020017 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226477 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020489 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2021-02-01 | 1244907 | Sus | N | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
21-0023475 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Transformer only | 2 | 9 | 2021-02-09 | 1251486 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0025009 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2021-02-12 | 1253719 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0027611 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2021-02-20 | 1258319 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0036154 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2021-03-13 | 1281611 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
21-0036159 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 13 | 2021-03-13 | 1281374 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0045049 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 5 | 2021-04-05 | 1307433 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0048792 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2021-04-15 | 1317253 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0054924 | 3rd Party | Vehicle | Other | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2021-04-29 | 1337049 | Sus | N | 3rdParty¦Vehicle¦Other¦Broken
21-0058735 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2021-05-07 | 1343614 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0061707 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 14 | 2021-05-14 | 1349550 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0062402 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2021 | Tier 3 - Extreme | Transformer only | 5 | 17 | 2021-05-17 | 1351761 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0090203 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 7 | 15 | 2021-07-15 | 1405391 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
21-0095855 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2021-07-27 | 1416830 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0097131 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 29 | 2021-07-29 | 1420516 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0099889 | Environmental/External | Fire, Forest/Grass | Circuit Breaker | Normal | 2021 | Tier 2 - Elevated | Substation - Transmission | 8 | 4 | 2021-08-04 | 1433873 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦CircuitBreaker¦Normal
21-0101527 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 7 | 2021-08-07 | 1436462 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0107594 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2021-08-20 | 1448966 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0112367 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2021-09-01 | 1460317 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0115685 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2021-09-10 | 1466928 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0120662 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2021-09-21 | 1477428 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
21-0128999 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1493625 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0129483 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1493717 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135239 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2021-10-22 | 1505963 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136989 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1515674 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0139596 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2021-10-29 | 1524902 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0143910 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2021-11-09 | 1538553 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0149290 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2021-11-21 | 1552648 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0156995 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1565733 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157511 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568405 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0157637 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568948 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0158282 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1571977 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158704 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573341 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0159875 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 12 | 20 | 2021-12-20 | 1578069 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0160706 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581875 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160824 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582569 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161829 | Environmental/External | Ice or snow | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 30 | 2021-12-30 | 1589779 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Transformer¦FailedFaulted
22-0005036 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2021-12-29 | 1589122 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
22-0006139 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585256 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0008068 | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | 2022 | Tier 3 - Extreme | Transformer only | 1 | 9 | 2022-01-09 | 1598928 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Burnedflashed
22-0010532 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 1 | 17 | 2022-01-17 | 1604117 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0012748 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607644 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0023172 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2022-02-16 | 1629318 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0033745 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 14 | 2022-03-14 | 1648400 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0036046 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2022-03-19 | 1651778 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing
22-0036046 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2022-03-19 | 1651778 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing
22-0045141 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2022-04-10 | 1667556 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
22-0045178 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 4 | 10 | 2022-04-10 | 1667694 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0045822 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669542 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0048588 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 14 | 2022-04-14 | 1672543 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0051315 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2022-05-25 | 1710406 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
22-0055335 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2022-04-27 | 1683392 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0065840 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 5 | 24 | 2022-05-24 | 1709101 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0066532 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 25 | 2022-05-25 | 1710688 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0070309 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Contaminated | 2022 | Tier 2 - Elevated | Transformer only | 6 | 5 | 2022-06-05 | 1719520 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Contaminated
22-0071156 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2022-06-07 | 1721618 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0073155 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 11 | 2022-06-11 | 1728248 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0081605 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 4 | 2022-07-04 | 1748562 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083578 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2022-07-09 | 1752316 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0085713 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 7 | 15 | 2022-07-15 | 1756765 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0091323 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2022-07-29 | 1768127 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0093943 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2022-08-04 | 1773544 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0093966 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Transformer only | 8 | 4 | 2022-08-04 | 1773636 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
22-0096107 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2022 | Tier 2 - Elevated | Transformer only | 8 | 10 | 2022-08-10 | 1778192 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
22-0097362 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2022-08-14 | 1780895 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100219 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2022-08-21 | 1786664 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0102290 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 26 | 2022-08-26 | 1792166 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0102703 | Company Initiated | Construction Activity/equip, company | Transformer | Normal | 2022 | Tier 2 - Elevated | Transformer only | 9 | 16 | 2022-09-16 | 1812546 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Normal
22-0111832 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 9 | 18 | 2022-09-18 | 1815485 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0115521 | 3rd Party | Vehicle | Fuse | Normal | 2022 | Tier 3 - Extreme | Transformer only | 9 | 27 | 2022-09-27 | 1822946 | Sus | Y | 3rdParty¦Vehicle¦Fuse¦Normal
22-0117994 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 5 | 2022-10-05 | 1828907 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0119370 | Animal | Squirrel | Cutout, fuse holder | Burned/flashed | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2022-10-08 | 1831802 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Burnedflashed
22-0124417 | Animal | Other | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2022-10-24 | 1844592 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
22-0134979 | Animal | Other | Transformer (OH) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2022-11-29 | 1871647 | Sus | Y | Animal¦Other¦Transformer(OH)¦Normal
22-0137516 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2022-12-07 | 1878517 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0138065 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880355 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138430 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882589 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0139149 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1886815 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0139296 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 12 | 12 | 2022-12-12 | 1887195 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0139317 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1886399 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Burnedflashed
22-0140651 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 12 | 19 | 2022-12-19 | 1892889 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
15-0014875 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 2 | 22 | 2015-02-22 | 1194085 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0018010 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2015-03-07 | 1200526 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0020384 | Equipment Failure/Involved | Other | Transformer | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2015-03-18 | 1205009 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Burnedflashed
15-0023363 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2015-03-31 | 1210793 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0024782 | Vegetation | Tree - fell into line | Secondary | Bent or Twisted | 2015 | Tier 2 - Elevated | Transformer only | 4 | 7 | 2015-04-07 | 1214631 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦BentorTwisted
15-0032068 | Vegetation | Tree - branch fell on line | Secondary | Broken | 2015 | Tier 2 - Elevated | Transformer only | 5 | 6 | 2015-05-06 | 1229717 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Broken
15-0032305 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2015-05-06 | 1230035 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0035589 | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2015-05-21 | 1237763 | Sus | Y | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Brokenwireonground
15-0042037 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 19 | 2015-06-19 | 1253150 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
15-0042263 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 20 | 2015-06-20 | 1253701 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
15-0044384 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 6 | 30 | 2015-06-30 | 1259690 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0045147 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 2 | 2015-07-02 | 1262012 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0054155 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 10 | 2015-08-10 | 1286115 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
15-0054682 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 13 | 2015-08-13 | 1287608 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0055332 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2015-08-16 | 1289297 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0062603 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 21 | 2015-09-21 | 1309642 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
15-0063582 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 9 | 25 | 2015-09-25 | 1311940 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0067694 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2015-10-03 | 1316295 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0071345 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324421 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0072322 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 20 | 2015-10-20 | 1326903 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0075574 | Animal | Other | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 4 | 2015-11-04 | 1335365 | Sus | Y | Animal¦Other¦Fuse¦FailedFaulted
15-0077231 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2015-11-11 | 1339409 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0079864 | Animal | Squirrel | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2015-11-21 | 1346474 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0080563 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 24 | 2015-11-24 | 1347856 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
15-0083777 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1356834 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083951 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357317 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0086107 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2015-12-18 | 1366297 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0086791 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2015-12-22 | 1368785 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0087419 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2015-12-26 | 1371984 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0006967 | Animal | Bird found | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2016-01-20 | 1388885 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
16-0010405 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2016-02-03 | 1397965 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0012875 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2016-02-16 | 1404181 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0012897 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 2 | 16 | 2016-02-16 | 1404289 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0013867 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1408518 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018177 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1420933 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0019929 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2016-03-10 | 1426496 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
16-0020554 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1428018 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0020997 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430346 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0022739 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2016-03-20 | 1434540 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0023061 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 3 | 21 | 2016-03-21 | 1435383 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
16-0027881 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 4 | 11 | 2016-04-11 | 1449082 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
16-0029258 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2016 | Tier 2 - Elevated | Transformer only | 4 | 17 | 2016-04-17 | 1452445 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
16-0035102 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2016-05-10 | 1467565 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Burnedflashed
16-0036772 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Transformer only | 5 | 18 | 2016-05-18 | 1471926 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0037924 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 23 | 2016-05-23 | 1475498 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0039945 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2016-05-31 | 1479793 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
16-0041148 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2016-06-05 | 1483259 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
16-0042042 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2016-06-08 | 1485537 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0046273 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 28 | 2016-06-28 | 1497292 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
16-0048243 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 6 | 2016-07-06 | 1502045 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
16-0056780 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 8 | 11 | 2016-08-11 | 1525099 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0061876 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2016-09-02 | 1535708 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
16-0065050 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 15 | 2016-09-15 | 1542571 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
16-0071875 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1558274 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
16-0072566 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561380 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0084918 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2016-12-10 | 1598311 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0084982 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2016-12-10 | 1598509 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0085655 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602254 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0085731 | Vegetation | Tree - fell into line | Service conductor | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602797 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
16-0086763 | 3rd Party | Fire, house or bldg. | Secondary | Burned Open | 2016 | Tier 2 - Elevated | Transformer only | 12 | 22 | 2016-12-22 | 1609354 | Sus | N | 3rdParty¦Firehouseorbldg¦Secondary¦BurnedOpen
16-0087371 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2016-12-30 | 1613191 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0002709 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2017-01-01 | 1614267 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0004577 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2017-01-07 | 1620942 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0004852 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1622283 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0004974 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2017-01-08 | 1622814 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0005581 | Vegetation | Tree - branch fell on line | Transformer | Normal | 2017 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2017-01-08 | 1625487 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦Normal
17-0005730 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628985 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006597 | Environmental/External | Flood/Erosion | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1633309 | Sus | N | EnvironmentalExternal¦FloodErosion¦ConductorOverhead¦Brokenwireonground
17-0007320 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638322 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007935 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640572 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0010483 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 1 | 18 | 2017-01-18 | 1647964 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0011776 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1654801 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013433 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1656171 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0013603 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662752 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0013895 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664378 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0017464 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2017-02-04 | 1674879 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0018072 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677340 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018097 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677406 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019118 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682039 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0019472 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683091 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0019548 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683721 | Sus | N | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
17-0023881 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703487 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0024706 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705166 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0027081 | Equipment Failure/Involved | Overhead | Transformer |  | 2017 | Tier 2 - Elevated | Transformer only | 2 | 27 | 2017-02-27 | 1715062 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦
17-0028483 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2017-03-05 | 1719943 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0030270 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 3 | 12 | 2017-03-12 | 1725565 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0034804 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2017 | Tier 2 - Elevated | Transformer only | 3 | 29 | 2017-03-29 | 1738395 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
17-0038222 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1751567 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0038297 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2017-04-08 | 1752694 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0040614 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 16 | 2017-04-16 | 1758911 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0041260 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 18 | 2017-04-18 | 1760596 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0043783 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 28 | 2017-04-28 | 1769724 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0045011 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 5 | 3 | 2017-05-03 | 1773707 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0047504 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 12 | 2017-05-12 | 1780596 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0049277 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 19 | 2017-05-19 | 1785790 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0051591 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2017 | Tier 2 - Elevated | Transformer only | 5 | 30 | 2017-05-30 | 1793548 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
17-0055113 | Equipment Failure/Involved | Other | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2017-06-14 | 1804016 | Sus | Y | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Broken
17-0056779 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2017-06-19 | 1811577 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
17-0059699 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2017-07-14 | 1831352 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
17-0060068 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2017-07-01 | 1822176 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
17-0061479 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 7 | 8 | 2017-07-08 | 1827082 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0079671 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2017-09-18 | 1880795 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0086754 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899364 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed
17-0087374 | Environmental/External | Fire, Forest/Grass | Secondary | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2017-10-14 | 1900807 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Secondary¦Brokenwireonground
17-0087506 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 12 | 2017-10-12 | 1901302 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken
17-0087735 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2017-10-16 | 1901786 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0088176 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 18 | 2017-10-18 | 1903029 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0088421 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1903645 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
17-0088578 | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1904083 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Burnedflashed
17-0088763 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2017-10-19 | 1904654 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0089052 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 10 | 20 | 2017-10-20 | 1905619 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0089061 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1904968 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0091941 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2017-11-02 | 1914198 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
17-0093730 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2017-11-08 | 1918818 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0098191 | Animal | Other | Cutout, fuse holder | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2017-11-28 | 1931263 | Sus | Y | Animal¦Other¦Cutoutfuseholder¦Normal
17-0099240 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2017-12-02 | 1933891 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0009564 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2018-01-27 | 15217 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0011666 | 3rd Party | Customer Equipment | Fuse | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2018-02-05 | 19690 | Sus | N | 3rdParty¦CustomerEquipment¦Fuse¦Normal
18-0014928 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2018-02-16 | 25700 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0018302 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 33911 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0018403 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 34193 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0020862 | Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on object | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2018-03-08 | 40208 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonobject
18-0025307 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2018-03-22 | 50237 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0040399 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 11 | 2018-05-11 | 84129 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0044612 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 5 | 26 | 2018-05-26 | 94349 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0049822 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 6 | 11 | 2018-06-11 | 106722 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0050466 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 13 | 2018-06-13 | 108006 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
18-0051829 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 6 | 18 | 2018-06-18 | 111668 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0055899 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2018-06-30 | 121587 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0057593 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2018-07-06 | 125809 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0059685 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2018-07-13 | 131237 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0060399 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2018-07-17 | 133397 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0060637 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 17 | 2018-07-17 | 133764 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0066405 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2018-08-03 | 148017 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0067319 | 3rd Party | Vehicle | Connector or Splice (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2018-08-07 | 150372 | Sus | Y | 3rdParty¦Vehicle¦ConnectororSplice(OH)¦Normal
18-0075683 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2018-08-31 | 166375 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075782 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2018-09-01 | 166646 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0076904 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2018-09-05 | 168746 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0081000 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2018-09-18 | 176815 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0081711 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2018-09-20 | 178107 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0086414 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2018-10-03 | 187624 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
18-0087526 | Equipment Failure/Involved | Overhead | Anchor or Guy | Bent or Twisted | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2018-10-05 | 189329 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦BentorTwisted
18-0100881 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217946 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101226 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2018 | Tier 3 - Extreme | Transformer only | 11 | 19 | 2018-11-19 | 218570 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
18-0101788 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219891 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102308 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2018-11-22 | 221876 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0103776 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 225541 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
19-0005100 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255330 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0005909 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2019-01-07 | 259546 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0007563 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2019-01-10 | 262480 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009310 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2019-01-15 | 266342 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0010604 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 272121 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010673 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 272969 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0010996 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 273887 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011472 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 270135 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0011647 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 1 | 17 | 2019-01-17 | 274779 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0014200 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2019-01-24 | 280802 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017499 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2019-02-03 | 288456 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0017500 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2019-02-03 | 288465 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017683 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289376 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
19-0017894 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289644 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018385 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292215 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0018690 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 293014 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019338 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2019-02-05 | 293092 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0019377 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 294873 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020526 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 297820 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0021972 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301494 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0023919 | Company Initiated | Contact with High Voltage, company |  | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 14 | 2019-02-14 | 310902 | Sus | N | CompanyInitiated¦ContactwithHighVoltagecompany¦¦FailedFaulted
19-0025643 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 317271 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0025653 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 317462 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0027564 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2019-02-24 | 322329 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028654 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325126 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028805 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2019-02-27 | 326194 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0029171 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 327396 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
19-0031458 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 333076 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0032041 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2019-03-08 | 334352 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0032245 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2019-03-09 | 334897 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0034245 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2019-03-15 | 340375 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0034716 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Transformer only | 3 | 18 | 2019-03-18 | 341998 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0037044 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2019-03-26 | 347594 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
19-0037976 | 3rd Party | Metallic Balloon | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2019-03-28 | 349598 | Sus | N | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Normal
19-0039235 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 4 | 2 | 2019-04-02 | 352623 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0041199 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2019-04-10 | 357648 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0049787 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2019-05-07 | 375760 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0049845 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2019-05-07 | 376040 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0051868 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 5 | 14 | 2019-05-14 | 380419 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0052981 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2019-05-16 | 382846 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0057778 | Animal | Bird found | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2019-05-26 | 390702 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
19-0061904 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2019 | Tier 3 - Extreme | Transformer only | 6 | 3 | 2019-06-03 | 396519 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
19-0062429 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2019-06-04 | 397180 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0062574 | Vegetation | Tree - branch fell on line | Insulator | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 4 | 2019-06-04 | 397461 | Sus | Y | Vegetation¦Treebranchfellonline¦Insulator¦Broken
19-0062766 | Equipment Failure/Involved | Substation | Other | Malfunctioning | 2019 | Tier 2 - Elevated | Transmission line | 6 | 4 | 2019-06-04 | 397889 | Sus | Y | EquipmentFailureInvolved¦Substation¦Other¦Malfunctioning
19-0064853 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 6 | 9 | 2019-06-09 | 402516 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0068389 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 6 | 16 | 2019-06-16 | 417098 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
19-0069864 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2019-06-19 | 421963 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0072921 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 27 | 2019-06-27 | 432783 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0077011 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2019-07-13 | 447866 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0103077 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 24 | 2019-09-24 | 611194 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0104163 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2019-09-26 | 618773 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Burnedflashed
19-0110850 | Animal | Squirrel | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2019-10-12 | 655279 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
19-0123660 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2019-11-11 | 704642 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0130160 | Vegetation | Tree - bark fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 720816 | Sus | Y | Vegetation¦Treebarkfellintoline¦PoleWood¦Brokenwireonground
19-0130211 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 718444 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131020 | Animal | Squirrel | Pole-Wood | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2019-11-29 | 723346 | Sus | Y | Animal¦Squirrel¦PoleWood¦Normal
19-0131999 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2019-12-01 | 726050 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0132323 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2019-12-02 | 727489 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0134791 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 732329 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0136208 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2019-12-12 | 737515 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0138093 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2019-12-28 | 751564 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0005289 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 1 | 5 | 2020-01-05 | 755142 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0006588 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2020-01-08 | 757457 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0009471 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2020-01-15 |  | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0011065 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2020-01-18 | 765627 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0016403 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2020-02-02 | 775731 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0019469 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 783566 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0024606 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2020-02-21 | 798258 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0026431 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2020-02-27 | 815193 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
20-0031183 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2020-03-11 | 844795 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032271 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 852194 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0032724 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 853643 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032989 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855559 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground
20-0033447 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853938 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0033538 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 857104 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
20-0037889 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2020-04-02 | 878182 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Deteriorated
20-0038804 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2020-04-06 | 883564 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0040709 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2020-04-12 | 894299 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0045283 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2020 | Tier 2 - Elevated | Transformer only | 4 | 28 | 2020-04-28 | 903199 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
20-0049468 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 12 | 2020-05-12 | 912120 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0049857 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 13 | 2020-05-13 | 913175 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0053712 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 5 | 24 | 2020-05-24 | 920586 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0058248 | Company Initiated | Operating error | Recloser | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2020-06-05 | 932011 | Sus | Y | CompanyInitiated¦Operatingerror¦Recloser¦Normal
20-0060037 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 11 | 2020-06-11 | 936468 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0062875 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2020-06-18 | 942214 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
20-0067402 | Animal | Bird found | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 7 | 1 | 2020-07-01 | 956199 | Sus | Y | Animal¦Birdfound¦Transformer¦FailedFaulted
20-0081834 | Animal | Squirrel | Cutout, fuse holder | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2020-08-10 | 991048 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
20-0084014 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2020-08-14 | 1003269 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
20-0085586 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1014307 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0088530 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2020-08-21 | 1026377 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
20-0091371 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2020-08-29 | 1040852 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0095730 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2020-09-09 | 1062390 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0096690 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 11 | 2020-09-11 | 1065295 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0104180 | Equipment Failure/Involved | Overhead | Service conductor | Broken | 2020 | Tier 2 - Elevated | Transformer only | 10 | 1 | 2020-10-01 | 1105715 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Broken
20-0121804 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2020 | Tier 2 - Elevated | Transformer only | 11 | 17 | 2020-11-17 | 1146998 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
20-0122311 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2020-11-18 | 1148227 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
20-0128377 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167310 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0128544 | Equipment Failure/Involved | Overhead | Transformer | Broken, wire on object | 2020 | Tier 2 - Elevated | Transformer only | 12 | 7 | 2020-12-07 | 1167414 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonobject
20-0128594 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2020-12-07 | 1168868 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0009370 | 3rd Party | Other | Service conductor | Normal | 2021 | Tier 2 - Elevated | Transformer only | 1 | 16 | 2021-01-16 | 1211497 | Sus | N | 3rdParty¦Other¦Serviceconductor¦Normal
21-0010058 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214167 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0010085 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214144 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0011815 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1219380 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0013175 | 3rd Party | Other | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2021-01-23 | 1221538 | Sus | N | 3rdParty¦Other¦ConductorOverhead¦Normal
21-0013669 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223696 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0013723 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223862 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0013858 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224124 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0015735 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1230347 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0016363 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1232107 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016555 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1236407 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0018247 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2021-01-29 | 1240943 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0019243 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1242970 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0020054 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 31 | 2021-01-31 | 1244071 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0027769 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 2 | 20 | 2021-02-20 | 1258762 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0034318 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 3 | 10 | 2021-03-10 | 1276668 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0039987 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2021-03-23 | 1294386 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
21-0061766 | Environmental/External | Fire, Forest/Grass | Service conductor | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 5 | 15 | 2021-05-15 | 1349716 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Serviceconductor¦BurnedOpen
21-0064139 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Transformer only | 5 | 20 | 2021-05-20 | 1355087 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
21-0072160 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2021-06-09 | 1369616 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0072389 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2021-06-10 | 1369861 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0083668 | Vegetation | Tree - fell into line | Bushing | Broken | 2021 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2021-07-01 | 1390143 | Sus | Y | Vegetation¦Treefellintoline¦Bushing¦Broken
21-0085070 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2021-07-06 | 1392553 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0091212 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2021-07-17 | 1406766 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
21-0091249 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 7 | 17 | 2021-07-17 | 1406872 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0094214 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2021-07-23 | 1412037 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0098238 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 8 | 1 | 2021-08-01 | 1428181 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0104818 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2021-08-15 | 1443539 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(UG)¦Broken
21-0106012 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445319 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0107177 | Animal | Squirrel | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2021-08-20 | 1448226 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Broken
21-0110065 | Animal | Squirrel | Cutout, fuse holder | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2021-08-27 | 1455109 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦FailedFaulted
21-0116586 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2021-09-12 | 1470309 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0119275 | Animal | Squirrel | Fuse | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2021-09-18 | 1474463 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
21-0119425 | Equipment Failure/Involved | Underground | Bushing | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2021-09-18 | 1474879 | Sus | Y | EquipmentFailureInvolved¦Underground¦Bushing¦Burnedflashed
21-0120523 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2021-09-21 | 1477240 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0126325 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2021-10-05 | 1487905 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0128412 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492038 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0129403 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2021-10-11 | 1493857 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0131017 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 10 | 14 | 2021-10-14 | 1497374 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0132294 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 18 | 2021-10-18 | 1500494 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135741 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508601 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136674 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1515636 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0137277 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1513001 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0138824 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Transformer only | 10 | 26 | 2021-10-26 | 1522376 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0142587 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2021-11-04 | 1535196 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0144369 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2021-11-09 | 1539327 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0145208 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2021-11-13 | 1542195 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0146202 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2021-11-16 | 1546693 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0152143 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2021-11-27 | 1555041 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0158820 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1572984 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0158965 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1574474 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0160876 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582816 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161051 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585169 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
21-0161085 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584700 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161086 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585661 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0161771 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1589609 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161887 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1590099 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0004997 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591436 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005453 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1593526 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0006730 | Environmental/External | Ice or snow | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2022-01-06 | 1596454 | Sus | N | EnvironmentalExternal¦Iceorsnow¦PoleWood¦Broken
22-0014087 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2022-01-25 | 1611943 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0017304 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2022-02-01 | 1618721 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0019065 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2022-02-06 | 1622168 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0019065 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2022-02-06 | 1622168 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0029001 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2022-03-03 | 1640930 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0031703 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2022-03-09 | 1645484 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
22-0036580 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on object | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2022-03-21 | 1652924 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonobject
22-0045244 | Company Initiated | Personnel, company | Relay | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1668062 | Sus | N | CompanyInitiated¦Personnelcompany¦Relay¦Normal
22-0056493 | 3rd Party | Fire, house or bldg. | Service conductor | Broken, wire on ground | 2022 | Tier 2 - Elevated | Transformer only | 4 | 30 | 2022-04-30 | 1685423 | Sus | N | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Brokenwireonground
22-0056812 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 5 | 2 | 2022-05-02 | 1686383 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
22-0069479 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 6 | 2 | 2022-06-02 | 1716829 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0073857 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 13 | 2022-06-13 | 1730592 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0076975 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2022-06-22 | 1738184 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
22-0077233 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2022-06-22 | 1738887 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0078717 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 6 | 26 | 2022-06-26 | 1742527 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
22-0080672 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2022-06-30 | 1746581 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0082479 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2022-07-06 | 1750173 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
22-0085031 | 3rd Party | Customer Equipment | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 7 | 13 | 2022-07-13 | 1755631 | Sus | Y | 3rdParty¦CustomerEquipment¦Secondary¦Broken
22-0086085 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2022-07-16 | 1757629 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0091658 | Company Initiated | Personnel, company | Fuse | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2022-07-30 | 1769024 | Sus | Y | CompanyInitiated¦Personnelcompany¦Fuse¦Normal
22-0093316 | Company Initiated | Personnel, company | Fuse | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 3 | 2022-08-03 | 1772290 | Sus | Y | CompanyInitiated¦Personnelcompany¦Fuse¦Normal
22-0094998 | Company Initiated | Personnel, company | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2022-08-08 | 1775949 | Sus | Y | CompanyInitiated¦Personnelcompany¦ConductorOverhead¦Normal
22-0100059 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2022-08-20 | 1785857 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0101214 | Animal | Bird found | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2022-08-24 | 1788825 | Sus | Y | Animal¦Birdfound¦Cutoutfuseholder¦Broken
22-0104378 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2022-09-01 | 1796453 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0111681 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1814500 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0114528 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 24 | 2022-09-24 | 1820871 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0114654 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 9 | 25 | 2022-09-25 | 1821300 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
22-0129630 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1858486 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
22-0131280 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2022-11-15 | 1863202 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0138603 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1881270 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0139219 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885830 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0140770 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2022-12-20 | 1894336 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
22-0141787 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899667 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0142084 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2022-12-29 | 1901557 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0142156 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2022-12-30 | 1901789 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
22-0142170 | Vegetation | Tree - branch fell on line | Recloser | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2022-12-30 | 1901869 | Sus | N | Vegetation¦Treebranchfellonline¦Recloser¦Normal
15-0006933 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2015-01-24 | 1168117 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
15-0012282 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1185958 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0017374 | Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2015-03-04 | 1199450 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonground
15-0022692 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2015-03-27 | 1209043 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0022826 | Equipment Failure/Involved | Other | Jumper | Broken | 2015 | Tier 2 - Elevated | Transformer only | 3 | 29 | 2015-03-29 | 1209574 | Sus | N | EquipmentFailureInvolved¦Other¦Jumper¦Broken
15-0032375 | Environmental/External | Lightning | Connector or Splice (OH) | Normal | 2015 | Tier 2 - Elevated | Transmission line | 5 | 7 | 2015-05-07 | 1230380 | Sus | Y | EnvironmentalExternal¦Lightning¦ConnectororSplice(OH)¦Normal
15-0041111 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 15 | 2015-06-15 | 1251174 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
15-0051527 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 30 | 2015-07-30 | 1279961 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0053489 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 8 | 6 | 2015-08-06 | 1284325 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
15-0056574 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 21 | 2015-08-21 | 1292472 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0056710 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 8 | 22 | 2015-08-22 | 1292875 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0057068 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2015-08-24 | 1293927 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
15-0059972 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Transformer only | 9 | 8 | 2015-09-08 | 1302113 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0066032 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2015-09-28 | 1312929 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
15-0072751 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2015-10-22 | 1327844 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0075928 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 11 | 5 | 2015-11-05 | 1336163 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0076584 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2015-11-09 | 1337696 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
15-0076675 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2015-11-09 | 1337990 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0077679 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 13 | 2015-11-13 | 1340708 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0077911 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1341958 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
15-0078690 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2015-11-17 | 1344190 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0079603 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 11 | 20 | 2015-11-20 | 1346206 | Sus | Y | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0081477 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2015-11-27 | 1349697 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
15-0083896 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357258 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083950 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2015-12-10 | 1357664 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0085517 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2015-12-15 | 1364164 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0086757 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2015-12-22 | 1368955 | Sus | N | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Broken
15-0087108 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2015-12-24 | 1370995 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0087439 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2015-12-26 | 1372090 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0003092 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 1 | 5 | 2016-01-05 | 1377326 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
16-0003537 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 1 | 6 | 2016-01-06 | 1378479 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0003774 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 7 | 2016-01-07 | 1379225 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0007298 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2016-01-22 | 1389721 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0007539 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2016-01-22 | 1390155 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0009960 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2016-02-02 | 1396825 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0010856 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2016-02-05 | 1398706 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0013501 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406421 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0016005 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2016-02-27 | 1412995 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
16-0017353 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 4 | 2016-03-04 | 1416136 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
16-0017585 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417301 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0017982 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420462 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0024168 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2016-03-26 | 1438970 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0025527 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 1 | 2016-04-01 | 1442655 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0026719 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2016-04-07 | 1445999 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
16-0030888 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2016-04-23 | 1456517 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0031840 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2016-04-27 | 1459864 | Sus | N | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦Deteriorated
16-0032482 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2016 | Tier 3 - Extreme | Transformer only | 4 | 28 | 2016-04-28 | 1461083 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
16-0033013 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2016-05-01 | 1462532 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0033045 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 1 | 2016-05-01 | 1462735 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0036274 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2016-05-16 | 1470423 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
16-0047580 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 2 | 2016-07-02 | 1500053 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0048609 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2016-07-08 | 1502761 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0048858 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 10 | 2016-07-10 | 1507688 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0051811 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2016-07-22 | 1514128 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
16-0051977 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2016 | Tier 2 - Elevated | Transformer only | 7 | 23 | 2016-07-23 | 1514604 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
16-0058541 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2016-08-19 | 1528926 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0063278 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2016-09-08 | 1538520 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0071916 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2016-10-14 | 1558242 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072106 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1559567 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0073000 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1563425 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
16-0073279 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2016-10-17 | 1564482 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0075621 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2016-10-26 | 1570268 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0082431 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589678 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0085281 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2016-12-12 | 1600666 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0087307 | Company Initiated | Other Circuits | Pole-Wood | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2016-12-29 | 1612816 | Sus | N | CompanyInitiated¦OtherCircuits¦PoleWood¦Deteriorated
17-0002825 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 2 | 2017-01-02 | 1615025 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0004344 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2017-01-06 | 1620419 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0004569 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1621000 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005280 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626387 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0005293 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626598 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0005295 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626097 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
17-0005819 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626019 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006994 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1633956 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007404 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1638068 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0007778 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639110 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0008418 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1640379 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0010494 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648748 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011761 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1654426 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0013961 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663171 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0014394 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1665826 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0015284 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2017-01-26 | 1667653 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0019016 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2017-02-08 | 1681863 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019723 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1684265 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0021922 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1691532 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023138 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1693487 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0023608 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2017-02-19 | 1702198 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023796 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703223 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024267 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705900 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025000 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1706663 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0025160 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1708413 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025942 | Company Initiated | Operating error | Recloser | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2017-02-23 | 1711799 | Sus | N | CompanyInitiated¦Operatingerror¦Recloser¦Normal
17-0028910 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 6 | 2017-03-06 | 1721336 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0031039 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2017-03-15 | 1727907 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038201 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2017-04-08 | 1752250 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0038780 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2017-04-10 | 1754033 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0038892 | Vegetation | Tree - fell into line |  | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 10 | 2017-04-10 | 1754421 | Sus | N | Vegetation¦Treefellintoline¦¦FailedFaulted
17-0040246 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 14 | 2017-04-14 | 1757647 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0040575 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2017-04-16 | 1758761 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
17-0044050 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 30 | 2017-04-30 | 1771164 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0044677 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 2 | 2017-05-02 | 1772789 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0045217 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2017-05-03 | 1774494 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0045774 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 6 | 2017-05-06 | 1776072 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
17-0053488 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2017-06-07 | 1799155 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0058646 | Equipment Failure/Involved | Overhead | Bushing | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 26 | 2017-06-26 | 1818216 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦BurnedOpen
17-0066819 | Equipment Failure/Involved | Electrical Overload | Transformer | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2017-07-31 | 1843380 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Deteriorated
17-0070980 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2017-08-17 | 1854082 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0071059 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2017-08-17 | 1854274 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0071108 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2017-08-17 | 1854283 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0074951 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2017-09-01 | 1865259 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0076857 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2017-09-07 | 1873042 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0083006 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2017-09-30 | 1888426 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0083841 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2017-10-03 | 1890228 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Together
17-0087430 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2017-10-14 | 1901024 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0088360 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1903474 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0092124 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2017-11-02 | 1914351 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0092431 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 3 | 2017-11-03 | 1915122 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0092816 | 3rd Party | Vehicle | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 5 | 2017-11-05 | 1916476 | Sus | Y | 3rdParty¦Vehicle¦Fuse¦FailedFaulted
17-0093004 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2017-11-06 | 1916879 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0093737 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2017-11-09 | 1918958 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
17-0097694 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2017-11-27 | 1929822 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0097694 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2017-11-27 | 1929822 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0099747 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2017-12-04 | 1935692 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0103554 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2017-12-28 | 1952720 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
18-0010338 | 3rd Party | Vehicle | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2018-01-30 | 16835 | Sus | N | 3rdParty¦Vehicle¦Fuse¦FailedFaulted
18-0011823 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2018-02-06 | 19917 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0013228 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2018-02-11 | 22678 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0016942 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Transformer only | 2 | 24 | 2018-02-24 | 30794 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
18-0019485 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2018-03-03 | 37674 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0021291 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2018-03-09 | 40927 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0023563 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46170 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0029220 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 4 | 4 | 2018-04-04 | 59533 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0029340 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 4 | 4 | 2018-04-04 | 59656 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0030132 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2018-04-06 | 61308 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0035413 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2018-04-25 | 73582 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0039983 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2018-05-10 | 83264 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
18-0040416 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2018-05-11 | 84265 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
18-0048357 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Transformer only | 6 | 7 | 2018-06-07 | 103581 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
18-0049210 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2018-06-09 | 105013 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0052472 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2018-06-19 | 113290 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0056267 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 7 | 2 | 2018-07-02 | 122925 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0057305 | Vegetation | Tree - fell into line | Service conductor | Broken | 2018 | Tier 2 - Elevated | Transformer only | 7 | 5 | 2018-07-05 | 125118 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
18-0058121 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2018-07-09 | 127621 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0058144 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2018-07-09 | 127692 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0058799 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2018-07-11 | 129001 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0063216 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2018 | Tier 2 - Elevated | Transformer only | 7 | 24 | 2018-07-24 | 139231 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
18-0065587 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 1 | 2018-08-01 | 146349 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0072253 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2018-08-22 | 159845 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075067 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Transmission line | 8 | 30 | 2018-08-30 | 165470 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0075700 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 31 | 2018-08-31 | 166411 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0078114 | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2018-09-10 | 171378 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed
18-0085314 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2018-10-01 | 185136 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Together
18-0089271 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 10 | 2018-10-10 | 192849 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0091048 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2018-10-16 | 196564 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0092305 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2018-10-19 | 198878 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0098438 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 211953 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
18-0100823 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 217842 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0103973 | Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | 2018 | Tier 2 - Elevated | Transmission line | 11 | 27 | 2018-11-27 | 225885 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted
18-0104810 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 227969 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0105207 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228885 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0107951 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2018-12-07 | 235860 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0109264 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 239939 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0110327 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2018-12-22 | 245534 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0110951 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2018-12-28 | 248601 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0110980 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2018-12-28 | 248978 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0003398 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 1 | 2019-01-01 | 251237 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0005051 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255066 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0005695 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 258392 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0007446 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2019-01-10 | 262402 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
19-0008209 | Vegetation | Tree - fell into line | Service conductor | Broken | 2019 | Tier 3 - Extreme | Transformer only | 1 | 12 | 2019-01-12 | 263646 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
19-0010408 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 271064 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0010782 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 272307 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011109 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 271152 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0011658 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 1 | 17 | 2019-01-17 | 274780 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0014868 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 1 | 27 | 2019-01-27 | 282303 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0015725 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Transformer only | 1 | 29 | 2019-01-29 | 283627 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0016964 | Animal | Other | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286531 | Sus | N | Animal¦Other¦PoleWood¦Brokenwireonground
19-0017584 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2019-02-03 | 289025 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018324 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 292018 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018653 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 292945 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0018662 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292958 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0020322 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2019-02-08 | 297018 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020774 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298160 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0020830 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 297757 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0021239 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 2 | 11 | 2019-02-11 | 300135 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0023364 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 309625 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
19-0025179 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 316019 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025577 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 317439 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025585 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2019-02-18 | 317170 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0027585 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 24 | 2019-02-24 | 322457 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0028138 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324075 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0028383 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324636 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
19-0029257 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 327772 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0032267 | Vegetation | Tree - cutting, PG&E contractor | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2019-03-09 | 334928 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦Fuse¦FailedFaulted
19-0032668 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2019-03-11 | 336069 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0035351 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2019-03-20 | 343814 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0036272 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2019-03-23 | 345695 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0038506 | Vegetation | Tree - branch fell on line | Secondary | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 30 | 2019-03-30 | 350831 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Normal
19-0040894 | Equipment Failure/Involved | Overhead | Other | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2019-04-09 | 356591 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Deteriorated
19-0041116 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 9 | 2019-04-09 | 357200 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0045923 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2019-04-25 | 367749 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0050506 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2019-05-09 | 377209 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0051008 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2019-05-11 | 378524 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
19-0053902 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2019-05-19 | 384972 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0059998 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2019-05-30 | 393515 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0062312 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2019-06-03 | 396938 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0080077 | 3rd Party | Customer Equipment | Circuit Breaker | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 23 | 2019-07-23 | 468666 | Sus | Y | 3rdParty¦CustomerEquipment¦CircuitBreaker¦Normal
19-0080373 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2019-07-23 | 468723 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0082106 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2019-07-29 | 474542 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0086107 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2019-08-09 | 495659 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0089185 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2019-08-18 | 521560 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0091771 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2019-08-24 | 536713 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal
19-0094378 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2019-08-31 | 549880 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
19-0095076 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2019-09-04 | 552091 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0105044 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2019-09-28 | 628337 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0112000 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 10 | 15 | 2019-10-15 | 659780 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0114862 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2019-10-23 | 678801 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0115158 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on object | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2019-10-23 | 677569 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonobject
19-0120977 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2019 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2019-11-04 | 699355 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
19-0128214 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 25 | 2019-11-25 | 714138 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0129994 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 717868 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130726 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 722420 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130958 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2019-11-28 | 723205 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0131841 | Equipment Failure/Involved | Overhead | Woodpin | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2019-12-01 | 725597 | Sus | N | EquipmentFailureInvolved¦Overhead¦Woodpin¦Broken
19-0133174 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2019-12-04 | 729386 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0134166 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 5 | 2019-12-05 | 730974 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0136668 | Equipment Failure/Involved | Electrical Overload | Secondary | Burned/flashed | 2019 | Tier 3 - Extreme | Transformer only | 12 | 15 | 2019-12-15 | 740413 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Secondary¦Burnedflashed
19-0137628 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2019-12-22 | 748266 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0138207 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2019-12-30 | 752311 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
20-0005203 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2020-01-04 | 754893 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0010304 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 763324 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0016910 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2020-02-03 | 777189 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0017840 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2020-02-05 | 778777 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0018527 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2020-02-07 | 780106 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0019451 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 782829 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032166 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 851642 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0032379 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2020-03-15 | 852178 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0038525 | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 5 | 2020-04-05 | 882638 | Sus | N | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Malfunctioning
20-0039736 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Transformer only | 4 | 8 | 2020-04-08 | 890614 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0046496 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2020-05-01 | 905515 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
20-0048461 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2020-05-08 | 909476 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0049748 | Animal | Other | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 13 | 2020-05-13 | 912987 | Sus | Y | Animal¦Other¦PoleWood¦Broken
20-0050091 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2020-05-14 | 913472 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
20-0051502 | Environmental/External | Lightning | Lightning Arrestor | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2020-05-18 | 916835 | Sus | Y | EnvironmentalExternal¦Lightning¦LightningArrestor¦FailedFaulted
20-0052650 | 3rd Party | Dig in, 3rd party | Conductor, Underground | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2020-05-20 | 918645 | Sus | Y | 3rdParty¦Digin3rdparty¦ConductorUnderground¦Broken
20-0055953 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 30 | 2020-05-30 | 926390 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0059211 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 6 | 9 | 2020-06-09 | 935073 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0060826 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2020-06-12 | 938133 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0066857 | Equipment Failure/Involved | Overhead | Other | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 30 | 2020-06-30 | 955174 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
20-0068849 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2020 | Tier 3 - Extreme | Transformer only | 7 | 6 | 2020-07-06 | 958908 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
20-0070817 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 11 | 2020-07-11 | 962281 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0072894 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 17 | 2020-07-17 | 966332 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0082354 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 11 | 2020-08-11 | 993388 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0083875 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2020-08-14 | 999247 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0085693 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2020-08-17 | 1015314 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0086457 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2020-08-17 | 1015999 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
20-0089098 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2020-08-23 | 1027876 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0090920 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 28 | 2020-08-28 | 1035494 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0095852 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2020-09-10 | 1062557 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0099601 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1085595 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0102122 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1095253 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0104768 | Environmental/External | Fire, Forest/Grass | Pole-Wood | On Ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1109233 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦OnGround
20-0107312 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2020-10-11 | 1115167 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
20-0112411 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1126889 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Fuse¦Normal
20-0112818 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1125778 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0122195 | Equipment Failure/Involved | Overhead | Jumper | Arcing | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 17 | 2020-11-17 | 1148067 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing
20-0124276 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2020-11-23 | 1153366 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0124371 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2020-11-23 | 1153480 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0130320 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2020-12-14 | 1184531 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
21-0010872 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2021-01-19 | 1216201 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0011753 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1219299 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011818 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1219385 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0013274 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2021-01-23 | 1221809 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0013405 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2021-01-24 | 1222272 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013932 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223467 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0014083 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 25 | 2021-01-25 | 1224735 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0014134 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1225137 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0014152 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224909 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0015397 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1230230 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016182 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1235320 | Sus | N | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
21-0016528 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234179 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0017236 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1238662 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
21-0017356 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1235081 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0017935 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1240557 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
21-0017943 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1240586 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0018396 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1241837 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0019208 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 30 | 2021-01-30 | 1242845 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0019985 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1243869 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020251 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 2 | 1 | 2021-02-01 | 1244577 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0020287 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2021-02-01 | 1244572 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0020603 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1245496 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0021137 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2021-02-03 | 1246630 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0024743 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 2 | 11 | 2021-02-11 | 1253203 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
21-0025386 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 2 | 13 | 2021-02-13 | 1254561 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0025681 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2021-02-15 | 1255381 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0028021 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2021-02-22 | 1259166 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0029417 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2021-02-25 | 1261879 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0032566 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2021-03-05 | 1270090 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
21-0034551 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2021-03-10 | 1277030 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0039039 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 20 | 2021-03-20 | 1290554 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0039880 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2021-03-23 | 1293997 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
21-0041343 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2021-03-26 | 1298648 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0044550 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 4 | 2021-04-04 | 1306708 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0058206 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2021-05-07 | 1342957 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0061980 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 16 | 2021-05-16 | 1350776 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0073405 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2021-06-12 | 1371316 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0075252 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 16 | 2021-06-16 | 1375645 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
21-0087338 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 7 | 9 | 2021-07-09 | 1396632 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0087533 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2021-07-10 | 1398579 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0100034 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2021-08-04 | 1434067 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0104484 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2021-08-14 | 1442405 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0105839 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2021-08-17 | 1444876 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
21-0118887 | 3rd Party | Customer Equipment | Customer Equipment | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 17 | 2021-09-17 | 1473906 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Burnedflashed
21-0122502 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 26 | 2021-09-26 | 1480915 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0122669 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2021-09-27 | 1481287 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0124475 | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2021-09-30 | 1484273 | Sus | Y | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal
21-0127169 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 7 | 2021-10-07 | 1489496 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
21-0132171 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499794 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0132234 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1500403 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0132567 | Animal | Squirrel | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 18 | 2021-10-18 | 1501054 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
21-0136554 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514772 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0138387 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1515418 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0139925 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2021-10-29 | 1525338 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0144747 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2021-11-11 | 1540377 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0149305 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 22 | 2021-11-22 | 1552734 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0149400 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 11 | 22 | 2021-11-22 | 1552780 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0157603 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568213 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158483 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2021-12-15 | 1572736 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
21-0158502 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569760 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0158665 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2021-12-15 | 1573617 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
21-0160010 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2021 | Tier 3 - Extreme | Transformer only | 12 | 21 | 2021-12-21 | 1578864 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
21-0160879 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1583208 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0161012 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584730 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
21-0161253 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584334 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0005125 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591915 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0005247 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 1 | 1 | 2022-01-01 | 1591954 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0012977 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2022-01-22 | 1608954 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0020639 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2022-02-10 | 1624542 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0022578 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2022-02-15 | 1627992 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0025720 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2022-02-23 | 1634743 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0032169 | Vegetation | Tree - fell into line | Transformer (OH) | Broken, wire on ground | 2022 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2022-03-10 | 1645965 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦Brokenwireonground
22-0033278 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2022-03-12 | 1647531 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
22-0044069 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2022-04-07 | 1665261 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0054119 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2022-04-25 | 1681163 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0057002 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Transformer only | 5 | 2 | 2022-05-02 | 1686660 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0059972 | 3rd Party | Vehicle | Pole-Wood | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 9 | 2022-05-09 | 1692486 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
22-0061528 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 12 | 2022-05-12 | 1694972 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0062417 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2022-05-16 | 1697382 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦ConnectororSplice(OH)¦Deteriorated
22-0064270 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2022-05-20 | 1705118 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
22-0064973 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 5 | 22 | 2022-05-22 | 1707408 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0068781 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | 2022 | Tier 3 - Extreme | Transformer only | 6 | 1 | 2022-06-01 | 1715271 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Normal
22-0070779 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | 2022 | Tier 2 - Elevated | Transformer only | 6 | 6 | 2022-06-06 | 1720809 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Normal
22-0071234 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 7 | 2022-06-07 | 1721766 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0075865 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2022-06-18 | 1734470 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0081260 | Animal | Bird found | Jumper | Bent or Twisted | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2022-07-01 | 1747458 | Sus | Y | Animal¦Birdfound¦Jumper¦BentorTwisted
22-0081610 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 4 | 2022-07-04 | 1748571 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0083680 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2022-07-10 | 1752744 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0090520 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 27 | 2022-07-27 | 1766830 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
22-0106269 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 9 | 5 | 2022-09-05 | 1801064 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0111746 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1815036 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0124090 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2022-10-23 | 1843558 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0125130 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2022-10-26 | 1846335 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0129392 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2022-11-08 | 1858433 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0129436 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2022-11-09 | 1858623 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0129954 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 9 | 2022-11-09 | 1859300 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0134345 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2022-11-28 | 1869999 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0136450 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2022-12-04 | 1875831 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0138371 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1881626 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0138899 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2022-12-10 | 1882675 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0139455 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2022-12-13 | 1888091 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0140079 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2022-12-15 | 1889953 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0141870 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2022-12-28 | 1900044 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0010035 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1173968 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0010818 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1178755 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0019742 | Equipment Failure/Involved | Other | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2015-03-16 | 1203992 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Brokenwireonground
15-0027700 | Equipment Failure/Involved | Other | Jumper | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2015-04-20 | 1221799 | Sus | N | EquipmentFailureInvolved¦Other¦Jumper¦Burnedflashed
15-0033442 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2015-05-11 | 1232872 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0034285 | Environmental/External | Lightning | Transformer (OH) | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2015-05-14 | 1234602 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal
15-0038457 | 3rd Party | Metallic Balloon | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2015-06-04 | 1243580 | Sus | Y | 3rdParty¦MetallicBalloon¦Fuse¦FailedFaulted
15-0040924 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2015-06-14 | 1250696 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0043755 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 27 | 2015-06-27 | 1257784 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
15-0045694 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2015-07-06 | 1263537 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0047510 | Equipment Failure/Involved | Overhead |  | Burned Open | 2015 | Tier 2 - Elevated | Transformer only | 7 | 14 | 2015-07-14 | 1268243 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦BurnedOpen
15-0057515 | Animal | Squirrel | Transformer (OH) | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 26 | 2015-08-26 | 1294917 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
15-0057702 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 27 | 2015-08-27 | 1295490 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0057912 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2015-08-28 | 1295949 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
15-0062401 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2015-09-10 | 1309024 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062505 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2015-09-21 | 1309379 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0068051 | Animal | Squirrel | Connector or Splice (UG) | Normal | 2015 | Zone 1 - HHZ | Distribution Circuit | 10 | 5 | 2015-10-05 | 1317174 | Sus | Y | Animal¦Squirrel¦ConnectororSplice(UG)¦Normal
15-0069645 | 3rd Party | Fire, house or bldg. | Transformer (OH) | Normal | 2015 | Tier 3 - Extreme | Transformer only | 10 | 12 | 2015-10-12 | 1320546 | Sus | Y | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Normal
15-0070041 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2015-10-13 | 1321336 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
15-0071296 | Environmental/External | Lightning | Switch (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324270 | Sus | Y | EnvironmentalExternal¦Lightning¦Switch(OH)¦FailedFaulted
15-0073574 | Animal | Squirrel | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2015-10-27 | 1329757 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0075831 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 5 | 2015-11-05 | 1336024 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
15-0077693 | Company Initiated | Personnel, company | Transformer (OH) | Leaking | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2015-11-13 | 1340787 | Sus | Y | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Leaking
15-0078832 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2015-11-18 | 1344555 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
15-0084849 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361270 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0084976 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1362667 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0087660 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2015-12-28 | 1373146 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0002603 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 1 | 3 | 2016-01-03 | 1376380 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0003669 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2016-01-06 | 1379193 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
16-0003745 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2016-01-07 | 1379456 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0005743 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Transmission line | 1 | 15 | 2016-01-15 | 1384787 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0009207 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 3 - Extreme | Transformer only | 1 | 29 | 2016-01-29 | 1394180 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0010798 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2016-02-04 | 1398525 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013188 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1405446 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0014997 | Animal | Squirrel | Cutout, fuse holder | Burned/flashed | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2016-02-23 | 1410940 | Sus | N | Animal¦Squirrel¦Cutoutfuseholder¦Burnedflashed
16-0018025 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420604 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018079 | Vegetation | Tree - fell into line | Pole-Wood | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420179 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦OnGround
16-0018145 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418518 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018927 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2016 | Tier 2 - Elevated | Transformer only | 3 | 7 | 2016-03-07 | 1423047 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
16-0019106 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2016-03-07 | 1424728 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0019178 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2016-03-08 | 1424832 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0021036 | Vegetation | Tree - fell into line | Conductor, Overhead | Contaminated | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430481 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Contaminated
16-0023130 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2016-03-21 | 1435835 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0034636 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 5 | 7 | 2016-05-07 | 1466335 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0036312 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2016-05-16 | 1470628 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Together
16-0037277 | Vegetation | Tree - grew into line | Transformer | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 5 | 20 | 2016-05-20 | 1473293 | Sus | Y | Vegetation¦Treegrewintoline¦Transformer¦Brokenwireonground
16-0037581 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2016-05-21 | 1474337 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0038829 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2016-05-26 | 1477710 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0046167 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2016-06-28 | 1497213 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0051412 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2016-07-21 | 1513399 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0052556 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2016-07-26 | 1516201 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
16-0057522 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2016-08-15 | 1526982 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0058520 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Transformer only | 8 | 19 | 2016-08-19 | 1528960 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0058633 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2016-08-19 | 1529109 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
16-0059593 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2016-08-24 | 1531283 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0060484 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2016-08-27 | 1533073 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0070095 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 10 | 6 | 2016-10-06 | 1553809 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
16-0070541 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2016-10-08 | 1554965 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0072472 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2016-10-15 | 1560819 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0072837 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562232 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
16-0072956 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1563065 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0076787 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2016-10-30 | 1573108 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0081510 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2016-11-21 | 1586691 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0083067 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 11 | 30 | 2016-11-30 | 1591701 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0084555 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2016-12-08 | 1597067 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0084762 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 9 | 2016-12-09 | 1597598 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0084867 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 9 | 2016-12-09 | 1598123 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0085392 | Animal | Squirrel | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2016-12-13 | 1601038 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
17-0002775 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2017-01-02 | 1614628 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0004622 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1621122 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0004920 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622496 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0005828 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1629940 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005879 | Environmental/External | Flood/Erosion | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2017-01-09 | 1630069 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Brokenwireonground
17-0011171 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652273 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0012851 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1659328 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013032 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1656976 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0013510 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1662391 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0018167 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677780 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018851 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1681318 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0020315 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2017-02-11 | 1685973 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0022025 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1692182 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0022793 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698480 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0023652 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1702398 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0025288 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1709217 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0027730 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2017-03-01 | 1717127 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
17-0028411 | Environmental/External | Lightning | Transformer |  | 2017 | Tier 2 - Elevated | Transformer only | 3 | 5 | 2017-03-05 | 1719665 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦
17-0028895 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1721329 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0029266 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2017-03-08 | 1722202 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0030201 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2017-03-11 | 1725289 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0032387 | 3rd Party | Vehicle | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2017-03-21 | 1732030 | Sus | N | 3rdParty¦Vehicle¦Transformer(OH)¦Broken
17-0034506 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2017-03-28 | 1737739 | Sus | N | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
17-0037447 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748349 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0037455 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1746273 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0037475 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1746107 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0037706 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1748995 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0038061 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1751460 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0038249 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2017-04-08 | 1752445 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0042499 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2017-04-24 | 1765994 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0047402 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 11 | 2017-05-11 | 1780410 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0061404 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2017-07-08 | 1826234 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0061404 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2017-07-08 | 1826234 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0064476 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 7 | 21 | 2017-07-21 | 1836799 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
17-0067520 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2017-08-02 | 1845024 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0073226 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 8 | 27 | 2017-08-27 | 1860850 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
17-0073546 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2017-08-28 | 1861667 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
17-0077175 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2017-09-09 | 1873808 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0077743 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 9 | 11 | 2017-09-11 | 1875288 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0081325 | Equipment Failure/Involved | Underground | Other | Malfunctioning | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2017-09-24 | 1885000 | Sus | Y | EquipmentFailureInvolved¦Underground¦Other¦Malfunctioning
17-0085338 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1894690 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0085600 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893857 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0086435 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2017-10-11 | 1898722 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0086820 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899490 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0088692 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1904427 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0095996 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 17 | 2017-11-17 | 1924996 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
17-0096183 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2017-11-18 | 1925592 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0096218 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2017-11-18 | 1925738 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0096960 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2017-11-21 | 1927545 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0097992 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2017 | Tier 2 - Elevated | Transformer only | 11 | 27 | 2017-11-27 | 1930643 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
17-0100403 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2017-12-07 | 1937837 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0100538 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2017-12-07 | 1938130 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0101874 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2017-12-15 | 1943904 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0102957 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2017 | Tier 3 - Extreme | Transformer only | 12 | 21 | 2017-12-21 | 1949743 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
18-0000793 | Equipment Failure/Involved | Substation | Other | Malfunctioning | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2018-05-20 | 90313 | Sus | Y | EquipmentFailureInvolved¦Substation¦Other¦Malfunctioning
18-0008638 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2018-01-24 | 13303 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0009418 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2018-01-26 | 14836 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0012590 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2018 | Tier 2 - Elevated | Transformer only | 2 | 8 | 2018-02-08 | 21496 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
18-0015273 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2018-02-18 | 26773 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0021498 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2018-03-10 | 41332 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
18-0021627 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2018-03-10 | 41781 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0023797 | Vegetation | Tree - fell into line | Transformer |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2018-03-17 | 46739 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦
18-0028371 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2018-04-02 | 57643 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0034129 | Equipment Failure/Involved | Electrical Overload | Other | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 4 | 20 | 2018-04-20 | 70764 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Other¦FailedFaulted
18-0034510 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2018-04-23 | 71814 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0052014 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2018 | Tier 2 - Elevated | Transformer only | 6 | 18 | 2018-06-18 | 112220 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
18-0054887 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 27 | 2018-06-27 | 119125 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0055837 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2018-06-29 | 121490 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0058794 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 11 | 2018-07-11 | 129039 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0062512 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2018-07-22 | 137620 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0062517 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2018-07-22 | 137629 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0063231 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 24 | 2018-07-24 | 139367 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0068095 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Transformer only | 8 | 8 | 2018-08-08 | 151680 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0071302 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2018-08-17 | 157417 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0072702 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2018-08-23 | 160721 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0075736 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 3 - Extreme | Transformer only | 8 | 31 | 2018-08-31 | 166479 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0096177 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2018-11-01 | 206740 | Sus | Y | WildfireMitigation¦CWSPVegetationRemoval¦¦
18-0097627 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2018-11-07 | 210128 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0098208 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 211509 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
18-0102403 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2018-11-22 | 222330 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0103144 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 24 | 2018-11-24 | 224327 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
18-0103198 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 224336 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104224 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2018-11-28 | 226222 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0109617 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 17 | 2018-12-17 | 242145 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
18-0110949 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 28 | 2018-12-28 | 248608 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0004720 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 253949 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0005539 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 256173 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0008279 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 12 | 2019-01-12 | 264015 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
19-0009851 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 267118 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
19-0010141 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 269394 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0010482 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 270483 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0011665 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 272558 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0016364 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 1 | 31 | 2019-01-31 | 284443 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0016888 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286081 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0017006 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2019-02-01 | 285648 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0018392 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292231 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0018602 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292834 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0020092 | Vegetation | Tree - fell into line | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 2 | 7 | 2019-02-07 | 296374 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Broken
19-0021077 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2019-02-11 | 299832 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0021751 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301028 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0022218 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 302991 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0022368 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 304063 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023266 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 304574 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025017 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2019-02-16 | 315153 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
19-0026893 | Vegetation | Tree - fell into line | Service conductor | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2019-02-21 | 320415 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
19-0028296 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324110 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
19-0029399 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 328067 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0031431 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 333053 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
19-0034927 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2019-03-19 | 342631 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0035186 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2019-03-19 | 343211 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0035589 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2019-03-20 | 344202 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0037290 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2019-03-27 | 348191 | Sus | N | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Burnedflashed
19-0037530 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Transformer only | 3 | 27 | 2019-03-27 | 348572 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0037803 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 3 | 28 | 2019-03-28 | 349249 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0041495 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2019-04-11 | 358530 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0042964 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2019-04-16 | 361931 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0043742 | Animal | Squirrel | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 17 | 2019-04-17 | 362672 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
19-0049023 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2019-05-05 | 374156 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0055088 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2019-05-21 | 387424 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0061542 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 2 | 2019-06-02 | 395865 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
19-0062674 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 6 | 4 | 2019-06-04 | 397596 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0070628 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2019-06-21 | 425318 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0073410 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 30 | 2019-06-30 | 437197 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0076228 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Transformer only | 7 | 11 | 2019-07-11 | 444871 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0078579 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2019-07-17 | 456867 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0080295 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transmission line | 7 | 23 | 2019-07-23 | 469401 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
19-0084186 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2019-08-04 | 482528 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Burnedflashed
19-0088508 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2019-08-15 | 513878 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0088709 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2019-08-16 | 515146 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
19-0088974 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 16 | 2019-08-16 | 518688 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0096532 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2019-09-08 | 562348 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0098779 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 9 | 13 | 2019-09-13 | 576661 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0109335 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2019-10-09 | 648881 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0117340 | Wildfire Mitigation | Public Safety Power Shut-off | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 688008 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConnectororSplice(OH)¦Brokenwireonground
19-0120651 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2019-11-04 | 698985 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130308 | Vegetation | Tree - bark fell into line | Secondary | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 721426 | Sus | Y | Vegetation¦Treebarkfellintoline¦Secondary¦Brokenwireonground
19-0130671 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2019-11-27 | 722260 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0130779 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722664 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0131060 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 11 | 29 | 2019-11-29 | 723434 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0131866 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 725392 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0132841 | Animal | Bird found | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2019-12-03 | 728501 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
19-0135037 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2019-12-08 | 733813 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0136190 | Animal | Squirrel | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2019-12-12 | 737551 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
19-0136323 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2019-12-13 | 738098 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
19-0136410 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2019-12-13 | 738497 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0005316 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2020-01-05 | 755189 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0010080 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 763116 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
20-0010712 | Vegetation | Tree - branch fell on line | Insulator | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2020-01-17 | 764882 | Sus | N | Vegetation¦Treebranchfellonline¦Insulator¦Broken
20-0010920 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 765118 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0031680 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2020-03-13 | 848533 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033203 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 856383 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0033295 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 856548 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0033335 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 856589 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0034641 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2020-03-18 | 859606 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
20-0034902 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2020-03-21 | 860180 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0037290 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2020-03-30 | 871201 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0037659 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 1 | 2020-04-01 | 875713 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0040603 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2020-04-11 | 893961 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0041085 | Equipment Failure/Involved | Underground | Transformer | Burned/flashed | 2020 | Tier 2 - Elevated | Transformer only | 4 | 14 | 2020-04-14 | 894885 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦Burnedflashed
20-0042167 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2020-04-16 | 896750 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
20-0044152 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 23 | 2020-04-23 | 900175 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0044492 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Transmission line | 4 | 24 | 2020-04-24 | 901102 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0051568 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 18 | 2020-05-18 | 917083 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0053980 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 26 | 2020-05-26 | 921407 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
20-0053982 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2020-05-26 | 921226 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0058470 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Transformer only | 6 | 6 | 2020-06-06 | 932778 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0064360 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2020-06-24 | 945974 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0068261 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 3 | 2020-07-03 | 957420 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0068298 | 3rd Party | Fire, house or bldg. | Other | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2020-07-03 | 957603 | Sus | Y | 3rdParty¦Firehouseorbldg¦Other¦Burnedflashed
20-0069345 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2020-07-07 | 959677 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0070941 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 7 | 12 | 2020-07-12 | 962677 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0076522 | 3rd Party | Vehicle | Pole-Wood | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2020-07-27 | 973136 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
20-0079261 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 3 | 2020-08-03 | 978182 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
20-0081876 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2020-08-10 | 991056 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0089152 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2020-08-24 | 1028006 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
20-0090306 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1032995 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0090956 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2020-08-28 | 1035958 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0094601 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Normal | 2020 | Tier 2 - Elevated | Transmission line | 9 | 8 | 2020-09-08 | 1060334 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Other¦Normal
20-0095685 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 9 | 2020-09-09 | 1062303 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0100640 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1089854 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0101862 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 9 | 26 | 2020-09-26 | 1093850 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0102129 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1095339 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0106033 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 7 | 2020-10-07 | 1112504 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0108297 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2020-10-14 | 1117702 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0111154 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 21 | 2020-10-21 | 1122137 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0112093 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2020-10-25 | 1127865 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0114351 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2020-10-28 | 1130767 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0114650 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2020-10-29 | 1131250 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0123942 | Equipment Failure/Involved | Underground | Bus | Contaminated | 2020 | Tier 2 - Elevated | Transformer only | 11 | 22 | 2020-11-22 | 1152719 | Sus | Y | EquipmentFailureInvolved¦Underground¦Bus¦Contaminated
20-0129988 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2020-12-12 | 1180642 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0010064 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1213174 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0014731 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226450 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0015027 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1227688 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0015943 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1228482 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0016419 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1233414 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016704 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1236947 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0017096 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237906 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0017216 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1238874 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0017945 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2021-01-28 | 1240369 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0018194 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1241243 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
21-0019184 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1242591 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0020402 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1245015 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0020605 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2021-02-01 | 1245505 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0020708 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2021-02-01 | 1245552 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
21-0021814 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2021-02-04 | 1247967 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
21-0025300 | Equipment Failure/Involved | Overhead | Other | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2021-02-13 | 1254351 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
21-0026714 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2021-02-17 | 1256891 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0055697 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2021-05-01 | 1338394 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0055697 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2021-05-01 | 1338394 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0056521 | Animal | Bird found | Transformer (OH) | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 4 | 2021-05-04 | 1340341 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
21-0061934 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2021-05-15 | 1350597 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0061937 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2021-05-15 | 1350559 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0080816 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 6 | 28 | 2021-06-28 | 1386665 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
21-0083089 | Equipment Failure/Involved | Underground | Elbow | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 1 | 2021-07-01 | 1389476 | Sus | Y | EquipmentFailureInvolved¦Underground¦Elbow¦FailedFaulted
21-0094890 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 7 | 26 | 2021-07-26 | 1414788 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
21-0105560 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445623 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
21-0107980 | Animal | Squirrel | Fuse | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2021-08-22 | 1450184 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
21-0110465 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2021-08-27 | 1455980 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0113549 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2021 | Tier 2 - Elevated | Transformer only | 9 | 3 | 2021-09-03 | 1461749 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
21-0116014 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 10 | 2021-09-10 | 1467941 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0127084 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2021-10-07 | 1489319 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0129915 | Equipment Failure/Involved | Electrical Overload | Transformer | Malfunctioning | 2021 | Tier 2 - Elevated | Transformer only | 10 | 12 | 2021-10-12 | 1495612 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Malfunctioning
21-0135698 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508294 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0136599 | Vegetation | Tree - branch fell on line | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1515148 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦BurnedOpen
21-0136833 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1516064 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0137480 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2021-10-25 | 1517369 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0145525 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 11 | 15 | 2021-11-15 | 1544117 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0145790 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 15 | 2021-11-15 | 1545080 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0155322 | Equipment Failure/Involved | Overhead | Secondary | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 12 | 6 | 2021-12-06 | 1560296 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen
21-0157106 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1566698 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0157199 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1566895 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0157517 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568170 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158523 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1572683 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0158938 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1574187 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0160916 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Transmission line | 12 | 27 | 2021-12-27 | 1583567 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0161139 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585586 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0024414 | Animal | Other | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2022-02-19 | 1632274 | Sus | N | Animal¦Other¦ConductorOverhead¦Normal
22-0028383 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2022 | Tier 2 - Elevated | Transformer only | 3 | 1 | 2022-03-01 | 1640125 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
22-0038128 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2022-03-24 | 1655167 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0041261 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2022-03-31 | 1660509 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
22-0060349 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 5 | 10 | 2022-05-10 | 1692913 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0062583 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2022-05-16 | 1697637 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0063647 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2022-05-18 | 1702310 | Sus | Y | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0067731 | Animal | Bird found |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2022-05-28 | 1712880 | Sus | Y | Animal¦Birdfound¦¦
22-0070354 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2022-06-05 | 1719696 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0072723 | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2022-06-10 | 1727255 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Malfunctioning
22-0073387 | Animal | Squirrel | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2022-06-12 | 1729320 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
22-0083378 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2022-07-08 | 1751564 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0084578 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 13 | 2022-07-13 | 1754962 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0085227 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 7 | 14 | 2022-07-14 | 1755953 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
22-0104952 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2022-09-02 | 1797259 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0106072 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2022-09-05 | 1800733 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0112626 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 9 | 20 | 2022-09-20 | 1817298 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0116514 | 3rd Party | Customer Equipment | Generator | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2022-09-30 | 1824818 | Sus | Y | 3rdParty¦CustomerEquipment¦Generator¦Normal
22-0117882 | Animal | Squirrel | Transformer (OH) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2022-10-04 | 1828745 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
22-0118475 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2022-10-06 | 1829923 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0120108 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 10 | 11 | 2022-10-11 | 1834877 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0123839 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2022-10-22 | 1842674 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0123883 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2022-10-22 | 1842786 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0124435 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2022-10-24 | 1844485 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0124706 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2022-10-25 | 1845241 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0125885 | 3rd Party | Fire, house or bldg. | Pole-Wood | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 10 | 29 | 2022-10-29 | 1848105 | Sus | Y | 3rdParty¦Firehouseorbldg¦PoleWood¦Burnedflashed
22-0127449 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 11 | 3 | 2022-11-03 | 1852448 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0128308 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2022-11-06 | 1855309 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0128338 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2022-11-06 | 1855474 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0130713 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 13 | 2022-11-13 | 1861714 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0135848 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 12 | 2 | 2022-12-02 | 1873820 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0136254 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 3 | 2022-12-03 | 1874858 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0138919 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1885347 | Sus | N | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
22-0138983 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 12 | 11 | 2022-12-11 | 1885646 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0139108 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1886547 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0139865 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2022-12-14 | 1888970 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0142219 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2022-12-30 | 1902089 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0009819 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1173191 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
15-0010260 | Vegetation | Tree - fell into line | Fuse | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2015-02-06 | 1174580 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦Normal
15-0012568 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2015-02-10 | 1187996 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0016215 | Equipment Failure/Involved | Other | Crossarm, Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2015-02-27 | 1196550 | Sus | N | EquipmentFailureInvolved¦Other¦CrossarmWood¦Brokenwireonground
15-0016304 | Equipment Failure/Involved | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 2 | 27 | 2015-02-27 | 1196967 | Sus | N | EquipmentFailureInvolved¦Lightning¦Transformer¦FailedFaulted
15-0019549 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 3 | 13 | 2015-03-13 | 1203365 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0032767 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2015-05-07 | 1231349 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0039900 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2015-06-09 | 1248076 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
15-0044177 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2015-06-30 | 1259102 | Sus | Y | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Brokenwireonground
15-0046603 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2015-07-09 | 1265511 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0049854 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 22 | 2015-07-22 | 1275249 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0049912 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2015-07-22 | 1275375 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
15-0054374 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 11 | 2015-08-11 | 1286723 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0060567 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Transmission line | 9 | 10 | 2015-09-10 | 1303533 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
15-0064535 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 26 | 2015-09-26 | 1312323 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0068208 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 6 | 2015-10-06 | 1317557 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0071708 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 18 | 2015-10-18 | 1325758 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0074258 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2015-10-30 | 1331504 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0079399 | Animal | Other | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2015-11-19 | 1345550 | Sus | Y | Animal¦Other¦Fuse¦FailedFaulted
15-0084249 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2015-12-11 | 1358652 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
15-0084616 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1360205 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086944 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Transformer only | 12 | 23 | 2015-12-23 | 1370139 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0087143 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 24 | 2015-12-24 | 1371082 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0087403 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2015-12-25 | 1371913 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0003253 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2016-01-06 | 1377965 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0004345 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2016-01-10 | 1381138 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0005994 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2016-01-18 | 1385860 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0007242 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2016-01-21 | 1389588 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0007379 | Animal | Bird found | Jumper | Bent or Twisted | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2016-01-22 | 1389882 | Sus | N | Animal¦Birdfound¦Jumper¦BentorTwisted
16-0013508 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407188 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
16-0013526 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407245 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0013667 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2016-02-18 | 1407801 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0014290 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2016-02-19 | 1409367 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0016615 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 3 | 1 | 2016-03-01 | 1414449 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0018242 | Vegetation | Tree - fell into line | Service conductor | Broken | 2016 | Tier 2 - Elevated | Transformer only | 3 | 5 | 2016-03-05 | 1418309 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
16-0019935 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2016-03-10 | 1426448 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0022424 | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2016-03-18 | 1433633 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated
16-0022424 | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2016-03-18 | 1433633 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated
16-0022740 | Animal | Bird found | Cutout, fuse holder | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2016-03-20 | 1434469 | Sus | N | Animal¦Birdfound¦Cutoutfuseholder¦FailedFaulted
16-0022871 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2016-03-21 | 1435083 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0023093 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2016-03-21 | 1435705 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0028140 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2016-04-12 | 1449667 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0029048 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2016-04-15 | 1451658 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0030075 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2016-04-20 | 1454513 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦OnGround
16-0030602 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2016-04-22 | 1455712 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0030826 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2016-04-22 | 1456236 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0030934 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2016-04-23 | 1456640 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
16-0031519 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 26 | 2016-04-26 | 1459085 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0031795 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 27 | 2016-04-27 | 1459772 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0033779 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 4 | 2016-05-04 | 1464536 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0042192 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 9 | 2016-06-09 | 1485877 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0051932 | Animal | Bird found | Transformer (OH) | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2016-07-22 | 1514396 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
16-0056982 | Animal | Bird found | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2016-08-12 | 1525339 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
16-0057668 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2016-08-16 | 1527340 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0059898 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 25 | 2016-08-25 | 1531862 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
16-0061882 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2016-09-02 | 1535725 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0062238 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 9 | 3 | 2016-09-03 | 1536287 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
16-0062338 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 4 | 2016-09-04 | 1536622 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
16-0071963 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1558789 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken
16-0072659 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561901 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0072835 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562617 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0074750 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2016-10-22 | 1567449 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0076553 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 10 | 28 | 2016-10-28 | 1572054 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0076741 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2016-10-30 | 1572999 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
16-0079360 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2016-11-11 | 1579666 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
16-0082453 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589726 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0084254 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2016-12-06 | 1595783 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0085598 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2016-12-14 | 1602045 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0086020 | 3rd Party | Vehicle | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2016-12-16 | 1604571 | Sus | N | 3rdParty¦Vehicle¦CrossarmWood¦Broken
17-0002974 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1615543 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0004864 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1622269 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0004966 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622810 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0004997 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622527 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0005508 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623981 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005745 | Equipment Failure/Involved | Overhead | Other | Normal | 2017 | Tier 3 - Extreme | Transmission line | 1 | 8 | 2017-01-08 | 1629403 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Normal
17-0005873 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628054 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0007010 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632895 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0007025 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2017 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2017-01-10 | 1636168 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
17-0008685 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 13 | 2017-01-13 | 1642225 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0010869 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2017-01-19 | 1650879 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
17-0012055 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655870 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
17-0012368 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1657241 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0012591 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1657921 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0013676 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662982 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0017065 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673421 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018423 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677732 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0020886 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2017-02-14 | 1687951 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0022629 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698166 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023118 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1693331 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023401 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2017-02-19 | 1701330 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0023442 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 19 | 2017-02-19 | 1701387 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0023933 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703915 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0025020 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704907 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0028809 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 3 | 6 | 2017-03-06 | 1720840 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0032559 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 21 | 2017-03-21 | 1732526 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0037715 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748220 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0038351 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2017-04-08 | 1753022 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0040700 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2017-04-16 | 1759108 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0040953 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 17 | 2017-04-17 | 1759844 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
17-0045407 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 4 | 2017-05-04 |  | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0053115 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2017-06-06 | 1798194 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0054571 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2017-06-12 | 1802709 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0056036 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Transformer only | 6 | 17 | 2017-06-17 | 1806658 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
17-0060088 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 2 | 2017-07-02 | 1822440 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0066146 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2017-07-27 | 1841204 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0071193 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 8 | 17 | 2017-08-17 | 1854523 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0072708 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2017-08-24 | 1858821 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0076828 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2017-09-07 | 1872829 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0078108 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2017-09-12 | 1876905 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0080032 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 19 | 2017-09-19 | 1881748 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0080378 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2017-09-20 | 1882534 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086487 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1898940 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
17-0087205 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1900347 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0087358 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2017-10-14 | 1900701 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0088258 | Environmental/External | Fire, Forest/Grass | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 13 | 2017-10-13 | 1903203 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦FailedFaulted
17-0088433 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Burned/flashed | 2017 | Tier 3 - Extreme | Transformer only | 10 | 9 | 2017-10-09 | 1903673 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed
17-0093750 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2017-11-09 | 1919031 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
17-0099460 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2017-12-04 | 1934453 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0005906 | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 2018 | Tier 2 - Elevated | Transformer only | 1 | 13 | 2018-01-13 | 7628 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground
18-0007020 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2018-01-18 | 10212 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0011528 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2018-02-05 | 19467 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0015418 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2018 | Tier 3 - Extreme | Transformer only | 2 | 19 | 2018-02-19 | 27209 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
18-0021500 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2018-03-10 | 41315 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0022707 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 43906 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0025469 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2018-03-22 | 50526 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0028195 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 3 | 31 | 2018-03-31 | 57116 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0030212 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2018-04-07 | 61730 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0031569 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2018-04-12 | 65331 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0032011 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Transformer only | 4 | 13 | 2018-04-13 | 66207 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
18-0038170 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2018-05-03 | 79230 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0042235 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2018-05-18 | 88942 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0044648 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2018-05-26 | 94516 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0049489 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2018-06-10 | 106001 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0051037 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2018-06-14 | 109231 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0051341 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2018-06-15 | 109991 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0056540 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 3 - Extreme | Transformer only | 7 | 3 | 2018-07-03 | 123439 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0062030 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2018-07-20 | 136510 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0062478 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2018-07-22 | 137465 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0079579 | Equipment Failure/Involved | Underground | Connector or Splice (OH) | Burned/flashed | 2018 | Tier 3 - Extreme | Transformer only | 9 | 13 | 2018-09-13 | 174058 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConnectororSplice(OH)¦Burnedflashed
18-0084608 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2018-09-28 | 183383 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0087487 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 10 | 5 | 2018-10-05 | 189166 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
18-0089438 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2018-10-11 | 193254 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0090290 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2018-10-14 | 195020 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
18-0090561 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2018-10-15 | 195594 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0093082 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2018-10-22 | 200418 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0098745 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2018 | Tier 2 - Elevated | Transformer only | 11 | 9 | 2018-11-09 | 212614 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
18-0099049 | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2018-11-11 | 213501 | Sus | Y | 3rdParty¦Treecutting3rdparty¦PoleWood¦Brokenwireonground
18-0100798 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217800 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101090 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218354 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104781 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 227674 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0110405 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 12 | 23 | 2018-12-23 | 245953 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0111063 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2018-12-29 | 249410 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0111165 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2018-12-31 | 249945 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
18-0111234 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2018-12-31 | 250415 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0006642 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2019-01-09 | 261191 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017346 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287982 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0018197 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 290845 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
19-0019972 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2019-02-08 | 295953 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
19-0021835 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301520 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0021890 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303093 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0022128 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303686 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0022999 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 306363 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023523 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 309279 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
19-0028464 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324583 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0029023 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326095 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
19-0029402 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2019-02-28 | 328073 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0033220 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2019-03-12 | 337994 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0036204 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2019-03-22 | 345501 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0036357 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 3 | 23 | 2019-03-23 | 346040 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0036742 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 25 | 2019-03-25 | 346988 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0037715 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 27 | 2019-03-27 | 348849 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0044300 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2019-04-19 | 363701 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0044542 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2019-04-20 | 364161 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0055084 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2019-05-21 | 387392 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0060725 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2019-05-31 | 394171 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0074901 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2019-07-06 | 441673 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0080862 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 24 | 2019-07-24 | 470571 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0081562 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2019-07-26 | 472570 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0084133 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2019-08-04 | 482301 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0086570 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2019-08-10 | 501054 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
19-0094475 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2019-09-01 | 550549 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
19-0104359 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2019-09-27 | 619858 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
19-0113949 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2019-10-21 | 675933 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0118985 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2019-10-30 | 695318 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0122746 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2019-11-08 | 702393 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0123484 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2019-11-11 | 704240 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0129802 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 719540 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0132226 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 2 | 2019-12-02 | 726974 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0132615 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2019-12-02 | 727835 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0134719 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 732155 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0134730 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2019-12-07 | 732502 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0135069 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2019-12-08 | 733944 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0136105 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 12 | 12 | 2019-12-12 | 737233 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0136464 | Vegetation | Tree - fell into line | Other | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2019-12-13 | 738631 | Sus | N | Vegetation¦Treefellintoline¦Other¦Normal
20-0004193 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 1 | 2020-01-01 | 753192 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0013398 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 1 | 24 | 2020-01-24 | 769466 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0019691 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 786755 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0020254 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 788047 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0020292 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 788093 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0022417 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2020-02-14 | 791250 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0027608 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2020-03-02 | 821106 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0027889 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 2 | 2020-03-02 | 823615 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0030733 | 3rd Party | Dig in, 3rd party | Transformer | Broken | 2020 | Tier 2 - Elevated | Transformer only | 3 | 10 | 2020-03-10 | 843368 | Sus | N | 3rdParty¦Digin3rdparty¦Transformer¦Broken
20-0033601 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2020 | Tier 3 - Extreme | Transformer only | 3 | 18 | 2020-03-18 | 857285 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
20-0034376 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 19 | 2020-03-19 | 859170 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0034579 | 3rd Party | Vehicle | Anchor or Guy | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2020-03-20 | 859434 | Sus | N | 3rdParty¦Vehicle¦AnchororGuy¦Normal
20-0047098 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Transformer only | 5 | 4 | 2020-05-04 | 907090 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0048999 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2020-05-11 | 910916 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0053416 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2020-05-22 | 919792 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Burnedflashed
20-0055758 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2020-05-29 | 925678 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0058623 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 7 | 2020-06-07 | 933474 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0068011 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2020-07-02 | 957031 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0082585 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 12 | 2020-08-12 | 993954 | Sus | Y | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Broken
20-0085339 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1013336 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0086621 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 8 | 18 | 2020-08-18 | 1018341 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0090405 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033275 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
20-0093205 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2020-09-03 | 1053220 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0093839 | Animal | Bird found | Jumper | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2020-09-06 | 1056784 | Sus | Y | Animal¦Birdfound¦Jumper¦BurnedOpen
20-0099282 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 20 | 2020-09-20 | 1083245 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0099678 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1085853 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0099777 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086057 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100552 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1089257 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100642 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1089893 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0106314 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2020-10-07 | 1113136 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0110972 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2020-10-20 | 1121862 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0126201 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2020-12-01 | 1156855 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0130137 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2020 | Tier 3 - Extreme | Transformer only | 12 | 13 | 2020-12-13 | 1182505 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
20-0131847 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2020-12-26 | 1198855 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0131847 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2020-12-26 | 1198855 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0131895 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2020-12-26 | 1199231 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0007463 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 1 | 11 | 2021-01-11 | 1208319 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0007831 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Transformer only | 1 | 12 | 2021-01-12 | 1209111 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0009544 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2021-01-17 | 1211966 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0009848 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1212896 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0010680 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216713 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0010739 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216306 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011796 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 20 | 2021-01-20 | 1218976 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
21-0013286 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2021-01-23 | 1221699 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
21-0013584 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223032 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0013829 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224008 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0014010 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223333 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0014999 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226652 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
21-0016135 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1235187 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016159 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1227705 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
21-0017072 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237290 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0017932 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2021-01-28 | 1240552 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0021052 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2021-02-02 | 1246503 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
21-0022008 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2021-02-04 | 1248175 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0022398 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2021-02-05 | 1248797 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0022782 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2021-02-07 | 1250007 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0029192 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261329 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0033073 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 6 | 2021-03-06 | 1270911 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0038121 | Equipment Failure/Involved | Overhead |  | Normal | 2021 | Tier 2 - Elevated | Transformer only | 3 | 18 | 2021-03-18 | 1287615 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦Normal
21-0042975 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2021-03-30 | 1303817 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0049285 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2021 | Tier 3 - Extreme | Transmission line | 4 | 15 | 2021-04-15 | 1318895 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
21-0049532 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 16 | 2021-04-16 | 1319786 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0052953 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2021-04-25 | 1333650 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0058934 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2021-05-08 | 1344155 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0061861 | Animal | Squirrel | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2021-05-15 | 1350067 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
21-0064136 | Vegetation | Tree - grew into line | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Transformer only | 5 | 20 | 2021-05-20 | 1355059 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Broken
21-0067006 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2021 | Tier 3 - Extreme | Transformer only | 5 | 27 | 2021-05-27 | 1360175 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
21-0069735 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2021-06-03 | 1365211 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0069934 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2021-06-04 | 1365509 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0076012 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2021-06-18 | 1377153 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0077989 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2021-06-23 | 1382942 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0087500 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 10 | 2021-07-10 | 1398286 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0087652 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 7 | 11 | 2021-07-11 | 1398996 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0092086 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2021-07-19 | 1408554 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0105521 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2021-08-17 | 1444628 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
21-0109181 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2021-08-25 | 1452947 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0111070 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2021-08-30 | 1458252 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0112363 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 1 | 2021-09-01 | 1460265 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0114942 | Company Initiated | Personnel, company | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2021-09-08 | 1464967 | Sus | Y | CompanyInitiated¦Personnelcompany¦Transformer(OH)¦Normal
21-0116299 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 9 | 10 | 2021-09-10 | 1468537 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0119338 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2021-09-18 | 1474520 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0119689 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Transformer only | 9 | 19 | 2021-09-19 | 1475791 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0128770 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492892 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0129523 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2021-10-11 | 1493202 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0135792 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508122 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136340 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511073 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0136572 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514832 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Deteriorated
21-0138255 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509332 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0138868 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2021-10-27 | 1522708 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0139966 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2021-10-29 | 1525346 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0147221 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 17 | 2021-11-17 | 1548042 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
21-0148213 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 11 | 18 | 2021-11-18 | 1549460 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0148715 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 19 | 2021-11-19 | 1549973 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0149162 | Animal | Squirrel | Cutout, fuse holder | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2021-11-21 | 1552415 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
21-0157240 | Vegetation | Tree - branch fell on line | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 12 | 13 | 2021-12-13 | 1567057 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Broken
21-0157524 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1568348 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0157838 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569835 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing
21-0157924 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569344 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0158490 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1572899 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158631 | Equipment Failure/Involved | Overhead | Fuse | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2021-12-15 | 1573250 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Brokenwireonground
21-0158986 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1575227 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0159335 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2021-12-17 | 1575791 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160458 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 24 | 2021-12-24 | 1580787 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161033 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584429 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161775 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2021-12-30 | 1589637 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0006734 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1596457 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0008216 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2022-01-10 | 1599650 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
22-0008481 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2022-01-11 | 1599935 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0010258 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 3 - Extreme | Transformer only | 1 | 15 | 2022-01-15 | 1602637 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0012378 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607226 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0017348 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2022-02-02 | 1618801 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0019144 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2022-02-07 | 1622385 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0030274 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2022-03-05 | 1642901 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0030463 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2022-03-06 | 1643490 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0037893 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 3 | 24 | 2022-03-24 | 1654805 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
22-0044775 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2022-04-08 | 1666310 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0045784 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1669794 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0054272 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2022-04-25 | 1681313 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
22-0061623 | Animal | Bird found | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 13 | 2022-05-13 | 1695156 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
22-0064957 | Equipment Failure/Involved | Overhead | Other | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 22 | 2022-05-22 | 1707382 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
22-0067836 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 5 | 28 | 2022-05-28 | 1713196 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0078363 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Transformer only | 6 | 24 | 2022-06-24 | 1741578 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
22-0078684 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 6 | 25 | 2022-06-25 | 1742380 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0088412 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2022-07-21 | 1762703 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0091825 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2022-07-31 | 1769601 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
22-0092861 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2022 | Tier 3 - Extreme | Transformer only | 8 | 2 | 2022-08-02 | 1771441 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
22-0093392 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2022-08-03 | 1772556 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0096985 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 12 | 2022-08-12 | 1779602 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
22-0103331 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2022-08-29 | 1794473 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
22-0104931 | Environmental/External | Fire, Forest/Grass | Secondary | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2022-09-01 | 1797206 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Secondary¦Burnedflashed
22-0105552 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2022-09-03 | 1798524 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0106603 | 3rd Party | Fire, house or bldg. | Secondary | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2022-09-06 | 1801925 | Sus | Y | 3rdParty¦Firehouseorbldg¦Secondary¦Burnedflashed
22-0109467 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2022 | Tier 2 - Elevated | Transformer only | 9 | 12 | 2022-09-12 | 1809428 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
22-0111698 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2022-09-18 | 1814590 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0114219 | Company Initiated | Coordination failure | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2022-09-23 | 1820036 | Sus | Y | CompanyInitiated¦Coordinationfailure¦ConductorOverhead¦Normal
22-0117090 | Company Initiated | Construction Activity/equip, company | Transformer | Deteriorated | 2022 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2022-10-03 | 1826414 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Transformer¦Deteriorated
22-0126757 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 11 | 1 | 2022-11-01 | 1850733 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0126805 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2022-11-01 | 1850832 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0128547 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2022-11-07 | 1856027 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0128548 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 7 | 2022-11-07 | 1855933 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0134537 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 11 | 28 | 2022-11-28 | 1870502 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0141257 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2022-12-25 | 1897202 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0141509 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898287 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0141790 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898082 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0142481 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1902999 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0004495 | Equipment Failure/Involved | Other | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 14 | 2015-01-14 | 1163620 | Sus | N | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Normal
15-0010559 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1176374 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0011639 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2015-02-08 | 1183027 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0011981 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2015-02-08 | 1185613 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0023934 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 3 | 2015-04-03 | 1211981 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0027972 | Equipment Failure/Involved | Other | Crossarm, Wood | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2015-04-20 | 1222099 | Sus | N | EquipmentFailureInvolved¦Other¦CrossarmWood¦Deteriorated
15-0035560 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 5 | 20 | 2015-05-20 | 1237602 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0038280 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2015-06-03 | 1243225 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0038992 | Environmental/External | Lightning |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 5 | 2015-06-05 | 1244521 | Sus | Y | EnvironmentalExternal¦Lightning¦¦FailedFaulted
15-0044131 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 30 | 2015-06-30 | 1259085 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0048361 | Animal | Squirrel | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2015-07-18 | 1270010 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
15-0048704 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1271946 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0049098 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1273396 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0050493 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2015-07-25 | 1277194 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0050671 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 27 | 2015-07-27 | 1277784 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0051294 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Transformer only | 7 | 29 | 2015-07-29 | 1279452 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0051789 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 7 | 30 | 2015-07-30 | 1280525 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0052039 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 1 | 2015-08-01 | 1281064 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0053476 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 8 | 6 | 2015-08-06 | 1284272 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
15-0061043 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2015-09-12 | 1304739 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
15-0061098 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2015-09-13 | 1304991 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0062997 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2015 | Tier 3 - Extreme | Transformer only | 9 | 23 | 2015-09-23 | 1311001 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
15-0063566 | Animal | Squirrel | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2015-09-25 | 1311798 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦FailedFaulted
15-0069198 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2015-10-09 | 1319202 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0073123 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2015-10-24 | 1328676 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0073417 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2015-10-26 | 1329468 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
15-0076838 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 11 | 9 | 2015-11-09 | 1338212 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0082324 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 2 | 2015-12-02 | 1352101 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0003331 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2016-01-06 | 1378134 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0009084 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2016-01-29 | 1393789 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0012517 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2016-02-13 | 1403030 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0027132 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2016 | Tier 3 - Extreme | Transformer only | 4 | 8 | 2016-04-08 | 1446888 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
16-0037423 | Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 20 | 2016-05-20 | 1473607 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed
16-0037699 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2016-05-22 | 1474871 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0046459 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2016-06-28 | 1497885 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0046521 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2016-06-29 | 1498050 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0047241 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2016-06-30 | 1499210 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0049479 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2016-07-12 | 1509120 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0052350 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2016-07-25 | 1515796 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0053070 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2016-07-27 | 1517384 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
16-0053298 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2016-07-28 | 1517875 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0055175 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 4 | 2016-08-04 | 1521649 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0072667 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561802 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0081037 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2016-11-19 | 1584550 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0084646 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 8 | 2016-12-08 | 1597134 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0086708 | Animal | Bird found | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2016-12-22 | 1608994 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0002831 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2017-01-02 | 1615021 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005258 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626096 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
17-0005841 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2017-01-09 | 1629912 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005927 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1629643 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0006088 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1631090 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
17-0007060 | Vegetation | Tree - fell into line | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 8 | 2017-01-08 | 1625073 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Broken
17-0007701 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1638151 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007828 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639979 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0012168 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1657202 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0017660 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2017-02-06 | 1675825 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0018092 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677630 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018425 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1678936 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018519 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679369 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018744 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679549 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019333 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1682868 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0019741 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2017-02-09 | 1684439 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0020477 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2017-02-12 | 1686645 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0020792 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 13 | 2017-02-13 | 1687719 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0022527 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transmission line | 2 | 17 | 2017-02-17 | 1697645 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0023393 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2017-02-18 | 1701289 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0024232 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705779 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
17-0027227 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2017-02-28 | 1715675 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0027326 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2017-02-28 | 1715732 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0028997 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2017-03-07 |  | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0028997 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2017-03-07 |  | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0029244 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2017-03-08 | 1722184 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0037381 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1747089 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0037522 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1748900 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0044730 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2017-05-02 | 1772895 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0052514 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2017-06-03 | 1796079 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0053206 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2017-06-07 | 1798474 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0061917 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 10 | 2017-07-10 | 1828680 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0066872 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 1 | 2017-08-01 | 1843538 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0075429 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 2 | 2017-09-02 | 1867532 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0078594 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 13 | 2017-09-13 | 1878104 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0081291 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2017-09-24 | 1884909 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0084237 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2017-10-04 | 1890936 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0086825 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899496 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0086865 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 12 | 2017-10-12 | 1899519 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0087431 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2017-10-14 | 1901043 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0088772 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2017-10-19 | 1904680 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0093059 | Equipment Failure/Involved | Overhead | Other | Malfunctioning | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2017-11-06 | 1916942 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Malfunctioning
17-0093234 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2017-11-07 | 1917580 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0096436 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 20 | 2017-11-20 | 1926329 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
17-0097277 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2017-11-23 | 1928286 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0099793 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2017 | Tier 3 - Extreme | Transformer only | 12 | 4 | 2017-12-04 | 1935938 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
17-0102894 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2017-12-21 | 1949174 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0006760 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2018-01-17 | 9713 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0015649 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2018-02-20 | 27825 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0017621 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2018-02-27 | 32514 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0022640 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2018-03-14 | 43941 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0025322 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 50228 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0026003 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 23 | 2018-03-23 | 51757 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0026169 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2018-03-23 | 52221 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0028165 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2018-03-31 | 57046 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0035662 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 25 | 2018-04-25 | 74049 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0036580 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 29 | 2018-04-29 | 76108 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0042518 | 3rd Party | Customer Equipment | Customer Equipment | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2018-07-03 | 123603 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Normal
18-0043060 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 22 | 2018-05-22 | 91358 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
18-0047048 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2018-06-04 | 100567 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0059522 | Vegetation | Tree - fell into line | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2018-07-13 | 130642 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Burnedflashed
18-0068452 | Environmental/External | Fire, Forest/Grass | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 8 | 9 | 2018-08-09 | 152356 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer¦FailedFaulted
18-0068946 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 11 | 2018-08-11 | 153397 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0069938 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 15 | 2018-08-15 | 155857 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0074956 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2018 | Tier 3 - Extreme | Transformer only | 8 | 29 | 2018-08-29 | 165135 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
18-0076008 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2018-09-03 | 167532 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0077352 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2018-09-06 | 169640 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
18-0080726 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2018-09-18 | 176278 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0081445 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 19 | 2018-09-19 | 177690 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
18-0084010 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2018-09-26 | 182226 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0084833 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 29 | 2018-09-29 | 183780 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0089127 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2018-10-10 | 192503 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0090227 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2018-10-14 | 195071 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
18-0092525 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 10 | 20 | 2018-10-20 | 199473 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
18-0093952 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2018-10-24 | 201780 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0094297 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 10 | 25 | 2018-10-25 | 202295 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0097431 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2018-11-06 | 209772 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0098856 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 10 | 2018-11-10 | 213027 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0102160 | Equipment Failure/Involved | Overhead | Recloser | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2018-11-21 | 221189 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Recloser¦FailedFaulted
18-0102456 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2018-11-23 | 222470 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0102485 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2018-11-23 | 222485 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
18-0103247 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 224548 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0103572 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 225199 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0103952 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2018-11-27 | 225727 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0105274 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 229452 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0105330 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 229530 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
18-0111257 | Equipment Failure/Involved | Overhead | Insulator | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2018-12-31 | 250744 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Normal
19-0003480 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 1 | 1 | 2019-01-01 | 251649 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0007797 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2019-01-11 | 262958 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0008325 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2019-01-12 | 264036 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009444 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 266590 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0010147 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 268465 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0011525 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 275202 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
19-0014534 | Vegetation | Tree - branch fell on line | Customer Equipment | Normal | 2019 | Tier 3 - Extreme | Transformer only | 1 | 25 | 2019-01-25 | 281281 | Sus | N | Vegetation¦Treebranchfellonline¦CustomerEquipment¦Normal
19-0017551 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287858 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0017633 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2019-02-03 | 289103 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
19-0019162 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2019-02-06 | 294268 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019162 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2019-02-06 | 294268 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0019460 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2019-02-07 | 294994 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0019615 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2019-02-07 | 295331 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0020321 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2019-02-09 | 297005 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0021908 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 302894 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0023902 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 311741 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0024262 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2019-02-15 | 312684 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0026627 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2019-02-20 | 319878 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0028036 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 25 | 2019-02-25 | 323585 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0029021 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2019-02-27 | 327043 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0029130 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2019-02-27 | 327202 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
19-0031368 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2019-03-06 | 332935 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0035412 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2019-03-20 | 343716 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0036076 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2019-03-24 | 346225 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0038569 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2019-03-31 | 351126 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0038609 | Company Initiated | Operating error | Switch (OH) | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2019-03-31 | 351199 | Sus | N | CompanyInitiated¦Operatingerror¦Switch(OH)¦Normal
19-0045948 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 4 | 25 | 2019-04-25 | 367789 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
19-0049871 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2019-05-08 | 376086 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0053180 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 17 | 2019-05-17 | 383308 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0057790 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 26 | 2019-05-26 | 390767 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0061572 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 6 | 2 | 2019-06-02 | 395799 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0064281 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2019-06-07 | 400656 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
19-0065507 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2019-06-10 | 404332 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
19-0067779 | Company Initiated | Construction Activity/equip, company | Jumper | Arcing | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 14 | 2019-06-14 | 412393 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Arcing
19-0067979 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2019-06-14 | 412779 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0074191 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2019-07-03 | 440230 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0079398 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 19 | 2019-07-19 | 462462 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
19-0088578 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2019-08-15 | 514127 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0089745 | Equipment Failure/Involved | Underground | Conductor, Underground | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2019-08-20 | 524207 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Burnedflashed
19-0091861 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 24 | 2019-08-24 | 537939 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0096523 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2019-09-07 | 562205 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0096633 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 9 | 2019-09-09 | 562675 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0098520 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 12 | 2019-09-12 | 576553 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0102604 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 23 | 2019-09-23 | 607255 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
19-0102747 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2019-09-23 | 607987 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0114945 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 23 | 2019-10-23 | 677346 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0124139 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 13 | 2019-11-13 | 705681 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0125393 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2019-11-16 | 708222 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0129343 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 716727 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0129647 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 717249 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0129707 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 717630 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130370 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 721472 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0133147 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2019-12-04 | 729248 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0137820 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2019-12-24 | 749792 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0005272 | Equipment Failure/Involved | Fire, pole | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2020-01-05 | 755058 | Sus | N | EquipmentFailureInvolved¦Firepole¦CrossarmWood¦Brokenwireonground
20-0010276 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2020-01-16 | 763212 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
20-0010996 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2020-01-17 | 764957 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0014195 | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2020-01-27 | 771247 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Deteriorated
20-0019593 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782560 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0024409 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 2 | 20 | 2020-02-20 | 797375 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0024886 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2020-02-22 | 800557 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0029741 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2020-03-07 | 838006 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0032150 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 851523 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0034397 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 14 | 2020-03-14 | 859272 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0035033 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2020-03-21 | 861119 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
20-0035459 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2020-03-23 | 862543 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0036442 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2020-03-26 | 867596 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0043004 | Equipment Failure/Involved | Underground | Secondary | Broken | 2020 | Tier 2 - Elevated | Transformer only | 4 | 20 | 2020-04-20 | 898164 | Sus | N | EquipmentFailureInvolved¦Underground¦Secondary¦Broken
20-0048677 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2020-05-08 | 909863 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0050590 | Vegetation | Tree - fell into line | Secondary | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2020-05-15 | 914251 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Broken
20-0053634 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2020-05-23 | 920316 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
20-0053828 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 25 | 2020-05-25 | 920949 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0055972 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2020-05-30 | 926451 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0064019 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 945233 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0067038 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2020-07-01 | 955503 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0070960 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2020-07-12 | 962820 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0071010 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2020-07-12 | 962980 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0075438 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2020-07-23 | 970871 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0076085 | 3rd Party | Metallic Balloon | Conductor, Overhead | Arcing | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2020-07-26 | 972228 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Arcing
20-0086124 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2020-08-17 | 1015541 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0086546 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2020-08-18 | 1018095 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0086960 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2020-08-18 | 1020504 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Deteriorated
20-0091399 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2020-08-30 | 1040980 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
20-0107394 | Animal | Squirrel | Cutout, fuse holder | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2020-10-11 | 1115466 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
20-0113024 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1125785 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0128370 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 7 | 2020-12-07 | 1167256 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0130385 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2020-12-14 | 1184755 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0009700 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2021-01-18 | 1212113 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0009893 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1213268 | Sus | N | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
21-0010799 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1217159 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0011233 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1218160 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0011583 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214186 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013293 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2021-01-22 | 1221870 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013309 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 1 | 23 | 2021-01-23 | 1221893 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0014357 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 26 | 2021-01-26 | 1225677 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0015168 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1228299 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0018537 | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1242157 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround
21-0021060 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 2 | 2 | 2021-02-02 | 1246430 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
21-0024749 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 2 | 11 | 2021-02-11 | 1253084 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0025371 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 2 | 13 | 2021-02-13 | 1254442 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0027518 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 2 | 19 | 2021-02-19 | 1258077 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0029536 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2021-02-25 | 1261856 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0029774 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2021-02-25 | 1262624 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0030376 | 3rd Party | Vehicle | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 2 | 27 | 2021-02-27 | 1263985 | Sus | N | 3rdParty¦Vehicle¦Serviceconductor¦Brokenwireonground
21-0034823 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2021-03-10 | 1277567 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
21-0054163 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 28 | 2021-04-28 | 1335981 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0066594 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2021 | Tier 3 - Extreme | Transformer only | 5 | 26 | 2021-05-26 | 1359403 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
21-0073961 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2021 | Tier 3 - Extreme | Transformer only | 6 | 14 | 2021-06-14 | 1372830 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
21-0074839 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2021-06-15 | 1374830 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0076449 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2021-06-18 | 1378322 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0077271 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 6 | 21 | 2021-06-21 | 1381676 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
21-0081097 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2021-06-28 | 1387506 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0086227 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 7 | 2021-07-07 | 1394143 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0091965 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2021-07-19 | 1408346 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0092835 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 7 | 21 | 2021-07-21 | 1409660 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0100188 | Animal | Squirrel | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2021-08-05 | 1434514 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Broken
21-0101714 | 3rd Party | Metallic Balloon | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2021-08-08 | 1437364 | Sus | Y | 3rdParty¦MetallicBalloon¦ConductorOverhead¦Broken
21-0105835 | 3rd Party | Vehicle | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445184 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Normal
21-0106656 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 18 | 2021-08-18 | 1446988 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
21-0108826 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2021-08-24 | 1452288 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0115664 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transmission line | 9 | 10 | 2021-09-10 | 1467070 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0120709 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 21 | 2021-09-21 | 1477507 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0122893 | Equipment Failure/Involved | Underground | Switch (UG) | Leaking | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2021-09-28 | 1482827 | Sus | Y | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Leaking
21-0124131 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2021-09-30 | 1483835 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0124693 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2021-10-01 | 1484623 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
21-0136839 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512629 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0136890 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1517030 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0139426 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2021-10-28 | 1524374 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0142728 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 5 | 2021-11-05 | 1535588 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
21-0145578 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on object | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2021-11-15 | 1544363 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonobject
21-0149995 | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2021 | Tier 3 - Extreme | Transformer only | 11 | 23 | 2021-11-23 | 1553536 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed
21-0155600 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | 2021 | Tier 3 - Extreme | Transformer only | 12 | 7 | 2021-12-07 | 1561148 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Normal
21-0157087 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1566571 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0157617 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Transmission line | 12 | 13 | 2021-12-13 | 1568842 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0158726 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1574009 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0160636 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581708 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0161095 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585448 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0003623 | Company Initiated | Personnel, company | Transformer | Normal | 2022 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2022-01-19 | 1605063 | Sus | N | CompanyInitiated¦Personnelcompany¦Transformer¦Normal
22-0005111 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 1 | 2022-01-01 | 1591861 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005509 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2022-01-03 | 1593647 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
22-0008197 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2022-01-10 | 1599281 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken
22-0012761 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 1 | 21 | 2022-01-21 | 1607752 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Broken
22-0017171 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2022-02-01 | 1618237 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0019378 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2022-02-07 | 1622766 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0020046 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 2 | 8 | 2022-02-08 | 1623638 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0024827 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2022-02-22 | 1633434 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
22-0031526 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 9 | 2022-03-09 | 1645064 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0040705 | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 30 | 2022-03-30 | 1659668 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed
22-0040814 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 30 | 2022-03-30 | 1659699 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0043143 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 5 | 2022-04-05 | 1663718 | Sus | N | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0048357 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2022-04-14 | 1672549 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0051262 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2022-04-19 | 1676180 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0052221 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2022-04-20 | 1677758 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
22-0052788 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2022-04-21 | 1678511 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
22-0053604 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2022-04-23 | 1679798 | Sus | N | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
22-0053801 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2022-04-24 | 1680494 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0059915 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 9 | 2022-05-09 | 1692391 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0061740 | Equipment Failure/Involved | Electrical Overload | Transformer | Leaking | 2022 | Tier 2 - Elevated | Transformer only | 5 | 13 | 2022-05-13 | 1695186 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Leaking
22-0063638 | Animal | Other | Insulator | Burned/flashed | 2022 | Tier 2 - Elevated | Transmission line | 5 | 18 | 2022-05-18 | 1702290 | Sus | Y | Animal¦Other¦Insulator¦Burnedflashed
22-0064527 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 20 | 2022-05-20 | 1706026 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0064531 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2022-05-20 | 1706028 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0068880 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2022-06-01 | 1715759 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0068939 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 1 | 2022-06-01 | 1715779 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
22-0074238 | Equipment Failure/Involved | Substation | Other | Burned/flashed | 2022 | Tier 2 - Elevated | Transmission line | 6 | 14 | 2022-06-14 | 1731382 | Sus | Y | EquipmentFailureInvolved¦Substation¦Other¦Burnedflashed
22-0074798 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2022-06-15 | 1732417 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
22-0084301 | Equipment Failure/Involved | Overhead | Secondary | Bent or Twisted | 2022 | Tier 2 - Elevated | Transformer only | 7 | 12 | 2022-07-12 | 1754431 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦BentorTwisted
22-0086247 | 3rd Party | Aircraft | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 17 | 2022-07-17 | 1758367 | Sus | Y | 3rdParty¦Aircraft¦ConductorOverhead¦Brokenwireonground
22-0088948 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2022-07-23 | 1763805 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0089171 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 24 | 2022-07-24 | 1764543 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0091570 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2022-07-29 | 1768682 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0094540 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2022-08-06 | 1774683 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0102610 | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2022-08-26 | 1792554 | Sus | Y | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal
22-0109222 | Animal | Squirrel | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2022-09-12 | 1808997 | Sus | Y | Animal¦Squirrel¦Fuse¦BurnedOpen
22-0109362 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2022 | Tier 3 - Extreme | Transformer only | 9 | 12 | 2022-09-12 | 1809057 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
22-0109642 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 9 | 13 | 2022-09-13 | 1810005 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0115151 | Equipment Failure/Involved | Overhead | Secondary | Normal | 2022 | Tier 2 - Elevated | Transformer only | 9 | 27 | 2022-09-27 | 1822426 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal
22-0115829 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2022-09-28 | 1823462 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
22-0124368 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2022 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2022-10-24 | 1844402 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
22-0124449 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2022-10-24 | 1844651 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Burnedflashed
22-0124449 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2022-10-24 | 1844651 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Burnedflashed
22-0126691 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1850554 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0128206 | 3rd Party | Thrown Object | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Transmission line | 11 | 5 | 2022-11-05 | 1854690 | Sus | Y | 3rdParty¦ThrownObject¦ConductorOverhead¦Normal
22-0129321 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2022-11-08 | 1857780 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0129842 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2022-11-09 | 1859562 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0134713 | Company Initiated | Return Circuit Normal | Conductor, Underground | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2022-11-29 | 1871411 | Sus | Y | CompanyInitiated¦ReturnCircuitNormal¦ConductorUnderground¦Normal
22-0136622 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2022-12-05 | 1876296 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0141297 | Animal | Squirrel | Fuse | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 12 | 26 | 2022-12-26 | 1897353 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0002361 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2015-01-04 | 1159125 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0009735 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2015-02-05 | 1172923 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0010857 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1179665 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0012442 | Equipment Failure/Involved | Other | Crossarm, Wood |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1187778 | Sus | N | EquipmentFailureInvolved¦Other¦CrossarmWood¦
15-0014857 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 22 | 2015-02-22 | 1194042 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0032370 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230346 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0033557 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2015-05-12 | 1233279 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
15-0034015 | Equipment Failure/Involved | Overhead | Other | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2015-05-14 | 1234135 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Burnedflashed
15-0038501 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2015-06-04 | 1243643 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0038998 | Environmental/External | Lightning |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 5 | 2015-06-05 | 1244484 | Sus | Y | EnvironmentalExternal¦Lightning¦¦FailedFaulted
15-0041682 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2015-06-17 | 1252318 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
15-0046142 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 7 | 7 | 2015-07-07 | 1264513 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0046278 | Animal | Squirrel | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 8 | 2015-07-08 | 1264883 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
15-0052343 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 3 | 2015-08-03 | 1281982 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0062709 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2015-09-13 | 1310147 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0067107 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2015-10-01 | 1314895 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
15-0068826 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2015-10-08 | 1318579 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0071238 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324183 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0075576 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2015-11-04 | 1335250 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0077035 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2015-11-10 | 1338948 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0077872 | Equipment Failure/Involved | Overhead | Transformer | Burned Open | 2015 | Tier 2 - Elevated | Transformer only | 11 | 15 | 2015-11-15 | 1341579 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦BurnedOpen
15-0078080 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342684 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0079406 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2015-11-19 | 1345654 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0080201 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2015-11-23 | 1347524 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0082538 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1353029 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0084774 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361376 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0084942 | Unknown Cause | Patrol - found nothing | Sectionalizer | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361821 | Sus | N | UnknownCause¦Patrolfoundnothing¦Sectionalizer¦Normal
15-0085538 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2015-12-15 | 1364401 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0086473 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2015-12-21 | 1368011 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0003656 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2016-01-06 | 1379123 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0005472 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 14 | 2016-01-14 | 1384040 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0006609 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2016-01-19 | 1387796 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0007746 | Vegetation | Tree - branch fell on line | Jumper | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2016-01-23 | 1390655 | Sus | N | Vegetation¦Treebranchfellonline¦Jumper¦Broken
16-0008875 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2016-01-28 | 1393460 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0014307 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2016-02-19 | 1409526 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
16-0015040 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 23 | 2016-02-23 | 1411030 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0019021 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 7 | 2016-03-07 | 1424545 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0020774 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2016-03-12 | 1429385 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0022976 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2016-03-21 | 1435131 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0027321 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2016-04-08 | 1447153 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0028480 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2016-04-14 | 1450423 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0033308 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2016-05-02 | 1463384 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0034900 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 9 | 2016-05-09 | 1467036 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together
16-0035986 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 13 | 2016-05-13 | 1469469 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0036666 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 18 | 2016-05-18 | 1471733 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
16-0036666 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 18 | 2016-05-18 | 1471733 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
16-0038735 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 26 | 2016-05-26 | 1477350 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0050760 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2016-07-19 | 1512250 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0055522 | 3rd Party | Metallic Balloon | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2016-08-06 | 1522545 | Sus | Y | 3rdParty¦MetallicBalloon¦Fuse¦FailedFaulted
16-0061266 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2016-08-31 | 1534802 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0062848 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 9 | 7 | 2016-09-07 | 1537651 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
16-0069011 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2016-10-02 | 1551221 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0072617 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561763 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0076827 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 30 | 2016-10-30 | 1573376 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0086380 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 19 | 2016-12-19 | 1606766 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0086503 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2016-12-20 | 1607468 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0003586 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Bent or Twisted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1618309 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦BentorTwisted
17-0003662 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1618495 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005261 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624711 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007691 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1639100 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0008527 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637108 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013271 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1659272 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013614 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662998 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0013796 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1664016 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0014253 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664460 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0017071 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673416 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0017409 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2017-02-04 | 1674561 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018054 | Environmental/External | Flood/Erosion | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677342 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Brokenwireonground
17-0019934 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2017-02-10 | 1685107 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
17-0019942 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2017-02-10 | 1684909 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
17-0020654 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2017-02-13 | 1687131 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0021388 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 15 | 2017-02-15 | 1689547 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0022385 | Vegetation | Tree - fell into line | Secondary | Normal | 2017 | Tier 2 - Elevated | Transformer only | 2 | 17 | 2017-02-17 | 1695279 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Normal
17-0023319 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2017-02-18 | 1700697 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
17-0024008 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703782 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0025166 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707480 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0029874 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 3 | 10 | 2017-03-10 | 1723711 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0037941 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2017-04-07 | 1750166 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
17-0038229 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2017-04-08 | 1752315 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0039753 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2017-04-13 | 1756647 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0043269 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 27 | 2017-04-27 | 1768243 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0049094 | Animal | Squirrel | Cutout, fuse holder | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2017-05-19 | 1785233 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
17-0051173 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 27 | 2017-05-27 | 1792006 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0054164 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2017-06-10 | 1800952 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0054216 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2017-06-10 | 1801282 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0058398 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2017-06-24 | 1817442 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
17-0058441 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2017-06-25 | 1817620 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0058632 | Vegetation | Tree - fell into line | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 26 | 2017-06-26 | 1818212 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦FailedFaulted
17-0059935 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 1 | 2017-07-01 | 1821841 | Sus | Y | EquipmentFailureInvolved¦Firepole¦PoleWood¦Brokenwireonground
17-0060065 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 7 | 2 | 2017-07-02 | 1822321 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0066266 | Equipment Failure/Involved | Overhead | Transformer | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 7 | 28 | 2017-07-28 | 1841576 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Brokenwireonground
17-0074660 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2017-09-01 | 1864501 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0076718 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 7 | 2017-09-07 | 1872332 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0077803 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 11 | 2017-09-11 | 1875699 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0080854 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2017-09-21 | 1883684 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0085251 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1894047 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0085308 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893970 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0089392 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2017-10-21 | 1906908 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0089595 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2017-10-22 | 1907423 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0095980 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 17 | 2017-11-17 | 1924979 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0099905 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2017-12-05 | 1936230 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0101260 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2017-12-12 | 1940992 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0005897 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2018-01-12 | 7608 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0007609 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2018 | Tier 2 - Elevated | Transformer only | 1 | 20 | 2018-01-20 | 11378 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
18-0011183 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2018-02-02 | 18323 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0023755 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46305 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
18-0025256 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 49953 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0025271 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 49968 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
18-0034301 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2018-04-21 | 71087 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0036581 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2018-04-29 | 76101 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0040123 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2018-05-11 | 83515 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0060882 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 18 | 2018-07-18 | 134352 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
18-0062435 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 21 | 2018-07-21 | 137379 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0073109 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 8 | 24 | 2018-08-24 | 161499 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0077261 | Animal | Bird found | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2018-09-06 | 169465 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Together
18-0077351 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Transformer only | 9 | 6 | 2018-09-06 | 169654 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0077860 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 9 | 2018-09-09 | 170933 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦FailedFaulted
18-0087330 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2018-10-05 | 188984 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0094260 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2018-10-25 | 202326 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0097822 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 7 | 2018-11-07 | 210200 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0101476 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219114 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101706 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2018-11-21 | 219536 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0101745 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 21 | 2018-11-21 | 219506 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0106827 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 12 | 4 | 2018-12-04 | 233517 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0108992 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2018-12-13 | 239399 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0110157 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 12 | 20 | 2018-12-20 | 244703 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
19-0009300 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2019-01-15 | 266190 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0011078 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 274135 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011281 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 271317 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017469 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 288286 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
19-0020833 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298636 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0023075 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 307326 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0023187 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 309107 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Broken
19-0023470 | Vegetation | Tree - branch fell on line | Service conductor | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 2 | 14 | 2019-02-14 | 310082 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Brokenwireonground
19-0023623 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 309475 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0024730 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 16 | 2019-02-16 | 314744 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0026126 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 318962 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0026311 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2019-02-20 | 319303 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
19-0028206 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 323865 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0029693 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 328734 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0030238 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 3 | 2019-03-03 | 330017 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0035554 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 3 | 20 | 2019-03-20 | 344056 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0036288 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2019-03-23 | 345761 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
19-0038660 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 4 | 1 | 2019-04-01 | 351518 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
19-0048973 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2019-05-05 | 373992 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0052312 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2019-05-15 | 381296 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0058934 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2019-05-29 | 392464 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0061511 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2019-06-02 | 395731 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0061813 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2019-06-03 | 396208 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0069224 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 6 | 18 | 2019-06-18 | 419448 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0073204 | 3rd Party | Contact with High Voltage, 3rd party | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2019-06-28 | 434334 | Sus | Y | 3rdParty¦ContactwithHighVoltage3rdparty¦ConductorOverhead¦Brokenwireonground
19-0073933 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2019-07-02 | 439853 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0074967 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2019-07-06 | 441950 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0074992 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2019-07-07 | 442061 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0079508 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 20 | 2019-07-20 | 463994 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0079932 | Environmental/External | Fire, Forest/Grass | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2019-07-22 | 467735 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal
19-0082140 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 29 | 2019-07-29 | 474623 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0082505 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2019-07-30 | 475286 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0085019 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Transformer only | 8 | 6 | 2019-08-06 | 487569 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0094263 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2019-08-30 | 549275 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
19-0094389 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Transformer only | 8 | 31 | 2019-08-31 | 550183 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
19-0095031 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 9 | 3 | 2019-09-03 | 551961 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0098773 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 13 | 2019-09-13 | 577975 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0099241 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 15 | 2019-09-15 | 583289 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0102501 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2019-09-23 | 606374 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0105107 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 28 | 2019-09-28 | 628454 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0121703 | Vegetation | Tree - fell into line | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 6 | 2019-11-06 | 700489 | Sus | Y | Vegetation¦Treefellintoline¦Insulator¦Broken
19-0129702 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 717887 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0129798 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 719529 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0130227 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2019-11-26 | 719171 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131018 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2019-11-29 | 723372 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131568 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724857 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0134757 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2019-12-07 | 732557 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0012296 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2020-01-22 | 768000 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
20-0020805 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2020-02-11 | 789193 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
20-0032120 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2020-03-14 | 851495 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
20-0032391 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 15 | 2020-03-15 | 852615 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0032506 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 853545 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0038424 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 4 | 2020-04-04 | 882379 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0041519 | Animal | Squirrel | Fuse | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2020-04-15 | 895726 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
20-0048970 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2020-05-11 | 910890 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0049527 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 12 | 2020-05-12 | 912176 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0050204 | Equipment Failure/Involved | Overhead | Transformer | Arcing | 2020 | Tier 2 - Elevated | Transformer only | 5 | 14 | 2020-05-14 | 913551 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Arcing
20-0050251 | 3rd Party | Tree - cutting, 3rd party | Insulator | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 14 | 2020-05-14 | 913640 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Insulator¦Broken
20-0051755 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2020-05-19 | 917459 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
20-0052638 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 20 | 2020-05-20 | 918623 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
20-0062432 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2020-06-17 | 941511 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
20-0067633 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Transformer only | 7 | 2 | 2020-07-02 | 956671 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0071453 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 13 | 2020-07-13 | 963811 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0072599 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2020-07-16 | 965956 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
20-0080552 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2020-08-06 | 981054 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0084619 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transmission line | 8 | 16 | 2020-08-16 | 1009708 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0085860 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 17 | 2020-08-17 | 1016266 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
20-0085879 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1016898 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
20-0088811 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2020-08-22 | 1026870 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
20-0090282 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 20 | 2020-08-20 | 1032644 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0101938 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2020-09-27 | 1095691 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0104965 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2020-10-04 | 1110881 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0112102 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2020-10-23 | 1124050 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0112639 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1126322 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0116150 | Company Initiated | Construction Activity/equip, company | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2020-11-02 | 1134587 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦CrossarmWood¦Broken
20-0118258 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 11 | 7 | 2020-11-07 | 1138504 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0118592 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2020-11-08 | 1139806 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
20-0123976 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 11 | 22 | 2020-11-22 | 1152880 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0124964 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 25 | 2020-11-25 | 1154363 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0004919 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2021-01-04 | 1203748 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0010614 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214034 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011150 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2021-01-19 | 1216148 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013943 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224158 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0015155 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1228298 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016757 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1237122 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0016969 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1231452 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0017536 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 27 | 2021-01-27 | 1239640 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0020599 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2021-02-01 | 1245280 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0027890 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2021-02-21 | 1259062 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0029631 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 25 | 2021-02-25 | 1262369 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
21-0030872 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2021-03-01 | 1264905 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Burnedflashed
21-0036051 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2021-03-13 | 1280686 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0045528 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2021-04-06 | 1308390 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0048987 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2021 | Tier 3 - Extreme | Transformer only | 4 | 15 | 2021-04-15 | 1318027 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
21-0061923 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 15 | 2021-05-15 | 1350561 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0076907 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 6 | 21 | 2021-06-21 | 1380753 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
21-0078626 | Equipment Failure/Involved | Substation | Circuit Breaker | Malfunctioning | 2021 | Tier 2 - Elevated | Substation - Transmission | 6 | 24 | 2021-06-24 | 1383502 | Sus | Y | EquipmentFailureInvolved¦Substation¦CircuitBreaker¦Malfunctioning
21-0081469 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 29 | 2021-06-29 | 1387967 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0081508 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 6 | 29 | 2021-06-29 | 1388000 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0090835 | Vegetation | Tree - grew into line | Secondary | Normal | 2021 | Tier 2 - Elevated | Transformer only | 7 | 16 | 2021-07-16 | 1406133 | Sus | Y | Vegetation¦Treegrewintoline¦Secondary¦Normal
21-0096410 | Animal | Squirrel | Fuse | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2021-07-28 | 1417908 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
21-0101658 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2021-08-08 | 1437111 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0101861 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2021-08-09 | 1438046 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0104046 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 13 | 2021-08-13 | 1441752 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0105909 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445869 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0111939 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2021-09-01 | 1459635 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0115669 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2021-09-10 | 1467160 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
21-0116279 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2021-09-10 | 1468461 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
21-0128480 | Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492086 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Recloser¦Normal
21-0128675 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1492623 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0129980 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 12 | 2021-10-12 | 1495960 | Sus | Y | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonground
21-0136504 | Vegetation | Tree - branch fell on line | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2021-10-24 | 1508592 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Broken
21-0136548 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511490 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0140343 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2021-10-31 | 1526421 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0142245 | Vegetation | Tree - fell into line | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2021-11-04 | 1534717 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦FailedFaulted
21-0143578 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1537810 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0143740 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1538311 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0144170 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2021-11-09 | 1539038 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0151356 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2021-11-26 | 1554667 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0154456 | Equipment Failure/Involved | Overhead | Anchor or Guy | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2021-12-03 | 1558440 | Sus | N | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Deteriorated
21-0157092 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1565958 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0158919 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574897 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0159877 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2021-12-20 | 1578140 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160653 | Vegetation | Tree - fell into line | Transformer (OH) | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581870 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦Brokenwireonground
21-0160690 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582115 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0161312 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1584169 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161566 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588418 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0161799 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 30 | 2021-12-30 | 1589660 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
21-0161910 | Animal | Squirrel | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Transformer only | 12 | 30 | 2021-12-30 | 1590204 | Sus | N | Animal¦Squirrel¦PoleWood¦Burnedflashed
22-0005346 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1593277 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0012690 | Vegetation | Tree - fell into line | Anchor or Guy | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2022-01-21 | 1607656 | Sus | N | Vegetation¦Treefellintoline¦AnchororGuy¦Brokenwireonground
22-0014097 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2022-01-25 | 1611738 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0015120 | Animal | Squirrel | Insulator | Burned/flashed | 2022 | Tier 2 - Elevated | Substation - Distribution | 1 | 27 | 2022-01-27 | 1613968 | Sus | N | Animal¦Squirrel¦Insulator¦Burnedflashed
22-0017145 | Equipment Failure/Involved | Overhead | Other | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2022-02-01 | 1618165 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Normal
22-0017711 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2022-02-02 | 1619430 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0023630 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2022-02-17 | 1630199 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0024561 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2022-02-20 | 1632782 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0027109 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2022 | Tier 2 - Elevated | Transformer only | 2 | 26 | 2022-02-26 | 1638083 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
22-0027130 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 2 - Elevated | Transformer only | 2 | 26 | 2022-02-26 | 1638227 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0029166 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2022-03-03 | 1640972 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0030222 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2022-03-04 | 1642685 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0034893 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2022-03-16 | 1650168 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0037647 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2022-03-23 | 1654559 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0041370 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2022-03-31 | 1660573 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0044018 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2022 | Zone 1 - HHZ | Distribution Circuit | 4 | 7 | 2022-04-07 | 1665281 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
22-0045614 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2022-04-11 | 1668637 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0047442 | Vegetation | Tree - fell into line | Service conductor | Bent or Twisted | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2022-04-13 | 1671734 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦BentorTwisted
22-0047446 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2022-04-13 | 1671783 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0053740 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 23 | 2022-04-23 | 1680152 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0058457 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 5 | 5 | 2022-05-05 | 1689065 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0064926 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 22 | 2022-05-22 | 1707220 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0066243 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 5 | 25 | 2022-05-25 | 1709977 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Burnedflashed
22-0068109 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2022 | Tier 2 - Elevated | Transformer only | 5 | 31 | 2022-05-31 | 1714227 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
22-0068244 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2022-05-31 | 1714535 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0070683 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2022-06-06 | 1720801 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0076582 | Company Initiated | Operating error | Relay | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 21 | 2022-06-21 | 1736756 | Sus | Y | CompanyInitiated¦Operatingerror¦Relay¦Normal
22-0077917 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 23 | 2022-06-23 | 1740426 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
22-0082041 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 7 | 5 | 2022-07-05 | 1749315 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0082722 | Equipment Failure/Involved | Overhead | Capacitor | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 7 | 2022-07-07 | 1750623 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Capacitor¦FailedFaulted
22-0083230 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2022-07-08 | 1751451 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0085947 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 7 | 15 | 2022-07-15 | 1757119 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0086022 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2022 | Tier 3 - Extreme | Transformer only | 7 | 15 | 2022-07-15 | 1757338 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
22-0098291 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2022-08-16 | 1782517 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0103560 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2022-08-30 | 1794861 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Normal
22-0105801 | Animal | Squirrel | Cutout, fuse holder | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 4 | 2022-09-04 | 1799196 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
22-0113700 | Company Initiated | Personnel, company | Transformer | Normal | 2022 | Tier 2 - Elevated | Transformer only | 9 | 22 | 2022-09-22 | 1819067 | Sus | Y | CompanyInitiated¦Personnelcompany¦Transformer¦Normal
22-0113779 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 22 | 2022-09-22 | 1819333 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0115042 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 26 | 2022-09-26 | 1822173 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0122982 | Vegetation | Tree - branch fell on line | Jumper | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2022-10-19 | 1840738 | Sus | Y | Vegetation¦Treebranchfellonline¦Jumper¦Broken
22-0127311 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2022-11-03 | 1852173 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0128569 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 7 | 2022-11-07 | 1855955 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0130080 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2022-11-09 | 1859520 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0132714 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865663 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0134488 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2022 | Tier 2 - Elevated | Transformer only | 11 | 28 | 2022-11-28 | 1870475 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
22-0135377 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2022-12-01 | 1872601 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0137987 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 9 | 2022-12-09 | 1879966 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
22-0139089 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 11 | 2022-12-11 | 1886436 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0141323 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2022-12-26 | 1897508 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0009450 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2015-02-05 | 1172510 | Sus | N | EquipmentFailureInvolved¦Other¦ConnectororSplice(OH)¦Brokenwireonground
15-0010795 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1178673 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
15-0017938 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 7 | 2015-03-07 | 1200350 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0027020 | Equipment Failure/Involved | Other | Cutout, fuse holder | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2015-04-15 | 1220162 | Sus | N | EquipmentFailureInvolved¦Other¦Cutoutfuseholder¦Broken
15-0031293 | Animal | Bird found | Fuse | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2015-05-02 | 1228518 | Sus | Y | Animal¦Birdfound¦Fuse¦Normal
15-0032996 | Environmental/External | Lightning | Transformer (OH) | Normal | 2015 | Tier 3 - Extreme | Transformer only | 5 | 7 | 2015-05-07 | 1231764 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal
15-0039991 | Equipment Failure/Involved | Other | Conductor, Overhead | Broken | 2015 | Tier 2 - Elevated | Transformer only | 6 | 10 | 2015-06-10 | 1248207 | Sus | Y | EquipmentFailureInvolved¦Other¦ConductorOverhead¦Broken
15-0040021 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 10 | 2015-06-10 | 1248190 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0040024 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 6 | 10 | 2015-06-10 | 1248352 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
15-0040741 | Equipment Failure/Involved | Electrical Overload | Other | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 6 | 12 | 2015-06-12 | 1249902 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Other¦FailedFaulted
15-0044120 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 29 | 2015-06-29 | 1259023 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0049803 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2015-07-22 | 1275212 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
15-0053066 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2015-08-06 | 1283343 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0055696 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2015-08-17 | 1290631 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0058481 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2015-09-01 | 1297961 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0058481 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2015-09-01 | 1297961 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0058764 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2015-09-01 | 1298595 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
15-0061997 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 17 | 2015-09-17 | 1307885 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0066012 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2015-09-28 | 1312910 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0067714 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2015-10-03 | 1316376 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0067750 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 3 | 2015-10-03 | 1316227 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0067810 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2015-10-04 | 1316684 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0068530 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2015-10-07 | 1318019 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0071987 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 10 | 19 | 2015-10-19 | 1326356 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
15-0078273 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2015-11-16 | 1342941 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0082437 | Equipment Failure/Involved | Overhead | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352514 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦OnGround
15-0083939 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1356837 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0084989 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 13 | 2015-12-13 | 1362226 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0085066 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1362839 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0086506 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2015-12-21 | 1368197 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086783 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369545 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0087644 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2015-12-28 | 1373325 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0007105 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 1 | 21 | 2016-01-21 | 1389152 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
16-0009134 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Transformer only | 1 | 29 | 2016-01-29 | 1394032 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0009252 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2016-01-29 | 1394339 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0009356 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 31 | 2016-01-31 | 1394703 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0013392 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406951 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0013566 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407069 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0013615 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407847 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0013834 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406663 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
16-0017888 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 3 | 5 | 2016-03-05 | 1417745 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0018214 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1420964 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0019030 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 3 | 7 | 2016-03-07 | 1424443 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0019634 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2016-03-09 | 1425854 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
16-0019742 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2016 | Tier 2 - Elevated | Transformer only | 3 | 9 | 2016-03-09 | 1426108 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
16-0020476 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427929 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
16-0020914 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430003 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0022338 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2016-03-17 | 1433466 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0022491 | Equipment Failure/Involved | Overhead | Jumper | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2016-03-18 | 1433914 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦Broken
16-0023084 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2016 | Tier 2 - Elevated | Transformer only | 3 | 21 | 2016-03-21 | 1435524 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
16-0029269 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 18 | 2016-04-18 | 1452624 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0030803 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2016-04-22 | 1456157 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0032225 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 28 | 2016-04-28 | 1460648 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0036342 | Vegetation | Tree - fell into line | Transformer | On Ground | 2016 | Tier 3 - Extreme | Transformer only | 5 | 16 | 2016-05-16 | 1470697 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦OnGround
16-0043375 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2016 | Tier 2 - Elevated | Transformer only | 6 | 15 | 2016-06-15 | 1489128 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
16-0044286 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2016-06-18 | 1492042 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦FailedFaulted
16-0044286 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2016-06-18 | 1492042 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConnectororSplice(UG)¦FailedFaulted
16-0053603 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2016-07-29 | 1518576 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0057689 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2016 | Tier 3 - Extreme | Transformer only | 8 | 16 | 2016-08-16 | 1527377 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
16-0058179 | 3rd Party | Customer Equipment | Other | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 8 | 18 | 2016-08-18 | 1528223 | Sus | Y | 3rdParty¦CustomerEquipment¦Other¦FailedFaulted
16-0062240 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2016-09-03 | 1536318 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
16-0067100 | Unknown Cause | Patrol - found nothing |  | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2016-09-23 | 1546709 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦FailedFaulted
16-0068276 | Equipment Failure/Involved | Overhead | Secondary | Burned Open | 2016 | Tier 3 - Extreme | Transformer only | 9 | 28 | 2016-09-28 | 1549651 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen
16-0070025 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2016-10-06 | 1553754 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
16-0075877 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 27 | 2016-10-27 | 1570658 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0081208 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 20 | 2016-11-20 | 1585485 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
16-0083736 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2016-12-03 | 1593925 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Together
16-0085658 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602368 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0085800 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1603175 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
16-0086619 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2016-12-21 | 1608367 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0004980 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622900 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0005592 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626146 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0005600 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1627581 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005869 | Vegetation | Tree - fell into line | Transformer | Broken | 2017 | Tier 3 - Extreme | Transformer only | 1 | 8 | 2017-01-08 | 1628495 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Broken
17-0006207 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1630946 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006258 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2017-01-09 | 1631241 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006303 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1632222 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006503 | Environmental/External | Water | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632783 | Sus | N | EnvironmentalExternal¦Water¦PoleWood¦Brokenwireonground
17-0009835 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Bent or Twisted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1645889 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦BentorTwisted
17-0010352 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1647706 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0011474 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2017-01-20 | 1653762 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0011739 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1654540 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
17-0012757 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1658494 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0018308 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1678016 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019008 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1681812 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0019008 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1681812 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0019121 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682240 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0020354 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2017-02-11 | 1686206 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0022792 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698546 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0024156 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 20 | 2017-02-20 | 1705372 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0024836 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1706964 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0028546 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 5 | 2017-03-05 | 1720369 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0028601 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720602 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0028750 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720545 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0034655 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2017-03-29 | 1738218 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
17-0035249 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2017-03-30 | 1739821 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0036796 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 5 | 2017-04-05 | 1744823 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
17-0037345 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748026 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0037345 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748026 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0037721 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1749536 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0037945 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1750120 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0037971 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1746939 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0038177 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 8 | 2017-04-08 | 1752099 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0038311 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 8 | 2017-04-08 | 1752449 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0039920 | Environmental/External | Lightning | Transformer (OH) | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 13 | 2017-04-13 | 1756854 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal
17-0042081 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2017-04-22 | 1764577 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0051324 | Vegetation | Tree - fell into line | Conductor, Overhead | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2017-05-29 | 1792792 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Burnedflashed
17-0055575 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2017-06-15 | 1805352 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0055767 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 6 | 16 | 2017-06-16 | 1805862 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
17-0056185 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2017-06-18 | 1808181 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0057996 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2017-06-23 | 1815783 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0058266 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 6 | 24 | 2017-06-24 | 1816913 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0060198 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2017 | Tier 2 - Elevated | Transformer only | 7 | 3 | 2017-07-03 | 1822703 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
17-0072267 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2017-08-23 | 1857531 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0073115 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 8 | 26 | 2017-08-26 | 1860080 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0080928 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 9 | 22 | 2017-09-22 | 1883792 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0084572 | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 5 | 2017-10-05 | 1891597 | Sus | Y | 3rdParty¦CustomerEquipment¦CustomerEquipment¦Malfunctioning
17-0085320 | Environmental/External | Fire, Forest/Grass | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893948 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦FailedFaulted
17-0088299 | Environmental/External | Fire, Forest/Grass | Other | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1903332 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Other¦Brokenwireonground
17-0088895 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2017-10-20 | 1905095 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0089407 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2017-10-21 | 1906865 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0089820 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2017-10-23 | 1908338 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0095696 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2017-11-16 | 1924092 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0097547 | Vegetation | Tree - palm frond fell into line | Other | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 11 | 25 | 2017-11-25 | 1929130 | Sus | Y | Vegetation¦Treepalmfrondfellintoline¦Other¦FailedFaulted
17-0099046 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2017-12-01 | 1933632 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
17-0102134 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2017-12-16 | 1944954 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
17-0102285 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 17 | 2017-12-17 | 1946085 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0103502 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2017-12-28 | 1952460 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
18-0003705 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2018-01-04 | 2172 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
18-0007656 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2018-01-21 | 11555 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
18-0007845 | 3rd Party | Customer Equipment | Generator | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2018-01-22 | 11994 | Sus | N | 3rdParty¦CustomerEquipment¦Generator¦Normal
18-0010673 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 1 | 2018-02-01 | 17457 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0010981 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 2 | 1 | 2018-02-01 | 18048 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
18-0017478 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2018-02-26 | 32053 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0023315 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 45300 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0025769 | Environmental/External | Flood/Erosion | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 51194 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Broken
18-0025995 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2018-03-22 | 50853 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0026331 | Vegetation | Tree - fell into line | Crossarm, Steel | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2018-03-24 | 52760 | Sus | N | Vegetation¦Treefellintoline¦CrossarmSteel¦Broken
18-0028245 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 31 | 2018-03-31 | 57319 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0029961 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2018-04-06 | 60874 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0040487 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2018-05-12 | 84764 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0048801 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 8 | 2018-06-08 | 104260 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0050779 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 6 | 13 | 2018-06-13 | 108655 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0051736 | Animal | Bird found | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 17 | 2018-06-17 | 111330 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
18-0054123 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2018-06-24 | 117237 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0058909 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2018 | Tier 3 - Extreme | Transformer only | 7 | 11 | 2018-07-11 | 129245 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
18-0059381 | 3rd Party | Vehicle | Transformer (UG) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2018-07-12 | 130334 | Sus | Y | 3rdParty¦Vehicle¦Transformer(UG)¦Broken
18-0060387 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2018-07-16 | 133350 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0066172 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2018-07-26 | 147588 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0069495 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 14 | 2018-08-14 | 154892 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0073434 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2018-08-25 | 162306 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
18-0073462 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2018-08-26 | 162487 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
18-0080130 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2018-09-16 | 175290 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0084305 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2018-09-27 | 182870 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0084487 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2018-09-28 | 183306 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0085628 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2018-10-02 | 185934 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0090238 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 14 | 2018-10-14 | 195062 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
18-0093824 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2018-10-24 | 201543 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0098083 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Arcing | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 211074 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Arcing
18-0100807 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217815 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0101490 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 219148 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102383 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 22 | 2018-11-22 | 222244 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
18-0102389 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2018-11-22 | 222271 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0108127 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 12 | 8 | 2018-12-08 | 236453 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0108403 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2018-12-11 | 237598 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109469 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2018-12-16 | 241373 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0109583 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2018-12-17 | 241687 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
18-0109895 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 17 | 2018-12-17 | 243198 | Sus | N | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
19-0005414 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 256332 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009150 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2019-01-15 | 265871 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009899 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 266985 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010781 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 273271 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010808 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 267713 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010901 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 273614 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0010985 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 273858 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0013268 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2019 | Tier 2 - Elevated | Transformer only | 1 | 22 | 2019-01-22 | 279328 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
19-0017640 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2019-02-03 | 289350 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0018344 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 291597 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0018651 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 292939 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0021206 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2019-02-11 | 300235 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0021973 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 303078 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
19-0022960 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 307864 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0023047 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 307046 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023632 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 307795 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0024130 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2019-02-15 | 311791 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
19-0025299 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 316643 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025319 | 3rd Party | Vehicle |  | Normal | 2019 | Tier 3 - Extreme | Transformer only | 2 | 17 | 2019-02-17 | 316576 | Sus | N | 3rdParty¦Vehicle¦¦Normal
19-0025564 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 315657 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025566 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2019-02-18 | 317158 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025627 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 317648 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0028294 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 323901 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0028520 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 325116 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0031179 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2019-03-06 | 332244 | Sus | N | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦FailedFaulted
19-0031225 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2019-03-06 | 332166 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0032237 | Vegetation | Tree - fell into line | Insulator | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 9 | 2019-03-09 | 334833 | Sus | N | Vegetation¦Treefellintoline¦Insulator¦Normal
19-0032590 | Animal | Squirrel | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 11 | 2019-03-11 | 336067 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
19-0035586 | Environmental/External | Lightning | Transformer (OH) | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2019-03-20 | 344179 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Normal
19-0042282 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2019-04-14 | 360474 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0042374 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2019-04-15 | 360736 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0044622 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2019-04-20 | 364648 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
19-0049170 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2019-05-06 | 374422 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0050588 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Transmission line | 5 | 10 | 2019-05-10 | 377508 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0052505 | Animal | Other | Insulator | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2019-05-16 | 381850 | Sus | Y | Animal¦Other¦Insulator¦FailedFaulted
19-0060971 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2019-05-31 | 394808 | Sus | Y | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
19-0069596 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 19 | 2019-06-19 | 421045 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0072381 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | 2019 | Tier 2 - Elevated | Transmission line | 6 | 26 | 2019-06-26 | 430104 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Burnedflashed
19-0077036 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 13 | 2019-07-13 | 448239 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0079992 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2019-07-22 | 468273 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0084203 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 4 | 2019-08-04 | 482544 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0085415 | Equipment Failure/Involved | Underground | Secondary | Broken | 2019 | Tier 3 - Extreme | Transformer only | 8 | 7 | 2019-08-07 | 488464 | Sus | Y | EquipmentFailureInvolved¦Underground¦Secondary¦Broken
19-0091674 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2019-08-23 | 534995 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0095840 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2019-09-05 | 556909 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0096438 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2019-09-07 | 561733 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0107540 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 10 | 4 | 2019-10-04 | 642794 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed
19-0116808 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 683080 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0120030 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2019-11-01 | 697399 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131574 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 724948 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131636 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2019-11-30 | 725217 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0132826 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2019-12-03 | 728652 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0137544 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2019-12-22 | 748192 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0138202 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 30 | 2019-12-30 | 752226 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0138208 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on object | 2019 | Tier 2 - Elevated | Transformer only | 12 | 30 | 2019-12-30 | 752453 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonobject
20-0014706 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on object | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 28 | 2020-01-28 | 772054 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonobject
20-0018928 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 781001 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0019265 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 783635 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0030343 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2020-03-10 | 841629 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032457 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853033 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0033923 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 18 | 2020-03-18 | 858453 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0041430 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 4 | 15 | 2020-04-15 | 895590 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0043519 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 22 | 2020-04-22 | 899131 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0044538 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 25 | 2020-04-25 | 901377 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0058444 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 6 | 2020-06-06 | 932811 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0059190 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 9 | 2020-06-09 | 935034 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0063895 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned Open | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 944974 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦BurnedOpen
20-0070988 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2020-07-12 | 962813 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
20-0073156 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 17 | 2020-07-17 | 966732 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0073338 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Contaminated | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2020-07-18 | 967419 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Contaminated
20-0073921 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2020-07-20 | 968800 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
20-0074605 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2020-07-22 | 969807 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0080060 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 5 | 2020-08-05 | 979432 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0081324 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2020-08-08 | 987093 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0085292 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1014194 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0086527 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 18 | 2020-08-18 | 1018054 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0088239 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2020-08-20 | 1025918 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091333 | Environmental/External | Fire, Forest/Grass | Other | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2020-08-18 | 1040799 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Other¦Burnedflashed
20-0091442 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1041116 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0094733 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transmission line | 9 | 8 | 2020-09-08 | 1060287 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0097506 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 15 | 2020-09-15 | 1070672 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0099100 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2020-09-18 | 1081952 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
20-0105715 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 10 | 6 | 2020-10-06 | 1111822 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0114684 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 29 | 2020-10-29 | 1131362 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0115663 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 10 | 31 | 2020-10-31 | 1132908 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0117264 | Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 5 | 2020-11-05 | 1136329 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated
20-0119714 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2020-11-11 | 1142062 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
20-0124027 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2020-11-23 | 1152973 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
21-0004460 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Arcing | 2021 | Tier 2 - Elevated | Transformer only | 1 | 3 | 2021-01-03 | 1202771 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Arcing
21-0010615 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216261 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Broken
21-0011017 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1217235 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0011129 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1218002 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0013689 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223593 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0014229 | Vegetation | Tree - fell into line | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 25 | 2021-01-25 | 1225338 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Broken
21-0014252 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1225431 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0014598 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226065 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0014750 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226428 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
21-0016060 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1234914 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
21-0016658 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1235960 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0017465 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1237143 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
21-0019944 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1228711 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0021016 | Environmental/External | Lightning | Circuit Breaker | Burned/flashed | 2021 | Tier 2 - Elevated | Substation - Distribution | 2 | 2 | 2021-02-02 | 1246408 | Sus | N | EnvironmentalExternal¦Lightning¦CircuitBreaker¦Burnedflashed
21-0030497 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2021-03-01 | 1264346 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0034497 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2021-03-10 | 1277153 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
21-0037110 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2021-03-16 | 1284130 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0073554 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 12 | 2021-06-12 | 1371735 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0075221 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 16 | 2021-06-16 | 1375485 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦FailedFaulted
21-0076376 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2021-06-18 | 1378013 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
21-0079730 | Company Initiated | Construction Activity/equip, company | Insulator | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 10 | 2021-07-10 | 1397710 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Insulator¦Broken
21-0097947 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2021-07-31 | 1425780 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0098256 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 8 | 1 | 2021-08-01 | 1428239 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
21-0100991 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2021-08-06 | 1435762 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
21-0104840 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2021-08-16 | 1443568 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
21-0108577 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2021-08-24 | 1451423 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0109410 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2021-08-25 | 1453394 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0110473 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 27 | 2021-08-27 | 1455999 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0114954 | Vegetation | Tree - branch fell on line | Secondary | Broken | 2021 | Tier 3 - Extreme | Transformer only | 9 | 8 | 2021-09-08 | 1464957 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Broken
21-0119311 | Equipment Failure/Involved | Underground | Conductor, Underground | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2021-09-18 | 1474596 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Normal
21-0124785 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2021-10-01 | 1484789 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
21-0125261 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2021-10-03 | 1485813 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135346 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2021-10-22 | 1506311 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136541 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514164 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0137634 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1514732 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0137880 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2021-10-25 | 1520366 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0145198 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2021-11-13 | 1542168 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
21-0156761 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2021-12-12 | 1564980 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0156974 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1565814 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0158230 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 12 | 14 | 2021-12-14 | 1571075 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0158652 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573742 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0160335 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2021-12-23 | 1580201 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161404 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1587320 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161621 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 26 | 2021-12-26 | 1588786 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0162051 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1591013 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0005227 | Equipment Failure/Involved | Electrical Overload | Transformer | Normal | 2022 | Tier 3 - Extreme | Transformer only | 1 | 2 | 2022-01-02 | 1592563 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Normal
22-0006054 | Environmental/External | Ice or snow | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 4 | 2022-01-04 | 1594986 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Normal
22-0007615 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 27 | 2021-12-27 | 1598220 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0007744 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1598659 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
22-0012742 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 1 | 21 | 2022-01-21 | 1607668 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0013172 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2022-01-22 | 1609880 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0016012 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2022-01-29 | 1615766 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
22-0019577 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 2 | 7 | 2022-02-07 | 1622941 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0026055 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 2 | 23 | 2022-02-23 | 1635169 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0037804 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 24 | 2022-03-24 | 1654674 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
22-0043661 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2022-04-06 | 1664515 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0044445 | Company Initiated | Construction Activity/equip, company | Pole-Wood | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2022-04-08 | 1665907 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Normal
22-0045153 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2022-04-10 | 1667567 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0059512 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 5 | 8 | 2022-05-08 | 1691190 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0061972 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 5 | 13 | 2022-05-13 | 1695862 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083349 | Animal | Bird found | Transformer (OH) | Burned/flashed | 2022 | Tier 2 - Elevated | Transformer only | 7 | 8 | 2022-07-08 | 1751513 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Burnedflashed
22-0091566 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2022-07-29 | 1768636 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0092843 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 2 | 2022-08-02 | 1771356 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
22-0104292 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 8 | 31 | 2022-08-31 | 1796263 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
22-0108645 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 9 | 2022-09-09 | 1807281 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0109030 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2022-09-11 | 1808566 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
22-0113215 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2022-09-21 | 1818545 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0118370 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 2 - Elevated | Transformer only | 10 | 5 | 2022-10-05 | 1829515 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0121011 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 13 | 2022-10-13 | 1836348 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0121729 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2022-10-14 | 1837487 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0125308 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2022-10-27 | 1846854 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0125680 | Equipment Failure/Involved | Overhead | Bushing | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2022-10-28 | 1847679 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Bushing¦Broken
22-0128758 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 7 | 2022-11-07 | 1856526 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0130593 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 12 | 2022-11-12 | 1861320 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0133929 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 23 | 2022-11-23 | 1868539 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0138080 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1880205 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
22-0140334 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2022-12-16 | 1891089 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
22-0141349 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2022-12-26 | 1897601 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0141702 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1899313 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0142620 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1903504 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
22-0142780 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1905778 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0004380 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 13 | 2015-01-13 | 1163366 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0010865 | Equipment Failure/Involved | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 2 | 6 | 2015-02-06 | 1177565 | Sus | N | EquipmentFailureInvolved¦Lightning¦Transformer¦FailedFaulted
15-0012001 | Equipment Failure/Involved | Other | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1185688 | Sus | N | EquipmentFailureInvolved¦Other¦CrossarmWood¦Broken
15-0012166 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2015-02-09 | 1186529 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0012468 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2015-02-10 | 1187870 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0028043 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 4 | 21 | 2015-04-21 | 1222270 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0032314 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2015-05-06 | 1230077 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
15-0034739 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2015 | Tier 2 - Elevated | Transformer only | 5 | 17 | 2015-05-17 | 1235875 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
15-0038038 | 3rd Party | Metallic Balloon | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2015-06-02 | 1242889 | Sus | Y | 3rdParty¦MetallicBalloon¦Cutoutfuseholder¦FailedFaulted
15-0038947 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2015-06-05 | 1244476 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0048659 | Environmental/External | Lightning | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2015-07-19 | 1272239 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦OnGround
15-0049704 | Equipment Failure/Involved | Overhead | Other | Broken | 2015 | Tier 2 - Elevated | Transformer only | 7 | 21 | 2015-07-21 | 1275026 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
15-0051316 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2015-07-29 | 1279425 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0052163 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 2 | 2015-08-02 | 1281563 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0053861 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2015-08-08 | 1285319 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
15-0054282 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 11 | 2015-08-11 | 1286486 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0057882 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 28 | 2015-08-28 | 1295916 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0058212 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2015-08-29 | 1296926 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
15-0058268 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2015-08-30 | 1297331 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0061110 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2015-09-12 | 1305093 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0062378 | Animal | Squirrel |  | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 20 | 2015-09-20 | 1308825 | Sus | Y | Animal¦Squirrel¦¦FailedFaulted
15-0067723 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 4 | 2015-10-04 | 1316412 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0074639 | Animal | Other | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2015-11-02 | 1332649 | Sus | Y | Animal¦Other¦PoleWood¦Burnedflashed
15-0075068 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2015-11-02 | 1333930 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0081350 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2015-11-27 | 1349274 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0084912 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361112 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086380 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 21 | 2015-12-21 | 1367444 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0086484 | Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2015-12-21 | 1368065 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted
15-0087938 | Vegetation | Tree - fell into line | Conductor, Underground | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2015-12-31 | 1375257 | Sus | N | Vegetation¦Treefellintoline¦ConductorUnderground¦Normal
16-0004190 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2016-01-09 | 1380613 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0004963 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 13 | 2016-01-13 | 1382511 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0005804 | Animal | Squirrel | Transformer | Broken | 2016 | Tier 2 - Elevated | Transformer only | 1 | 16 | 2016-01-16 | 1385154 | Sus | N | Animal¦Squirrel¦Transformer¦Broken
16-0006463 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2016-01-19 | 1387521 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0007262 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2016-01-21 | 1389600 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
16-0009047 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 29 | 2016-01-29 | 1393800 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0012454 | Animal | Other | Connector or Splice (OH) | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2016-02-13 | 1402765 | Sus | N | Animal¦Other¦ConnectororSplice(OH)¦BurnedOpen
16-0012454 | Animal | Other | Connector or Splice (OH) | Burned Open | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2016-02-13 | 1402765 | Sus | N | Animal¦Other¦ConnectororSplice(OH)¦BurnedOpen
16-0012688 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 2 | 15 | 2016-02-15 | 1403779 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0013051 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2016-02-17 | 1404558 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0013975 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1407049 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0015482 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 25 | 2016-02-25 | 1411930 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0017566 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417281 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0018069 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420038 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
16-0018486 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1422179 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
16-0018540 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421589 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0020745 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2016-03-12 | 1429195 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0022695 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 3 - Extreme | Transformer only | 3 | 19 | 2016-03-19 | 1434355 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0022843 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2016-03-21 | 1434983 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0030827 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2016-04-22 | 1456029 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0031080 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457263 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0031086 | Vegetation | Tree - fell into line |  | Burned Open | 2016 | Tier 3 - Extreme | Transformer only | 4 | 24 | 2016-04-24 | 1457293 | Sus | N | Vegetation¦Treefellintoline¦¦BurnedOpen
16-0058779 | Equipment Failure/Involved | Overhead | Fuse | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2016-08-20 | 1529522 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Broken
16-0059191 | Vegetation | Tree - branch fell on line | Service conductor | Together | 2016 | Tier 3 - Extreme | Transformer only | 8 | 22 | 2016-08-22 | 1530591 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Together
16-0070850 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2016-10-10 | 1555698 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0071588 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2016-10-13 | 1557414 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
16-0073103 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2016-10-17 | 1563873 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0075192 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2016-10-24 | 1569054 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0076651 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2016-10-29 | 1572501 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0085739 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602775 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0087207 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 27 | 2016-12-27 | 1611957 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0003722 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1618621 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0003835 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2017-01-05 | 1619041 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0004893 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622436 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0005344 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1626017 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006476 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632548 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0006529 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632967 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006657 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1633280 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0007384 | Vegetation | Tree - grew into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638538 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Together
17-0007431 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638560 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007520 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2017-01-11 | 1638291 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007645 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1639703 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0007740 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 11 | 2017-01-11 | 1639707 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0009281 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 15 | 2017-01-15 | 1643959 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
17-0009585 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 1 | 17 | 2017-01-17 | 1645130 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0010519 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648144 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0011296 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652487 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0011592 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1652948 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0012094 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655373 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0013543 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1662215 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013827 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664091 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013958 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1664628 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017161 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673611 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018582 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1680184 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018588 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 7 | 2017-02-07 | 1679718 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0018900 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2017-02-07 | 1677779 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0019737 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1684188 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
17-0020456 | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 2 | 12 | 2017-02-12 | 1686655 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground
17-0022105 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1691433 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0022959 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 18 | 2017-02-18 | 1698868 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023133 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2017-02-18 | 1699396 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0025256 | Equipment Failure/Involved | Electrical Overload | Transformer | Arcing | 2017 | Tier 2 - Elevated | Transformer only | 2 | 21 | 2017-02-21 | 1708879 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦Arcing
17-0028932 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2017-03-06 | 1721160 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0030148 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2017-03-11 | 1725037 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0030224 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2017-03-12 | 1725338 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0030254 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2017-03-12 | 1725519 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Burnedflashed
17-0033866 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 3 | 26 | 2017-03-26 | 1735856 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0037253 | Equipment Failure/Involved | Overhead | Service conductor | Broken, wire on ground | 2017 | Tier 3 - Extreme | Transformer only | 4 | 6 | 2017-04-06 | 1745782 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Brokenwireonground
17-0037746 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748343 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0040381 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 4 | 14 | 2017-04-14 | 1758014 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0042170 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 4 | 22 | 2017-04-22 | 1765009 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Deteriorated
17-0052201 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 1 | 2017-06-01 | 1795086 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0059130 | Vegetation | Tree - fell into line | Transformer | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 6 | 28 | 2017-06-28 | 1819573 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Deteriorated
17-0069497 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2017-08-10 | 1850150 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0072302 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 8 | 23 | 2017-08-23 | 1857771 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0075546 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 3 | 2017-09-03 | 1868077 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0075846 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 4 | 2017-09-04 | 1869798 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0085419 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1894682 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0085690 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1895702 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086808 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899465 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
17-0087571 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1901420 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Broken
17-0088106 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Burned/flashed | 2017 | Tier 3 - Extreme | Transformer only | 10 | 8 | 2017-10-08 | 1902841 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Burnedflashed
17-0089120 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2017-10-20 | 1905904 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0093658 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2017-11-08 | 1918676 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0093878 | Vegetation | Tree - branch fell on line | Cutout, fuse holder | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2017-11-09 | 1919124 | Sus | Y | Vegetation¦Treebranchfellonline¦Cutoutfuseholder¦Broken
17-0097261 | 3rd Party | Vehicle | Anchor or Guy | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2017-11-22 | 1928267 | Sus | Y | 3rdParty¦Vehicle¦AnchororGuy¦Broken
17-0097464 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 25 | 2017-11-25 | 1928879 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
17-0099660 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 4 | 2017-12-04 | 1935014 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0102701 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2017-12-20 | 1948113 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0103575 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2017-12-29 | 1952839 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0005147 | Equipment Failure/Involved | Overhead | Anchor or Guy | Burned/flashed | 2018 | Tier 2 - Elevated | Transformer only | 1 | 10 | 2018-01-10 | 6246 | Sus | N | EquipmentFailureInvolved¦Overhead¦AnchororGuy¦Burnedflashed
18-0007212 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2018-01-18 | 10538 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0008707 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2018-01-24 | 13431 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0012642 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2018-02-08 | 21596 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0018437 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 34403 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0023610 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 3 | 16 | 2018-03-16 | 46301 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0023612 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46219 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0027911 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 30 | 2018-03-30 | 56331 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0030329 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2018-04-07 | 62270 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0034469 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 22 | 2018-04-22 | 71781 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0037649 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2018-05-02 | 78205 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0038506 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2018-05-05 | 79784 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0042475 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2018-05-19 | 89527 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0043900 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2018-05-24 | 93033 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0044166 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2018-05-24 | 93276 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0044188 | Equipment Failure/Involved | Overhead | Jumper | Arcing | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2018-05-24 | 93312 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦Arcing
18-0046868 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2018-06-04 | 100466 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
18-0049301 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2018-06-09 | 105474 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0057821 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 8 | 2018-07-08 | 126717 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0059719 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2018-07-14 | 131365 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0062252 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 21 | 2018-07-21 | 136950 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
18-0068921 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 8 | 11 | 2018-08-11 | 153285 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0069227 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 8 | 13 | 2018-08-13 | 154212 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0073020 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2018-08-23 | 161244 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
18-0077899 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 9 | 2018-09-09 | 170953 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0079951 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 15 | 2018-09-15 | 174683 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0080858 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2018-09-18 | 176582 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
18-0081525 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2018-09-20 | 177816 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0084694 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2018-09-28 | 183499 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
18-0084803 | 3rd Party | Vehicle | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 29 | 2018-09-29 | 183734 | Sus | Y | 3rdParty¦Vehicle¦Fuse¦FailedFaulted
18-0087564 | 3rd Party | Fire, house or bldg. | Service conductor | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 6 | 2018-10-06 | 189475 | Sus | Y | 3rdParty¦Firehouseorbldg¦Serviceconductor¦Burnedflashed
18-0094602 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2018-10-26 | 203003 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
18-0094872 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 28 | 2018-10-28 | 203698 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0100902 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217981 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104018 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2018-11-27 | 225942 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0105016 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228069 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
18-0105114 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 229055 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
18-0108887 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2018-12-12 | 238954 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0109272 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2018-12-14 | 240017 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0109501 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 12 | 16 | 2018-12-16 | 241561 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0109863 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 18 | 2018-12-18 | 243059 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
18-0110485 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2018-12-24 | 246296 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0004892 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 254615 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
19-0005246 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255922 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0005388 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 256757 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0009985 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 268772 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0010676 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 271320 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0011442 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 275008 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0011483 | Vegetation | Tree - branch fell on line | Jumper | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2019-01-17 | 272809 | Sus | N | Vegetation¦Treebranchfellonline¦Jumper¦Broken
19-0011497 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 275097 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0011520 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2019-01-18 | 275164 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0012608 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 20 | 2019-01-20 | 277496 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
19-0016689 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2019-02-01 | 285502 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0017187 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 2 | 2019-02-02 | 287528 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0018245 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 291292 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0018552 | Vegetation | Tree - grew into line | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292741 | Sus | N | Vegetation¦Treegrewintoline¦Fuse¦FailedFaulted
19-0019229 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 291206 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0019245 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 294451 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
19-0020138 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 296520 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020708 | Animal | Squirrel | Bushing | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2019-02-10 | 298948 | Sus | N | Animal¦Squirrel¦Bushing¦Normal
19-0023005 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 307076 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0023261 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 308968 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0024512 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 313801 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0024578 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 314158 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025123 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 315261 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025673 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2019-02-18 | 317676 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0025741 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 2 | 16 | 2019-02-16 | 313766 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0025840 | Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Transmission line | 2 | 19 | 2019-02-19 | 318307 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated
19-0026621 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 320089 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0028088 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 323838 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0028336 | Equipment Failure/Involved | Overhead | Transformer | Arcing | 2019 | Tier 3 - Extreme | Transformer only | 2 | 26 | 2019-02-26 | 324476 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Arcing
19-0028697 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 326235 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0029162 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2019-02-27 | 327352 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0029680 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 325305 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
19-0029711 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2019-03-01 | 328684 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0030554 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2019-03-04 | 330910 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
19-0037919 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 3 | 28 | 2019-03-28 | 349471 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0038013 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2019-03-28 | 349532 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0042317 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Transformer only | 4 | 14 | 2019-04-14 | 360530 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0054008 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 5 | 19 | 2019-05-19 | 384976 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0056876 | Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 24 | 2019-05-24 | 389504 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated
19-0057559 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2019-05-25 | 389956 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0057976 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 27 | 2019-05-27 | 391101 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0061473 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2019-06-02 | 395641 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0063015 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2019-06-05 | 398149 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0065120 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 10 | 2019-06-10 | 403185 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0069339 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2019-06-18 | 420154 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Leaking
19-0074968 | Equipment Failure/Involved | Fire, pole | Connector or Splice (OH) | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2019-07-06 | 441993 | Sus | Y | EquipmentFailureInvolved¦Firepole¦ConnectororSplice(OH)¦Burnedflashed
19-0086646 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 10 | 2019-08-10 | 501726 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
19-0088029 | Equipment Failure/Involved | Overhead |  | Broken | 2019 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2019-08-14 | 510987 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦Broken
19-0089501 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2019-08-19 | 523008 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0091837 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 24 | 2019-08-24 | 537870 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0094520 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2019-09-02 | 550703 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0094677 | Animal | Squirrel | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 3 | 2019-09-03 | 551150 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
19-0099931 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2019-09-16 | 585542 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0103378 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 25 | 2019-09-25 | 612875 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0103835 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2019-09-25 | 615448 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
19-0108040 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 6 | 2019-10-06 | 645545 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131012 | Company Initiated | Improper Construction | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2019-11-29 | 723286 | Sus | Y | CompanyInitiated¦ImproperConstruction¦ConductorOverhead¦Together
19-0131139 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2019-11-29 | 723872 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0131911 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2019-12-01 | 725744 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0136154 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2019-12-12 | 737143 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
19-0136411 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2019-12-13 | 738331 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0137697 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2019 | Tier 2 - Elevated | Transformer only | 12 | 23 | 2019-12-23 | 749150 | Sus | N | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
20-0012075 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2020-01-22 | 767638 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0016680 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2020-02-03 | 776816 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0019271 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 784184 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0024406 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 20 | 2020-02-20 | 797317 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0026282 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2020-02-26 | 813294 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0033294 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2020-03-17 | 856544 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0034570 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 20 | 2020-03-20 | 859489 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0038289 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 3 | 2020-04-03 | 881513 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0043860 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 4 | 22 | 2020-04-22 | 899693 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0048357 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2020-05-08 | 909339 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
20-0050967 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2020-05-17 | 915040 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0051582 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Transmission line | 5 | 18 | 2020-05-18 | 917215 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0058070 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2020-06-05 | 931681 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0068351 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 4 | 2020-07-04 | 957710 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0071491 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2020-07-13 | 963979 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0071491 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 13 | 2020-07-13 | 963979 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
20-0075114 | Animal | Squirrel | Fuse | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2020-07-23 | 970421 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
20-0084931 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2020-08-15 | 1012710 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
20-0090481 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1033384 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
20-0094354 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 7 | 2020-09-07 | 1058591 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0094971 | 3rd Party | Customer Equipment | Secondary | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2020-09-08 | 1060879 | Sus | Y | 3rdParty¦CustomerEquipment¦Secondary¦Burnedflashed
20-0096890 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2020-09-12 | 1067158 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0102316 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2020-09-28 | 1096137 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0109082 | Company Initiated | Construction Activity/equip, company | Jumper | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2020-10-15 | 1118377 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦Jumper¦Burnedflashed
20-0112836 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2020-10-25 | 1126146 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0114035 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 27 | 2020-10-27 | 1130239 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
20-0116713 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 3 | 2020-11-03 | 1135349 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0117302 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 5 | 2020-11-05 | 1136493 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
20-0119622 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2020-11-11 | 1141628 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0132076 | Equipment Failure/Involved | Overhead | Bushing | Burned/flashed | 2020 | Tier 2 - Elevated | Transformer only | 12 | 28 | 2020-12-28 | 1200327 | Sus | N | EquipmentFailureInvolved¦Overhead¦Bushing¦Burnedflashed
20-0132167 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2020 | Tier 2 - Elevated | Transformer only | 12 | 29 | 2020-12-29 | 1200626 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
21-0009488 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 1 | 17 | 2021-01-17 | 1211788 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0010111 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214339 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0010121 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214423 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0012877 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 1 | 22 | 2021-01-22 | 1221336 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013745 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223605 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0013826 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223926 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0013929 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1224346 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0014715 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226409 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0014994 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1228079 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0016557 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 27 | 2021-01-27 | 1236411 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0019941 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 31 | 2021-01-31 | 1243741 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0021031 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1246401 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0021853 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 2 | 4 | 2021-02-04 | 1247750 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0023431 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2021-02-09 | 1251257 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0023558 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 2 | 9 | 2021-02-09 | 1251477 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0023975 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2021 | Tier 2 - Elevated | Transformer only | 2 | 10 | 2021-02-10 | 1252300 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
21-0024513 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2021-02-11 | 1253049 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0025106 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2021-02-12 | 1253863 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0025205 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2021-02-12 | 1254095 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0029061 | Company Initiated | Construction Activity/equip, company | Fuse | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261133 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Normal
21-0033043 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2021-03-05 | 1270544 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0033994 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 9 | 2021-03-09 | 1274769 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0037152 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2021-03-16 | 1285012 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0040580 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 24 | 2021-03-24 | 1296129 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0047839 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2021-04-13 | 1314238 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0049081 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 15 | 2021-04-15 | 1318287 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0055702 | Animal | Bird found | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2021-05-01 | 1338404 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Together
21-0056564 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 4 | 2021-05-04 | 1340425 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
21-0058922 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2021-05-08 | 1344159 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0075348 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 17 | 2021-06-17 | 1375823 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0088055 | Equipment Failure/Involved | Overhead | Switch (OH) | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2021-07-12 | 1402513 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦Broken
21-0089802 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 14 | 2021-07-14 | 1404760 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0092037 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2021-07-19 | 1408507 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0099376 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2021-08-03 | 1430091 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0107816 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 8 | 21 | 2021-08-21 | 1449848 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0107886 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 22 | 2021-08-22 | 1450042 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0109898 | Equipment Failure/Involved | Underground | Transformer | Broken | 2021 | Tier 2 - Elevated | Transformer only | 8 | 26 | 2021-08-26 | 1454914 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦Broken
21-0110250 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 27 | 2021-08-27 | 1455491 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0111349 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 30 | 2021-08-30 | 1458376 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0123392 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2021-09-28 | 1482720 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0128214 | Animal | Squirrel | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 10 | 9 | 2021-10-09 | 1491061 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
21-0129056 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2021-10-11 | 1493864 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0132067 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2021-10-17 | 1499622 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0134859 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2021-10-22 | 1505284 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136337 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512133 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0136665 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1515601 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0139942 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 3 - Extreme | Transformer only | 10 | 29 | 2021-10-29 | 1525351 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0141254 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2021-11-02 | 1531859 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0142443 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2021-11-04 | 1535015 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Broken
21-0143629 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1538170 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0149380 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2021-11-22 | 1552893 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0154544 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 12 | 3 | 2021-12-03 | 1558423 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
21-0155509 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2021-12-06 | 1560746 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0158069 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569827 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158076 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2021-12-14 | 1569550 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158815 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574370 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160213 | Equipment Failure/Involved | Fire, pole | Pole-Wood | Burned/flashed | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2021-12-23 | 1579480 | Sus | N | EquipmentFailureInvolved¦Firepole¦PoleWood¦Burnedflashed
21-0160232 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2021-12-23 | 1579546 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0160662 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 25 | 2021-12-25 | 1581865 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0160807 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582698 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0161562 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588061 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161577 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588389 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0005203 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2022-01-02 | 1592456 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
22-0006530 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2022-01-05 | 1595811 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0008585 | Vegetation | Tree - fell into line | Fuse | Burned Open | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 11 | 2022-01-11 | 1600221 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦BurnedOpen
22-0010709 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2022-01-18 | 1604497 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
22-0028446 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2022-03-02 | 1640210 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0036838 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2022-03-22 | 1653504 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0037352 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2022-03-23 | 1654221 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0042514 | Equipment Failure/Involved | Overhead |  | Burned Open | 2022 | Tier 3 - Extreme | Transformer only | 4 | 4 | 2022-04-04 | 1662760 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦BurnedOpen
22-0045520 | Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2022-04-11 | 1668622 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted
22-0052447 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 21 | 2022-04-21 | 1678012 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0056612 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | 2022 | Tier 2 - Elevated | Transformer only | 5 | 1 | 2022-05-01 | 1685842 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Arcing
22-0059365 | 3rd Party | Kite | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2022-05-07 | 1690894 | Sus | Y | 3rdParty¦Kite¦ConductorOverhead¦Normal
22-0064642 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 20 | 2022-05-20 | 1706096 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0067749 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2022-05-28 | 1712989 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0073926 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2022-06-14 | 1730711 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0078701 | Animal | Squirrel | Switch (OH) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 26 | 2022-06-26 | 1742473 | Sus | Y | Animal¦Squirrel¦Switch(OH)¦Normal
22-0090989 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2022-07-28 | 1767482 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0091347 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Transformer only | 7 | 29 | 2022-07-29 | 1768157 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0095652 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 10 | 2022-08-10 | 1777455 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0102124 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2022-08-25 | 1791731 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0111541 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 18 | 2022-09-18 | 1813679 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0113595 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 9 | 22 | 2022-09-22 | 1818853 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0113715 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 9 | 22 | 2022-09-22 | 1819106 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0115073 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 27 | 2022-09-27 | 1822246 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
22-0121231 | Company Initiated | Personnel, company | Jumper | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 13 | 2022-10-13 | 1836671 | Sus | Y | CompanyInitiated¦Personnelcompany¦Jumper¦Normal
22-0123396 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 20 | 2022-10-20 | 1841703 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0126724 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1850301 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0127065 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2022-11-02 | 1851398 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0129424 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2022-11-09 | 1858627 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0129631 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 11 | 9 | 2022-11-09 | 1859125 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
22-0139965 | 3rd Party | Vehicle | Anchor or Guy | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2022-12-14 | 1889437 | Sus | N | 3rdParty¦Vehicle¦AnchororGuy¦Normal
22-0141616 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2022-12-27 | 1898684 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0004056 | Equipment Failure/Involved | Other | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 1 | 12 | 2015-01-12 | 1162755 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦FailedFaulted
15-0008971 | Equipment Failure/Involved | Other | Secondary | Broken | 2015 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2015-02-03 | 1171556 | Sus | N | EquipmentFailureInvolved¦Other¦Secondary¦Broken
15-0016520 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2015-03-01 | 1197865 | Sus | N | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
15-0034669 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 5 | 16 | 2015-05-16 | 1235646 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0039059 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 6 | 2015-06-06 | 1244902 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0040269 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2015-06-11 | 1248954 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
15-0040948 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2015-06-14 | 1250834 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0045408 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2015-07-03 | 1262546 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0050486 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 25 | 2015-07-25 | 1276972 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0057121 | Company Initiated | Operating error | Transformer Power | Normal | 2015 | Tier 3 - Extreme | Substation - Transmission | 8 | 25 | 2015-08-25 | 1294126 | Sus | Y | CompanyInitiated¦Operatingerror¦TransformerPower¦Normal
15-0059602 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 9 | 6 | 2015-09-06 | 1300996 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0061325 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 14 | 2015-09-14 | 1305442 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0071338 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324064 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0071348 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 17 | 2015-10-17 | 1324429 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0072822 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 10 | 22 | 2015-10-22 | 1327957 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0073546 | Environmental/External | Lightning | Transformer | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 27 | 2015-10-27 | 1329678 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦Broken
15-0077938 | Environmental/External | Lightning | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342001 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Brokenwireonground
15-0082524 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352861 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0082926 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Transformer only | 12 | 5 | 2015-12-05 | 1354207 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083769 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 10 | 2015-12-10 | 1356827 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0084498 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1359859 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0085196 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1362244 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086801 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369688 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0086815 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369521 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0086918 | Equipment Failure/Involved | Overhead | Secondary |  | 2015 | Tier 2 - Elevated | Transformer only | 12 | 23 | 2015-12-23 | 1370073 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦
16-0006203 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2016-01-19 | 1386681 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0008263 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2016 | Tier 2 - Elevated | Transformer only | 1 | 26 | 2016-01-26 | 1392183 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
16-0009262 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 30 | 2016-01-30 | 1394341 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0011257 | 3rd Party | Vehicle | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 2 | 8 | 2016-02-08 | 1400098 | Sus | N | 3rdParty¦Vehicle¦Transformer(OH)¦Broken
16-0014537 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2016-02-21 | 1409996 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0017746 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417948 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0017826 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1417227 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0019655 | 3rd Party | Vandalism | Circuit Breaker | Normal | 2016 | Tier 2 - Elevated | Substation - Distribution | 3 | 9 | 2016-03-09 | 1425840 | Sus | N | 3rdParty¦Vandalism¦CircuitBreaker¦Normal
16-0022331 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2016-03-17 | 1433396 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0024145 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2016-03-26 | 1438890 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0024186 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2016-03-26 | 1439111 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0028730 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 14 | 2016-04-14 | 1450782 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0030473 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 22 | 2016-04-22 | 1455494 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
16-0031132 | Environmental/External | Lightning | Fuse | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457440 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦Normal
16-0032757 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 29 | 2016-04-29 | 1461840 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0033052 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 1 | 2016-05-01 | 1462722 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0033056 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 5 | 1 | 2016-05-01 | 1462731 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0037678 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 22 | 2016-05-22 | 1474777 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0038446 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2016-05-25 | 1476631 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
16-0040353 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 6 | 1 | 2016-06-01 | 1480991 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0045212 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2016-06-22 | 1494395 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0046843 | Equipment Failure/Involved | Overhead | Switch | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2016-09-01 | 1535314 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Switch¦FailedFaulted
16-0053756 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2016-07-29 | 1518770 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0053970 | Environmental/External | Fire, Forest/Grass | Fuse | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2016-07-31 | 1519526 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Fuse¦Normal
16-0055425 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 5 | 2016-08-05 | 1522230 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0060101 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 25 | 2016-08-25 | 1532234 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0063425 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 9 | 2016-09-09 | 1538852 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Brokenwireonground
16-0069159 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2016-10-03 | 1552235 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
16-0070965 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 10 | 2016-10-10 | 1556018 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
16-0071258 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2016 | Tier 2 - Elevated | Transformer only | 10 | 11 | 2016-10-11 | 1556714 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
16-0071865 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2016-10-14 | 1558200 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0073695 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 18 | 2016-10-18 | 1565388 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0074101 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2016-10-19 | 1566010 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0074834 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 23 | 2016-10-23 | 1567890 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0075153 | Vegetation | Tree - fell into line | Other | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2016-10-24 | 1568803 | Sus | Y | Vegetation¦Treefellintoline¦Other¦Normal
16-0076208 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 28 | 2016-10-28 | 1571369 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
16-0076875 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2016-10-30 | 1573483 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0079396 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2016-11-11 | 1579825 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0080378 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2016-11-16 | 1582516 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0082462 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 27 | 2016-11-27 | 1589982 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
16-0083747 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2016-12-03 | 1593935 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0085506 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 14 | 2016-12-14 | 1601564 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0086591 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 12 | 20 | 2016-12-20 | 1608126 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0003396 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2017-01-04 | 1617529 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0004977 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623186 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005157 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624846 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005290 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625554 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0005607 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628653 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0005774 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1629067 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
17-0005784 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1628527 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0005890 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2017-01-09 | 1630127 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0006682 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1633520 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
17-0007467 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1636324 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0010451 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2017-01-18 | 1648443 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0012030 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655461 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0012068 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655732 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0012099 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 21 | 2017-01-21 | 1655474 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0013057 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660436 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0013185 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1659270 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013704 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662774 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0014309 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2017-01-24 | 1665716 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0014334 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2017-01-23 | 1664970 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
17-0014457 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2017 | Tier 2 - Elevated | Transformer only | 1 | 24 | 2017-01-24 | 1665874 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
17-0016472 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 1 | 31 | 2017-01-31 | 1671619 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0019978 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 10 | 2017-02-10 | 1685116 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0020779 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2017-02-13 | 1687764 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0023754 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1701824 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0023863 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703263 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0024082 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705858 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0024680 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1704608 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
17-0024833 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1706817 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0024871 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707398 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0024912 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707611 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0026902 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2017-02-26 | 1714612 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0027069 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Transformer only | 2 | 27 | 2017-02-27 | 1714864 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0028341 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 4 | 2017-03-04 | 1719397 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0028424 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2017-03-05 | 1719728 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonobject
17-0032114 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2017-03-20 | 1731253 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0032965 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 3 | 22 | 2017-03-22 | 1733383 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0037315 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1746543 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0037336 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1745886 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0043546 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 4 | 28 | 2017-04-28 | 1769093 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
17-0047162 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2017-05-11 | 1779872 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0048154 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2017-05-16 | 1782867 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
17-0049280 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 5 | 19 | 2017-05-19 | 1785802 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0054430 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2017-06-11 | 1802186 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
17-0055361 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 15 | 2017-06-15 | 1804829 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0058949 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 27 | 2017-06-27 | 1819188 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0062342 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2017-07-12 | 1829829 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0063248 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 16 | 2017-07-16 | 1832770 | Sus | Y | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Brokenwireonground
17-0063703 | 3rd Party | Dig in, 3rd party | Connector or Splice (OH) | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 18 | 2017-07-18 | 1835006 | Sus | Y | 3rdParty¦Digin3rdparty¦ConnectororSplice(OH)¦Broken
17-0067859 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 3 | 2017-08-03 | 1846066 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0073631 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 8 | 28 | 2017-08-28 | 1861861 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0075098 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 2 | 2017-09-02 | 1866059 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer(OH)¦Broken
17-0075354 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 9 | 2 | 2017-09-02 | 1867429 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0079692 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2017-09-18 | 1880935 | Sus | Y | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Normal
17-0080867 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Transformer only | 9 | 22 | 2017-09-22 | 1883757 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0085450 | Environmental/External | Fire, Forest/Grass | Pole - Tower, steel | Broken | 2017 | Tier 2 - Elevated | Transmission line | 10 | 9 | 2017-10-09 | 1896001 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleTowersteel¦Broken
17-0085803 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1897055 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0086349 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2017-10-11 | 1898511 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0086846 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899532 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0088687 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 13 | 2017-10-13 | 1904404 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0093764 | Equipment Failure/Involved | Fire, pole | Conductor, Overhead | Arcing | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2017-11-09 | 1919132 | Sus | Y | EquipmentFailureInvolved¦Firepole¦ConductorOverhead¦Arcing
17-0094359 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2017-11-10 | 1920348 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0099652 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2017-12-04 | 1934989 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0099874 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 12 | 5 | 2017-12-05 | 1936212 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0102040 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2017-12-16 | 1944335 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0102228 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2017-12-16 | 1945873 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0102798 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2017-12-20 | 1948551 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0003974 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2018-01-06 | 3054 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0007685 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 1 | 21 | 2018-01-21 | 11653 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0009105 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2018-01-25 | 14060 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0011263 | Animal | Bird found | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 3 | 2018-02-03 | 18613 | Sus | N | Animal¦Birdfound¦Transformer(OH)¦Normal
18-0019426 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2018-03-03 | 37454 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0023544 | Vegetation | Tree - fell into line | Service conductor | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2018-03-16 | 46005 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
18-0023945 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 18 | 2018-03-18 | 47462 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0025983 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 23 | 2018-03-23 | 51960 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0028472 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2018-04-02 | 58019 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
18-0031454 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2018-04-11 | 64923 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
18-0036649 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 29 | 2018-04-29 | 76336 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0039984 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2018-05-10 | 83164 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0045630 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2018-05-30 | 96680 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
18-0050200 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 6 | 12 | 2018-06-12 | 107328 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦FailedFaulted
18-0058129 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2018-07-09 | 127639 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0065682 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2018-07-29 | 146496 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0068482 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2018-07-26 | 152555 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Normal
18-0078779 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2018-09-11 | 172700 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
18-0091146 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2018-10-16 | 196932 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
18-0091146 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2018-10-16 | 196932 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
18-0091963 | Animal | Bird found | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 18 | 2018-10-18 | 198296 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0094889 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 28 | 2018-10-28 | 203653 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0102451 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 22 | 2018-11-22 | 222445 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0106035 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2018-12-01 | 231401 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0106155 | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 231953 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Normal
18-0107706 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2018-12-06 | 235239 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0109508 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2018-12-16 | 241646 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0110620 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2018-12-25 | 246960 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0110826 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2018-12-27 | 248070 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
19-0004905 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2019-01-05 | 254726 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0005101 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255144 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0008794 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 14 | 2019-01-14 | 265169 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0009280 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2019-01-15 | 266083 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0010115 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 267196 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0012083 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 3 - Extreme | Transformer only | 1 | 19 | 2019-01-19 | 276528 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0012704 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2019-01-20 | 277662 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0012901 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 1 | 21 | 2019-01-21 | 278509 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0016872 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 286107 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0017776 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 289480 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0017867 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289879 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0018351 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 292106 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0018428 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 292453 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018959 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 292665 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018963 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2019-02-06 | 293848 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0019090 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2019-02-06 | 294114 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0022339 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 304780 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0023199 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 304545 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
19-0023803 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2019-02-15 | 311123 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0023817 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 14 | 2019-02-14 | 310190 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
19-0024550 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 314409 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0025073 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 315506 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0025139 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 315866 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025699 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 318005 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
19-0028271 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 324271 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028629 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 26 | 2019-02-26 | 325351 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0028724 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325565 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0029276 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 28 | 2019-02-28 | 327742 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0030273 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | 2019 | Tier 2 - Elevated | Transformer only | 3 | 3 | 2019-03-03 | 330116 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing
19-0033222 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2019-03-12 | 337367 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0033975 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | 2019 | Tier 3 - Extreme | Transmission line | 3 | 14 | 2019-03-14 | 339589 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed
19-0037535 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2019-03-27 | 348654 | Sus | N | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
19-0037733 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 28 | 2019-03-28 | 349088 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0045853 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 4 | 24 | 2019-04-24 | 367676 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
19-0047778 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 3 - Extreme | Transformer only | 5 | 1 | 2019-05-01 | 371337 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0047851 | 3rd Party | Customer Equipment | Metering Equipment | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2019-05-01 | 371654 | Sus | Y | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Normal
19-0048831 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 4 | 2019-05-04 | 373510 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0052593 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2019-05-16 | 381818 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0052624 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 16 | 2019-05-16 | 382110 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0052883 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 16 | 2019-05-16 | 382697 | Sus | Y | Vegetation¦Treebranchfellonline¦ConnectororSplice(OH)¦Broken
19-0054868 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2019-05-21 | 386883 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0058684 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 28 | 2019-05-28 | 392192 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
19-0058911 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2019 | Tier 3 - Extreme | Transformer only | 5 | 29 | 2019-05-29 | 392400 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
19-0063535 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2019-06-05 | 399298 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0069524 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 6 | 18 | 2019-06-18 | 420773 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0071021 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2019-06-22 | 426071 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0071391 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2019-06-24 | 427431 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
19-0072044 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2019-06-25 | 429121 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0078972 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 18 | 2019-07-18 | 459754 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0080441 | Animal | Other | Pothead(Riser Termination) | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 23 | 2019-07-23 | 469732 | Sus | Y | Animal¦Other¦Pothead(RiserTermination)¦Burnedflashed
19-0084722 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2019-08-06 | 485536 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0085645 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 8 | 8 | 2019-08-08 | 491535 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0088110 | Vegetation | Tree - fell into line | Anchor or Guy | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 15 | 2019-08-15 | 511472 | Sus | Y | Vegetation¦Treefellintoline¦AnchororGuy¦Broken
19-0093516 | Animal | Squirrel | Transformer (OH) | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2019-08-29 | 546336 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
19-0095220 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 4 | 2019-09-04 | 552753 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0096539 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2019-09-08 | 562391 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0104484 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2019 | Tier 2 - Elevated | Transformer only | 9 | 27 | 2019-09-27 | 619884 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
19-0105037 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2019 | Tier 2 - Elevated | Transformer only | 9 | 28 | 2019-09-28 | 628266 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0108949 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2019-10-09 | 648874 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
19-0115316 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 23 | 2019-10-23 | 678777 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0116802 | Animal | Bird found | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2019-10-26 | 680759 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
19-0122489 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2019-11-07 | 701974 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0126412 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 19 | 2019-11-19 | 710357 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonobject
19-0130178 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 719649 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0130855 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 722881 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0130919 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2019-11-28 | 722942 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0131890 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 2 - Elevated | Transformer only | 12 | 1 | 2019-12-01 | 725685 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0133810 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2019-12-05 | 730492 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Burnedflashed
19-0134593 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2019-12-06 | 731806 | Sus | N | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Normal
19-0135055 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2019-12-08 | 733826 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0137936 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2019-12-26 | 750567 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0011021 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2020-01-18 | 765339 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0011162 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2020-01-19 | 766023 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0019384 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 784261 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0019684 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 782813 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0020264 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 10 | 2020-02-10 | 788128 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0028990 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2020-03-05 | 831295 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0029374 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2020-03-06 | 834499 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0030741 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2020-03-10 | 843415 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0032151 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 14 | 2020-03-14 | 851482 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032619 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 854162 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0032967 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 853735 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0033497 | 3rd Party | Customer Equipment | Metering Equipment | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2020-03-17 | 856891 | Sus | N | 3rdParty¦CustomerEquipment¦MeteringEquipment¦Normal
20-0034761 | Vegetation | Tree - fell into line | Anchor or Guy | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 18 | 2020-03-18 | 858545 | Sus | N | Vegetation¦Treefellintoline¦AnchororGuy¦Broken
20-0046206 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2020-05-01 | 905042 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Together
20-0046620 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 2 | 2020-05-02 | 905875 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0047915 | Animal | Bird found | Transformer (OH) | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2020-05-06 | 908257 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
20-0048874 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 10 | 2020-05-10 | 910612 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0051577 | Environmental/External | Lightning | Insulator | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 18 | 2020-05-18 | 917202 | Sus | Y | EnvironmentalExternal¦Lightning¦Insulator¦Burnedflashed
20-0051988 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2020-05-19 | 917622 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0054037 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 26 | 2020-05-26 | 921412 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0060438 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2020-06-11 | 937291 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0062864 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 6 | 18 | 2020-06-18 | 942237 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0063814 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 22 | 2020-06-22 | 944855 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0063914 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2020-06-23 | 944899 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0070089 | Equipment Failure/Involved | Overhead | Other | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2020-07-09 | 960921 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦Broken
20-0082021 | Animal | Squirrel | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 11 | 2020-08-11 | 991946 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
20-0085014 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1010563 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0085270 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 16 | 2020-08-16 | 1013634 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0085414 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 8 | 16 | 2020-08-16 | 1014484 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0085644 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2020-08-17 | 1015664 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦Burnedflashed
20-0087455 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 19 | 2020-08-19 | 1023418 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
20-0096361 | Environmental/External | Fire, Forest/Grass | Transformer (OH) | Normal | 2020 | Tier 3 - Extreme | Transformer only | 8 | 19 | 2020-08-19 | 1064200 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Transformer(OH)¦Normal
20-0099656 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1085701 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0099892 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 21 | 2020-09-21 | 1086259 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0107352 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 11 | 2020-10-11 | 1115303 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0110552 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2020-10-19 | 1121222 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
20-0111577 | Animal | Squirrel | Transformer (OH) | Burned/flashed | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2020-10-22 | 1123323 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Burnedflashed
20-0112120 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2020-10-25 | 1127966 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦Switch(OH)¦Broken
20-0112685 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2020 | Tier 3 - Extreme | Transformer only | 10 | 24 | 2020-10-24 | 1124476 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
20-0115723 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2020-11-01 | 1133253 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0120399 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2020-11-13 | 1143219 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0122181 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 17 | 2020-11-17 | 1148014 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0122816 | Animal | Bird found | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 19 | 2020-11-19 | 1149165 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
20-0125634 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 28 | 2020-11-28 | 1155618 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
20-0127395 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2020-12-03 | 1161369 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0131801 | Equipment Failure/Involved | Overhead | Transformer | Malfunctioning | 2020 | Tier 2 - Elevated | Transformer only | 12 | 25 | 2020-12-25 | 1198670 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Malfunctioning
21-0004883 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 4 | 2021-01-04 | 1203925 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0006431 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2021-01-08 | 1206550 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0009922 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2021-01-18 | 1213371 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0010260 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1215123 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011022 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216595 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0011727 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2021-01-18 | 1219218 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0012678 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2021-01-22 | 1220742 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0014720 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226031 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0016840 | Environmental/External | Ice or snow | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Transformer only | 1 | 27 | 2021-01-27 | 1236765 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Cutoutfuseholder¦Broken
21-0029406 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261741 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0030066 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2021-02-26 | 1263035 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0040173 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2021-03-23 | 1294839 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0041691 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2021-03-26 | 1300079 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0042256 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 29 | 2021-03-29 | 1302613 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
21-0047199 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2021-04-10 | 1312797 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0051120 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2021-04-20 | 1326078 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0054827 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 29 | 2021-04-29 | 1336898 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0056387 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 3 | 2021-05-03 | 1340183 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0058946 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2021 | Tier 3 - Extreme | Transformer only | 5 | 8 | 2021-05-08 | 1344191 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
21-0061774 | Animal | Bird found | Fuse | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 15 | 2021-05-15 | 1349830 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
21-0066073 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2021-05-25 | 1358732 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0069997 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 4 | 2021-06-04 | 1365603 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
21-0075301 | Equipment Failure/Involved | Overhead |  | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 6 | 16 | 2021-06-16 | 1375665 | Sus | Y | EquipmentFailureInvolved¦Overhead¦¦FailedFaulted
21-0075792 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2021 | Tier 2 - Elevated | Transformer only | 6 | 17 | 2021-06-17 | 1376514 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
21-0085615 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2021-07-06 | 1393129 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0086934 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Transformer only | 7 | 9 | 2021-07-09 | 1395312 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0089701 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2021-07-14 | 1404757 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0091903 | Environmental/External | Fire, Forest/Grass | Footings, Tower or Pole | Normal | 2021 | Tier 2 - Elevated | Transmission line | 7 | 19 | 2021-07-19 | 1408231 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦FootingsTowerorPole¦Normal
21-0097684 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2021-07-30 | 1423284 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0101606 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2021 | Tier 3 - Extreme | Distribution Circuit | 8 | 7 | 2021-08-07 | 1436959 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
21-0104059 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2021 | Tier 2 - Elevated | Transformer only | 8 | 13 | 2021-08-13 | 1441842 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
21-0104837 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 8 | 15 | 2021-08-15 | 1443532 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0108395 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 8 | 23 | 2021-08-23 | 1450905 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0110507 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2021-08-28 | 1456143 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0113773 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2021-09-05 | 1462585 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0116527 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 12 | 2021-09-12 | 1469906 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0119550 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2021 | Tier 3 - Extreme | Transformer only | 9 | 19 | 2021-09-19 | 1475557 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
21-0122506 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 9 | 26 | 2021-09-26 | 1480924 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0135824 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1509088 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136177 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511222 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0136458 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1511232 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0136802 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1516238 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0140582 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 11 | 1 | 2021-11-01 | 1527204 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0153458 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 1 | 2021-12-01 | 1556999 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
21-0155015 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 5 | 2021-12-05 | 1559534 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157060 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1565998 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0157442 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1567840 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0157500 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 12 | 13 | 2021-12-13 | 1568103 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158402 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1572473 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158436 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1572633 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158533 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573059 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161461 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2021-12-28 | 1587561 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0161647 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588882 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
21-0161654 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 29 | 2021-12-29 | 1588921 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0161994 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1590751 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0006000 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1594904 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
22-0007757 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1598684 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0012932 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2022-01-22 | 1608589 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0013024 | Vegetation | Tree - branch fell on line | Bushing | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2022-01-22 | 1608895 | Sus | N | Vegetation¦Treebranchfellonline¦Bushing¦Broken
22-0018417 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned Open | 2022 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2022-02-03 | 1620659 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦BurnedOpen
22-0020223 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 2 | 9 | 2022-02-09 | 1623827 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0025898 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 23 | 2022-02-23 | 1634968 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0032444 | Company Initiated | Construction Activity/equip, company | Fuse | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2022-03-10 | 1646279 | Sus | N | CompanyInitiated¦ConstructionActivityequipcompany¦Fuse¦Normal
22-0032515 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 10 | 2022-03-10 | 1646345 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0036308 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2022-03-21 | 1652401 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0044286 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2022-04-07 | 1665586 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0045120 | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2022-04-10 | 1667422 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground
22-0045867 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 3 - Extreme | Transformer only | 4 | 11 | 2022-04-11 | 1668874 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0046471 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2022-04-12 | 1670231 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Broken
22-0051195 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 18 | 2022-04-18 | 1676025 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0061673 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 13 | 2022-05-13 | 1695201 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0063910 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2022 | Tier 3 - Extreme | Transformer only | 5 | 19 | 2022-05-19 | 1703247 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
22-0067965 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Transformer only | 5 | 29 | 2022-05-29 | 1713603 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0069977 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 3 | 2022-06-03 | 1717755 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0072426 | Equipment Failure/Involved | Electrical Overload | Recloser | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2022-06-09 | 1726692 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Recloser¦Normal
22-0077755 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 23 | 2022-06-23 | 1740128 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Pothead(RiserTermination)¦Burnedflashed
22-0079524 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2022-06-28 | 1744474 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0082053 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 5 | 2022-07-05 | 1749542 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0086095 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 16 | 2022-07-16 | 1757646 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
22-0087759 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2022-07-20 | 1761463 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0091858 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 7 | 31 | 2022-07-31 | 1769743 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0094719 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 7 | 2022-08-07 | 1775345 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0095858 | Company Initiated | Personnel, company | Recloser | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2022-08-10 | 1777808 | Sus | Y | CompanyInitiated¦Personnelcompany¦Recloser¦Normal
22-0103198 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 8 | 29 | 2022-08-29 | 1794278 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0107402 | Equipment Failure/Involved | Overhead | Service conductor | Normal | 2022 | Tier 3 - Extreme | Transformer only | 9 | 7 | 2022-09-07 | 1804460 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦Normal
22-0107574 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2022-09-07 | 1804801 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0107812 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 8 | 2022-09-08 | 1805733 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0108998 | Animal | Squirrel | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2022-09-11 | 1808359 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
22-0121305 | 3rd Party | Tree - cutting, 3rd party | Bushing | Broken | 2022 | Tier 3 - Extreme | Distribution Circuit | 10 | 13 | 2022-10-13 | 1836783 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Bushing¦Broken
22-0123738 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 21 | 2022-10-21 | 1842436 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0126451 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1849641 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0128428 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 6 | 2022-11-06 | 1855519 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0128868 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1856664 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0134976 | 3rd Party | Vehicle | Service conductor | Broken | 2022 | Tier 3 - Extreme | Transformer only | 11 | 29 | 2022-11-29 | 1871624 | Sus | Y | 3rdParty¦Vehicle¦Serviceconductor¦Broken
22-0135611 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2022-12-01 | 1873116 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0136441 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 4 | 2022-12-04 | 1875539 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
22-0141558 | Vegetation | Tree - fell into line | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 12 | 27 | 2022-12-27 | 1898000 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦FailedFaulted
22-0142603 | Equipment Failure/Involved | Underground | Switch (UG) | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2022-12-31 | 1904006 | Sus | N | EquipmentFailureInvolved¦Underground¦Switch(UG)¦Broken
15-0008784 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2015-02-02 | 1171256 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0021128 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | 2015 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2015-03-21 | 1206241 | Sus | N | EquipmentFailureInvolved¦Other¦Transformer¦Malfunctioning
15-0032359 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230259 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0032518 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 7 | 2015-05-07 | 1230618 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0045358 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 3 | 2015-07-03 | 1262385 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0051405 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2015-07-29 | 1279538 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0051774 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2015 | Tier 2 - Elevated | Transformer only | 7 | 30 | 2015-07-30 | 1280504 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
15-0055151 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 14 | 2015-08-14 | 1288434 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
15-0062259 | Animal | Squirrel | Transformer (OH) | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 9 | 19 | 2015-09-19 | 1308467 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦Normal
15-0062706 | Environmental/External | Fire, Forest/Grass | Conductor, Underground | Burned/flashed | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 13 | 2015-09-13 | 1310144 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorUnderground¦Burnedflashed
15-0066432 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 9 | 29 | 2015-09-29 | 1313859 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
15-0074758 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2015-11-02 | 1333001 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0077998 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342187 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0081923 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 1 | 2015-12-01 | 1351160 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0084322 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 12 | 11 | 2015-12-11 | 1359066 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
15-0084361 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2015-12-12 | 1359227 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0084537 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1359913 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0086494 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 21 | 2015-12-21 | 1368099 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
15-0087601 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2015-12-27 | 1373067 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
15-0087855 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 12 | 30 | 2015-12-30 | 1374763 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0003259 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2016-01-06 | 1377966 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0003660 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2016 | Tier 2 - Elevated | Transformer only | 1 | 6 | 2016-01-06 | 1379188 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
16-0005146 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2016-01-13 | 1382943 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0005913 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385553 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0006298 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2016-01-19 | 1387064 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0007839 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2016-01-24 | 1391134 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0015205 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 2 | 24 | 2016-02-24 | 1411436 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0017076 | 3rd Party | Tree - cutting, 3rd party | Crossarm, Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 3 | 2016-03-03 | 1415341 | Sus | N | 3rdParty¦Treecutting3rdparty¦CrossarmWood¦Brokenwireonground
16-0017456 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416511 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0017545 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1416837 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018100 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420849 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0018210 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2016-03-05 | 1418517 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0027792 | 3rd Party | Tree - cutting, 3rd party | Jumper | Burned Open | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2016-04-11 | 1448794 | Sus | N | 3rdParty¦Treecutting3rdparty¦Jumper¦BurnedOpen
16-0031158 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457474 | Sus | N | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
16-0031303 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 4 | 25 | 2016-04-25 | 1458498 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0034307 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 3 - Extreme | Transformer only | 5 | 5 | 2016-05-05 | 1465658 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0036015 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Transformer only | 5 | 14 | 2016-05-14 | 1469593 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0041028 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 6 | 4 | 2016-06-04 | 1482649 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0043626 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 15 | 2016-06-15 | 1489760 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
16-0045704 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 24 | 2016-06-24 | 1495517 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0045996 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 27 | 2016-06-27 | 1496631 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0049140 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 11 | 2016-07-11 | 1508345 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0049654 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 7 | 13 | 2016-07-13 | 1509485 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0049719 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2016-07-14 | 1509739 | Sus | Y | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
16-0053083 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 7 | 27 | 2016-07-27 | 1517449 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0053644 | Environmental/External | Fire, Forest/Grass | Other | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 29 | 2016-07-29 | 1518538 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦Other¦Normal
16-0053944 | Animal | Bird found | Transformer (OH) | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 7 | 31 | 2016-07-31 | 1519367 | Sus | Y | Animal¦Birdfound¦Transformer(OH)¦Normal
16-0057512 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 15 | 2016-08-15 | 1526988 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
16-0059258 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2016 | Tier 3 - Extreme | Transformer only | 8 | 23 | 2016-08-23 | 1530694 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
16-0068563 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 9 | 29 | 2016-09-29 | 1550141 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0069250 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2016-10-03 | 1552036 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0072516 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 15 | 2016-10-15 | 1561002 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0077637 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2016-11-02 | 1575532 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0079537 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 11 | 13 | 2016-11-13 | 1580482 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0079725 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2016-11-14 | 1580994 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
16-0084252 | 3rd Party | Vehicle | Pole-Wood | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2016-12-06 | 1595778 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Normal
16-0085641 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1602263 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0086821 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2016-12-23 | 1609838 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0003302 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1616686 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0003343 | Equipment Failure/Involved | Overhead |  | Burned Open | 2017 | Tier 3 - Extreme | Transformer only | 1 | 3 | 2017-01-03 | 1616984 | Sus | N | EquipmentFailureInvolved¦Overhead¦¦BurnedOpen
17-0003747 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1618694 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0004142 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1619903 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0004705 | Equipment Failure/Involved | Underground | Elbow | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 7 | 2017-01-07 | 1621822 | Sus | N | EquipmentFailureInvolved¦Underground¦Elbow¦Burnedflashed
17-0004897 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1622441 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0004964 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623081 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0005076 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623454 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0005197 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1623441 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
17-0005666 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625775 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0005936 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1630118 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0006382 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632419 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0007366 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637638 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0007538 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637058 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0008250 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637987 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0011855 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1655154 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
17-0013148 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660504 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
17-0013365 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 22 | 2017-01-22 | 1661927 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0013934 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1663805 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0015801 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 28 | 2017-01-28 | 1669347 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0016246 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 31 | 2017-01-31 | 1671031 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0017977 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2017-02-06 | 1676983 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0019126 | Vegetation | Other ground vegetation | Conductor, Overhead | Contaminated | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682319 | Sus | N | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Contaminated
17-0019838 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2017-02-10 | 1684797 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0020360 | Environmental/External | Ice or snow | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Transformer only | 2 | 11 | 2017-02-11 | 1685986 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Broken
17-0021883 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1692163 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
17-0022338 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1695518 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
17-0022701 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698000 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0024723 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705491 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0024934 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1707450 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025175 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1708200 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0025274 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 21 | 2017-02-21 | 1709254 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0026543 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 24 | 2017-02-24 | 1713270 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
17-0027136 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 27 | 2017-02-27 | 1715069 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0029453 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 8 | 2017-03-08 | 1722598 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0034352 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2017-03-28 | 1737261 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0035872 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2017-04-02 | 1742492 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0037600 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2017-04-06 | 1748568 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0037692 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1751270 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0040069 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 13 | 2017-04-13 | 1757192 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0051247 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 28 | 2017-05-28 | 1792382 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0052321 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transformer only | 6 | 2 | 2017-06-02 | 1795511 | Sus | Y | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
17-0052549 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Transformer only | 6 | 3 | 2017-06-03 | 1796216 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
17-0053124 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2017 | Tier 2 - Elevated | Transformer only | 6 | 6 | 2017-06-06 | 1797973 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
17-0065742 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 7 | 26 | 2017-07-26 | 1840421 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0066096 | 3rd Party | Gun Shot | Conductor, Overhead | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 7 | 27 | 2017-07-27 | 1841166 | Sus | Y | 3rdParty¦GunShot¦ConductorOverhead¦Deteriorated
17-0071392 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 18 | 2017-08-18 | 1854890 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0072940 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 25 | 2017-08-25 | 1859461 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0073606 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2017-08-28 | 1861975 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
17-0073984 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2017-08-30 | 1862960 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0074024 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2017-08-30 | 1863014 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0082308 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 27 | 2017-09-27 | 1887079 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0086457 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1898859 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
17-0087180 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 12 | 2017-10-12 | 1900263 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Brokenwireonground
17-0087661 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2017-10-16 | 1901560 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0088504 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 19 | 2017-10-19 | 1903870 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
17-0089221 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1906134 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0092604 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 4 | 2017-11-04 | 1915725 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0092765 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 5 | 2017-11-05 | 1916375 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0097939 | Company Initiated | Return Circuit Normal | Generator | Normal | 2017 | Tier 2 - Elevated | Transformer only | 11 | 27 | 2017-11-27 | 1930510 | Sus | Y | CompanyInitiated¦ReturnCircuitNormal¦Generator¦Normal
17-0100860 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2017-12-08 | 1939140 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
17-0101442 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2017-12-13 | 1941881 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0103473 | Animal | Bird found | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 12 | 28 | 2017-12-28 | 1952290 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
18-0004227 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2018-01-08 | 3652 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
18-0012132 | 3rd Party | Fire, house or bldg. | Secondary | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2018-02-07 | 20763 | Sus | N | 3rdParty¦Firehouseorbldg¦Secondary¦Burnedflashed
18-0016456 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2018-02-22 | 29446 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0025024 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 21 | 2018-03-21 | 49536 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0028358 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 2 | 2018-04-02 | 57640 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0030256 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 7 | 2018-04-07 | 62059 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
18-0036835 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 30 | 2018-04-30 | 76548 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0049049 | 3rd Party | Vehicle | Pole-Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 8 | 2018-06-08 | 104640 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
18-0059846 | Animal | Squirrel |  | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 7 | 14 | 2018-07-14 | 131614 | Sus | Y | Animal¦Squirrel¦¦FailedFaulted
18-0059900 | Animal | Other | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 14 | 2018-07-14 | 132021 | Sus | Y | Animal¦Other¦ConductorOverhead¦Brokenwireonground
18-0062150 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Transformer only | 7 | 20 | 2018-07-20 | 136715 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
18-0066787 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2018-08-04 | 149012 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0069774 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 14 | 2018-08-14 | 155356 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Normal
18-0078314 | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2018-09-10 | 171789 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted
18-0086246 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 3 | 2018-10-03 | 187230 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0086861 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Transformer only | 10 | 4 | 2018-10-04 | 188040 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0095350 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 29 | 2018-10-29 | 204633 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0098175 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2018-11-08 | 211267 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Normal
18-0100731 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 18 | 2018-11-18 | 217577 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0101414 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218972 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0105145 | Vegetation | Tree - fell into line | Recloser | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2018-11-29 | 228386 | Sus | Y | Vegetation¦Treefellintoline¦Recloser¦Normal
18-0109520 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2018-12-16 | 241712 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
18-0109795 | Equipment Failure/Involved | Electrical Overload | Conductor, Overhead | Annealed | 2018 | Tier 3 - Extreme | Transformer only | 12 | 17 | 2018-12-17 | 242609 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦ConductorOverhead¦Annealed
18-0110395 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 23 | 2018-12-23 | 245916 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0004858 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 5 | 2019-01-05 | 254438 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
19-0005074 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255153 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0005641 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 256779 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0006643 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 9 | 2019-01-09 | 261164 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
19-0006786 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2019-01-09 | 261293 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0008947 | Vegetation | Tree - fell into line | Secondary | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2019-01-15 | 265421 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Normal
19-0010046 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 269292 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0012126 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2019-01-19 | 276765 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
19-0012624 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2019-01-20 | 277550 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0017037 | 3rd Party | Vehicle | Pole-Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 2 | 2019-02-02 | 287008 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
19-0018075 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2019-02-04 | 290570 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018333 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2019-02-05 | 291856 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0021345 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2019-02-12 | 300407 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
19-0021845 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 303010 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0022505 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2019-02-13 | 302351 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0025215 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 17 | 2019-02-17 | 316365 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0029000 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325676 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0029559 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 28 | 2019-02-28 | 328202 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0029970 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 3 | 1 | 2019-03-01 | 329298 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
19-0034412 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2019-03-16 | 340904 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0037080 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Transformer only | 3 | 25 | 2019-03-25 | 346748 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0038874 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 4 | 1 | 2019-04-01 | 351766 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Burnedflashed
19-0041539 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 11 | 2019-04-11 | 358557 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0044238 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2019-04-19 | 363561 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0044774 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 22 | 2019-04-22 | 365176 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦Normal
19-0045471 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 23 | 2019-04-23 | 366716 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0050651 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 10 | 2019-05-10 | 377950 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
19-0052745 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Transformer only | 5 | 16 | 2019-05-16 | 382428 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0058876 | Company Initiated | Construction Activity/equip, company | Pole-Wood | Deteriorated | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 29 | 2019-05-29 | 392317 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Deteriorated
19-0059946 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 5 | 30 | 2019-05-30 | 393237 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0064146 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 7 | 2019-06-07 | 400438 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0068643 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2019 | Tier 3 - Extreme | Transformer only | 6 | 17 | 2019-06-17 | 417733 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
19-0069673 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2019-06-19 | 421325 | Sus | Y | Vegetation¦Treefellintoline¦ConnectororSplice(OH)¦Normal
19-0074146 | 3rd Party | Vehicle | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 2 | 2019-07-02 | 440133 | Sus | Y | 3rdParty¦Vehicle¦ConductorOverhead¦Brokenwireonground
19-0077091 | Vegetation | Tree - branch fell on line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 7 | 13 | 2019-07-13 | 448993 | Sus | Y | Vegetation¦Treebranchfellonline¦Transformer¦Brokenwireonground
19-0077708 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 15 | 2019-07-15 | 453145 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
19-0078985 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2019 | Tier 2 - Elevated | Distribution Circuit | 7 | 18 | 2019-07-18 | 459768 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
19-0083975 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 2 | 2019-08-02 | 479202 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
19-0105033 | Vegetation | Tree - branch fell on line | Service conductor | Broken | 2019 | Tier 3 - Extreme | Transformer only | 9 | 28 | 2019-09-28 | 627193 | Sus | Y | Vegetation¦Treebranchfellonline¦Serviceconductor¦Broken
19-0114776 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2019-10-22 | 677086 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0119116 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2019-10-30 | 695526 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0124135 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 12 | 2019-11-12 | 705638 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130351 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 27 | 2019-11-27 | 719578 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0130940 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2019-11-28 | 723153 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0136635 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2019-12-15 | 739995 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0137319 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2019-12-20 | 747125 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0137658 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2019-12-22 | 748718 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0005281 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2020-01-05 | 755074 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0009667 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2020-01-16 | 762500 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0013050 | Equipment Failure/Involved | Electrical Overload | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 1 | 23 | 2020-01-23 | 769017 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦FailedFaulted
20-0018333 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 2 | 6 | 2020-02-06 | 779662 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0019310 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2020-02-09 | 783540 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0019538 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 9 | 2020-02-09 | 784733 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0034614 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 20 | 2020-03-20 | 859398 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0035070 | Equipment Failure/Involved | Overhead | Secondary | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 15 | 2020-03-15 | 861481 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Brokenwireonground
20-0038891 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 6 | 2020-04-06 | 885253 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
20-0043226 | Animal | Bird found | Fuse | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 21 | 2020-04-21 | 898747 | Sus | N | Animal¦Birdfound¦Fuse¦FailedFaulted
20-0046525 | Animal | Bird found | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2020-05-01 | 905621 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Brokenwireonground
20-0047925 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 6 | 2020-05-06 | 908450 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0048350 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2020-05-08 | 909309 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0054952 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 27 | 2020-05-27 | 923884 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0055477 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Transformer only | 5 | 28 | 2020-05-28 | 924793 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0055847 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 30 | 2020-05-30 | 925987 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0058833 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 6 | 8 | 2020-06-08 | 934200 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0068872 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 6 | 2020-07-06 | 958855 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0073459 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 19 | 2020-07-19 | 967824 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0074673 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2020-07-22 | 969925 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0079753 | 3rd Party | Fire, house or bldg. | Pole-Wood | Burned/flashed | 2020 | Tier 2 - Elevated | Transformer only | 8 | 4 | 2020-08-04 | 978886 | Sus | Y | 3rdParty¦Firehouseorbldg¦PoleWood¦Burnedflashed
20-0091315 | Unknown Cause | Patrol - not conducted |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 8 | 29 | 2020-08-29 | 1039813 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
20-0091436 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1041110 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0099709 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1085939 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0099787 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086068 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0110088 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 10 | 18 | 2020-10-18 | 1120269 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0112209 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 3 - Extreme | Transformer only | 10 | 23 | 2020-10-23 | 1124048 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0112811 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2020-10-25 | 1125637 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
20-0115748 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2020-11-01 | 1133326 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0118393 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2020-11-08 | 1139110 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0125653 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2020-11-28 | 1155690 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0129289 | Animal | Squirrel |  | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 12 | 9 | 2020-12-09 | 1174663 | Sus | N | Animal¦Squirrel¦¦FailedFaulted
20-0130083 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Transformer only | 12 | 13 | 2020-12-13 | 1182319 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
20-0131845 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Contaminated | 2020 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2020-12-25 | 1198796 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Contaminated
21-0004634 | Equipment Failure/Involved | Overhead | Service conductor | Burned Open | 2021 | Tier 3 - Extreme | Transformer only | 1 | 4 | 2021-01-04 | 1203113 | Sus | N | EquipmentFailureInvolved¦Overhead¦Serviceconductor¦BurnedOpen
21-0009977 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1213789 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0010102 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214308 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0010137 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1214485 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0010695 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216472 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0011075 | Equipment Failure/Involved | Underground | Transformer (UG) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1218419 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦FailedFaulted
21-0011720 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1219192 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
21-0012858 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2021-01-22 | 1221316 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0013484 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Transformer only | 1 | 24 | 2021-01-24 | 1222679 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
21-0013744 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223795 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013757 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223560 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
21-0014776 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 26 | 2021-01-26 | 1226723 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0015259 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1229899 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
21-0018596 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1242135 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0018711 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1242582 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0020142 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 31 | 2021-01-31 | 1244228 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
21-0022332 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 5 | 2021-02-05 | 1248731 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0022928 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2021-02-08 | 1250427 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0023436 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2021-02-09 | 1251264 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0025377 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2021-02-13 | 1254551 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0027891 | Equipment Failure/Involved | Underground | Secondary | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 2 | 21 | 2021-02-21 | 1258952 | Sus | N | EquipmentFailureInvolved¦Underground¦Secondary¦Deteriorated
21-0030251 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 2 | 27 | 2021-02-27 | 1263421 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0033029 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2021-03-06 | 1271109 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0038456 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 19 | 2021-03-19 | 1288422 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0039099 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 3 | 21 | 2021-03-21 | 1290711 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0052957 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 4 | 25 | 2021-04-25 | 1333783 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
21-0053734 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 27 | 2021-04-27 | 1335178 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0062893 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 5 | 18 | 2021-05-18 | 1352313 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
21-0064991 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Transformer only | 5 | 24 | 2021-05-24 | 1357039 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0066626 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 3 - Extreme | Transformer only | 5 | 26 | 2021-05-26 | 1359432 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0071133 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 6 | 7 | 2021-06-07 | 1367792 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
21-0076520 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2021-06-19 | 1378609 | Sus | Y | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
21-0079201 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 24 | 2021-06-24 | 1384165 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0091270 | Animal | Bird found | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 7 | 17 | 2021-07-17 | 1406880 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Normal
21-0101786 | 3rd Party | Vehicle | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2021-08-09 | 1437679 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
21-0110729 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2021 | Tier 3 - Extreme | Transformer only | 8 | 29 | 2021-08-29 | 1457323 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
21-0112971 | Equipment Failure/Involved | Overhead | Secondary | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 9 | 2 | 2021-09-02 | 1461138 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦BurnedOpen
21-0115910 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2021-09-10 | 1467296 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0116352 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2021-09-11 | 1468912 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
21-0122024 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 24 | 2021-09-24 | 1479526 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0124011 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 9 | 29 | 2021-09-29 | 1483544 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0135662 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508123 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0135705 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1508344 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0136383 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2021-10-24 | 1512549 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
21-0137630 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2021-10-25 | 1519650 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0137630 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 25 | 2021-10-25 | 1519650 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0139077 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 10 | 26 | 2021-10-26 | 1523328 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0142347 | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Arcing | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 4 | 2021-11-04 | 1535019 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Switch(OH)¦Arcing
21-0144819 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 11 | 2021-11-11 | 1540650 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0145193 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2021-11-13 | 1542155 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0145448 | Animal | Squirrel | Cutout, fuse holder | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 14 | 2021-11-14 | 1543966 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦Normal
21-0156391 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 9 | 2021-12-09 | 1563095 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0157004 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2021-12-12 | 1565580 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158090 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1571382 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0158195 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 14 | 2021-12-14 | 1570551 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0158868 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2021-12-16 | 1574644 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0159515 | Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 18 | 2021-12-18 | 1576569 | Sus | N | EquipmentFailureInvolved¦Overhead¦Regulator¦Malfunctioning
21-0160239 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 23 | 2021-12-23 | 1579607 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160790 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582627 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0161034 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1585309 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0005691 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1594009 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0005715 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1594153 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
22-0006431 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2022-01-03 | 1594049 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0009429 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | 2022 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2022-01-13 | 1601532 | Sus | N | EquipmentFailureInvolved¦Overhead¦Recloser¦Malfunctioning
22-0012873 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2022-01-22 | 1608554 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
22-0013737 | Vegetation | Tree - fell into line | Secondary | Together | 2022 | Tier 3 - Extreme | Distribution Circuit | 1 | 24 | 2022-01-24 | 1611183 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Together
22-0017322 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 2 | 1 | 2022-02-01 | 1618777 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
22-0024468 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2022-02-19 | 1632439 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0033141 | Company Initiated | Return Circuit Normal | Fuse | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 12 | 2022-03-12 | 1647248 | Sus | N | CompanyInitiated¦ReturnCircuitNormal¦Fuse¦Normal
22-0045081 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 10 | 2022-04-10 | 1667215 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0055729 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 4 | 28 | 2022-04-28 | 1684061 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0058742 | Equipment Failure/Involved | Overhead | Insulator | Failed/Faulted | 2022 | Zone 1 - HHZ | Distribution Circuit | 5 | 5 | 2022-05-05 | 1689492 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦FailedFaulted
22-0062747 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2022-05-17 | 1697904 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0065468 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 23 | 2022-05-23 | 1708457 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Burnedflashed
22-0074804 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 6 | 15 | 2022-06-15 | 1732443 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0076050 | 3rd Party | Customer Equipment | Pole-Wood | Burned/flashed | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 19 | 2022-06-19 | 1735358 | Sus | Y | 3rdParty¦CustomerEquipment¦PoleWood¦Burnedflashed
22-0079278 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2022-06-28 | 1743971 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0083587 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 9 | 2022-07-09 | 1752328 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0086029 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 15 | 2022-07-15 | 1757476 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0089645 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 26 | 2022-07-26 | 1765652 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0098443 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 8 | 17 | 2022-08-17 | 1783082 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100126 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2022-08-20 | 1786177 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
22-0102159 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2022-08-26 | 1791822 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0102609 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2022-08-26 | 1792571 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0121816 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2022-10-15 | 1838055 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
22-0128175 | Equipment Failure/Involved | Overhead | Secondary | Normal | 2022 | Tier 3 - Extreme | Transformer only | 11 | 5 | 2022-11-05 | 1854399 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Normal
22-0129396 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 8 | 2022-11-08 | 1858494 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
22-0129619 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2022-11-08 | 1858744 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
22-0132181 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 11 | 17 | 2022-11-17 | 1864571 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0132402 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 3 - Extreme | Distribution Circuit | 11 | 18 | 2022-11-18 | 1865155 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0134995 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2022-11-30 | 1871680 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
22-0138339 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1881682 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
22-0138808 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 10 | 2022-12-10 | 1884403 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0139093 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 11 | 2022-12-11 | 1886129 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0139265 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2022-12-12 | 1887187 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Normal
22-0139483 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 12 | 2022-12-12 | 1887840 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
15-0012348 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2015-02-10 | 1187457 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
15-0024218 | Equipment Failure/Involved | Other | Jumper | Arcing | 2015 | Tier 2 - Elevated | Transformer only | 4 | 4 | 2015-04-04 | 1212699 | Sus | N | EquipmentFailureInvolved¦Other¦Jumper¦Arcing
15-0037508 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 5 | 31 | 2015-05-31 | 1241847 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0038979 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2015-06-05 | 1244458 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0053804 | Animal | Squirrel | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2015-08-08 | 1285124 | Sus | Y | Animal¦Squirrel¦Cutoutfuseholder¦FailedFaulted
15-0053874 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2015 | Tier 2 - Elevated | Transformer only | 8 | 8 | 2015-08-08 | 1285205 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
15-0056541 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Annealed | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2015-08-21 | 1292462 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Annealed
15-0061370 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on object | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 15 | 2015-09-15 | 1305903 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonobject
15-0061370 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on object | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 15 | 2015-09-15 | 1305903 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonobject
15-0066997 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 1 | 2015-10-01 | 1314604 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
15-0067296 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 1 | 2015-10-01 | 1315171 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0071315 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2015-10-17 | 1324035 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
15-0073568 | 3rd Party | Customer Equipment | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 10 | 27 | 2015-10-27 | 1329764 | Sus | Y | 3rdParty¦CustomerEquipment¦Fuse¦FailedFaulted
15-0077024 | 3rd Party | Contact with High Voltage, 3rd party | Pothead(Riser Termination) | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 10 | 2015-11-10 | 1338958 | Sus | Y | 3rdParty¦ContactwithHighVoltage3rdparty¦Pothead(RiserTermination)¦Broken
15-0077731 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2015 | Tier 2 - Elevated | Transformer only | 11 | 14 | 2015-11-14 | 1340891 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
15-0081330 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2015-11-26 | 1349228 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
15-0082505 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1352805 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0082608 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 3 | 2015-12-03 | 1353223 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0083651 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | 2015 | Tier 2 - Elevated | Transformer only | 12 | 9 | 2015-12-09 | 1356354 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Arcing
15-0084823 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1361207 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
15-0086775 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2015-12-22 | 1369454 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
15-0087296 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 25 | 2015-12-25 | 1371703 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
15-0087442 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 12 | 26 | 2015-12-26 | 1372125 | Sus | N | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
16-0005043 | Equipment Failure/Involved | Overhead | Transformer |  | 2016 | Tier 2 - Elevated | Transformer only | 1 | 13 | 2016-01-13 | 1382838 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦
16-0005498 | Unknown Cause | Patrol - found nothing | Insulator | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2016-01-15 | 1384271 | Sus | N | UnknownCause¦Patrolfoundnothing¦Insulator¦Broken
16-0005710 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 15 | 2016-01-15 | 1384715 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0005897 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2016-01-17 | 1385486 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0006568 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2016-01-19 | 1387838 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Brokenwireonground
16-0009394 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 31 | 2016-01-31 | 1394803 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0010312 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2016-02-03 | 1397768 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0011141 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 2 | 7 | 2016-02-07 | 1399695 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0011142 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 7 | 2016-02-07 | 1399707 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0012944 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2016-02-16 | 1404411 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0013496 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2016-02-17 | 1406988 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0020193 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 11 | 2016-03-11 | 1427074 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0020855 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 12 | 2016-03-12 | 1429757 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
16-0025938 | 3rd Party | Vehicle | Pole-Wood | Broken | 2016 | Tier 3 - Extreme | Distribution Circuit | 4 | 4 | 2016-04-04 | 1444026 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
16-0027542 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 9 | 2016-04-09 | 1448017 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
16-0031020 | Animal | Squirrel | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 24 | 2016-04-24 | 1457042 | Sus | N | Animal¦Squirrel¦Fuse¦FailedFaulted
16-0034647 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 7 | 2016-05-07 | 1466393 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0052294 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2016 | Tier 3 - Extreme | Transformer only | 7 | 25 | 2016-07-25 | 1515762 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
16-0053404 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2016 | Tier 3 - Extreme | Distribution Circuit | 7 | 28 | 2016-07-28 | 1518012 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
16-0054961 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2016-08-04 | 1521277 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0056156 | 3rd Party | Customer Equipment | Transformer (OH) | Normal | 2016 | Tier 2 - Elevated | Transformer only | 8 | 10 | 2016-08-10 | 1524128 | Sus | Y | 3rdParty¦CustomerEquipment¦Transformer(OH)¦Normal
16-0060567 | 3rd Party | Customer Equipment | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 8 | 28 | 2016-08-28 | 1533440 | Sus | Y | 3rdParty¦CustomerEquipment¦ConductorOverhead¦Normal
16-0062454 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2016-09-06 | 1536989 | Sus | Y | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
16-0067461 | Animal | Squirrel | Fuse | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 9 | 26 | 2016-09-26 | 1547579 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
16-0068809 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2016 | Tier 2 - Elevated | Distribution Circuit | 9 | 30 | 2016-09-30 | 1550627 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
16-0069058 | Unknown Cause | Patrol - not conducted |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 2 | 2016-10-02 | 1551509 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
16-0072917 | Vegetation | Tree - fell into line | Service conductor | Broken | 2016 | Tier 2 - Elevated | Transformer only | 10 | 16 | 2016-10-16 | 1563038 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
16-0073199 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 17 | 2016-10-17 | 1564445 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0073512 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 10 | 17 | 2016-10-17 | 1564887 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
16-0081495 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 21 | 2016-11-21 | 1586648 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0082155 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 11 | 24 | 2016-11-24 | 1588365 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0082313 | Environmental/External | Lightning | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2016-11-26 | 1589389 | Sus | Y | EnvironmentalExternal¦Lightning¦Fuse¦FailedFaulted
16-0082326 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2016-11-26 | 1589388 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0085199 | Company Initiated | Other Circuits |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2016-12-12 | 1600273 | Sus | N | CompanyInitiated¦OtherCircuits¦¦
16-0085824 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2016-12-15 | 1603365 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
16-0086522 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 12 | 20 | 2016-12-20 | 1607552 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0005395 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 8 | 2017-01-08 | 1625380 | Sus | N | Vegetation¦Treefellintoline¦CrossarmWood¦Brokenwireonground
17-0006435 | Vegetation | Tree - fell into line | Conductor, Overhead | Arcing | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1632511 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Arcing
17-0007331 | Vegetation | Tree - branch fell on line | Recloser | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1636254 | Sus | N | Vegetation¦Treebranchfellonline¦Recloser¦Normal
17-0007429 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1638850 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
17-0010934 | Equipment Failure/Involved | Overhead | Transformer | Contaminated | 2017 | Tier 2 - Elevated | Transformer only | 1 | 19 | 2017-01-19 | 1650124 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Contaminated
17-0012164 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2017-01-20 | 1655294 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0012533 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 21 | 2017-01-21 | 1657292 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0013221 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 22 | 2017-01-22 | 1660615 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0013587 | 3rd Party | Customer Equipment | Other | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662843 | Sus | N | 3rdParty¦CustomerEquipment¦Other¦Normal
17-0013731 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662913 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0013945 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 23 | 2017-01-23 | 1662834 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0014730 | Vegetation | Tree - fell into line | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2017-01-25 | 1666725 | Sus | N | Vegetation¦Treefellintoline¦Fuse¦FailedFaulted
17-0017082 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673492 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017206 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 3 | 2017-02-03 | 1673803 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0017850 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 6 | 2017-02-06 | 1675999 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0019086 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682041 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0019476 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 9 | 2017-02-09 | 1683101 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0020781 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2017-02-13 | 1687774 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0020781 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 13 | 2017-02-13 | 1687774 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0021355 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 15 | 2017-02-15 | 1689463 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0023299 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2017-02-17 | 1698283 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0023853 | Vegetation | Tree - branch fell on line | Conductor, Overhead | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1703542 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦OnGround
17-0028446 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 5 | 2017-03-05 | 1719738 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0032180 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2017-03-21 | 1731539 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0037337 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 6 | 2017-04-06 | 1746351 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
17-0037540 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1749050 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0038088 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2017-04-07 | 1751535 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0039414 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2017-04-12 | 1755841 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0040421 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Burned/flashed | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 14 | 2017-04-14 | 1758222 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Burnedflashed
17-0040527 | Vegetation | Tree - cutting, PG&E contractor | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 15 | 2017-04-15 | 1758619 | Sus | N | Vegetation¦TreecuttingPG&Econtractor¦PoleWood¦Brokenwireonground
17-0041300 | Animal | Bird found | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 4 | 19 | 2017-04-19 | 1760766 | Sus | N | Animal¦Birdfound¦ConductorOverhead¦Normal
17-0049102 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 19 | 2017-05-19 | 1785255 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0049193 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 19 | 2017-05-19 | 1785581 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0050503 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 25 | 2017-05-25 | 1790015 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer(UG)¦Broken
17-0051741 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 31 | 2017-05-31 | 1793763 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0053872 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2017-06-09 | 1800186 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0053904 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2017-06-09 | 1800188 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0060045 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 7 | 2 | 2017-07-02 | 1822249 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0071543 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2017-08-20 | 1855573 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0072305 | Vegetation | Tree - fell into line | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 23 | 2017-08-23 | 1857778 | Sus | Y | Vegetation¦Treefellintoline¦Insulator¦Broken
17-0073170 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 8 | 27 | 2017-08-27 | 1860419 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0074224 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2017-08-30 | 1863425 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0074396 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 8 | 31 | 2017-08-31 | 1863867 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0075111 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 2 | 2017-09-02 | 1866067 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Broken
17-0075596 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 9 | 3 | 2017-09-03 | 1868183 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0077361 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 10 | 2017-09-10 | 1874493 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
17-0078598 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 13 | 2017-09-13 | 1877921 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0079542 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 9 | 17 | 2017-09-17 | 1880412 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0080022 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 9 | 19 | 2017-09-19 | 1881625 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0080346 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 20 | 2017-09-20 | 1882279 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0081269 | Animal | Squirrel | Fuse | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 24 | 2017-09-24 | 1884868 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
17-0085066 | 3rd Party | Gun Shot | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Transmission line | 10 | 8 | 2017-10-08 | 1893305 | Sus | Y | 3rdParty¦GunShot¦ConductorOverhead¦Brokenwireonground
17-0085166 | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893440 | Sus | Y | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground
17-0085836 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2017-10-10 | 1897097 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0086818 | Environmental/External | Fire, Forest/Grass | Pole-Wood | On Ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1899486 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦OnGround
17-0088957 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1905467 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Brokenwireonground
17-0089269 | 3rd Party | Vehicle | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 20 | 2017-10-20 | 1906323 | Sus | Y | 3rdParty¦Vehicle¦Fuse¦FailedFaulted
17-0089506 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2017-10-22 | 1907263 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0092015 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2017-11-02 | 1914158 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0095569 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 16 | 2017-11-16 | 1923738 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0098445 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2017-11-29 | 1931992 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0100978 | Vegetation | Tree - fell into line | Service conductor | Broken | 2017 | Tier 2 - Elevated | Transformer only | 12 | 10 | 2017-12-10 | 1939804 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
17-0101830 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 12 | 15 | 2017-12-15 | 1943452 | Sus | N | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
17-0101979 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 12 | 16 | 2017-12-16 | 1944391 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0003999 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2018-01-06 | 3143 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0015146 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2018-02-17 | 26437 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
18-0015281 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 2 | 18 | 2018-02-18 | 26839 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0017750 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2018-02-27 | 32832 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0018727 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 35204 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0019249 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 36555 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0021202 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 3 | 8 | 2018-03-08 | 40653 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
18-0022718 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 14 | 2018-03-14 | 44107 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0023236 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2018 | Tier 2 - Elevated | Transformer only | 3 | 16 | 2018-03-16 | 45206 | Sus | N | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
18-0023719 | Equipment Failure/Involved | Electrical Overload | Other | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 3 | 17 | 2018-03-17 | 46524 | Sus | N | EquipmentFailureInvolved¦ElectricalOverload¦Other¦FailedFaulted
18-0030193 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2018-04-07 | 61675 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0030838 | Equipment Failure/Involved | Overhead | Other | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2018-04-10 | 63759 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
18-0032434 | Vegetation | Tree - bark fell into line | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 4 | 15 | 2018-04-15 | 67301 | Sus | N | Vegetation¦Treebarkfellintoline¦Fuse¦FailedFaulted
18-0040438 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 11 | 2018-05-11 | 84485 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0042525 | Animal | Squirrel | Transformer (OH) | Failed/Faulted | 2018 | Tier 3 - Extreme | Distribution Circuit | 5 | 19 | 2018-05-19 | 89602 | Sus | Y | Animal¦Squirrel¦Transformer(OH)¦FailedFaulted
18-0051412 | Unknown Cause | Patrol - not conducted |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 15 | 2018-06-15 | 110157 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
18-0052078 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2018-06-18 | 112323 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0053690 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 3 - Extreme | Transformer only | 6 | 22 | 2018-06-22 | 115226 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0054424 | Vegetation | Tree - branch fell on line | Fuse | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2018-06-25 | 118081 | Sus | Y | Vegetation¦Treebranchfellonline¦Fuse¦Normal
18-0055251 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Transmission line | 6 | 28 | 2018-06-28 | 119921 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0055544 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 28 | 2018-06-28 | 120466 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer(OH)¦Normal
18-0061721 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 20 | 2018-07-20 | 136060 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0062470 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 22 | 2018-07-22 | 137455 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
18-0066824 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 4 | 2018-08-04 | 149153 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0068878 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 8 | 10 | 2018-08-10 | 153096 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0076681 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 5 | 2018-09-05 | 168551 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0084766 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 9 | 28 | 2018-09-28 | 183600 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
18-0085495 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2018-10-02 | 185453 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0085561 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 2 | 2018-10-02 | 185662 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
18-0086490 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2018 | Tier 2 - Elevated | Transformer only | 10 | 3 | 2018-10-03 | 187827 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
18-0090214 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2018-10-14 | 195110 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
18-0091524 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 10 | 17 | 2018-10-17 | 197672 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0097840 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2018-11-07 | 210505 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0100864 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217920 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0100882 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 217947 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0104254 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 28 | 2018-11-28 | 226304 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0105287 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2018-11-29 | 229412 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
19-0004708 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 253704 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0005797 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 6 | 2019-01-06 | 255878 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0005925 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2019 | Tier 2 - Elevated | Transformer only | 1 | 7 | 2019-01-07 | 259595 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
19-0008373 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Transformer only | 1 | 13 | 2019-01-13 | 264156 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0009422 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 266491 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
19-0009893 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Transmission line | 1 | 16 | 2019-01-16 | 267844 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0010275 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 271088 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0010275 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 16 | 2019-01-16 | 271088 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0011236 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 17 | 2019-01-17 | 273636 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0016408 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 31 | 2019-01-31 | 284760 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
19-0019116 | Vegetation | Tree - fell into line | Transformer (OH) | On Ground | 2019 | Tier 3 - Extreme | Transformer only | 2 | 4 | 2019-02-04 | 294201 | Sus | N | Vegetation¦Treefellintoline¦Transformer(OH)¦OnGround
19-0019543 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 6 | 2019-02-06 | 295191 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0023114 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 14 | 2019-02-14 | 307299 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0023753 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2019 | Tier 3 - Extreme | Transformer only | 2 | 14 | 2019-02-14 | 310941 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
19-0024402 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 16 | 2019-02-16 | 313508 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0025194 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 315780 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0025296 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 17 | 2019-02-17 | 316590 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
19-0027386 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 22 | 2019-02-22 | 321619 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
19-0028320 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Transformer only | 2 | 26 | 2019-02-26 | 324268 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0028863 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 26 | 2019-02-26 | 325721 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
19-0029710 | Environmental/External | Ice or snow | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2019-03-01 | 328777 | Sus | N | EnvironmentalExternal¦Iceorsnow¦ConductorOverhead¦Brokenwireonground
19-0032432 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 3 | 10 | 2019-03-10 | 335576 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0044551 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 4 | 20 | 2019-04-20 | 364241 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0050088 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | 2019 | Tier 3 - Extreme | Transformer only | 5 | 8 | 2019-05-08 | 376477 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Leaking
19-0059234 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2019-05-29 | 392863 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0064884 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 6 | 9 | 2019-06-09 | 402677 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0066255 | Equipment Failure/Involved | Electrical Overload | Recloser | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 6 | 11 | 2019-06-11 | 406671 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Recloser¦Normal
19-0075500 | Company Initiated | Construction Activity/equip, company | Pole-Wood | Burned/flashed | 2019 | Tier 3 - Extreme | Distribution Circuit | 7 | 9 | 2019-07-09 | 443337 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦PoleWood¦Burnedflashed
19-0087320 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 8 | 13 | 2019-08-13 | 505188 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0092040 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2019 | Tier 2 - Elevated | Distribution Circuit | 8 | 26 | 2019-08-26 | 538581 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
19-0120277 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2019-11-01 | 697670 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0123466 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 11 | 2019-11-11 | 704209 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130628 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 26 | 2019-11-26 | 717953 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0130781 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2019 | Tier 3 - Extreme | Transformer only | 11 | 27 | 2019-11-27 | 722469 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
19-0130918 | Equipment Failure/Involved | Overhead | Insulator | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 28 | 2019-11-28 | 722908 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Insulator¦Brokenwireonground
19-0131049 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 11 | 29 | 2019-11-29 | 723396 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
19-0135058 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on object | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 8 | 2019-12-08 | 733881 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonobject
19-0137540 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2019-12-22 | 748172 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0137619 | Unknown Cause | Patrol - not conducted |  |  | 2019 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2019-12-22 | 748596 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
20-0011183 | Equipment Failure/Involved | Overhead | Other | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2020-01-19 | 766129 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
20-0017894 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2020-02-05 | 778782 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
20-0018323 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2020-02-06 | 779682 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0020562 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 2 | 11 | 2020-02-11 | 788324 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0029687 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 6 | 2020-03-06 | 837715 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032832 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 854528 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
20-0032935 | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | 2020 | Tier 2 - Elevated | Distribution Circuit | 3 | 16 | 2020-03-16 | 855460 | Sus | N | EnvironmentalExternal¦FloodErosion¦PoleWood¦Deteriorated
20-0033045 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 855728 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
20-0033337 | Vegetation | Tree - branch fell on line | Transformer (OH) | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 17 | 2020-03-17 | 856523 | Sus | N | Vegetation¦Treebranchfellonline¦Transformer(OH)¦FailedFaulted
20-0033527 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 17 | 2020-03-17 | 856960 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0033536 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 16 | 2020-03-16 | 853074 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
20-0034232 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 3 | 19 | 2020-03-19 | 858816 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0036360 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 3 | 26 | 2020-03-26 | 866593 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
20-0039902 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2020-04-08 | 892626 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0045866 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 4 | 30 | 2020-04-30 | 904341 | Sus | N | WildfireMitigation¦CWSPVegetationRemoval¦ConductorOverhead¦Normal
20-0047778 | Company Initiated | Construction Activity/equip, company | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 6 | 2020-05-06 | 908124 | Sus | Y | CompanyInitiated¦ConstructionActivityequipcompany¦ConductorOverhead¦Normal
20-0050391 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 5 | 14 | 2020-05-14 | 913980 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
20-0050992 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 5 | 17 | 2020-05-17 | 915133 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0051095 | Equipment Failure/Involved | Underground | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 5 | 18 | 2020-05-18 | 915565 | Sus | Y | EquipmentFailureInvolved¦Underground¦Transformer¦FailedFaulted
20-0074822 | 3rd Party | Vehicle | Pole-Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 22 | 2020-07-22 | 970142 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
20-0077080 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2020 | Tier 2 - Elevated | Distribution Circuit | 7 | 28 | 2020-07-28 | 973881 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
20-0081183 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2020 | Tier 2 - Elevated | Transformer only | 8 | 7 | 2020-08-07 | 984290 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
20-0084291 | Equipment Failure/Involved | Overhead | Transformer | Leaking | 2020 | Tier 3 - Extreme | Transformer only | 8 | 15 | 2020-08-15 | 1005291 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Leaking
20-0085075 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1010503 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
20-0085297 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 16 | 2020-08-16 | 1009948 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
20-0089240 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 24 | 2020-08-24 | 1028136 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
20-0091439 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Normal | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 19 | 2020-08-19 | 1041113 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Normal
20-0091471 | Vegetation | Tree - fell into line | Crossarm, Wood | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 8 | 30 | 2020-08-30 | 1041161 | Sus | Y | Vegetation¦Treefellintoline¦CrossarmWood¦Broken
20-0094123 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 9 | 6 | 2020-09-06 | 1057466 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0099637 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1085647 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0099793 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1086079 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0100125 | Environmental/External | Fire, Forest/Grass | Conductor, Overhead | Burned/flashed | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 7 | 2020-09-07 | 1087524 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦ConductorOverhead¦Burnedflashed
20-0102687 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 3 - Extreme | Distribution Circuit | 9 | 29 | 2020-09-29 | 1097357 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0105758 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 10 | 6 | 2020-10-06 | 1112085 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
20-0109429 | Animal | Other | Conductor, Overhead | Normal | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 15 | 2020-10-15 | 1118953 | Sus | Y | Animal¦Other¦ConductorOverhead¦Normal
20-0112750 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Transformer only | 10 | 24 | 2020-10-24 | 1124475 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0113264 | Unknown Cause | Patrol - found nothing |  |  | 2020 | Tier 2 - Elevated | Distribution Circuit | 10 | 26 | 2020-10-26 | 1128293 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
20-0115947 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 2 | 2020-11-02 | 1133665 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
20-0117353 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2020 | Tier 3 - Extreme | Distribution Circuit | 11 | 5 | 2020-11-05 | 1136371 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
20-0120664 | Vegetation | Tree - branch fell on line | Crossarm, Wood | Broken, wire on ground | 2020 | Tier 2 - Elevated | Distribution Circuit | 11 | 13 | 2020-11-13 | 1143683 | Sus | Y | Vegetation¦Treebranchfellonline¦CrossarmWood¦Brokenwireonground
20-0125136 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2020 | Tier 2 - Elevated | Transformer only | 11 | 25 | 2020-11-25 | 1154511 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
21-0007917 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 12 | 2021-01-12 | 1209145 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0009483 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1213864 | Sus | N | WildfireMitigation¦PublicSafetyPowerShutoff¦¦
21-0010544 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2021-01-19 | 1215657 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0010890 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 19 | 2021-01-19 | 1216856 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0012262 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 18 | 2021-01-18 | 1220179 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0013615 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223517 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0013662 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 1 | 25 | 2021-01-25 | 1223400 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0016458 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 26 | 2021-01-26 | 1236064 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0017787 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2021 | Tier 2 - Elevated | Transformer only | 1 | 28 | 2021-01-28 | 1239932 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
21-0018101 | Equipment Failure/Involved | Overhead | Switch (OH) | Failed/Faulted | 2021 | Tier 2 - Elevated | Transformer only | 1 | 28 | 2021-01-28 | 1240812 | Sus | N | EquipmentFailureInvolved¦Overhead¦Switch(OH)¦FailedFaulted
21-0018118 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 1 | 29 | 2021-01-29 | 1240917 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0022519 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2021 | Tier 3 - Extreme | Transformer only | 2 | 5 | 2021-02-05 | 1248946 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
21-0022714 | Vegetation | Tree - fell into line | Service conductor | Broken, wire on ground | 2021 | Tier 3 - Extreme | Transformer only | 2 | 6 | 2021-02-06 | 1249685 | Sus | N | Vegetation¦Treefellintoline¦Serviceconductor¦Brokenwireonground
21-0029323 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 2 | 24 | 2021-02-24 | 1261677 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Brokenwireonground
21-0030166 | 3rd Party | Fire, house or bldg. | Transformer (OH) | Normal | 2021 | Tier 2 - Elevated | Transformer only | 2 | 26 | 2021-02-26 | 1263288 | Sus | N | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦Normal
21-0030741 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 1 | 2021-03-01 | 1264711 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0041863 | Animal | Other | Anchor or Guy | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 3 | 27 | 2021-03-27 | 1300816 | Sus | N | Animal¦Other¦AnchororGuy¦Broken
21-0044222 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Deteriorated | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 2 | 2021-04-02 | 1305943 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Deteriorated
21-0047122 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2021 | Tier 2 - Elevated | Transformer only | 4 | 10 | 2021-04-10 | 1312460 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
21-0047510 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 4 | 12 | 2021-04-12 | 1313583 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Deteriorated
21-0049292 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2021 | Tier 2 - Elevated | Transformer only | 4 | 15 | 2021-04-15 | 1319037 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
21-0051288 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 4 | 21 | 2021-04-21 | 1326759 | Sus | N | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0055715 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 5 | 1 | 2021-05-01 | 1338469 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0056499 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 5 | 4 | 2021-05-04 | 1340343 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0082945 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 6 | 30 | 2021-06-30 | 1389417 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0091372 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2021 | Tier 3 - Extreme | Distribution Circuit | 7 | 18 | 2021-07-18 | 1407307 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
21-0097848 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2021 | Tier 3 - Extreme | Transformer only | 7 | 31 | 2021-07-31 | 1424369 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
21-0101119 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 6 | 2021-08-06 | 1435936 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Deteriorated
21-0101706 | 3rd Party | Vehicle | Pole-Wood | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 8 | 2021-08-08 | 1437327 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Normal
21-0106005 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2021-08-17 | 1445751 | Sus | Y | WildfireMitigation¦PublicSafetyPowerShutoff¦ConductorOverhead¦Normal
21-0107098 | Vegetation | Tree - grew into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 20 | 2021-08-20 | 1448164 | Sus | Y | Vegetation¦Treegrewintoline¦ConductorOverhead¦Normal
21-0107642 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 8 | 21 | 2021-08-21 | 1449268 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0121678 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 9 | 23 | 2021-09-23 | 1478969 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
21-0125806 | Animal | Squirrel | Bus | Normal | 2021 | Tier 2 - Elevated | Substation - Distribution | 10 | 4 | 2021-10-04 | 1486706 | Sus | Y | Animal¦Squirrel¦Bus¦Normal
21-0127088 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 7 | 2021-10-07 | 1489329 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0128212 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2021-10-09 | 1491212 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
21-0131022 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 14 | 2021-10-14 | 1497690 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
21-0134865 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 22 | 2021-10-22 | 1505478 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0138341 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 26 | 2021-10-26 | 1521293 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
21-0138782 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 10 | 27 | 2021-10-27 | 1523009 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0139080 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 3 - Extreme | Distribution Circuit | 10 | 27 | 2021-10-27 | 1523641 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0140328 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2021-10-31 | 1526405 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
21-0142706 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | 2021 | Tier 2 - Elevated | Transformer only | 11 | 5 | 2021-11-05 | 1535370 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Deteriorated
21-0143645 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 8 | 2021-11-08 | 1538220 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
21-0144186 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 9 | 2021-11-09 | 1539199 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0152442 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 29 | 2021-11-29 | 1555422 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0152863 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2021-11-30 | 1556042 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
21-0155829 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 7 | 2021-12-07 | 1561467 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0157346 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2021-12-13 | 1567398 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
21-0157903 | Unknown Cause | Patrol - not conducted |  |  | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2021-12-13 | 1569014 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
21-0158422 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Together | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 15 | 2021-12-15 | 1572074 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Together
21-0158547 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 15 | 2021-12-15 | 1573220 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
21-0159371 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 17 | 2021-12-17 | 1576113 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
21-0159825 | Unknown Cause | Patrol - found nothing |  |  | 2021 | Tier 3 - Extreme | Transformer only | 12 | 20 | 2021-12-20 | 1577722 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
21-0160792 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2021 | Tier 3 - Extreme | Distribution Circuit | 12 | 26 | 2021-12-26 | 1582638 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0005564 | Environmental/External | Ice or snow | Fuse | Burned Open | 2021 | Tier 2 - Elevated | Distribution Circuit | 12 | 27 | 2021-12-27 | 1589821 | Sus | N | EnvironmentalExternal¦Iceorsnow¦Fuse¦BurnedOpen
22-0006048 | Equipment Failure/Involved | Overhead | Fuse | Normal | 2022 | Tier 3 - Extreme | Transformer only | 1 | 4 | 2022-01-04 | 1594821 | Sus | N | EquipmentFailureInvolved¦Overhead¦Fuse¦Normal
22-0033196 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Transformer only | 3 | 12 | 2022-03-12 | 1647366 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0035337 | 3rd Party | Vehicle | Pole-Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 3 | 17 | 2022-03-17 | 1650636 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
22-0041448 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 3 | 31 | 2022-03-31 | 1660719 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0059400 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2022-05-08 | 1690995 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0062158 | Equipment Failure/Involved | Underground | Switch (UG) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2022-05-14 | 1696453 | Sus | Y | EquipmentFailureInvolved¦Underground¦Switch(UG)¦FailedFaulted
22-0072186 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2022-06-09 | 1726460 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0072435 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 9 | 2022-06-09 | 1726713 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0074691 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 6 | 15 | 2022-06-15 | 1732224 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0074940 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 3 - Extreme | Distribution Circuit | 6 | 16 | 2022-06-16 | 1732829 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0076080 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Transformer only | 6 | 19 | 2022-06-19 | 1735515 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0078826 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 6 | 27 | 2022-06-27 | 1742929 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0081228 | Equipment Failure/Involved | Overhead | Secondary | Broken | 2022 | Tier 2 - Elevated | Transformer only | 7 | 1 | 2022-07-01 | 1747401 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Broken
22-0084426 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 12 | 2022-07-12 | 1754658 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
22-0084495 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2022 | Tier 2 - Elevated | Distribution Circuit | 8 | 17 | 2022-08-17 | 1783469 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
22-0091695 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 7 | 30 | 2022-07-30 | 1769083 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0100602 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Arcing | 2022 | Tier 2 - Elevated | Transformer only | 8 | 22 | 2022-08-22 | 1787281 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Arcing
22-0104449 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 1 | 2022-09-01 | 1796543 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0111737 | Unknown Cause | Patrol - found nothing |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 9 | 18 | 2022-09-18 | 1815164 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
22-0114614 | Animal | Squirrel | Pothead(Riser Termination) | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2022-09-25 | 1821256 | Sus | Y | Animal¦Squirrel¦Pothead(RiserTermination)¦Normal
22-0118962 | Equipment Failure/Involved | Overhead | Transformer | Broken | 2022 | Tier 2 - Elevated | Transformer only | 10 | 7 | 2022-10-07 | 1831079 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦Broken
22-0123049 | Equipment Failure/Involved | Overhead | Transformer (OH) | Failed/Faulted | 2022 | Tier 3 - Extreme | Transformer only | 10 | 19 | 2022-10-19 | 1840852 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦FailedFaulted
22-0123853 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 10 | 22 | 2022-10-22 | 1842717 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0125974 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | 2022 | Tier 3 - Extreme | Transformer only | 10 | 29 | 2022-10-29 | 1848493 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦BurnedOpen
22-0126427 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 11 | 1 | 2022-11-01 | 1849618 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
22-0126734 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Arcing | 2022 | Tier 2 - Elevated | Transformer only | 11 | 1 | 2022-11-01 | 1850474 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Arcing
22-0134793 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | 2022 | Tier 2 - Elevated | Transformer only | 11 | 29 | 2022-11-29 | 1871384 | Sus | Y | EquipmentFailureInvolved¦Overhead¦LightningArrestor¦Broken
22-0135152 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Broken | 2022 | Tier 2 - Elevated | Transformer only | 11 | 30 | 2022-11-30 | 1872156 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦Broken
22-0136972 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 6 | 2022-12-06 | 1877209 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
22-0139319 | Animal | Squirrel | Transformer (OH) | Normal | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 12 | 2022-12-12 | 1887447 | Sus | N | Animal¦Squirrel¦Transformer(OH)¦Normal
22-0140800 | Unknown Cause | Patrol - not conducted |  |  | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 20 | 2022-12-20 | 1894469 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
22-0141028 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | 2022 | Tier 2 - Elevated | Distribution Circuit | 12 | 22 | 2022-12-22 | 1896070 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Deteriorated
22-0142439 | Vegetation | Tree - fell into line | Conductor, Overhead | Bent or Twisted | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 30 | 2022-12-30 | 1902878 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦BentorTwisted
22-0142614 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2022 | Tier 3 - Extreme | Distribution Circuit | 12 | 31 | 2022-12-31 | 1904119 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
15-0005853 | 3rd Party | Vehicle | Pole-Wood | Broken | 2015 | Tier 3 - Extreme | Distribution Circuit | 1 | 20 | 2015-01-20 | 1166628 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Broken
15-0009830 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 2 | 6 | 2015-02-06 | 1173380 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Broken
15-0012335 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2015-02-08 | 1185228 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0033688 | Animal | Other | Recloser | Burned/flashed | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 12 | 2015-05-12 | 1233533 | Sus | Y | Animal¦Other¦Recloser¦Burnedflashed
15-0033965 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 14 | 2015-05-14 | 1234094 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0035646 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 5 | 21 | 2015-05-21 | 1237861 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0039895 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 6 | 9 | 2015-06-09 | 1248088 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0040956 | Animal | Bird found | Fuse | Failed/Faulted | 2015 | Tier 2 - Elevated | Distribution Circuit | 6 | 14 | 2015-06-14 | 1250852 | Sus | Y | Animal¦Birdfound¦Fuse¦FailedFaulted
15-0045634 | Equipment Failure/Involved | Electrical Overload | Transformer |  | 2015 | Tier 2 - Elevated | Transformer only | 7 | 6 | 2015-07-06 | 1263450 | Sus | Y | EquipmentFailureInvolved¦ElectricalOverload¦Transformer¦
15-0045735 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 7 | 6 | 2015-07-06 | 1263568 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0053273 | 3rd Party | Tree - cutting, 3rd party | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 8 | 6 | 2015-08-06 | 1283608 | Sus | Y | 3rdParty¦Treecutting3rdparty¦Fuse¦FailedFaulted
15-0053911 | Environmental/External | Lightning | Transformer (OH) | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 8 | 9 | 2015-08-09 | 1285490 | Sus | Y | EnvironmentalExternal¦Lightning¦Transformer(OH)¦FailedFaulted
15-0053922 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 9 | 2015-08-09 | 1285524 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0054147 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 8 | 10 | 2015-08-10 | 1285896 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0060307 | 3rd Party | Fire, house or bldg. | Transformer (OH) | Failed/Faulted | 2015 | Tier 3 - Extreme | Transformer only | 9 | 9 | 2015-09-09 | 1302883 | Sus | Y | 3rdParty¦Firehouseorbldg¦Transformer(OH)¦FailedFaulted
15-0061797 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 9 | 16 | 2015-09-16 | 1307199 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0067306 | Vegetation | Tree - cutting, PG&E contractor | Conductor, Overhead | Arcing | 2015 | Tier 2 - Elevated | Transformer only | 10 | 1 | 2015-10-01 | 1315190 | Sus | Y | Vegetation¦TreecuttingPG&Econtractor¦ConductorOverhead¦Arcing
15-0071710 | Environmental/External | Lightning | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 2 - Elevated | Transformer only | 10 | 18 | 2015-10-18 | 1325549 | Sus | Y | EnvironmentalExternal¦Lightning¦Cutoutfuseholder¦FailedFaulted
15-0074369 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 30 | 2015-10-30 | 1331715 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0074446 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 2 - Elevated | Distribution Circuit | 10 | 31 | 2015-10-31 | 1331961 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
15-0074981 | Equipment Failure/Involved | Underground | Conductor, Underground | Broken | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 2 | 2015-11-02 | 1333661 | Sus | Y | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Broken
15-0076313 | Animal | Bird found | Cutout, fuse holder | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 7 | 2015-11-07 | 1336937 | Sus | Y | Animal¦Birdfound¦Cutoutfuseholder¦FailedFaulted
15-0077833 | Unknown Cause | Patrol - not conducted |  |  | 2015 | Tier 2 - Elevated | Transmission line | 11 | 15 | 2015-11-15 | 1341441 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
15-0078075 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2015 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2015-11-15 | 1342660 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
15-0078375 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2015-11-16 | 1343133 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
15-0083011 | Vegetation | Tree - bark fell into line | Conductor, Overhead | Normal | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 6 | 2015-12-06 | 1354560 | Sus | N | Vegetation¦Treebarkfellintoline¦ConductorOverhead¦Normal
15-0084418 | Vegetation | Tree - fell into line | Secondary | Broken, wire on ground | 2015 | Tier 2 - Elevated | Transformer only | 12 | 12 | 2015-12-12 | 1359366 | Sus | N | Vegetation¦Treefellintoline¦Secondary¦Brokenwireonground
15-0084594 | Unknown Cause | Patrol - found nothing |  |  | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 13 | 2015-12-13 | 1360533 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
15-0084615 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2015 | Tier 2 - Elevated | Distribution Circuit | 12 | 13 | 2015-12-13 | 1360617 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
15-0086661 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2015 | Tier 3 - Extreme | Distribution Circuit | 12 | 22 | 2015-12-22 | 1368765 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0002477 | 3rd Party | Vehicle | Pole-Wood | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 1 | 2 | 2016-01-02 | 1375825 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦OnGround
16-0005740 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2016-01-15 | 1384702 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0010720 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 2 | 4 | 2016-02-04 | 1398397 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0018103 | Vegetation | Tree - fell into line | Conductor, Overhead | On Ground | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 5 | 2016-03-05 | 1420877 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦OnGround
16-0018365 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2016-03-06 | 1421756 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0020871 | Vegetation | Tree - branch fell on line | Fuse | Failed/Faulted | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2016-03-13 | 1429846 | Sus | N | Vegetation¦Treebranchfellonline¦Fuse¦FailedFaulted
16-0020959 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 13 | 2016-03-13 | 1430230 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0022978 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | 2016 | Tier 2 - Elevated | Transformer only | 3 | 21 | 2016-03-21 | 1435282 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Broken
16-0023129 | Vegetation | Tree - branch fell on line | Secondary | Broken, wire on ground | 2016 | Tier 3 - Extreme | Transformer only | 3 | 21 | 2016-03-21 | 1435854 | Sus | N | Vegetation¦Treebranchfellonline¦Secondary¦Brokenwireonground
16-0024430 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 3 | 28 | 2016-03-28 | 1439806 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0025879 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 4 | 2016-04-04 | 1443861 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0027253 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 8 | 2016-04-08 | 1446987 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
16-0027606 | Vegetation | Other ground vegetation | Pole-Wood | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 4 | 10 | 2016-04-10 | 1448277 | Sus | N | Vegetation¦Othergroundvegetation¦PoleWood¦Normal
16-0030838 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 22 | 2016-04-22 | 1456324 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0032499 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 4 | 28 | 2016-04-28 | 1461151 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
16-0033709 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2016 | Tier 2 - Elevated | Distribution Circuit | 5 | 4 | 2016-05-04 | 1464435 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
16-0039612 | 3rd Party | Tree - cutting, 3rd party | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 5 | 29 | 2016-05-29 | 1478884 | Sus | Y | 3rdParty¦Treecutting3rdparty¦ConductorOverhead¦Brokenwireonground
16-0040555 | Equipment Failure/Involved | Overhead | Cutout, fuse holder | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 6 | 2 | 2016-06-02 | 1481448 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Cutoutfuseholder¦FailedFaulted
16-0044585 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 6 | 20 | 2016-06-20 | 1492891 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0046042 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 2 - Elevated | Transformer only | 6 | 27 | 2016-06-27 | 1496627 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0056463 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 11 | 2016-08-11 | 1524625 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0060812 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 8 | 29 | 2016-08-29 | 1533890 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
16-0067145 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2016 | Tier 2 - Elevated | Transformer only | 9 | 23 | 2016-09-23 | 1546854 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
16-0072855 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2016-10-16 | 1562767 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
16-0072972 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Together | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 16 | 2016-10-16 | 1563367 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Together
16-0073984 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2016 | Tier 3 - Extreme | Distribution Circuit | 10 | 19 | 2016-10-19 | 1566015 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
16-0075519 | Unknown Cause | Patrol - found nothing |  |  | 2016 | Tier 2 - Elevated | Distribution Circuit | 10 | 25 | 2016-10-25 | 1569955 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
16-0077304 | Vegetation | Tree - fell into line | Service conductor | Broken | 2016 | Tier 2 - Elevated | Transformer only | 11 | 1 | 2016-11-01 | 1574520 | Sus | Y | Vegetation¦Treefellintoline¦Serviceconductor¦Broken
16-0078129 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2016 | Tier 2 - Elevated | Transformer only | 11 | 4 | 2016-11-04 | 1576708 | Sus | Y | Vegetation¦Treefellintoline¦PoleWood¦Broken
16-0078379 | Animal | Other | Fuse | Failed/Faulted | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 7 | 2016-11-07 | 1577606 | Sus | Y | Animal¦Other¦Fuse¦FailedFaulted
16-0078410 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 11 | 7 | 2016-11-07 | 1577534 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
16-0082267 | Equipment Failure/Involved | Overhead | PGs, Kearneys | Burned/flashed | 2016 | Tier 2 - Elevated | Distribution Circuit | 11 | 26 | 2016-11-26 | 1589016 | Sus | Y | EquipmentFailureInvolved¦Overhead¦PGsKearneys¦Burnedflashed
16-0086736 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2016 | Tier 3 - Extreme | Transformer only | 12 | 22 | 2016-12-22 | 1609315 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0003221 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 3 | 2017-01-03 | 1616550 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0003998 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2017-01-05 | 1619398 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0004650 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1621595 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Broken
17-0005086 | Equipment Failure/Involved | Overhead | Other | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 8 | 2017-01-08 | 1624604 | Sus | N | EquipmentFailureInvolved¦Overhead¦Other¦Broken
17-0006364 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 3 | 2017-01-03 | 1632442 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonobject
17-0007051 | Vegetation | Tree - fell into line | Pole-Wood | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 1 | 10 | 2017-01-10 | 1635639 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Broken
17-0007238 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1637989 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
17-0007281 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 10 | 2017-01-10 | 1638008 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0008368 | Vegetation | Tree - fell into line |  | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 1 | 12 | 2017-01-12 | 1641077 | Sus | N | Vegetation¦Treefellintoline¦¦FailedFaulted
17-0008709 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 13 | 2017-01-13 | 1642391 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0010866 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 19 | 2017-01-19 | 1650564 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
17-0014311 | Equipment Failure/Involved | Underground | Conductor, Underground | Deteriorated | 2017 | Tier 2 - Elevated | Distribution Circuit | 1 | 24 | 2017-01-24 | 1665541 | Sus | N | EquipmentFailureInvolved¦Underground¦ConductorUnderground¦Deteriorated
17-0017362 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 2 | 3 | 2017-02-03 | 1674104 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0017375 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 2 | 3 | 2017-02-03 | 1674397 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0019131 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 8 | 2017-02-08 | 1682331 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0020370 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 11 | 2017-02-11 | 1686305 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0020425 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 12 | 2017-02-12 | 1686508 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
17-0023276 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 2 | 18 | 2017-02-18 | 1699943 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
17-0023609 | Environmental/External | Lightning | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 19 | 2017-02-19 | 1702203 | Sus | N | EnvironmentalExternal¦Lightning¦Transformer¦FailedFaulted
17-0024061 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 20 | 2017-02-20 | 1705723 | Sus | N | UnknownCause¦Patrolnotconducted¦¦
17-0025622 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 2 | 21 | 2017-02-21 | 1708858 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0028684 | Equipment Failure/Involved | Overhead | Insulator | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 6 | 2017-03-06 | 1720555 | Sus | N | EquipmentFailureInvolved¦Overhead¦Insulator¦Broken
17-0032550 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 21 | 2017-03-21 | 1732453 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0033214 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 23 | 2017-03-23 | 1733923 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0033875 | 3rd Party | Tree - cutting, 3rd party | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2017-03-26 | 1735945 | Sus | N | 3rdParty¦Treecutting3rdparty¦PoleWood¦Broken
17-0035253 | Vegetation | Tree - branch fell on line | Insulator | Broken | 2017 | Tier 3 - Extreme | Distribution Circuit | 3 | 30 | 2017-03-30 | 1740068 | Sus | N | Vegetation¦Treebranchfellonline¦Insulator¦Broken
17-0039375 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | 2017 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2017-04-11 | 1755671 | Sus | N | EquipmentFailureInvolved¦Overhead¦Jumper¦BurnedOpen
17-0045677 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 5 | 2017-05-05 | 1775464 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0046307 | Animal | Bird found | Conductor, Overhead | Together | 2017 | Tier 3 - Extreme | Distribution Circuit | 5 | 8 | 2017-05-08 | 1777937 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Together
17-0047694 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 5 | 13 | 2017-05-13 | 1781229 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0049781 | Equipment Failure/Involved | Overhead | Other | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 5 | 22 | 2017-05-22 | 1788132 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Other¦FailedFaulted
17-0052545 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 2 - Elevated | Transformer only | 6 | 3 | 2017-06-03 | 1796109 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0052858 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 6 | 5 | 2017-06-05 | 1797530 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0053851 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | 2017 | Tier 3 - Extreme | Transformer only | 6 | 9 | 2017-06-09 | 1800090 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Secondary¦Deteriorated
17-0055463 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2017 | Tier 2 - Elevated | Transformer only | 6 | 15 | 2017-06-15 | 1805077 | Sus | Y | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
17-0056199 | Unknown Cause | Patrol - not conducted |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 6 | 18 | 2017-06-18 | 1808436 | Sus | Y | UnknownCause¦Patrolnotconducted¦¦
17-0078065 | Equipment Failure/Involved | Overhead | Fuse | Failed/Faulted | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 11 | 2017-09-11 | 1875993 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Fuse¦FailedFaulted
17-0080578 | Animal | Squirrel | Conductor, Overhead | Normal | 2017 | Tier 2 - Elevated | Distribution Circuit | 9 | 21 | 2017-09-21 | 1883081 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
17-0081826 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 9 | 26 | 2017-09-26 | 1886137 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
17-0085365 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 8 | 2017-10-08 | 1893980 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0085418 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1895763 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0085749 | 3rd Party | Vehicle | Pole-Wood | Broken | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1896843 | Sus | Y | 3rdParty¦Vehicle¦PoleWood¦Broken
17-0086005 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 10 | 2017-10-10 | 1897119 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0086284 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 9 | 2017-10-09 | 1898319 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0086448 | 3rd Party | Fire, house or bldg. | Other | Burned/flashed | 2017 | Tier 2 - Elevated | Distribution Circuit | 10 | 11 | 2017-10-11 | 1898773 | Sus | Y | 3rdParty¦Firehouseorbldg¦Other¦Burnedflashed
17-0087527 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Broken, wire on ground | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 9 | 2017-10-09 | 1901335 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Brokenwireonground
17-0087855 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 16 | 2017-10-16 | 1902278 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
17-0089932 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 10 | 24 | 2017-10-24 | 1908370 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0093745 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 9 | 2017-11-09 | 1919003 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0095337 | Unknown Cause | Patrol - found nothing |  |  | 2017 | Tier 3 - Extreme | Distribution Circuit | 11 | 15 | 2017-11-15 | 1923224 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
17-0095402 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 16 | 2017-11-16 | 1923407 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
17-0097254 | Equipment Failure/Involved | Overhead | Transformer | Failed/Faulted | 2017 | Tier 3 - Extreme | Transformer only | 11 | 22 | 2017-11-22 | 1928251 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer¦FailedFaulted
17-0098537 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on object | 2017 | Tier 2 - Elevated | Distribution Circuit | 11 | 30 | 2017-11-30 | 1932318 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonobject
18-0004839 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 1 | 9 | 2018-01-09 | 5359 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Broken
18-0017766 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | 2018 | Tier 3 - Extreme | Distribution Circuit | 2 | 27 | 2018-02-27 | 32676 | Sus | N | EquipmentFailureInvolved¦Overhead¦PoleWood¦Broken
18-0018834 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 1 | 2018-03-01 | 35557 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0019077 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 2 | 2018-03-02 | 36039 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0022413 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2018-03-13 | 43531 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0022413 | 3rd Party | Vehicle | Pole-Wood | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 13 | 2018-03-13 | 43531 | Sus | N | 3rdParty¦Vehicle¦PoleWood¦Brokenwireonground
18-0023908 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 18 | 2018-03-18 | 47252 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0025263 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 3 | 22 | 2018-03-22 | 50100 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0025390 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 22 | 2018-03-22 | 50432 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0026797 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 3 | 26 | 2018-03-26 | 53895 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0029097 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Transformer only | 4 | 4 | 2018-04-04 | 59216 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0030259 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 7 | 2018-04-07 | 61913 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
18-0031439 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 4 | 11 | 2018-04-11 | 64943 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0039109 | Animal | Bird found | Conductor, Overhead | Deteriorated | 2018 | Tier 2 - Elevated | Distribution Circuit | 5 | 8 | 2018-05-08 | 81268 | Sus | Y | Animal¦Birdfound¦ConductorOverhead¦Deteriorated
18-0047539 | Animal | Squirrel | Fuse | Failed/Faulted | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 5 | 2018-06-05 | 101809 | Sus | Y | Animal¦Squirrel¦Fuse¦FailedFaulted
18-0054314 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 6 | 25 | 2018-06-25 | 117800 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0055273 | Animal | Squirrel | Fuse | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 6 | 28 | 2018-06-28 | 119924 | Sus | Y | Animal¦Squirrel¦Fuse¦Normal
18-0058149 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 7 | 10 | 2018-07-10 | 127735 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0059194 | Vegetation | Other ground vegetation | Conductor, Overhead | Normal | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 12 | 2018-07-12 | 129883 | Sus | Y | Vegetation¦Othergroundvegetation¦ConductorOverhead¦Normal
18-0061702 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 7 | 20 | 2018-07-20 | 136052 | Sus | Y | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
18-0066627 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 3 - Extreme | Distribution Circuit | 8 | 3 | 2018-08-03 | 148596 | Sus | Y | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
18-0075088 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 8 | 30 | 2018-08-30 | 165514 | Sus | Y | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
18-0083538 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 3 - Extreme | Distribution Circuit | 9 | 25 | 2018-09-25 | 181312 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0084182 | 3rd Party | Aircraft | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Transmission line | 9 | 27 | 2018-09-27 | 182729 | Sus | Y | 3rdParty¦Aircraft¦ConductorOverhead¦Brokenwireonground
18-0086354 | Environmental/External | Lightning | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Transmission line | 10 | 3 | 2018-10-03 | 187517 | Sus | Y | EnvironmentalExternal¦Lightning¦ConductorOverhead¦Normal
18-0094875 | Animal | Squirrel | Conductor, Overhead | Normal | 2018 | Tier 2 - Elevated | Distribution Circuit | 10 | 28 | 2018-10-28 | 203689 | Sus | Y | Animal¦Squirrel¦ConductorOverhead¦Normal
18-0095091 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | 2018 | Tier 2 - Elevated | Transformer only | 10 | 29 | 2018-10-29 | 204240 | Sus | Y | EquipmentFailureInvolved¦Overhead¦Transformer(OH)¦Normal
18-0101395 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 218938 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0102563 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 11 | 23 | 2018-11-23 | 222563 | Sus | Y | UnknownCause¦Patrolfoundnothing¦¦
18-0106148 | Environmental/External | Fire, Forest/Grass | Pole-Wood | Burned/flashed | 2018 | Tier 3 - Extreme | Distribution Circuit | 11 | 8 | 2018-11-08 | 231941 | Sus | Y | EnvironmentalExternal¦FireForestGrass¦PoleWood¦Burnedflashed
18-0109581 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 16 | 2018-12-16 | 241726 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦Broken
18-0110582 | Unknown Cause | Patrol - found nothing |  |  | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 24 | 2018-12-24 | 246794 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
18-0111309 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2018 | Tier 2 - Elevated | Distribution Circuit | 12 | 31 | 2018-12-31 | 251107 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0004701 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 5 | 2019-01-05 | 253821 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0005300 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 6 | 2019-01-06 | 255814 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0006108 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | 2019 | Tier 2 - Elevated | Transformer only | 1 | 8 | 2019-01-08 | 260138 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConnectororSplice(OH)¦BurnedOpen
19-0009348 | Vegetation | Tree - fell into line | Pole-Wood | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 15 | 2019-01-15 | 266378 | Sus | N | Vegetation¦Treefellintoline¦PoleWood¦Brokenwireonground
19-0010238 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 269555 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Brokenwireonground
19-0010884 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 16 | 2019-01-16 | 273570 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0011932 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 1 | 18 | 2019-01-18 | 276093 | Sus | N | Vegetation¦Treebranchfellonline¦PoleWood¦Brokenwireonground
19-0013546 | Equipment Failure/Involved | Overhead | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 3 - Extreme | Distribution Circuit | 1 | 23 | 2019-01-23 | 279467 | Sus | N | EquipmentFailureInvolved¦Overhead¦ConductorOverhead¦Brokenwireonground
19-0017836 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 4 | 2019-02-04 | 289665 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0018272 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 291604 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Brokenwireonground
19-0018761 | Vegetation | Tree - fell into line | Conductor, Overhead | Together | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 5 | 2019-02-05 | 291821 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Together
19-0020291 | Vegetation | Tree - fell into line | Conductor, Overhead | Normal | 2019 | Tier 3 - Extreme | Distribution Circuit | 2 | 8 | 2019-02-08 | 296506 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Normal
19-0020724 | Vegetation | Tree - fell into line | Conductor, Overhead | Broken, wire on ground | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 10 | 2019-02-10 | 298999 | Sus | N | Vegetation¦Treefellintoline¦ConductorOverhead¦Brokenwireonground
19-0021449 | Unknown Cause | Patrol - found nothing |  |  | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 300627 | Sus | N | UnknownCause¦Patrolfoundnothing¦¦
19-0021678 | Vegetation | Tree - fell into line | Transformer | Broken, wire on ground | 2019 | Tier 2 - Elevated | Transformer only | 2 | 12 | 2019-02-12 | 301550 | Sus | N | Vegetation¦Treefellintoline¦Transformer¦Brokenwireonground
19-0021863 | Vegetation | Tree - branch fell on line | Conductor, Overhead | Normal | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 12 | 2019-02-12 | 301323 | Sus | N | Vegetation¦Treebranchfellonline¦ConductorOverhead¦Normal
19-0022194 | Equipment Failure/Involved | Overhead | Crossarm, Wood | Broken | 2019 | Tier 2 - Elevated | Distribution Circuit | 2 | 13 | 2019-02-13 | 304151 | Sus | N | EquipmentFailureInvolved¦Overhead¦CrossarmWood¦Broken
19-0023164 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | 2019 | Tier 2 - Elevated | Transformer only | 2 | 13 | 2019-02-13 | 305890 | Sus | N | EquipmentFailureInvolved¦Overhead¦Transformer¦Burnedflashed