## Cover Sheet Tables 1-15
| Yes | No | <-- for dropdowns
Energy Safety Data Guidelines, Appendix D
Wildifire Mitigation Data Tables Template: Tables 1 - 15
Update the below table to establish which reporting period this submission this represents.
Utility Name |  | SDGE
First year of 3-year WMP cycle |  | 2023
Reporting Period year |  | 2024
Reporting Period quarter |  | Q3 |  | Q1 | 2023
Date Modified |  | 2024-11-01 |  | Q2 | 2024
|  |  |  | Q3 | 2025
Q4

## Table 1
UtilityID | SubmissionDate | InitiativeClassification | ProjectStartDate | ProjectEndDate | UtilityInitiativeName | InitiativeDescription | InitiativeObjective | WMPInitiativeCategory | WMPInitiativeCategory# | WMPInitiativeActivity | ActivityNameifOther | WMPInitiativeActivity# | UtilityInitiativeTrackingID | WMPInitiativeCode | WMPPageNumber | RiskTargetReduction | MidYearTarget (Yes/No) | QuantTargetUnits | AnnualQuantTarget | ProjectedQuantProgressQ1 | ProjectedQuantProgressQ1-2 | ProjectedQuantProgressQ1-3 | ProjectedQuantProgressQ1-4 | QuantActualProgressQ1 | QuantActualProgressQ1-2 | QuantActualProgressQ1-3 | QuantActualProgressQ1-4 | AnnualQualTarget | QualActualProgressQ1 | QualActualProgressQ1-2 | QualActualProgressQ1-3 | QualActualProgressQ1-4 | Status | CorrectiveActionsIfDelayed | REFERENCE: Compliance Branch Requirements --> | Audit | Audit File Documentation Requested | FolderLink | PersonInChargeName | PersonInChargeEmail
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Distribution overhead hardening (covered conductor) | NA | Covered conductor utilizes conductors manufactured with an internal semiconducting layer and external insulating ultraviolet-resistant layer to provide incidental contact protection. The Covered Conductor program has the potential to raise the threshold for PSPS events to higher wind speeds compared to bare conductor. | Grid Design, Operations, and Maintenance | 8.1 | Covered conductor installation | NA | 8.1.2.1 | WMP.455 | SDGE_Grid Design, Operations, and Maintainence_Covered Conductor Installation _WMP.455_2024 | 151 | Contact from vegetation ignition likelihood Contact by object ignition likelihood | No | Miles | 60 | 0 | 0 | 0 | 60 | 6.54 | 12.6 | 17.09 |  | NA | NA | NA | NA | NA | Delayed | Engineering delays impacted subsequent activities and pushed forecasted issuance of jobs to construction into fourth quarter 2024; supply chain issues with steel poles ​ | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Strategic undergrounding | NA | Strategic undergrounding converts overhead systems to underground, providing the dual benefits of nearly eliminating the risk of utility-caused wildfire and the need for PSPS events in these areas. | Grid Design, Operations, and Maintenance | 8.1 | Undergrounding of electric lines and/or equipment | NA | 8.1.2.2 | WMP.473 | SDGE_Grid Design, Operations, and Maintainence_Undergrounding of Electric Lines and/or Equipment _WMP.473_2024 | 153 | Equipment ignition likelihood Contact from vegetation ignition likelihood Contact by object ignition | No | Miles | 125 | 0 | 0 | 0 | 125 | 3.22 | 3.22 | 18.46 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Distribution overhead system hardening | NA | Bare Conductor Hardening includes the replacement of wood poles with steel, replacement of conductor with high-strength bare conductor, and in some cases permanent removal of overhead facilities. | Grid Design, Operations, and Maintenance | 8.1 | Traditional overhead hardening | NA | 8.1.2.5.1 | WMP.475 | SDGE_Grid Design, Operations, and Maintainence_Traditional Overhead Hardening (Distribution) _WMP.475_2024 | 157 | Equipment ignition likelihood | No | Miles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | NA | NA | NA | NA | NA | Completed | No target in 2024. |  |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Transmission overhead hardening | NA | The Transmission System Hardening Program is a program that utilizes enhanced design criteria to replace wood poles with steel poles, replace aging conductors with high strength conductors, and increase conductor spacing in the HFTD to reduce the chance of risk events and ignitions. | Grid Design, Operations, and Maintenance | 8.1 | Traditional overhead hardening | NA | 8.1.2.5.2 | WMP.543 | SDGE_Grid Design, Operations, and Maintainence_Traditional Overhead Hardening (Transmission) _WMP.543_2024 | 159 | Equipment ignition likelihood | No | Miles | 10.2 | 0 | 9.1 | 9.1 | 10.2 | 1.14 | 3.38 | 5.32 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Transmission overhead hardening (distribution underbuild) | NA | The Transmission System Hardening Program is a program that utilizes enhanced design criteria to replace wood poles with steel poles, replace aging conductors with high strength conductors, and increase conductor spacing in the HFTD to reduce the chance of risk events and ignitions. | Grid Design, Operations, and Maintenance | 8.1 | Traditional overhead hardening | NA | 8.1.2.5.2 | WMP.545 | SDGE_Grid Design, Operations, and Maintainence_Traditional Overhead Hardening (Distribution Underbuilt)_WMP.545_2024 | 159 | Equipment ignition likelihood | No | Miles | 1 | 0 | 1 | 1 | 1 | 1.83 | 3.46 | 5.98 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Advanced protection | NA | Advanced Protection creates higher visibility and situational awareness in fire-prone areas, and allow for the implementation of new relay and automation standards in locations where protection coordination is difficult due to lower fault currents attributed to high impedance faults. | Grid Design, Operations, and Maintenance | 8.1 | Installation of system automation equipment | NA | 8.1.2.8.1 | WMP.463 | SDGE_Grid Design, Operations, and Maintainence_Installation of System Automation Equipment (Advanced Protection)_WMP.463_2024 | 163 | Equipment ignition likelihood | No | Circuits | 8 | 0 | 3 | 6 | 8 | 0 | 0 | 2 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Early fault detection | NA | Early fault detection employs technologies such as Advance Radio Frequency Sensors (ARFS) and Power Quality (PQ) Meters to detect and prevent significant equipment failures before they occur. | Grid Design, Operations, and Maintenance | 8.1 | Installation of system automation equipment | NA | 8.1.2.8.2 | WMP.1195 | SDGE_Grid Design, Operations, and Maintainence_Installation of System Automation Equipment (EFD) _WMP.1195_2024 | 166 | Equipment ignition likelihood | No | Nodes | 60 | 0 | 30 | 60 | 60 | 17 | 20 | 28 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Distribution communications reliability improvements | NA | The Distribution Communications Reliability Improvement (DCRI) program enables APP and EFD technologies as a reliable communication network is necessary for initiatives that require continuous communication. | Grid Design, Operations, and Maintenance | 8.1 | Installation of system automation equipment | NA | 8.1.2.8.3 | WMP.549 | SDGE_Grid Design, Operations, and Maintainence_Installation of System Automation Equipment (LTE)_WMP.549_2024 | 170 | Wildfire hazard PSPS exposure potential | No | Base Stations | 60 | 0 | 15 | 30 | 60 | 0 | 2 | 3 |  | NA | NA | NA | NA | NA | Delayed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Capacitor maintenance and replacement program (SCADA) | NA | The SCADA Capacitors Maintenance and Replacement Program will detect and isolate issues before a capacitor rupture occurs, reducing the failure mode most likely to lead to an ignition. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.3 | WMP.453 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (SCADA) _WMP.453_2024 | 213 | Equipment ignition likelihood | No | Capacitors | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Expulsion fuse replacement | NA | The Expulsion Fuse Replacement Program replaces existing expulsion fuses with new, more fire safe expulsion fuses that are approved by CAL FIRE. These new expulsion fuses reduce the discharge expelled into the atmosphere, reducing the chance of a fuse operation leading to an ignition. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.4 | WMP.459 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Expulsion Fuse Replacement) _WMP.459_2024 | 214 | Equipment ignition likelihood | No | Fuses | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 39 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Maintenance, repair, and replacement of connectors, including hotline clamps | NA | The Hotline Clamps (HLC) Replacement Program replaces HLC connections that are connected directly onto the overhead primary conductors with compression connections to eliminate the risk of the wire down failure and the associated wildfire risk. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.5 | WMP.464 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (HLC)_WMP.464_2024 | 216 | Equipment ignition likelihood | No | HLCs | 250 | 50 | 150 | 225 | 250 | 130 | 430 | 578 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Lightning arrester removal and replacement | NA | Lightning Arrestors Replacement Program installs CAL FIRE-approved lightning arrestors to mitigate the impact of transient overvoltage on the electric system. CAL FIRE-approved lightning arrestors are equipped with an external device that operates prior to the arrestor overloading, dramatically reducing the potential of becoming an ignition source. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.6 | WMP.550 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Arrestors)_WMP.550_2024 | 218 | Equipment ignition likelihood | No | Arrestors | 1848 | 500 | 1200 | 1600 | 1848 | 111 | 651 | 1295 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Avian protection | NA | Avian Protection is aimed at improving reliability and reducing the risk of faults and wire-down events associated with avian contact that can lead to ignitions. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.2.10.1 | WMP.972 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Avian)_WMP.972_2024 | 171 | Contact by object ignition | No | Poles | 200 | 50 | 100 | 150 | 200 | 64 | 301 | 539 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Wireless Fault Indicators | NA | Wireless fault indicator technology is deployed to narrow the location of detected issues on the system. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.8.2 | WMP.449 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Wireless fault indicators)_WMP.449_2024 | 277 | Equipment ignition likelihood | No | WFIs | 300 | 0 | 0 | 0 | 300 | 0 | 0 | 0 |  | NA | NA | NA | NA | NA | Delayed | Delays due to manufacturer upgrades to the currently used fault indicators. | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Strategic pole replacement program | NA | Strategic Pole Replacement targets high-risk poles located throughout the service territory that are gas treated (also known as Cellon treatment) and are set in concrete and steel reinforced, steel reinforced and set in soil, or set in soil, and are not being address by other programs such as Covered Conductor Hardening or Strategic Undergrounding. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.2.10.2 | WMP.1189 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Pole Replacements)_WMP.1189_2024 | 173 | Equipment ignition likelihood | No | Poles | 267 | 44 | 64 | 131 | 200 | 16 | 29 | 33 |  | NA | NA | NA | NA | NA | Delayed | 2024 workplan was delayed due to finalizing the scope and steel pole shortage. | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | PSPS sectionalizing enhancements | NA | PSPS Sectionalizing Enhancement Program installs switches in strategic locations, improving the ability to isolate high-risk areas for potential de energization. For example, switches are installed on circuits that have significant sections undergrounded, allowing customers with this lower-risk infrastructure to remain energized during weather events. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.1 | WMP.461 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (PSPS Sectionalizing Enhancements)_WMP.461_2024 | 175 | PSPS exposure potential PSPS vulnerability | No | Switches | 10 | 2 | 8 | 10 | 10 | 1 | 10 | 10 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2023-01-01 | 2025-12-31 | Microgrids | NA | Microgrid backup generation and battery storage | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.7 | WMP.462 | SDGE_Grid Design & System Hardening_Microgrids_WMP.462_2022 | 161 | PSPS vulnerability | No | Microgrid | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | NA | NA | NA | NA | NA | Delayed | Delays in acquiring land rights and on-going supply chain issues impacted the completion of the renewable configurations for already-installed microgrids.​ | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2020-07-01 | 2025-12-31 | Standby power (fixed power backup) | NA | This program assists backcountry residences, businesses, and local communities in the HFTD by providing a fixed installation backup generator, or a solar panel and battery backup system to keep customers energized during PSPS. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.2 | WMP.468 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (Standby Power)_WMP.468_2024 | 175 | PSPS vulnerability | No | Generators | 300 | 75 | 150 | 225 | 300 | 30 | 33 | 46 |  | NA | NA | NA | NA | NA | Delayed | Program being evaluated for alternative offerings. | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2020-07-01 | 2025-12-31 | Generator grant program | NA | The Resiliency Grant Programs offer portable battery units with solar charging capacity to provide vulnerable customers with a means to keep small devices and appliances charged and powered during PSPS events. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.3 | WMP.466 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (Generator Grant Program)_WMP.466_2024 | 177 | PSPS vulnerability | No | Generators | NA | NA | NA | NA | NA | NA | NA | NA | NA | Q1: Define scope of work for vendor partner support and negotiate 2024 contract agreements. Configure updates in systems and databases to manage customer participation, invoicing and reporting. Complete product reviews of available backup battery options. Generate customer eligibility lists based on data parameters. Q2: Execute vendor partner agreements. Finalize customer communication, website, and outreach materials. Program go-live - systems and processes active for customer participation. Finalize procedures for emergency deployment of backup batteries to affected customers during active PSPS. Q3: Update customer eligibility lists based on current data parameters. Launch outreach communications to eligible MBL and Life Support customers. Program promotion and customer education at Wildfire Safety Fairs. Conduct ongoing customer service, delivery scheduling, and training on program offering. Partner with AFN and Tribal Relations stakeholders on outreach. Q4: Update customer eligibility lists based on current data parameters. Conduct customer delivery scheduling, delivery and training on program offering. Finalize end of year participation report. Begin follow up calls to previous year's customers (satisfaction survey, re-education, answer questions). | Scope of work for vendor finalized with 2024 procing and updated. Completed system configuration for 2024. Product analysis completed. Eligable customer list generated for 2024 - to be refreshed closer to program launch. | Final scope of work updates are being completed for vendor partner agreements. Edits to communication and marketing materials are underway, systems and processes are ready for customer participation. Processes in place for potential PSPS events. | Completed - Eligible customer list was generated and updated based on current data parameters and qualifying criteria for 2024. All eligible MBL and Life Support customer were sent program information in the mail on September 25th. Communicated about resiliency program offerings with over 1,900 customers attending the Wildfire Safety Fairs. Program staff and implementer continued to communicate with new and existing program participants, fielded customer interest, and kicked off outreach and appointment scheduling. Communicated with AFN and Tribal stakeholders on program status and updates. Presented program information and updates during the Q3 Regional PSPS Working Group meeting. | . | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Project | 2020-07-01 | 2025-12-31 | Generator assistance program | NA | The Resiliency Assistance Programs focus on enhancing resiliency for customers who reside in the HFTD and may be impacted by PSPS events. The program offers a rebate to customers providing a 70-to-90 percent discount on average portable generator models to mitigate the impacts of PSPS. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.4 | WMP.467 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (Generator Assistance Program)_WMP.467_2024 | 179 | PSPS vulnerability | No | Generators | NA | NA | NA | NA | NA | NA | NA | NA | NA | Q1: Execute vendor contract for 2024 program year. Complete analysis for Qualified Product List. Update all processes and procedures. Generate customer eligibility lists based on data parameters. Q2: Complete the configuration of updates in systems and databases to manage customer participation, invoicing and reporting. Finalize customer communication, website, and outreach materials. Complete the necessary updates on customer-facing portal systems. Program go-live - systems and processes active for customer participation. Q3: Launch marketing and outreach communications. Program promotion and customer education at Wildfire Safety Fairs. Update customer eligibility lists based on current data parameters. Begin to process and provide rebates to qualified customers on qualified products. Q4: Update customer eligibility lists based on current data parameters. Finalize & distribute end of year survey to participating customers. Finalize end of year participation report. Target participation of 500 customers. | 2024 vendor contract executed on 2/26/2024. Analysis for Qualified Products List completed 3/25/2024. Processes and procedures updated on 3/15/2024. | Systems/database (EECP) configurration completed. Vendor portal and SDGE website is live - customer list and QPL have been uploaded to vendor portal. GAP program launched - 2mo ahead of 2023. | Complete - Letters mailed 5/13/2024. Completion of all emails sent by 6/22/2024. Wildfire Safety Fairs completed for 5/18/2024, 6/8/2024,7/13/2024 & 8/24/2024. New process to update customer eligibility list monthly. CLEAResult has received 265 coupon requests and processed 55 rebates as of 10/8/2024. | . | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Distribution overhead detailed inspections | NA | Perform overhead detailed inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.1 | WMP.478 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Detailed Inspections of Distribution Electric Lines and Equipment)_WMP.478_2024 | 182 | Equipment ignition likelihood | Yes | Structures | 15450 | 12800 | 14850 | 15350 | 15450 | 7403 | 15096 | 16351 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Transmission overhead detailed inspections | NA | Perform overhead detailed inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.2 | WMP.479 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Detailed Inspections of Transmission Electric Lines and Equipment) _WMP.479_2024 | 185 | Equipment ignition likelihood | Yes | Structures | 1960 | 353 | 1121 | 1442 | 1960 | 588 | 1397 | 2201 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Distribution infrared inspections | NA | Perform infrared inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.3 | WMP.481 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Infrared Inspections of Distribution Electric Lines and Equipment)_WMP.481_2024 | 188 | Equipment ignition likelihood | Yes | Structures | 9532 | 0 | 0 | 9532 | 9532 | 0 | 282 | 3625 |  | NA | NA | NA | NA | NA | Delayed | Change order rejected; Reduced target to 300 for program optimization | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Transmission infrared inspections | NA | Perform infrared inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.4 | WMP.482 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Infrared Inspections of Transmission Electric Lines and Equipment)_WMP.482_2024 | 189 | Equipment ignition likelihood | Yes | Structures | 6179 | 0 | 0 | 0 | 6179 | 0 | 0 | 4503 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Distribution wood pole intrusive inspections | NA | Perform intrusive inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.5 | WMP.483 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Distribution Wood Pole Intrusive Pole Inspections)_WMP.483_2024 | 192 | Equipment ignition likelihood | Yes | Structures | 0 | 0 | 0 | 0 | 0 | 500 | 1471 | 1993 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Transmission wood pole intrusive inspections | NA | Perform intrusive inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.6 | WMP.1190 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Wood Pole Trans)_WMP.1190_2024 | 194 | Equipment ignition likelihood | Yes | Structures | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 149 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Drone assessments | NA | Perform drone inspections on highest risk structures in the HFTD and WUI areas. | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.7 | WMP.552 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Distribution Drone Assessments)_WMP.552_2024 | 194 | Equipment ignition likelihood | Yes | Structures | 13500 | 0 | 4500 | 9000 | 13500 | 16 | 16 | 222 |  | NA | NA | NA | NA | NA | Delayed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Distribution overhead patrol inspections | NA | Perform overhead patrol inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.8 | WMP.488 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Distribution overhead Patrol Inspections)_WMP.488_2024 | 200 | Equipment ignition likelihood | Yes | Structures | 86197 | 43600 | 71047 | 83247 | 86197 | 28863 | 59509 | 84637 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Transmission overhead patrol inspections | NA | Perform overhead patrol inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.9 | WMP.489 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Transmission Overhead Patrol)_WMP.489_2024 | 202 | Equipment ignition likelihood | Yes | Structures | 6337 | 0 | 6008 | 6008 | 6337 | 7038 | 7038 | 7174 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Transmission 69kV tier 3 visual inspections | NA | Perform supplemental inspections on all 69kV tielines in Tier 3 prior to wildfire season | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.10 | WMP.555 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Transmission 69kV Tier 3)_WMP.555_2024 | 206 | Equipment ignition likelihood | Yes | Structures | 1632 | 0 | 0 | 1632 | 1632 | 0 | 0 | 1605 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Substation patrol inspections | NA | Perform substation patrols, as scheduled, to reduce the risk of equipment failure and to manage vegetation hazards within the substation. | Grid Design, Operations, and Maintenance | 8.1 | Asset inspections | NA | 8.1.3.11 | WMP.492 | SDGE_Grid Design, Operations, and Maintainence_Asset inspections (Substation Patrol)_WMP.492_2024 | 207 | Equipment ignition likelihood | No | Substations | 384 | 89 | 192 | 261 | 384 | 92 | 198 | 288 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Quality assurance / quality control of transmission inspections | NA | Perform Quality assurance / quality control of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.1 | WMP.1191 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Secondary Trans)_WMP.1191_2024 | 226 | Equipment ignition likelihood | Yes | Findings | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Quality assurance / quality control of distribution detailed inspections | NA | Perform Quality assurance / quality control of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.2 | WMP.491 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Distribution Detailed)_WMP.491_2024 | 226 | Equipment ignition likelihood | No | Structures | 77 | 19 | 38 | 57 | 77 | 32 | 248 | 426 |  | NA | NA | NA | NA | NA | Completed | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Quality assurance / quality control of distribution drone assessments | NA | Perform Quality assurance / quality control of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.3 | WMP.1192 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Distribution Drone)_WMP.1192_2024 | 227 | Equipment ignition likelihood | No | Structures | 13500 | 0 | 4500 | 9000 | 13500 | 16 | 16 | 222 |  | NA | NA | NA | NA | NA | Delayed | Scope reevaluated to optimize number of inspections to perform, to accomplish desired risk reduction. | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Quality assurance / quality control of wood pole intrusive (transmission and distribution) | NA | Perform Quality assurance / quality control of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.4 | WMP.1193 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Wood Pole Dist &Trans)_WMP.1193_2024 | 227 | Equipment ignition likelihood | No | Structures | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | NA | NA | NA | NA | NA | Delayed | Delayed due new vendor selection impacting program. Expected to reach target by YE. | . |  |  |  | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Quality assurance / quality control of substation inspections | NA | Perform Quality assurance / quality control of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.5 | WMP.1194 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Periodic Review)_WMP.1194_2024 | 227 | Equipment ignition likelihood | No | Structures | 18 | 0 | 9 | 9 | 18 | 0 | 9 | 9 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | Jonathan Woldemariam | JWoldemariam@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Air quality index | NA | Perform routine maintenence and calibraton on particulate sensors. Sensors are for the automatic notification system to notify employees when the AQI for Particulate Matter 2.5 microns or smaller in diameter (PM2.5) exceeds 150 or exceeds 500 during wildfires. | Situational Awareness and Forecasting | 8.3 | Enviornmental monitoring System | NA | 4.1.2 | WMP.970 | SDGE_Situational Awareness and Forecasting_Environmental Monitoring System (Air Quality Index)_WMP.970_2024 | 298 | Wildfire hazard | No | Sensors | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | NA | NA | NA | NA | NA | Delayed | AQI sensor installations were completed in 2023. No additional sensors will be installed in 2024 | . |  |  |  | Sandeep Aujla | saujla@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Detailed inspections | NA | Vegetation management operations are driven by regulatory requirements and follow an annual, schedule that includes inspection, tree trimming, and auditing. During the annually scheduled routine inspection activity, all inventory trees are inspected to determine whether they require pruning to maintain mandated clearances from electrical lines. | Vegetation Management and Inspection | 8.2 | Vegetation management inspection program | NA | 8.2.2.1 | WMP.494 | SDGE_Vegetation Management and Inspection_Vegetation Management Inspection Program (Detailed inspections of vegetation around distribution electric lines and equipment) _WMP.494_2024 | 260 | Contact from vegetation ignition likelihood | No | Inspections | 485400 | 123100 | 241800 | 374200 | 485400 | 124744 | 247867 | 389110 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | John Baranowski | JBaranowski@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Off-cycle patrol | NA | Vegetation management operations are driven by regulatory requirements and follow an annual, schedule that includes inspection, tree trimming, and auditing. During the annually scheduled routine inspection activity, all inventory trees are inspected to determine whether they require pruning to maintain mandated clearances from electrical lines. | Vegetation Management and Inspection | 8.2 | Vegetation management inspection program | NA | 8.2.2.2 | WMP.508 | SDGE_Vegetation Management and Inspection_Vegetation Management Inspection Program (Off-Cycle)_WMP.508_2024 | 265 | Contact from vegetation ignition likelihood | No | VMAs | 106 | 0 | 9 | 106 | 106 | 27 | 53 | 104 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | John Baranowski | JBaranowski@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Fuels management | NA | Wildland fuel reduction involves the thinning, pruning, and in some cases, removal of vegetation for the purpose of minimizing source material that could ignite and propagate a wildfire. | Vegetation Management and Inspection | 8.2 | Wood and slash management | NA | 8.2.3 | WMP.497 | SDGE_Vegetation Management and Inspection_Fuel Management (slash) _WMP.497_2024 | 273 | Wildfire hazard | No | Poles Cleared | 500 | 100 | 100 | 200 | 500 | 82 | 101 | 136 |  | NA | NA | NA | NA | NA | Delayed | Reexamining the cost/benefit of its Fuels Management program to determine whether to continue and at what scale. | . |  |  |  | John Baranowski | JBaranowski@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Pole clearing (brushing) | NA | Pole brushing is a fire prevention measure involving the removal of vegetation at the base of poles that carry specific types of electrical hardware that could cause sparking or molten material to fall to the ground. | Vegetation Management and Inspection | 8.2 | Pole Clearing | NA | 8.2.3.1 | WMP.512 | SDGE_Vegetation Management and Inspection_Pole Clearing (Brushing)_WMP.501_2024 | 270 | Wildfire hazard | No | Poles Brushed | 33010 | 14270 | 25150 | 27890 | 33010 | 19410 | 32643 | 36263 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | John Baranowski | JBaranowski@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Clearance | NA | Vegetation Management defines enhanced clearances as greater than or equal to 12 feet at time of trim, which is the CPUC-recommended post-trim clearance for distribution voltages in the HFTD. SDG&E aims to achieve clearances up to 25 feet, where feasible, to achieve the optimal risk mitigation. | Vegetation Management and Inspection | 8.2 | Clearance | NA | 8.2.3.3 | WMP.501 | SDGE_Vegetation Management and Inspection_Clearance (Achieve clearances around electric lines and equipment) _WMP.512_2024 | 274 | Contact from vegetation ignition likelihood | No | Trees Trimmed or Removed | 11200 | 2570 | 5710 | 8600 | 11200 | 2960 | 5904 | 10240 |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | John Baranowski | JBaranowski@sdge.com
SDG&E | 2024-11-01 | Program | NA | NA | Quality assurance / quality control vegetation management | NA | SDG&E uses statistical sampling methodology in its audits of all Vegetation Management-related activities including pre-inspection, clearance (tree trimming), and pole clearing. Audit results are tracked, documented, and reported as a core component of contractor performance. | Vegetation Management and Inspection | 8.2 | Quality assurance / quality control | NA | 8.2.5 | WMP.505 | SDGE_Vegetation Management and Inspection_Quality assurance / quality control_WMP.505_2024 | 280 | Contact from vegetation ignition likelihood | No | Inspections | 15% | 15% | 15% | 15% | 15% | 38% | 26% | 37% |  | NA | NA | NA | NA | NA | In Progress | [5 empty] | John Baranowski | JBaranowski@sdge.com

## Table 2
| Utility | SDGE | Notes:
| Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2024-11-01 | HWW = High wind warning
RFW = Red flag warning
[10 empty] | Actuals | Projected
| Table 2: Performance Metrics | [8 empty] | Q3
Mar | Metric type | # | Metric name | Wind Warning Status | Program Name | HFTD Tier | Line Type | Inspection Type | Inspection Method | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 57 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 40 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | Non- HFTD | N/A | N/A | N/A | 139 |  |  |  | Number of events
| 1. Risk Events | 1.b. | Number of wires down | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 9 |  |  |  | Number of events
|  |  | Number of wires down | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 2 |  |  |  | Number of events
|  |  | Number of wires down | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of wires down | None | N/A | Non- HFTD | N/A | N/A | N/A | 14 |  |  |  | Number of events
| 1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 56 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 39 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | 135 |  |  |  | Number of events
| 1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 1 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 1 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 |  |  |  | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | 4 |  |  |  | Number of events
| 1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 4.6667 | 4.6667 | 4.6667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 1 | 1 | 1 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0.66667 | 0.66667 | 0.66667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 2.6667 | 2.6667 | 2.6667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 5 | 5 | 5 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 2 | 2 | 2 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0.33333 | 0.33333 | 0.33333 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 2 | 2 | 2 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0.66667 | 0.66667 | 0.66667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0.33333 | 0.33333 | 0.33333 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0.66667 | 0.66667 | 0.66667 | Number of events
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.2.a. | Median time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | 69 |  |  |  | hours
|  | 2.d.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | 147 |  |  |  | hours
|  | 2.d.3.a. | Median time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | 114 |  |  |  | hours
|  | 2.d.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | 153 |  |  |  | hours
|  | 2.d.4.a. | Median time | N/A |  | Non- HFTD | Distribution | N/A | N/A | 106 |  |  |  | hours
|  | 2.d.4.b. | 95 percentile time | N/A |  | Non- HFTD | Distribution | N/A | N/A | 187 |  |  |  | hours
|  | 2.t.2.a. | Median time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | 73 |  |  |  | hours
|  | 2.t.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | 149 |  |  |  | hours
|  | 2.t.3.a. | Median time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | 71 |  |  |  | hours
|  | 2.t.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | 159 |  |  |  | hours
|  | 2.t.4.a. | Median time | N/A |  | Non- HFTD | Transmission | N/A | N/A | 106 |  |  |  | hours
|  | 2.t.4.b. | 95 percentile time | N/A |  | Non- HFTD | Transmission | N/A | N/A | 161 |  |  |  | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 0 |  |  |  | hours
|  | 3.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 0 |  |  |  | hours
|  | 3.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 0 |  |  |  | hours
|  | 3.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 0 |  |  |  | hours
|  | 3.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 1 |  |  |  | hours
|  | 3.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 3 |  |  |  | hours
|  | 3.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 0 |  |  |  | hours
|  | 3.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 0 |  |  |  | hours
|  | 3.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 |  |  |  | hours
|  | 3.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 |  |  |  | hours
|  | 3.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 0 |  |  |  | hours
|  | 3.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 0 |  |  |  | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 430 |  |  |  | hours
|  | 4.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 1021 |  |  |  | hours
|  | 4.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 185 |  |  |  | hours
|  | 4.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 421 |  |  |  | hours
|  | 4.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 323 |  |  |  | hours
|  | 4.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 468 |  |  |  | hours
|  | 4.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 269 |  |  |  | hours
|  | 4.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 602 |  |  |  | hours
|  | 4.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 217 |  |  |  | hours
|  | 4.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 353 |  |  |  | hours
|  | 4.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 134 |  |  |  | hours
|  | 4.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 416 |  |  |  | hours
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A |  |  |  |  | hours |  | N/A
|  | 5.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A |  |  |  |  | hours |  | N/A
|  | 5.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A |  |  |  |  | hours |  | N/A
|  | 5.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A |  |  |  |  | hours |  | N/A
|  | 5.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A |  |  |  |  | hours |  | N/A
|  | 5.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A |  |  |  |  | hours |  | N/A
|  | 5.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 286 |  |  |  | hours
|  | 5.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 544 |  |  |  | hours
|  | 5.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 193 |  |  |  | hours
|  | 5.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 193 |  |  |  | hours
|  | 5.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 285 |  |  |  | hours
|  | 5.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 362 |  |  |  | hours
| 6. Vegetation management work orders | 6.a. | Number of vegetation management open work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 17617 | 16295 | 16295 | 16295 | Number of orders | Unit(s)= number of trees in HFTD. Open work orders by quarters are NOT accumulative. 2023Q2 was corrected during 2023Q3
|  | 6.b. | Number of vegetation management past due work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 334 | 1063.3333 | 1063.3333 | 1063.3333 | Number of orders | Unit(s)= number of trees in HFTD
| 7. Asset management work orders | 7.a. | Number of asset management open work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 3551 | 5163 | 5163 | 5163 | Number of orders | Unit(s)= notifications. Open work orders by quarters are NOT accumulative. 2023Q2 was corrected during 2023Q3 submission based on the latest.
|  | 7.b. | Number of asset management past due work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 90 | 6.6667 | 6.6667 | 6.6667 | Number of orders | Unit(s)= notifications. Past due work orders by quarters are NOT accumulative
| 8. Response Time | 8.a. | Response time to locked open circuit breaker | N/A | N/A | N/A | N/A | N/A | N/A | 1.31 |  |  |  | Hours | Only outages with valid ETS response time are considered for this calculation. PSPS and de energized for safetey are excluded.
| 9. Fatalities and injuries due to utility-related ignitions | 9.a. | Fatalities due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  |  |  | Number of fatalities
|  | 9.b. | Injuries due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  |  |  | Number of injuries
| 10. Value of assets destroyed by utility-related ignitions, listed by asset type | 10.a. | Value of assets destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  |  |  | 1000
| 11. Structures damaged or destroyed by utility-related ignitions | 11.a. | Number of structures destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  |  |  | Number of structures
|  | 11.b. | Critical infrastructure damaged/destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  |  |  | Number of structures
| 12. Acreage burned by utility-ignited wildfires | 12.a. | Acreage burned by utility-ignited wildfires | N/A | N/A | N/A | N/A | N/A | N/A | 47.14 |  |  |  | Acres
| 13. Number of utility-related ignitions | 13.a. | Number of ignitions | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
|  |  | Number of ignitions | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
|  |  | Number of ignitions | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
|  |  | Number of ignitions | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 7 | 7.6667 | 7.6667 | 7.6667 | Number of ignitions
|  |  | Number of ignitions | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | Number of ignitions
|  |  | Number of ignitions | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
|  |  | Number of ignitions | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | Number of ignitions
|  |  | Number of ignitions | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 4 | 8.3333 | 8.3333 | 8.3333 | Number of ignitions
|  |  | Number of ignitions | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
|  |  | Number of ignitions | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | Number of ignitions
|  |  | Number of ignitions | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | Number of ignitions
|  |  | Number of ignitions | None | N/A | Non- HFTD | N/A | N/A | N/A | 4 | 7 | 7 | 7 | Number of ignitions
x | 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 1485 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 13780 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 991 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 1653 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 57.5045 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 504.4532 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 42.8009 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 85.4214 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 3 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 118 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 49 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 1 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 948 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 8825 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 261 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 206 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 904 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 33.3403 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 343.3159 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 11.5862 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 9.0212 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 64.4237 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 2 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 12 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 1 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 37 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 2 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 51589 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 11894 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 6213 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 1106.6756 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 273.7761 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 48.8477 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 2 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 14 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 2 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 156 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 721 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 94 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 102 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 12 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 571 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 2333 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 84 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 55.12 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0.9 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 102.45 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 290.9 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 1 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 5 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 83 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 1 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 2 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 1831 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 27 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 1264 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 31.78 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 1.84 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 155.16 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 110 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 1 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 651 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 6148 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 101 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 24.06 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0.06 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 68.79 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of circuit miles inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 581.88 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 200 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 2 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 11 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 |  |  |  | # of findings from these asset inspections
x | 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 3 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 10 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 41 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 771 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 3 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 2 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 31 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 93 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 62 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 2 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 14 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 2 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 161 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 289 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 41 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 41 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 1 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 53 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 2 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 4 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 16 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 5 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 102 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 17 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 |  |  |  | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR |  |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 |  |  |  | # of asset inspection findings which have been fixed
x | 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | 32894 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other | 59782 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE records off-cycle work orders and VMAs, and all HFTD trees within the VMAs are counted as trees inspected.
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | This metric is based on vegetation related issues around structures from distribution asset drone inspection findings, total trees inspected is not tracked
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A for year 2023
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | 128 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | 42840 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other | 60278 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | 3 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | This metric is based on vegetation related issues around structures from distribution asset drone inspection findings, total trees inspected is not tracked
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A for year 2023
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | 228 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | other | 56262.0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | This metric is based on vegetation related issues around structures from distribution asset drone inspection findings, total trees inspected is not tracked
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A for year 2023
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | other | 431 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | 1183 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other | 2329 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | 723 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other | 484 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | other | 7386 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other | 0 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Drone |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR |  |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | other | 31 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
x | 17. Community outreach metrics | 17.a. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | Percentage of customers notified of evacuation | SDG&E does not track this data | N/A

## Table 3
Utility | SDGE
Table No. | 3
Date Modified | 2024-11-01
[5 empty] | Actual | Projected
Table 3: List and description of additional metrics |  |  |  |  | Q3
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Elevated FPI and Red Flag Warning Days | Number of High FPI days (elevated or extreme FPI) |  |  | No | 89 |  |  |  | Days
| Number of RFW days |  |  | No | 0 |  |  |  | Days
2. Ignition Events | Vegetation caused ignitons in HFTD with elevated or higher FPI |  |  | No | 1 |  |  |  | Ignitions
| Vegetation caused ignitons in HFTD with RFW |  |  | No | 0 |  |  |  | Ignitions
| Equipment caused ignitions in HFTD with elevated or higher FPI |  |  | No | 3 |  |  |  | Ignitions
| Equipment caused ignitions in HFTD with RFW |  |  | No | 0 |  |  |  | Ignitions
| Balloons caused ignitions in HFTD with elevated or higher FPI |  |  | No | 0 |  |  |  | Ignitions
| Balloons caused ignitions in HFTD with RFW |  |  | No | 0 |  |  |  | Ignitions
| Vehicles caused ignitions in HFTD with elevated or higher FPI |  |  | No | 2 |  |  |  | Ignitions
| Vehicles caused ignitions in HFTD with RFW |  |  | No | 0 |  |  |  | Ignitions
| Equipment caused ignition rate in HFTD during high FPI |  |  | No | 0.03 | 0.02 | 0.02 | 0.02 | Ignitions per high FPI day
| CPUC reportable secondary igntions |  |  | No | 2 |  |  |  | Ignitions | CPUC reportable secondary ignitions is not an available driver in Table 6
3. Distribution Outages | Vegetation caused outages in HFTD with Elevated FPI |  |  | No | 2 |  |  |  | Outages
| Vegetation caused outages in HFTD with RFW |  |  | No | 0 |  |  |  | Outages
| Overhead faults on circuits in HFTD with Elevated or higher FPI |  |  | No | 81 |  |  |  | Outages
| Overhead faults on circuits in HFTD with RFW |  |  | No | 0 |  |  |  | Outages
| Energized wire down events in HFTD with Elevated or higher FPI |  |  | No | 7 |  |  |  | Outages
| Energized wire down events in HFTD with RFW |  |  | No | 0 |  |  |  | Outages
| Number of non-CALFIRE rated fuse operations in HFTD with Elevated or higher FPI |  |  | No | 4 |  |  |  | Outages
| Number of non-CALFIRE rated fuse operations in HFTD with RFW |  |  | No | 0 |  |  |  | Outages
| Overhead fault rate in HFTD during High FPI |  |  | No | 0.85 |  |  |  | Overhead faults per high FPI day
4. Personnel Safety Leading Indicators | Near Miss Reporting |  |  | No | 359 |  |  |  | Near miss events reported
| Safety Observations |  |  | No | 14281 |  |  |  | Observations performed
5. Other PSPS | Percent of customers being de-energized on PSPS circuits |  |  | No |  | 42.231 | 42.231 | 42.231 | percent
| Number of circuits de-engergized |  |  | No |  | 15.67 | 15.67 | 15.67 | circuits
6. Situational Awareness | Communication success rate of weather stations |  |  | Yes | 99.26 | 97.51 | 97.51 | 97.51 | percent
| Post processing success rate - WRF simulations |  |  | Yes | 99.5 | 97.45 | 97.45 | 97.45 | percent
| Post processing success rate - ML gust model |  |  | No | 100 | 96.15 | 96.15 | 96.15 | percent
| Post processing success rate - SAWTI |  |  | No | 97.1 | 93 | 93 | 93 | percent
| Post processing success rate - FPI |  |  | No | 99.5 | 95.05 | 95.05 | 95.05 | percent
| Post processing success rate - OPI |  |  | No | 98.9 | 94.3 | 94.3 | 94.3 | percent
7. Emergency Preparedness | Percentage of community partners participating in local wildfire mitigation planning (in territory) |  |  | No | 100 | 90 | 90 | 90 | percent
| Percentage of Wildfire/PSPS events followed by an After-Action Review or feedback process |  |  | No |  | 95 | 95 | 100 | percent | No activities in 2024 Q3 | N/A
8. Community Outreach and Engagement | Percentage of individuals with AFN who were aware of what support and resources were available to them during a PSPS event. |  |  | No | 60% | 80 | 80 | 80 | percent |  | N/A
| Percentage of individuals with AFN who were able to use necessary medical equipment to maintain necessary life functions for the duration of any PSPS event that affected them |  |  | No |  | 80 | 80 | 80 | percent | No activities in 2024 Q3 | N/A
| Percentage of individuals who utilized mitigation services and reported they were satisfied with the level of support |  |  | No | 91% | 80 | 80 | 80 | percent |  | N/A
| Percentage of customers notified prior to a PSPS event impacting them |  |  | No |  | 100 | 100 | 100 | percent | No activities in 2024 Q3 | N/A

## Table 4
Utility | SDGE
Table No. | 4
Date Modified | 2024-11-01
Table 4: Weather patterns |  |  | Q3
Metric type | # | Metric name | 2024 | Unit(s) | Comments | Blank Meaning
1. Red flag warning only overhead circuit mile days | 1.a. | Red Flag Warning Only overhead circuit mile days - HFTD tier 2 | 0 | Sum of overhead circuit miles of utility grid subject to red flag warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW multiplied by the number of days those circuit miles were under said RFW. For example, if 100 overhead circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW OH circuit mile days would be 110.
| 1.b. | Red Flag Warning Only overhead circuit mile days - HFTD tier 3 | 0 | Red flag warning overhead circuit mile days, see above for definition
| 1.c. | Red Flag Warning Only overhead circuit mile days - non-HFTD | 0 | Red flag warning overhead circuit mile days, see above for definition
2. Wind condition overhead circuit mile days | 2.a. | High Wind Warning Only overhead circuit mile days - HFTD tier 2 | 0 | Sum of overhead circuit miles of utility grid subject to high wind warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of overhead circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 overhead circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW OH circuit mile days would be 110.
| 2.b. | High Wind Warning Only overhead circuit mile days - HFTD tier 3 | 0 | High wind warning overhead circuit mile days, see above for definition
| 2.c. | High Wind Warning Only overhead circuit mile days - non-HFTD | 0 | High wind warning overhead circuit mile days, see above for definition
3. Wind condition and Red flag warning overhead circuit mile days | 3.a. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 2 | 0 | Sum of overhead circuit miles of utility grid subject to concurrent red flag warning and a high wind warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW and HWW multiplied by the number of days those circuit miles were under said RFW and HWW. For example, if 100 overhead circuit miles were under an RFW and HWW for 1 day, and 10 of those miles were under RFW and HWW for an additional day, then the total RFW and HWW OH circuit mile days would be 110.
| 3.b. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 3 | 0 | High wind warning and red flag warning overhead circuit mile days, see above for definition
| 3.c. | High Wind Warning and Red Flag Warning overhead circuit mile days - non-HFTD | 0 | High wind warning and red flag warning overhead circuit mile days, see above for definition
4. Fire potential index overhead circuit mile days | 4.a. | Fire potential index circuit mile days - HFTD tier 2 | 187662 | Sum of overhead circuit miles of utility grid subject to high fire potential index (FPI, as defined by the utility in its WMP) each day within a given time period, calculated as the number of overhead circuit miles that were under a high FPI multiplied by the number of days those miles were under said FPI. For example, if 100 overhead circuit miles were under a high FPI for 1 day, and 10 of those miles were under a high FPI for an additional day, then the total FPI OH circuit mile days would be 110.
| 4.b. | Fire potential index circuit mile days - HFTD tier 3 | 166142 | Fire potential index overhead circuit mile days, see above for definition
| 4.c. | Fire potential index circuit mile days - non-HFTD | 139670 | Fire potential index overhead circuit mile days, see above for definition
5. Other | 5.a. | Other relevant weather pattern metrics tracked (add additional rows as needed)

## Table 5
| Utility | SDGE | Notes:
| Table No. | 5 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2024-11-01
[8 empty] | Actual number of risk events | Projected risk events
| Table 5: Risk event drivers | [6 empty] | Q3
x | Risk event category | Metric type | # | Risk event driver | Line Type | HFTD Tier | Are risk events tracked for ignition driver? (yes / no) | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
| Wire down event | 1. Fire | 1.a.d.0 | Fire | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) | 2023 Projection will remain the same as submitted in the 2023 Base WMP | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Wire down event | 1. Fire | 1.a.d.2 | Fire | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Wire down event | 1. Fire | 1.a.d.3 | Fire | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Wire down event | 1. Fire | 1.a.t.0 | Fire | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Wire down event | 1. Fire | 1.a.t.2 | Fire | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Wire down event | 1. Fire | 1.a.t.3 | Fire | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Wire down event | 2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD |  | 0 | 1.4 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 |  | 0 | 0.395 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 |  | 0 | 0.38 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD |  | 1 | 4.2 | 4 | 4 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 |  | 0 | 0.594 | 0.95191 | 0.89894 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 |  | 0 | 0.19 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD |  | 5 | 16 | 17 | 17 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 |  | 3 | 6.762 | 8.796 | 8.6192 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 |  | 0 | 1.933 | 2.9482 | 2.886 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD |  | 0 | 0 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 |  | 0 | 0.193 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.e.d.0 | 3rd party contact | Distribution | Non-HFTD |  | 0 | 0.8 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.d.2 | 3rd party contact | Distribution | HFTD Tier 2 |  | 0 | 0 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.e.t.0 | 3rd party contact | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.e.t.2 | 3rd party contact | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.f.d.0 | Other contact from object | Distribution | Non-HFTD |  | 3 | 5.6 | 3 | 3 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.d.2 | Other contact from object | Distribution | HFTD Tier 2 |  | 0 | 1.779 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | HFTD Tier 3 |  | 1 | 0.761 | 1.9429 | 1.8797 | # risk events (excluding ignitions)
| Wire down event | 2. Contact from object | 2.f.t.0 | Other contact from object | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.f.t.2 | Other contact from object | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 2. Contact from object | 2.g.d.0 | Unknown | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 2. Contact from object | 2.g.d.2 | Unknown | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 2. Contact from object | 2.g.t.0 | Unknown | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 2. Contact from object | 2.g.t.2 | Unknown | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD |  | 1 | 10.8 | 16 | 16 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 |  | 0 | 2.852 | 6.582 | 6.1507 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 |  | 1 | 1.867 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 |  | 0 | 0.198 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD |  | 2 | 17.4 | 23 | 23 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 |  | 2 | 6.544 | 2.741 | 0.94165 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 |  | 0 | 6.655 | 1.6918 | 1.5401 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 |  | 0 | 0.392 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.d.0 | Connector device | Distribution | Non-HFTD |  | 1 | 3.4 | 4 | 4 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.d.2 | Connector device | Distribution | HFTD Tier 2 |  | 3 | 2.37 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.d.3 | Connector device | Distribution | HFTD Tier 3 |  | 0 | 2.092 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.d.t.0 | Connector device | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.d.t.2 | Connector device | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.d.t.3 | Connector device | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD |  | 0 | 1 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 |  | 0 | 0.198 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 |  | 0 | 0.38 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD |  | 0 | 0.4 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and bushing | Distribution | Non-HFTD |  | 0 | 0.2 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and bushing | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrester | Distribution | Non-HFTD |  | 0 | 0.2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrester | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrester | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrester | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrester | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrester | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD |  | 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 |  | 0 | 0.79 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 |  | 0 | 0.38 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD |  | 0 | 0.4 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 |  | 0 | 0.19 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
| Wire down event | 4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD |  | 0 | 0.4 | 1 | 1 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 |  | 0 | 0.126 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 7. Vandalism/theft | 7.a.d.0 | Vandalism/theft | Distribution | Non-HFTD |  | 0 | 0.6 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 |  | 0 | 0.199 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 |  | 0 | 0.58 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 7. Vandalism/theft | 7.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 7. Vandalism/theft | 7.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 7. Vandalism/theft | 7.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 8. Lightning | 8.a.d.0 | Lightning | Distribution | Non-HFTD |  | 0 | 1.2 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.d.2 | Lightning | Distribution | HFTD Tier 2 |  | 1 | 0.994 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.d.3 | Lightning | Distribution | HFTD Tier 3 |  | 0 | 0.193 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 8. Lightning | 8.a.t.0 | Lightning | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 8. Lightning | 8.a.t.2 | Lightning | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 8. Lightning | 8.a.t.3 | Lightning | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 9. Unknown | 9.a.d.0 | Unknown | Distribution | Non-HFTD |  | 0 | 0 | 6 | 6 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.d.2 | Unknown | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.d.3 | Unknown | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 9. Unknown | 9.a.t.0 | Unknown | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 9. Unknown | 9.a.t.2 | Unknown | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 9. Unknown | 9.a.t.3 | Unknown | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 10. Other | 10.a.d.0 | All Other | Distribution | Non-HFTD |  | 1 | 0.8 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.d.2 | All Other | Distribution | HFTD Tier 2 |  | 0 | 0.398 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.d.3 | All Other | Distribution | HFTD Tier 3 |  | 0 | 0.58 | 0 | 0 | # risk events (excluding ignitions)
| Wire down event | 10. Other | 10.a.t.0 | All Other | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 10. Other | 10.a.t.2 | All Other | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
| Wire down event | 10. Other | 10.a.t.3 | All Other | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
x | Unplanned Outage | 11. Dig-in | 11.a.d.0 | Dig-in | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 11. Dig-in | 11.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 11. Dig-in | 11.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 11. Dig-in | 11.a.t.0 | Dig-in | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 11. Dig-in | 11.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 11. Dig-in | 11.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 12. Fire | 12.a.d.0 | Fire | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 12. Fire | 12.a.d.2 | Fire | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 12. Fire | 12.a.d.3 | Fire | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 12. Fire | 12.a.t.0 | Fire | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 12. Fire | 12.a.t.2 | Fire | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 12. Fire | 12.a.t.3 | Fire | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 13. Object contact | 13.a.d.0 | Animal contact | Distribution | Non-HFTD |  | 10 | 34.8 | 35 | 35 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.d.2 | Animal contact | Distribution | HFTD Tier 2 |  | 5 | 25.874 | 16.1887 | 15.3028 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.d.3 | Animal contact | Distribution | HFTD Tier 3 |  | 6 | 22.057 | 17.2922 | 16.5281 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.t.0 | Animal contact | Transmission | Non-HFTD |  | 0 | 1.6 | 5 | 5 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.t.2 | Animal contact | Transmission | HFTD Tier 2 |  | 0 | 1.978 | 6.9459 | 6.9213 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.a.t.3 | Animal contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.d.0 | Balloon contact | Distribution | Non-HFTD |  | 14 | 100.4 | 71 | 71 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 |  | 0 | 9.309 | 5.7115 | 5.3936 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 |  | 0 | 4.183 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.t.0 | Balloon contact | Transmission | Non-HFTD |  | 2 | 14.2 | 7 | 7 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 |  | 3 | 6.526 | 9.8215 | 9.7403 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.d.0 | Land vehicle contact | Distribution | Non-HFTD |  | 12 | 62.8 | 62 | 62 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 |  | 8 | 27.643 | 32.2521 | 31.6038 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 |  | 4 | 12.76 | 15.7236 | 15.392 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.t.0 | Land vehicle contact | Transmission | Non-HFTD |  | 0 | 1.4 | 4 | 4 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 |  | 0 | 0.4 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD |  | 0 | 0 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 |  | 0 | 0.193 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.d.0 | 3rd party contact | Distribution | Non-HFTD |  | 0 | 1.4 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.d.2 | 3rd party contact | Distribution | HFTD Tier 2 |  | 0 | 1.2 | 4 | 4 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 |  | 0 | 2.8 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.t.0 | 3rd party contact | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.t.2 | 3rd party contact | Transmission | HFTD Tier 2 |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.d.0 | Other | Distribution | Non-HFTD |  | 6 | 23.8 | 16 | 16 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.d.2 | Other | Distribution | HFTD Tier 2 |  | 2 | 8.698 | 3.7299 | 3.4323 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.d.3 | Other | Distribution | HFTD Tier 3 |  | 2 | 4.564 | 4.8573 | 4.6993 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.t.0 | Other | Transmission | Non-HFTD |  | 1 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.t.2 | Other | Transmission | HFTD Tier 2 |  | 1 | 0.196 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.f.t.3 | Other | Transmission | HFTD Tier 3 |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 13. Object contact | 13.g.d.0 | Unknown | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 13. Object contact | 13.g.d.2 | Unknown | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 13. Object contact | 13.g.d.3 | Unknown | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 13. Object contact | 13.g.t.0 | Unknown | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 13. Object contact | 13.g.t.2 | Unknown | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 13. Object contact | 13.g.t.3 | Unknown | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 14. Vegetation contact | 14.a.d.0 | Vegetation contact | Distribution | Non-HFTD |  | 4 | 29.6 | 50 | 50 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 |  | 1 | 5.35 | 8.4625 | 7.908 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 |  | 1 | 4.11 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.t.0 | Vegetation contact | Transmission | Non-HFTD |  | 0 | 0.2 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 14. Vegetation contact | 14.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.0 | Anchor/guy | Distribution | Non-HFTD |  | 0 | 0.6 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 |  | 0 | 0.79 | 0.55715 | 0.11202 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.0 | Anchor/guy | Transmission | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.0 | Capacitor bank | Distribution | Non-HFTD |  | 0 | 9 | 9 | 9 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 |  | 0 | 0.87 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 |  | 1 | 0.19 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.0 | Capacitor bank | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.0 | Conductor | Distribution | Non-HFTD |  | 3 | 26.4 | 32 | 32 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.2 | Conductor | Distribution | HFTD Tier 2 |  | 2 | 10.27 | 4.0387 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.3 | Conductor | Distribution | HFTD Tier 3 |  | 0 | 13.691 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.0 | Conductor | Transmission | Non-HFTD |  | 0 | 0.6 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.2 | Conductor | Transmission | HFTD Tier 2 |  | 0 | 0.96 | 2.973 | 2.9607 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.3 | Conductor | Transmission | HFTD Tier 3 |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.0 | Connection device | Distribution | Non-HFTD |  | 5 | 36.4 | 30 | 30 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.2 | Connection device | Distribution | HFTD Tier 2 |  | 5 | 10.665 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.3 | Connection device | Distribution | HFTD Tier 3 |  | 2 | 11.219 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.0 | Connection device | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.2 | Connection device | Transmission | HFTD Tier 2 |  | 0 | 0.384 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.3 | Connection device | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.0 | Crossarm | Distribution | Non-HFTD |  | 3 | 18.8 | 19 | 19 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.2 | Crossarm | Distribution | HFTD Tier 2 |  | 0 | 5.333 | 1.0107 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.3 | Crossarm | Distribution | HFTD Tier 3 |  | 0 | 6.465 | 1.6389 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.0 | Crossarm | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.2 | Crossarm | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.3 | Crossarm | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.0 | Fuse | Distribution | Non-HFTD |  | 3 | 15.8 | 23 | 23 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.2 | Fuse | Distribution | HFTD Tier 2 |  | 1 | 4.543 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.3 | Fuse | Distribution | HFTD Tier 3 |  | 1 | 4.754 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.0 | Fuse | Transmission | Non-HFTD |  | 0 |  |  |  | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.2 | Fuse | Transmission | HFTD Tier 2 |  | 0 |  |  |  | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.3 | Fuse | Transmission | HFTD Tier 3 |  | 0 |  |  |  | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.0 | Cutout | Distribution | Non-HFTD |  | 7 | 29.4 | 25 | 25 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.2 | Cutout | Distribution | HFTD Tier 2 |  | 1 | 5.4 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.3 | Cutout | Distribution | HFTD Tier 3 |  | 0 | 3 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.0 | Cutout | Transmission | Non-HFTD |  | 0 |  |  |  | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.2 | Cutout | Transmission | HFTD Tier 2 |  | 0 |  |  |  | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.3 | Cutout | Transmission | HFTD Tier 3 |  | 0 |  |  |  | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.0 | Insulator and bushing | Distribution | Non-HFTD |  | 1 | 5.2 | 4 | 4 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 |  | 0 | 2.173 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 |  | 0 | 0.57 | 3.4244 | 0.21937 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.0 | Insulator and bushing | Transmission | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 |  | 0 | 0.192 | 0.99459 | 0.99213 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.0 | Lightning arrester | Distribution | Non-HFTD |  | 6 | 15 | 14 | 14 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.2 | Lightning arrester | Distribution | HFTD Tier 2 |  | 2 | 5.333 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.3 | Lightning arrester | Distribution | HFTD Tier 3 |  | 2 | 3.803 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.0 | Lightning arrester | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.2 | Lightning arrester | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.3 | Lightning arrester | Transmission | HFTD Tier 3 |  | 0 | 0.4 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.0 | Pole | Distribution | Non-HFTD |  | 5 | 18.8 | 31 | 31 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.2 | Pole | Distribution | HFTD Tier 2 |  | 3 | 12.443 | 3.9405 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.3 | Pole | Distribution | HFTD Tier 3 |  | 2 | 13.5 | 0.29857 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.0 | Pole | Transmission | Non-HFTD |  | 0 | 1.2 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.2 | Pole | Transmission | HFTD Tier 2 |  | 0 | 0.192 | 0.99459 | 0.99213 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.3 | Pole | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.0 | Recloser | Distribution | Non-HFTD |  | 0 | 0.6 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.2 | Recloser | Distribution | HFTD Tier 2 |  | 0 | 0.79 | 0.23374 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.3 | Recloser | Distribution | HFTD Tier 3 |  | 0 | 0.391 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.0 | Recloser | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.2 | Recloser | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.3 | Recloser | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.0 | Relay | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver - relays are located within other pieces of equipment (sectionalizers/reclosers/etc.)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.2 | Relay | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver - relays are located within other pieces of equipment (sectionalizers/reclosers/etc.)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.3 | Relay | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver - relays are located within other pieces of equipment (sectionalizers/reclosers/etc.)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.0 | Relay | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.2 | Relay | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.3 | Relay | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.0 | Sectionalizer | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.0 | Sectionalizer | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.0 | Splice | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.2 | Splice | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.3 | Splice | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.0 | Splice | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.2 | Splice | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.3 | Splice | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.0 | Switch | Distribution | Non-HFTD |  | 3 | 12.4 | 16 | 16 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.2 | Switch | Distribution | HFTD Tier 2 |  | 0 | 1.975 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.3 | Switch | Distribution | HFTD Tier 3 |  | 0 | 0.19 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.0 | Switch | Transmission | Non-HFTD |  | 0 | 0.2 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.2 | Switch | Transmission | HFTD Tier 2 |  | 0 | 0.593 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.3 | Switch | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.0 | Tap | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.2 | Tap | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.3 | Tap | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.0 | Tap | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.2 | Tap | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.3 | Tap | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.0 | Tie wire | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.0 | Tie wire | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.0 | Transformer | Distribution | Non-HFTD |  | 7 | 19 | 24 | 24 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.2 | Transformer | Distribution | HFTD Tier 2 |  | 2 | 8.098 | 4.1459 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.3 | Transformer | Distribution | HFTD Tier 3 |  | 2 | 7.606 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.0 | Transformer | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.2 | Transformer | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.3 | Transformer | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 |  | 0 | 0.988 | 0.44643 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.0 | Unknown | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.2 | Unknown | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.3 | Unknown | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.0 | Unknown | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.2 | Unknown | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.3 | Unknown | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.0 | Other | Distribution | Non-HFTD |  | 0 | 0.4 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.2 | Other | Distribution | HFTD Tier 2 |  | 0 | 0.063 | 0.80844 | 0.67588 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.3 | Other | Distribution | HFTD Tier 3 |  | 0 | 0.307 | 0.69996 | 0.26873 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.0 | Other | Transmission | Non-HFTD |  | 0 | 0 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.2 | Other | Transmission | HFTD Tier 2 |  | 0 | 0.384 | 2.9892 | 2.9843 | # risk events (excluding ignitions)
| Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.3 | Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD |  | 0 | 1.4 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 |  | 0 | 1.383 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 |  | 0 | 0.38 | 1.9878 | 1.9746 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.d.0 | Contamination | Distribution | Non-HFTD |  | 1 | 1.2 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.d.2 | Contamination | Distribution | HFTD Tier 2 |  | 0 | 0.198 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.d.3 | Contamination | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.t.0 | Contamination | Transmission | Non-HFTD |  | 0 | 0.8 | 3 | 3 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.t.2 | Contamination | Transmission | HFTD Tier 2 |  | 0 | 0.194 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 17. Contamination | 17.a.t.3 | Contamination | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.d.0 | Vandalism/theft | Distribution | Non-HFTD |  | 1 | 1.4 | 4 | 4 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 |  | 0 | 0.994 | 0.9731 | 0.94978 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 |  | 1 | 1.16 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.t.0 | Vandalism/theft | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 18. Vandalism/theft | 18.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.d.0 | Lightning | Distribution | Non-HFTD |  | 0 | 23.8 | 8 | 8 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.d.2 | Lightning | Distribution | HFTD Tier 2 |  | 1 | 14.12 | 2.618 | 2.2869 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.d.3 | Lightning | Distribution | HFTD Tier 3 |  | 1 | 16.047 | 4.6525 | 4.2354 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.t.0 | Lightning | Transmission | Non-HFTD |  | 0 | 4 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.t.2 | Lightning | Transmission | HFTD Tier 2 |  | 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 19. Lightning | 19.a.t.3 | Lightning | Transmission | HFTD Tier 3 |  | 0 | 2.6 | 0 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 20. Government agency request | 20.a.d.0 | Government agency request | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 20. Government agency request | 20.a.d.2 | Government agency request | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 20. Government agency request | 20.a.d.3 | Government agency request | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 20. Government agency request | 20.a.t.0 | Government agency request | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 20. Government agency request | 20.a.t.2 | Government agency request | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 20. Government agency request | 20.a.t.3 | Government agency request | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 21. Customer request | 21.a.d.0 | Customer request | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 21. Customer request | 21.a.d.2 | Customer request | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 21. Customer request | 21.a.d.3 | Customer request | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 21. Customer request | 21.a.t.0 | Customer request | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 21. Customer request | 21.a.t.2 | Customer request | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 21. Customer request | 21.a.t.3 | Customer request | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 22. Emergency repairs | 22.a.d.0 | Emergency repairs | Distribution | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 22. Emergency repairs | 22.a.d.2 | Emergency repairs | Distribution | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 22. Emergency repairs | 22.a.d.3 | Emergency repairs | Distribution | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 22. Emergency repairs | 22.a.t.0 | Emergency repairs | Transmission | Non-HFTD | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 22. Emergency repairs | 22.a.t.2 | Emergency repairs | Transmission | HFTD Tier 2 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 22. Emergency repairs | 22.a.t.3 | Emergency repairs | Transmission | HFTD Tier 3 | [5 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| Unplanned Outage | 23. Unknown | 23.a.d.0 | Unknown | Distribution | Non-HFTD |  | 35 | 142.2 | 103 | 103 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.d.2 | Unknown | Distribution | HFTD Tier 2 |  | 13 | 57.548 | 29.8442 | 21.7409 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.d.3 | Unknown | Distribution | HFTD Tier 3 |  | 14 | 68.589 | 23.0146 | 0 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.t.0 | Unknown | Transmission | Non-HFTD |  | 0 | 3.2 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.t.2 | Unknown | Transmission | HFTD Tier 2 |  | 0 | 3.646 | 0.89724 | 0.85049 | # risk events (excluding ignitions)
| Unplanned Outage | 23. Unknown | 23.a.t.3 | Unknown | Transmission | HFTD Tier 3 |  | 0 | 0.4 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.d.0 | All Other | Distribution | Non-HFTD |  | 10 | 3.6 | 29 | 29 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.d.2 | All Other | Distribution | HFTD Tier 2 |  | 7 | 2.188 | 2.9408 | 2.8895 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.d.3 | All Other | Distribution | HFTD Tier 3 |  | 1 | 3.093 | 4.933 | 4.8526 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.t.0 | All Other | Transmission | Non-HFTD |  | 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.t.2 | All Other | Transmission | HFTD Tier 2 |  | 0 | 0 | 2 | 2 | # risk events (excluding ignitions)
| Unplanned Outage | 24. Other | 24.a.t.3 | All Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # risk events (excluding ignitions)

## Table 6
| Utility | SDGE | Notes:
| Table No. | 6 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2024-11-01
[7 empty] | Actual number of ignitions | Projected ignitions
| Table 6: Ignition drivers | [5 empty] | Q3
| Metric type | # | Ignition driver | Line Type | HFTD Tier | Are ignitions tracked for ignition driver? (yes / no) | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
| 1. Dig-in | 1.a.d.0 | Dig-in | Distribution | Non-HFTD | [5 empty] | # ignitions | 2023 Projection will remain the same as submitted in the 2023 Base WMP | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| 1. Dig-in | 1.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| 1. Dig-in | 1.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| 1. Dig-in | 1.a.t.0 | Dig-in | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| 1. Dig-in | 1.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
| 1. Dig-in | 1.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
x | 2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD |  | 0 | 0.2 | 1 | 1 | # ignitions
| 2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 |  | 2 | 0.4087 | 0 | 0 | # ignitions
| 2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 |  | 2 | 0.6871 | 1.8294 | 1.6384 | # ignitions
| 2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 |  | 1 | 0.19922 | 0 | 0 | # ignitions
| 2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 |  | 0 | 0.4 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD |  | 0 | 1.8 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 |  | 0 | 0.8095 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 |  | 0 | 0.6871 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD |  | 0 | 0.2 | 1 | 1 | # ignitions
| 2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 |  | 0 | 0.59922 | 0 | 0 | # ignitions
| 2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD |  | 0 | 0.4 | 0 | 0 | # ignitions
| 2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 |  | 1 | 1.0576 | 0 | 0 | # ignitions
| 2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 |  | 1 | 0.3648 | 0.874 | 0.723 | # ignitions
| 2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD |  | 0 | 0.4 | 0 | 0 | # ignitions
| 2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 |  | 0 | 0.2 | 0 | 0 | # ignitions
| 2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 2. Contact from object | 2.e.d.0 | 3rd party facility | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
| 2. Contact from object | 2.e.d.2 | 3rd party facility | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
| 2. Contact from object | 2.e.d.3 | 3rd party facility | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
| 2. Contact from object | 2.e.t.0 | 3rd party facility | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
| 2. Contact from object | 2.e.t.2 | 3rd party facility | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
| 2. Contact from object | 2.e.t.3 | 3rd party facility | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
| 2. Contact from object | 2.f.d.0 | Unknown | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 2. Contact from object | 2.f.d.2 | Unknown | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 2. Contact from object | 2.f.d.3 | Unknown | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 2. Contact from object | 2.f.t.0 | Unknown | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 2. Contact from object | 2.f.t.2 | Unknown | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 2. Contact from object | 2.f.t.3 | Unknown | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 2. Contact from object | 2.g.d.0 | Other | Distribution | Non-HFTD |  | 0 | 0.2 | 1 | 1 | # ignitions
| 2. Contact from object | 2.g.d.2 | Other | Distribution | HFTD Tier 2 |  | 0 | 0.0095 | 0 | 0 | # ignitions
| 2. Contact from object | 2.g.d.3 | Other | Distribution | HFTD Tier 3 |  | 0 | 0.2871 | 0 | 0 | # ignitions
| 2. Contact from object | 2.g.t.0 | Other | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 2. Contact from object | 2.g.t.2 | Other | Transmission | HFTD Tier 2 |  | 0 | 0.19922 | 0.954 | 0.933 | # ignitions
| 2. Contact from object | 2.g.t.3 | Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD |  | 0 | 1 | 1 | 1 | # ignitions
| 3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 |  | 1 | 0.28251 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD |  | 0 | 0.396 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 |  | 0 | 0.1959 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD |  | 0 | 0.196 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 |  | 3 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 |  | 0 | 0.1296 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.d.0 | Connection device | Distribution | Non-HFTD |  | 0 | 0.38 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.d.2 | Connection device | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.d.3 | Connection device | Distribution | HFTD Tier 3 |  | 0 | 0.2525 | 0.7735 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.t.0 | Connection device | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.t.2 | Connection device | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.d.t.3 | Connection device | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD |  | 0 | 0.396 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD |  | 0 | 0.4 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 |  | 0 | 0.2 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and bushing | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 |  | 0 | 1 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and bushing | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrester | Distribution | Non-HFTD |  | 0 | 0 | 1 | 1 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrester | Distribution | HFTD Tier 2 |  | 0 | 0.3963 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrester | Distribution | HFTD Tier 3 |  | 0 | 0.7736 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrester | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrester | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrester | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
| 4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
| 4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
| 4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
| 4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
| 4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
| 4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD |  | 0 | 0.196 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD |  | 1 | 0.196 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD |  | 1 | 0.58641 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 |  | 0 | 0.6 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 |  | 0 | 0.191 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 |  | 0 | 0.2 | 0 | 0 | # ignitions
| 4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD |  | 0 | 0.4 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 |  | 0 | 0.0087 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 7. Protective device operation | 7.a.d.0 | Protective device operation | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 7. Protective device operation | 7.a.d.2 | Protective device operation | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 7. Protective device operation | 7.a.d.3 | Protective device operation | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 7. Protective device operation | 7.a.t.0 | Protective device operation | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 7. Protective device operation | 7.a.t.2 | Protective device operation | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 7. Protective device operation | 7.a.t.3 | Protective device operation | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E does not currently track this driver
| 8. Vandalism/theft | 8.a.d.0 | Vandalism/theft | Distribution | Non-HFTD |  | 0 | 0.2 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 |  | 0 | 0.0576 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.t.0 | Vandalism/theft | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 8. Vandalism/theft | 8.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 9. Lightning | 9.a.d.0 | Lightning | Distribution | Non-HFTD | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 9. Lightning | 9.a.d.2 | Lightning | Distribution | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 9. Lightning | 9.a.d.3 | Lightning | Distribution | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 9. Lightning | 9.a.t.0 | Lightning | Transmission | Non-HFTD | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 9. Lightning | 9.a.t.2 | Lightning | Transmission | HFTD Tier 2 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 9. Lightning | 9.a.t.3 | Lightning | Transmission | HFTD Tier 3 | [5 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
| 10. Unknown | 10.a.d.0 | Unknown | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.d.2 | Unknown | Distribution | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.d.3 | Unknown | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.t.0 | Unknown | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.t.2 | Unknown | Transmission | HFTD Tier 2 |  | 0 | 0.39922 | 0 | 0 | # ignitions
| 10. Unknown | 10.a.t.3 | Unknown | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 11. Other | 11.a.d.0 | Other | Distribution | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 11. Other | 11.a.d.2 | Other | Distribution | HFTD Tier 2 |  | 0 | 0.2576 | 0.848 | 0.716 | # ignitions
| 11. Other | 11.a.d.3 | Other | Distribution | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions
| 11. Other | 11.a.t.0 | Other | Transmission | Non-HFTD |  | 0 | 0 | 0 | 0 | # ignitions
| 11. Other | 11.a.t.2 | Other | Transmission | HFTD Tier 2 |  | 0 | 0 | 0 | 0 | # ignitions
| 11. Other | 11.a.t.3 | Other | Transmission | HFTD Tier 3 |  | 0 | 0 | 0 | 0 | # ignitions

## Table 7
| Utility | SDGE
| Table No. | 7
| Date Modified | 2024-11-01
[7 empty] | Actual | Projected
| Table 7: State of service territory and utility equipment | [5 empty] | Q3
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | 393.6922 | 396.95 | 394.24 | 394.24 | Circuit miles
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | 2064.6814 | 2072.42 | 2066.75 | 2066.75 | Circuit miles
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | 174.1585 | 175.06 | 175.16 | 175.16 | Circuit miles
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | 177.0761 | 178.02 | 177.85 | 177.85 | Circuit miles
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | 34.832 | 34.68 | 34.83 | 34.83 | Circuit miles
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | 109.5269 | 109.39 | 109.61 | 109.61 | Circuit miles
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | 91.1377 | 91.06 | 91.38 | 91.38 | Circuit miles
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | 83.6055 | 83.17 | 83.79 | 83.7853 | Circuit miles
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | 844.8055 | 836.96 | 850.2244 | 849.9588 | Circuit miles
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | 587.297 | 571.01 | 591.188 | 590.6738 | Circuit miles
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | 20.304 | 20.17 | 20.3 | 20.2673 | Circuit miles
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | 151.8858 | 151.98 | 151.89 | 151.8531 | Circuit miles
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | 4.9068 | 4.77 | 4.9 | 4.9 | Circuit miles
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | 0.040341 | 0.04 | 0.04 | 0.04 | Circuit miles
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | 640.4867 | 637.07 | 644.5414 | 644.1085 | Circuit miles
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | 763.6462 | 740.68 | 770.7321 | 770.2912 | Circuit miles
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | 25.5191 | 24.16 | 25.51 | 25.5105 | Circuit miles
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | 162.5722 | 126.88 | 163.04 | 163.0388 | Circuit miles
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | 134.8481 | 134.71 | 135.9 | 135.9 | Circuit miles
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | 286.9144 | 286.76 | 288.2 | 288.2 | Circuit miles
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | 54.5802 | 55.46 | 55.48 | 55.48 | Circuit miles
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | 112.6219 | 113.58 | 113.37 | 113.37 | Circuit miles
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | 22.8058 | 22.81 | 22.81 | 22.81 | Circuit miles
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | 36.7976 | 36.41 | 36.72 | 36.72 | Circuit miles
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | 59.4868 | 58.22 | 59.5 | 59.5 | Circuit miles
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | 115.4098 | 118.09 | 115.48 | 115.48 | Circuit miles
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | 443.8106 | 443.23 | 443.79 | 443.79 | Circuit miles
|  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | 23.4249 | 23.42 | 23.42 | 23.42 | Circuit miles
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | 21.4391 | 22.02 | 21.44 | 21.44 | Circuit miles
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | 227.9255 | 229.49 | 226.24 | 226.24 | Circuit miles
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | 2.8169 | 2.82 | 2.82 | 2.82 | Circuit miles
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | 15.6849 | 15.68 | 15.68 | 15.68 | Circuit miles
x | 2. Underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | 1927.1652 | 1913.63 | 1921.96 | 1921.7363 | Circuit miles
|  | 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | 4920.6966 | 4880.8 | 4903.42 | 4902.6732 | Circuit miles
|  | 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | 600.0712 | 595.16 | 597.66 | 597.66 | Circuit miles
|  | 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | 887.3765 | 875.6 | 881.38 | 881.38 | Circuit miles
|  | 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | 17.8547 | 17.77 | 17.77 | 17.77 | Circuit miles
|  | 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | 58.0917 | 57.13 | 58.11 | 58.11 | Circuit miles
|  | 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | 773.4498 | 772.39 | 772.4884 | 772.4884 | Circuit miles
|  | 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | 157.5275 | 153.16 | 156.4047 | 155.8993 | Circuit miles
|  | 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | 1020.1945 | 1017.58 | 1011.6507 | 1041.1439 | Circuit miles
|  | 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | 362.8661 | 370.67 | 351.1688 | 347.9285 | Circuit miles
|  | 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | 1.5708 | 1.57 | 1.57 | 7.5381 | Circuit miles
|  | 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | 9.5678 | 9.03 | 9.0853 | 11.2106 | Circuit miles
|  | 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | 0.98561 | 0.65 | 0.99408 | 0.99408 | Circuit miles
|  | 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | 341.7331 | 359.6 | 327.403 | 358.2851 | Circuit miles
|  | 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | 174.6858 | 196.01 | 157.3199 | 166.4157 | Circuit miles
|  | 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | 10.3267 | 19.25 | 12.5856 | 20.8587 | Circuit miles
|  | 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | 27.4937 | 66.87 | 40.1927 | 39.5668 | Circuit miles
|  | 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | 28.7142 | 25.86 | 28.71 | 28.71 | Circuit miles
|  | 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | 68.0151 | 65.12 | 68.02 | 68.02 | Circuit miles
|  | 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | 10.1429 | 9.98 | 10.15 | 10.15 | Circuit miles
|  | 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | 22.5637 | 22.52 | 22.58 | 22.58 | Circuit miles
|  | 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | 0.34792 | 0.35 | 0.35 | 0.35 | Circuit miles
|  | 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | 13.2894 | 13.29 | 13.29 | 13.29 | Circuit miles
|  | 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | 1.3719 | 1.37 | 1.37 | 1.37 | Circuit miles
|  | 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | 12.6991 | 12.93 | 12.7 | 12.7 | Circuit miles
|  | 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | 8.5822 | 8.53 | 8.58 | 8.58 | Circuit miles
|  | 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | 0.93526 | 0.94 | 0.94 | 0.94 | Circuit miles
|  | 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | 4.4582 | 4.46 | 4.46 | 4.46 | Circuit miles
|  | 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | 2.1501 | 2.05 | 2.15 | 2.15 | Circuit miles
|  | 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
| 3. Critical facilities | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | 3025 | 3080 | 3045 | 3045 | Number of critical facilities
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 15226 | 15568 | 15203 | 15203 | Number of critical facilities
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | 713 | 721 | 710 | 710 | Number of critical facilities
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 2487 | 2597 | 2537 | 2537 | Number of critical facilities
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 3 | 3 | 3 | 3 | Number of critical facilities
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 135 | 137 | 138 | 138 | Number of critical facilities
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 850 | 879 | 882 | 882 | Number of critical facilities
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 347 | 346 | 340 | 340 | Number of critical facilities
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 1049 | 1060 | 1047 | 1047 | Number of critical facilities
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 964 | 945 | 934 | 934 | Number of critical facilities
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 11 | 20 | 20 | 20 | Number of critical facilities
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 85 | 83 | 81 | 81 | Number of critical facilities
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 5 | 5 | 4 | 4 | Number of critical facilities
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of critical facilities
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 489 | 517 | 515 | 515 | Number of critical facilities
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 790 | 793 | 781 | 781 | Number of critical facilities
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 42 | 44 | 45 | 45 | Number of critical facilities
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 91 | 75 | 76 | 76 | Number of critical facilities
| 4. Residential customers | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | 203582 | 201832 | 202909 | 202909 | Number of residential customers
|  | 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 893029 | 875662 | 885546 | 885546 | Number of residential customers
|  | 4.0.b.i | N/A | Non-HFTD | Rural | WUI | 37026 | 36776 | 37050 | 37050 | Number of residential customers
|  | 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 39025 | 38010 | 38803 | 38803 | Number of residential customers
|  | 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 1001 | 994 | 999 | 999 | Number of residential customers
|  | 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 1675 | 1665 | 1678 | 1678 | Number of residential customers
|  | 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 67475 | 66347 | 67135 | 67135 | Number of residential customers
|  | 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 17349 | 16620 | 17096 | 17096 | Number of residential customers
|  | 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 58709 | 58039 | 58507 | 58507 | Number of residential customers
|  | 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 23022 | 19964 | 20583 | 20583 | Number of residential customers
|  | 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 251 | 273 | 269 | 269 | Number of residential customers
|  | 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 497 | 468 | 477 | 477 | Number of residential customers
|  | 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 101 | 100 | 101 | 101 | Number of residential customers
|  | 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 3 | 3 | 3 | 3 | Number of residential customers
|  | 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 18341 | 18008 | 18125 | 18125 | Number of residential customers
|  | 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 8016 | 6882 | 7031 | 7031 | Number of residential customers
|  | 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 931 | 911 | 911 | 911 | Number of residential customers
|  | 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 887 | 857 | 861 | 861 | Number of residential customers
| 5. Commercial customers | 5.0.a.i | N/A | Non-HFTD | Urban | WUI | 14703 | 14613 | 14655 | 14655 | Number of commercial customers
|  | 5.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 93648 | 92909 | 93564 | 93564 | Number of commercial customers
|  | 5.0.b.i | N/A | Non-HFTD | Rural | WUI | 4631 | 4569 | 4569 | 4569 | Number of commercial customers
|  | 5.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 25039 | 24860 | 24920 | 24920 | Number of commercial customers
|  | 5.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 99 | 100 | 99 | 99 | Number of commercial customers
|  | 5.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 522 | 548 | 528 | 528 | Number of commercial customers
|  | 5.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 4334 | 4247 | 4375 | 4375 | Number of commercial customers
|  | 5.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 2469 | 2364 | 2406 | 2406 | Number of commercial customers
|  | 5.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 5054 | 5018 | 4978 | 4978 | Number of commercial customers
|  | 5.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 4208 | 4076 | 4137 | 4137 | Number of commercial customers
|  | 5.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 34 | 44 | 44 | 44 | Number of commercial customers
|  | 5.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 218 | 214 | 206 | 206 | Number of commercial customers
|  | 5.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 17 | 18 | 16 | 16 | Number of commercial customers
|  | 5.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of commercial customers
|  | 5.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 2229 | 2300 | 2296 | 2296 | Number of commercial customers
|  | 5.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 2554 | 2506 | 2498 | 2498 | Number of commercial customers
|  | 5.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 146 | 139 | 143 | 143 | Number of commercial customers
|  | 5.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 388 | 363 | 366 | 366 | Number of commercial customers
| 6. AFN customers | 6.0.a.i | N/A | Non-HFTD | Urban | WUI | 45305 | 46089 | 47132 | 47132 | Number of customers belonging to access and functional needs populations
|  | 6.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 304256 | 323802 | 316695 | 316695 | Number of customers belonging to access and functional needs populations
|  | 6.0.b.i | N/A | Non-HFTD | Rural | WUI | 7811 | 8143 | 8281 | 8281 | Number of customers belonging to access and functional needs populations
|  | 6.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 9329 | 9074 | 9557 | 9557 | Number of customers belonging to access and functional needs populations
|  | 6.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 308 | 301 | 318 | 318 | Number of customers belonging to access and functional needs populations
|  | 6.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 434 | 451 | 435 | 435 | Number of customers belonging to access and functional needs populations
|  | 6.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 14533 | 14517 | 14984 | 14984 | Number of customers belonging to access and functional needs populations
|  | 6.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 5215 | 5670 | 5243 | 5243 | Number of customers belonging to access and functional needs populations
|  | 6.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 11713 | 11939 | 12219 | 12219 | Number of customers belonging to access and functional needs populations
|  | 6.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 4845 | 4079 | 4449 | 4449 | Number of customers belonging to access and functional needs populations
|  | 6.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 90 | 94 | 99 | 99 | Number of customers belonging to access and functional needs populations
|  | 6.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 169 | 177 | 148 | 148 | Number of customers belonging to access and functional needs populations
|  | 6.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 28 | 31 | 27 | 27 | Number of customers belonging to access and functional needs populations
|  | 6.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 1 | 2 | 1 | 1 | Number of customers belonging to access and functional needs populations
|  | 6.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 5404 | 5213 | 5525 | 5525 | Number of customers belonging to access and functional needs populations
|  | 6.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 2115 | 1885 | 1965 | 1965 | Number of customers belonging to access and functional needs populations
|  | 6.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 251 | 255 | 266 | 266 | Number of customers belonging to access and functional needs populations
|  | 6.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 201 | 243 | 204 | 204 | Number of customers belonging to access and functional needs populations
| 7. Substations | 7.0.a.i | N/A | Non-HFTD | Urban | WUI | 12 | 12 | 11 | 11 | Number of substations
|  | 7.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 66 | 66 | 66 | 66 | Number of substations
|  | 7.0.b.i | N/A | Non-HFTD | Rural | WUI | 4 | 4 | 4 | 4 | Number of substations
|  | 7.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 26 | 26 | 26 | 26 | Number of substations
|  | 7.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 7.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 3 | 3 | 3 | 3 | Number of substations
|  | 7.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 1 | 1 | 1 | 0 | Number of substations
|  | 7.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 5 | 5 | 5 | 5 | Number of substations
|  | 7.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 5 | 5 | 5 | 5 | Number of substations
|  | 7.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 23 | 23 | 22 | 22 | Number of substations
|  | 7.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 7.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 1 | 1 | 1 | 1 | Number of substations
|  | 7.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 11 | 11 | 11 | 11 | Number of substations
|  | 7.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 2 | 2 | 2 | 2 | Number of substations
| 8. Weather stations | 8.0.a.i | N/A | Non-HFTD | Urban | WUI | 3 | 3 | 3 | 3 | Number of weather stations
|  | 8.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 13 | 13 | 13 | 13 | Number of weather stations
|  | 8.0.b.i | N/A | Non-HFTD | Rural | WUI | 1 | 1 | 1 | 1 | Number of weather stations
|  | 8.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 3 | 3 | 3 | 3 | Number of weather stations
|  | 8.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 8.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 2 | 2 | 2 | 2 | Number of weather stations
|  | 8.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 2 | 2 | 2 | 2 | Number of weather stations
|  | 8.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 4 | 4 | 4 | 4 | Number of weather stations
|  | 8.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 16 | 16 | 16 | 16 | Number of weather stations
|  | 8.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 52 | 52 | 52 | 52 | Number of weather stations
|  | 8.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 1 | 1 | 1 | 1 | Number of weather stations
|  | 8.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 7 | 7 | 7 | 7 | Number of weather stations
|  | 8.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 8.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 8.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 11 | 11 | 11 | 11 | Number of weather stations
|  | 8.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 85 | 85 | 86 | 86 | Number of weather stations
|  | 8.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 2 | 2 | 3 | 3 | Number of weather stations
|  | 8.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 18 | 18 | 18 | 18 | Number of weather stations

## Table 8
| Utility | SDGE |  |  |  |  | Notes:
| Table No. | 8 |  |  |  |  | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
| Date Modified | 2024-11-01 |  |  |  |  | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
[7 empty] | Actual | Projected
| Table 8: Location of utility equipment additions or removal | [5 empty] | Q3
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Planned net addition (or removal) - overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | -0.060417 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | -0.55114 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | -0.55114 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | -0.41761 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | -0.062311 | 0 | 0 | 0 | Circuit miles
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | -0.096591 | -0.2 | 0 | -0.0047379 | Circuit miles
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | -2.8061 | -12.28 | 0.0044342 | -0.26567 | Circuit miles
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | -0.29867 | -27.64 | -0.78197 | -0.51425 | Circuit miles
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | 0.00018939 | 0 | 0 | -0.032709 | Circuit miles
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | -0.036934 | Circuit miles
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | -0.96913 | -18.23 | -0.0086157 | -0.43293 | Circuit miles
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | -3.7252 | -37.74 | -0.25788 | -0.44094 | Circuit miles
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | 0 | -1.76 | 0 | 0.00049693 | Circuit miles
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | -0.0090909 | -36.03 | 0 | -0.0011922 | Circuit miles
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | 1.2688 | 0.5 | 0 | 0 | Circuit miles
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | 0.25417 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | 0.010642 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | 0.081432 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | -0.012206 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | -0.065809 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | 0.031839 | 0 | 0 | 0 | Circuit miles
x |  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | -0.00030303 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | 1.6873 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
x | 2. Planned net addition (or removal) - underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | 1.2958 | 0 | 0 | -0.2237 | Circuit miles
|  | 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | 5.1814 | 0 | 0 | -0.74685 | Circuit miles
|  | 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | 0.8858 | 0 | 0 | 0 | Circuit miles
|  | 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | 2.892 | 0 | 0 | 0 | Circuit miles
|  | 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | -0.024432 | 0 | 0 | 0 | Circuit miles
|  | 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | -0.039583 | 0 | 0 | 0 | Circuit miles
|  | 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | -0.084848 | 0.15 | -0.011574 | 0 | Circuit miles
|  | 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | -0.00056818 | 0 | -0.36535 | -0.50537 | Circuit miles
|  | 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | 3.2161 | 20.2 | 0.96066 | 29.4932 | Circuit miles
|  | 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | 0.82633 | 27.36 | -6.5212 | -3.2403 | Circuit miles
|  | 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 5.9681 | Circuit miles
|  | 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | 0.53504 | 0 | 0.055269 | 2.1254 | Circuit miles
|  | 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | 0 | 0.03 | 0.0040819 | 0 | Circuit miles
|  | 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | 4.2559 | 44.03 | -6.047 | 30.8821 | Circuit miles
|  | 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | 7.804 | 46.45 | -6.3001 | 9.0957 | Circuit miles
|  | 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | 0.0090909 | 10.81 | 2.2656 | 8.2731 | Circuit miles
|  | 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | 0.085606 | 41.26 | 13.3427 | -0.62588 | Circuit miles
|  | 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | -0.011458 | 0 | 0 | 0 | Circuit miles
|  | 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | -0.011326 | 0 | 0 | 0 | Circuit miles
|  | 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | -3.9394e-10 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
| 3. Planned net addition (or removal) - Substations | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | 0 | 0 | -1 | 0 | Number of substations
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 0 | 0 | 0 | -1 | Number of substations
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 0 | 0 | -1 | 0 | Number of substations
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
| 4. Planned net addition (or removal) - Weather stations | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.0.b.i | N/A | Non-HFTD | Rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 0 | 0 | 1 | 0 | Number of weather stations | Weather station removals or addtions are sourced from businesses, table 7 is sourced from GIS database. A small difference is observed due to data digitizing processes.
|  | 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 1 | 0 | Number of weather stations
|  | 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations

## Table 9
| Utility | SDGE
| Table No. | 9
| Date Modified | 2024-11-01
[7 empty] | Actual | Projected
| Table 9: Location of utility infrastructure upgrades | [5 empty] | Q3
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Number of overhead circuit miles planned for upgrade | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | 0 | 0 | 0 | 0.31913 | Circuit miles
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | 0 | 0 | 0.045833 | 0 | Circuit miles
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | 0 | 0 | 1.9767 | 4.4964 | Circuit miles
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | 0 | 5.92 | 8.6893 | 9.0597 | Circuit miles
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | 0.32649 | 17.81 | 20.6546 | 14.6035 | Circuit miles
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | 0 | 2.1 | 0 | 2.8334 | Circuit miles
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 1.51 | 0 | 9.975 | Circuit miles
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | 2.2285 | 19.96 | 10.5661 | 18.8553 | Circuit miles
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | 1.9312 | 31.32 | 11.4478 | 20.3124 | Circuit miles
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | 0 | 0.69 | 0 | 0.34128 | Circuit miles
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 3.57 | 0 | 0.38819 | Circuit miles
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | 0 | 0 | 2.3018 | 2.2544 | Circuit miles
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | 0 | 3.9 | 8.8408 | 2.4817 | Circuit miles
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | 4.0532 | 0 | 10.7593 | 5.2309 | Circuit miles
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | 0.31705 | 32 | 13.2892 | 18.7232 | Circuit miles
|  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | 0.088636 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | 0 | 0 | 0.65966 | 0 | Circuit miles
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | 0 | 10.3 | 1.1816 | 0.088636 | Circuit miles
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Circuit miles
x | 2. Number of substations planned for upgrades | 2.0.a.i | N/A | Non-HFTD | Urban | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 0 | 1 | 0 | 0 | Number of substations
|  | 2.0.b.i | N/A | Non-HFTD | Rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 0 | 0 | 0 | 1 | Number of substations
|  | 2.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 0 | 0 | 1 | 0 | Number of substations
|  | 2.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 0 | 1 | 0 | 0 | Number of substations
|  | 2.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 0 | 0 | 0 | 0 | Number of substations
| 3. Number of weather stations planned for upgrades | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | 1 | 1 | 0 | 0 | Number of weather stations
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | 6 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | 1 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | 1 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | 1 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | 7 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | 0 | 0 | 1 | 0 | Number of weather stations
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | 2 | 1 | 0 | 0 | Number of weather stations
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | 1 | 3 | 2 | 0 | Number of weather stations
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | 3 | 5 | 2 | 0 | Number of weather stations
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | 0 | 1 | 1 | 0 | Number of weather stations
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | 4 | 5 | 3 | 0 | Number of weather stations

## Table 10
Utility | SDGE |  | Notes:
Table No. | 10 |  | "PSPS" = Public Safety Power Shutoff
Date Modified | 2024-11-01 |  | In future submissions update planned upgrade numbers with actuals
|  |  |  | Actual | Projected
Table 10: Recent use of PSPS and other PSPS metrics |  |  |  | Q3
Metric type | # | Wind Warning Status | Metric name | 2024 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Recent use of PSPS and fast-trip | 1.a. | RFW only | Frequency of PSPS events (total) | 0 | 2.632 | 2.471 | 2.324 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
|  | HWW only | Frequency of PSPS events (total) | 0 | 0 | 0 | 0 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
|  | HWW & RFW | Frequency of PSPS events (total) | 0 | 1.128 | 1.059 | 0.996 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
|  | All (regardless of RFW/HWW status) | Frequency of PSPS events (total) | 0 | 3.76 | 3.53 | 3.32 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
| 1.b. | RFW only | Scope of PSPS events (total) | 0 | 155.3722 | 137.116 | 121.2214 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
|  | HWW only | Scope of PSPS events (total) | 0 | 0 | 0 | 0 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
|  | HWW & RFW | Scope of PSPS events (total) | 0 | 66.5881 | 58.764 | 51.952 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
|  | All (regardless of RFW/HWW status) | Scope of PSPS events (total) | 0 | 221.9603 | 195.88 | 173.1734 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
| 1.c. | RFW only | Duration of PSPS events (total) | 0 | 1002733.1899 | 942577.9986 | 886026.6711 | Customer hours per year
|  | HWW only | Duration of PSPS events (total) | 0 | 0 | 0 | 0 | Customer hours per year
|  | HWW & RFW | Duration of PSPS events (total) | 0 | 429742.7957 | 403961.9994 | 379725.7162 | Customer hours per year
|  | All (regardless of RFW/HWW status) | Duration of PSPS events (total) | 0 | 1432475.9856 | 1346539.9981 | 1265752.3874 | Customer hours per year
| 1.d. | RFW only | Frequency of fast-trip events (total) | 0 |  |  |  | Number of events
|  | HWW only | Frequency of fast-trip events (total) | 0 |  |  |  | Number of events
|  | HWW & RFW | Frequency of fast-trip events (total) | 0 |  |  |  | Number of events
|  | None | Frequency of fast-trip events (total) | 0 |  |  |  | Number of events
| 1.e | RFW only | Circuit mile days with fast-trip settings enabled (total) | 0 |  |  |  | Circuit mile days
|  | HWW only | Circuit mile days with fast-trip settings enabled (total) | 0 |  |  |  | Circuit mile days
|  | HWW & RFW | Circuit mile days with fast-trip settings enabled (total) | 0 |  |  |  | Circuit mile days
|  | None | Circuit mile days with fast-trip settings enabled (total) | 0 |  |  |  | Circuit mile days
2. Customer hours of PSPS and other outages | 2.a. | N/A | Customer hours of planned outages including PSPS (total) | 232438.08 |  |  |  | Total customer hours of planned outages per year
| 2.b. | N/A | Customer hours of unplanned outages, not including PSPS or fast-trip (total) | 453866.87 |  |  |  | Total customer hours of unplanned outages, not including PSPS or fast-trip, per year
| 2.c. | N/A | Customer hours of unplanned outages resulting from fast-trip | 0 |  |  |  | Total customer hours of outages due to fast-trip per year
| 2.d. | N/A | System Average Interruption Duration Index (SAIDI) (including PSPS) | 17.88 |  |  |  | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served
| 2.e. | N/A | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | 17.88 |  |  |  | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served
| 2.f. | N/A | System Average Interruption Frequency Index (SAIFI) (including PSPS) | 0.1355 |  |  |  | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served)
| 2.g. | N/A | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | 0.1355 |  |  |  | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served)
3. Critical infrastructure impacted by PSPS | 3.a. | N/A | Critical infrastructure impacted by PSPS | 0 |  |  |  | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year
4. Community outreach of PSPS metrics | 4.a. | N/A | # of customers impacted by PSPS | 0 | 47857 | 44986 | 42287 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer)
4. Community outreach of PSPS metrics | 4.b. | N/A | # of medical baseline customers impacted by PSPS | 0 |  |  |  | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer)
4. Community outreach of PSPS metrics | 4.c. | N/A | # of customers notified prior to initiation of PSPS event | 0 |  |  |  | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
4. Community outreach of PSPS metrics | 4.d. | N/A | # of medical baseline customers notified prior to initiation of PSPS event | 0 |  |  |  | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
4. Community outreach of PSPS metrics | 4.e. | N/A | # of customers notified prior to a PSPS event impacting them | 0 |  |  |  | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
4. Community outreach of PSPS metrics | 4.f. | N/A | # of medical baseline customers notified prior to a PSPS event impacting them | 0 |  |  |  | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
5. Other PSPS metrics | 5.a. | N/A | Number of PSPS events in which a notification was sent but no de-energization occurred | 0 |  |  |  | Number of events
| 5.b. | N/A | Average number of customers located on de-energized circuit | 0 |  |  |  | Number of customers
| 5.c. | N/A | Customer hours of PSPS per RFW OH circuit mile day | 0 |  |  |  | =1.c. / RFW OH circuit mile days in time period
|  | N/A | Customer hours of PSPS per HWW OH circuit mile day | 0 |  |  |  | =1.c. / HWW OH circuit mile days in time period
|  | N/A | Customer hours of PSPS per high FPIOH circuit mile day | 0 |  |  |  | =1.c. / FPI OH circuit mile days in time period
| 5.d. | N/A | Median time between de-energization, due to PSPS, and inspection of a circuit segment | 0 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.e. | N/A | 95 percentile of time between de-energization, due to PSPS, and inspection of a circuit segment | 0 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.f. | N/A | Median time between de-energization, due to fast-trip, and inspection of a circuit segment | 0 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.g. | N/A | 95 percentile of time between de-energization, due to fast-trip, and inspection of a circuit segment | 0 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.h. | N/A | Number of risk events occurring on a de-energized circuit | 0 |  |  |  | Number of risk events

## Table 11
Utility | SDGE | Notes:
Table No. | 11 | Territory spend refers to the sum total of initiative spending across all areas, including HFTDs. HFTD spend refers to initiative spending applied to HFTDs, and is a subset of territory spend.
Date Modified | 2024-11-01 | CAPEX = Capital expenditure; OPEX = Operating expenditure.
|  | As data is submitted each reporting period, replace projections for the current reporting period with actuals. | [9 empty] | Actuals |  |  |  | Projected
The units for the spend data are thousands of dollars.
Table 11: Mitigation initiative financials | [11 empty] | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands)
[12 empty] | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | Primary driver targeted | Secondary driver targeted | Year initiated | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compiance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Comments | 2024 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | Blank Meaning
Community Outreach and Engagement | Public outreach and education awareness program | WMP.527 | PSPS Vulnerability | NA | 2013 | NA | WMPMA | NA | NA | NA | [5 empty] | 3452.7423 | 3452.7423 | 4011.4024 | 4011.4024 | 0 | 0 | 3887.003 | 3887.003 | 0 | 0 | 4003.6131 | 4003.6131
Community Outreach and Engagement | Engagement with access and functional needs populations | WMP.532 | [13 empty] | 0 | 0 | 505.3225 | 505.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Engagement with access and functional needs populations | WMP.1198 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Collaboration on local wildfire mitigation planning | WMP.1199 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Best practice sharing with other utilities | WMP.1200 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Other | WMP.1337 | [8 empty] | Community Engagement |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 622.2562 | 622.2562 | 0 | 0 | 640.9239 | 640.9239
Emergency Preparedness | Other | WMP.514 | PSPS Vulnerability | [7 empty] | Crew-accompanying ignition prevention and suppression resources and services |  |  |  |  | 0 | 0 | 3844.3762 | 3844.3762 | 0 | 0 | 3724 | 3724 | 0 | 0 | 3835.72 | 3835.72
Emergency Preparedness | Other | WMP.557 | PSPS Vulnerability | [7 empty] | Aviation Firefighting Program |  |  |  |  | 7959.5967 | 7959.5967 | 9326 | 9326 | 4943.9702 | 4943.9702 | 8122.004 | 8122.004 | 688.6156 | 688.6156 | 8365.6642 | 8365.6642
Emergency Preparedness | Public emergency communication strategy | WMP.563 | PSPS Vulnerability | NA | 2013 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | [5 empty] | 0 | 0 | 6156.904 | 6156.904 | 13350.7871 | 13350.7871 | 5067 | 5067 | 7757.3264 | 7757.3264 | 5219.01 | 5219.01
Emergency Preparedness | Customer support in wildfire and PSPS emergencies | WMP.1007 | PSPS Vulnerability | NA | 2013 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Preparedness | Emergency preparedness plan | WMP.1008 | PSPS Vulnerability | NA | 2013 | NA | NA | NA | NA | NA | [5 empty] | 20285.7274 | 20285.7274 | 15052 | 15052 | 2628.9084 | 2628.9084 | 15677.4715 | 15677.4715 | 315.237 | 315.237 | 16147.7957 | 16147.7957
Emergency Preparedness | Preparedness and planning for service restoration | WMP.1009 | PSPS Vulnerability | NA | 2013 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Preparedness | External collaboration and coordination | WMP.1201 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.449 | PSPS - for sectionalization, etc. | NA | 2011 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | Wireless Fault Indicators |  |  |  |  | 50.849 | 19.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.453 | Equipment failure | NA | 2016 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | Capacitor Maintenance and replacement program (SCADA) |  |  |  |  | 1884.6407 | 251.2854 | 0 | 0 | 287.4126 | 38.3217 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Covered conductor installation | WMP.455 | Other contact with object | Equipment failure | 2020 | NA | WMPMA | Exceeds | G.O. 95 | NA | [5 empty] | 76806.3821 | 76806.3821 | 2220 | 2220 | 76889.6471 | 76889.6471 | 3000 | 3000 | 67631.904 | 67631.904 | 3090 | 3090
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.459 | Equipment failure | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | Expulsion fuse replacement |  |  |  |  | 93.1532 | 93.1532 | 0 | 0 | 1463.2166 | 1463.2166 | 0 | 0 | 1549.5688 | 1549.5688 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.464 | PSPS - for sectionalization, etc. | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | Maintenance, repair, and replacement of connectors, including hotline clamps |  |  |  |  | 0 | 0 | 486 | 466.56 | 1652 | 1486.8 | 50.1199 | 45.1079 | 1701.56 | 1450.8038 | 51.6235 | 44.0158
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.550 | Equipment failure | NA | 2020 | NA | WMPMA | Exceeds | G.O. 95 | NA | Lightning arrester removal and replacement |  |  |  |  | 3407.2892 | 3200.7868 | 0 | 0 | 2982.8287 | 2982.8287 | 0 | 0 | 3482.6461 | 3482.6461 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.972 | Other contact with object | NA | 2022 | NA | WMPMA | NA | NA | NA | Avian Protection |  |  |  |  | 2506.5864 | 2005.2691 | 19 | 15.2 | 1103.4298 | 882.7438 | 10 | 8 | 1512.351 | 1209.8808 | 10.3 | 8.24
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.1189 | Equipment failure | NA | 2021 | NA | NA | NA | NA | NA | Strategic Pole Replacement Program |  |  |  |  | 1710 | 1425 | 129.6563 | 108.0469 | 7014.9489 | 4387.6272 | 4 | 2.5019 | 6948.2708 | 6948.2708 | 4.12 | 4.12
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above | WMP.461 | PSPS - for sectionalization, etc. | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | PSPS Sectionalizing Enhancements |  |  |  |  | 1836.5477 | 1836.5477 | 0 | 0 | 1785.6162 | 1785.6162 | 0 | 0 | 1881.105 | 1881.105 | 0 | 0
Grid Design, Operations, and Maintenance | Microgrids | WMP.462 | PSPS - for sectionalization, etc. | NA | 2019 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | [5 empty] | 16576.3668 | 5525.4556 | 1651.514 | 550.5047 | 6312.4909 | 6312.4909 | 1402.5305 | 1402.5305 | 14127.3408 | 0 | 1444.6064 | 0
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above | WMP.466 | PSPS - for sectionalization, etc. | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Generator Grant Program |  |  |  |  | 0 | 0 | 7060 | 7060 | 0 | 0 | 3138.7674 | 3138.7674 | 0 | 0 | 3232.9305 | 3232.9305
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above | WMP.467 | PSPS - for sectionalization, etc. | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Generator Assistance Program |  |  |  |  | 0 | 0 | 1000.4265 | 1000.4265 | 0 | 0 | 485.9398 | 485.9398 | 0 | 0 | 500.518 | 500.518
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above | WMP.468 | PSPS - for sectionalization, etc. | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Standby Power Programs |  |  |  |  | 0 | 0 | 10350.44 | 10350.44 | 0 | 0 | 5377.3647 | 5377.3647 | 0 | 0 | 5538.6856 | 5538.6856
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above | WMP.1016 | Other contact with object | Equipment failure | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | CNF(Distribution Underground) |  |  |  |  | 1182.7006 | 1182.7006 | 2070 | 2070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above | WMP.1017 | Equipment failure | Other contact with object | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | CNF(Distribution Overhead) |  |  |  |  | 1471.1557 | 1471.1557 | 0 | 0 | 588.8086 | 588.8086 | 150 | 150 | 647.5506 | 647.5506 | 154.5 | 154.5
Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements | WMP.458 | Equipment failure | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Transmission pole/tower replacements and reinforcements | WMP.472 | Equipment failure | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | WMP.473 | Other contact with object | Equipment failure | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | [5 empty] | 196200.3624 | 196200.3624 | 435.5423 | 435.5423 | 300457.8368 | 300457.8368 | 1270.733 | 1270.733 | 358877.1056 | 358877.1056 | 1708.855 | 1708.855
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.475 | Equipment failure | Other contact with object | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | Distribution OH System Hardening |  |  |  |  | 1985.4335 | 1985.4335 | 1800 | 1800 | 2345.6071 | 2345.6071 | 935 | 935 | 1077.8421 | 1077.8421 | 963.05 | 963.05
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.543 | Equipment failure | Other contact with object | 2009 | NA | NA | Exceeds | G.O. 95 | NA | Transmission OH Hardening |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.545 | Equipment failure | Other contact with object | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | Transmission OH Hardening - Distribution Underbuild |  |  |  |  | 11397.0606 | 11397.0606 | 0 | 0 | 12460.268 | 12460.268 | 4 | 4 | 14693.955 | 14693.955 | 4.12 | 4.12
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.463 | PSPS - for sectionalization, etc. | NA | 2011 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Advanced Protection |  |  |  |  | 9705.984 | 9705.984 | 300 | 300 | 15613.367 | 15613.367 | 197.2722 | 197.2722 | 3382.8411 | 3382.8411 | 207.1358 | 207.1358
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.1195 | Wildfire Exposure | NA | 2023 | NA | NA | NA | NA | NA | Early Fault Detection |  |  |  |  | 5612.0466 | 5612.0466 | 9 | 9 | 4165.5161 | 4165.5161 | 4 | 4 | 3410.363 | 3410.363 | 4.12 | 4.12
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.549 | Wildfire Exposure Potential | PSPS exposure potential | 2010 | 2019 GRC | NA | NA | P.U. Code § 451 | NA | Distribution Communications Reliability Improvements |  |  |  |  | 81273.5543 | 81273.5543 | 1121.616 | 1121.616 | 30716.3232 | 28668.5683 | 970.116 | 905.4416 | 43212.84 | 42183.9629 | 999.2195 | 975.4285
Grid Design, Operations, and Maintenance | Line removals (in HFTD) | WMP.1202 | NA | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.478 | Equipment failure | NA | 1997 | 2019 GRC | NA | Meets | G.O. 95 | NA | [5 empty] | 7834.0159 | 2090.3264 | 620 | 165.4327 | 6040.6771 | 6040.6771 | 800.1901 | 800.1901 | 9562.6279 | 9562.6279 | 824.1958 | 824.1958
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.479 | Equipment failure | NA | 1997 | NA | NA | Meets | G.O. 95 | NA | [5 empty] | 841.957 | 425.885 | 9 | 9 | 1706.891 | 1706.891 | 36.4864 | 36.4864 | 1942.9246 | 1942.9246 | 37.581 | 37.581
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.481 | Equipment failure | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | [5 empty] | 0 | 0 | 175 | 147.7175 | 0 | 0 | 10.1577 | 0 | 0 | 0 | 10.4624 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.482 | Equipment failure | NA | 2010 | NA | NA | Meets | P.U. Code § 451 | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.483 | Equipment failure | NA | 1997 | 2019 GRC | NA | Meets | G.O. 95 | NA | [5 empty] | 1591.7566 | 4.04 | 24 | 0.060914 | 923.8084 | 923.8084 | 100.652 | 100.652 | 1462.4247 | 1462.4247 | 103.6716 | 103.6716
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.484 | Equipment failure | NA | 2011 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | [5 empty] | 0 | 0 | 1388 | 1388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.488 | Equipment failure | NA | 1997 | 2019 GRC | NA | Meets | G.O. 95 | NA | [5 empty] | 952.3247 | 370.64 | 285 | 110.9206 | 552.701 | 552.701 | 303.6373 | 303.6373 | 874.9473 | 874.9473 | 312.7464 | 312.7464
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.489 | Equipment failure | NA | 1997 | NA | NA | Meets | G.O. 95 | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.492 | Equipment ignition likelihood | NA | 1997 | 2019 GRC | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.551 | Equipment failure | NA | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | [5 empty] | 2574.2984 | 2574.2984 | 320 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.552 | Equipment failure | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | [5 empty] | 80740 | 80356.7032 | 53170.5592 | 52918.1427 | 64920.3739 | 62972.7626 | 30572.5565 | 29655.3798 | 54937.4594 | 53289.3357 | 31489.7332 | 30545.0412
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.555 | Equipment failure | NA | 2010 | NA | NA | Exceeds | G.O. 95 | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset inpsections | WMP.1190 | Equipment ignition likelihood | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.491 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Distribution Detailed Inspections |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1191 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Transmission Inspections |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1192 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Distribution Drone Assessments |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1193 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Wood Pole Intrusive (Transmission & Distribution) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1194 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Substation Inspections |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Open work orders | WMP.1203 | NA | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Equipment Settings to Reduce Wildfire Risk (Grid Ops) | WMP.1204 | NA | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Grid Response Procedures and Notifications (Grid Ops) | WMP.1205 | NA | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Workforce Planning | WMP.1206 | NA | NA | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Personnel Work Procedures and Training in Conditions of Elevated Fire Risk (Grid Ops) | WMP.515 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overview of the Service Territory | Environmental compliance and permitting | WMP.493 | NA | NA | 1998 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 999.5406 | 999.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Situational Awareness and Forecasting | Environmental monitoring systems | WMP.447 | [13 empty] | 415.5336 | 415.5336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Situational Awareness and Forecasting | Environmental monitoring systems | WMP.970 | [13 empty] | 58.1315 | 58.1315 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Situational Awareness and Forecasting | Environmental monitoring systems | WMP.1431 | [8 empty] | Air Quality Station Maintenance |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 71.9561 | 71.9561 | 0 | 0 | 74.1148 | 74.1148
Situational Awareness and Forecasting | Environmental monitoring systems | WMP.1430 | NA | NA | 2010 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Weather Station Maintenance and Calibration |  |  |  |  | 0 | 0 | 0 | 0 | 260.629 | 260.629 | 0 | 0 | 140.2615 | 140.2615 | 0 | 0
Situational Awareness and Forecasting | Weather forecasting | WMP.443 | Wildfire Exposure Potential | Wildfire Spread | 2009 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Situational Awareness and Forecasting | Fire potential index | WMP.450 | Wildfire Exposure Potential | NA | 2012 | 2019 GRC | NA | NA | NA | NA | [5 empty] | 2425.918 | 2425.918 | 3781.3532 | 3781.3532 | 1676.798 | 1676.798 | 4239 | 4239 | 1476.828 | 1476.828 | 4366.17 | 4366.17
Situational Awareness and Forecasting | Ignition detection systems | WMP.558 | Wildfire Exposure Potential | Wildfire Spread | NA | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Substation defensible space | WMP.492 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Vegetation Inspections | WMP.494 | Wildfire Exposure Potential | NA | 1998 | NA | NA | NA | G.O. 95, Rule 35; Public Resources Code 4293; FAC-003-4 | NA | [5 empty] | 0 | 0 | 44559.1517 | 23698.5197 | 0 | 0 | 60084 | 31688.3066 | 0 | 0 | 61886.52 | 32638.9558
Vegetation Management and Inspection | Emergency response vegetation management | WMP.496 | Wildfire hazard | NA | 1998 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Wood and slash management | WMP.497 | Contact with vegetation | NA | 2019 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | [5 empty] | 0 | 0 | 7010.8 | 7010.8 | 0 | 0 | 5833.2021 | 5833.2021 | 0 | 0 | 6008.1981 | 6008.1981
Vegetation Management and Inspection | Clearance | WMP.501 | Contact with vegetation | NA | 2019 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | [5 empty] | 0 | 0 | 10235 | 10235 | 0 | 0 | 10235 | 10235 | 0 | 0 | 10542.05 | 10542.05
Vegetation Management and Inspection | Quality assurance / quality control | WMP.505 | NA | NA | 1998 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Vegetation management enterprise system | WMP.511 | NA | NA | 2002 | NA | NA | NA | NA | NA | [5 empty] | 2096.1928 | 2096.1928 | 0 | 0 | 352.7207 | 352.7207 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Pole clearing | WMP.512 | Other contact with object | NA | 1998 | 2019 GRC | NA | Meets | P.U. Code § 451; Public Resources Code 4292 | NA | [5 empty] | 0 | 0 | 6410.8929 | 5634.0504 | 0 | 0 | 7893.1847 | 6936.7249 | 0 | 0 | 8129.9802 | 7144.8266
Vegetation Management and Inspection | Open work orders | WMP.1207 | NA | NA | 1198 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Workforce Planning | WMP.1208 | NA | NA | 2021 | NA | NA | NA | NA | NA | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | High-risk species | WMP.1325 | NA | NA | 2019 | NA | NA | NA | NA | NA | Right Tree Right Place |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 999.5999 | 999.5999 | 0 | 0 | 1029.5879 | 1029.5879
Vegetation Management and Inspection | High-risk species | WMP.1326 | NA | NA | 2019 | NA | NA | NA | NA | NA | Community Tree Rebate Program |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wildfire Mitigation Strategy Development | Other | WMP.519 | [8 empty] | Centralized repository for data |  |  |  |  | 11818.6819 | 11818.6819 | 1944.3008 | 1944.3008 | 9028.1815 | 9028.1815 | 1639 | 1639 | 15331.3366 | 15331.3366 | 1688.17 | 1688.17
Wildfire Mitigation Strategy Development | Other | WMP.442 | [8 empty] | A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment |  |  |  |  | 319.08 | 319.08 | 3597.0741 | 3597.0741 | 0 | 0 | 3335.7103 | 3335.7103 | 0 | 0 | 3435.7817 | 3435.7817
Wildfire Mitigation Strategy Development | Other | WMP.521 | [8 empty] | Documentation and disclosure of wildfire-related data and algorithms |  |  |  |  | 0 | 0 | 0 | 0 | 58.8677 | 58.8677 | 0 | 0 | 0 | 0 | 0 | 0
Wildfire Mitigation Strategy Development | Other | WMP.523 | [8 empty] | Allocation methodology development and application |  |  |  |  | 5276.8627 | 5276.8627 | 5291.4092 | 5291.4092 | 2719.7257 | 2719.7257 | 5363.4532 | 5363.4532 | 1106.2675 | 1106.2675 | 5524.3568 | 5524.3568

## Table 12
s | SDGE | Notes:
Table No. | 12
Date Modified | 2024-11-01
Table 12: WMP Midyear & End-of-Year Targets
Targets
[5 empty] | YTD end of Q2 | YTD end of Q3 | End of year | YTD end of Q2 | YTD end of Q3 | End of year | YTD end of Q2 | YTD end of Q3 | End of year
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | TargetType | Units | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | Method of Verification | Comments
Grid Design, Operations, and Maintenance | Covered conductor installation | WMP.455 | Quantitative | Miles | 16.8 | 52.92 | 60 | 0 | 0 | 60 |  |  | 40 | Quantitative | Distribution overhead hardening (covered conductor)
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | WMP.473 | Quantitative | Miles | 4.38 | 20.68 | 72 | 0 | 0 | 125 |  |  | 150 | Quantitative | Strategic undergrounding
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.475 | Quantitative | Miles | 1.78 | 2.13 | 2.33 | 0 | 0 | 0 |  |  | 0.6 | Quantitative | Distribution overhead system hardening
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.543 | Quantitative | Miles | 3.36 | 3.65 | 15.76 | 10.2 | 10.2 | 10.2 |  |  | 10.2 | Quantitative | Transmission overhead hardening
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.545 | Quantitative | Miles | 10.61 | 10.61 | 17.3 | 0 | 1 | 1 |  |  | 3.4 | Quantitative | Transmission overhead hardening (distribution underbuild)
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.463 | Quantitative | Circuits | 2 | 2 | 4 | 3 | 6 | 8 |  |  | 8 | Quantitative | Advanced protection
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.1195 | Quantitative | Nodes | 4 | 16 | 32 | 30 | 52 | 60 |  |  | 60 | Quantitative | Early fault detection
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.549 | Quantitative | Base Stations | 3 | 8 | 11 | 20 | 40 | 60 |  |  | 90 | Quantitative | Distribution communications reliability improvements
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.453 | Quantitative | Capacitors | 12 | 16 | 20 | 0 | 0 | 0 |  |  | 0 | Quantitative | Capacitor maintenance and replacement program (SCADA)
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.459 | Quantitative | Fuses | 8 | 18 | 36 | 0 | 0 | 0 |  |  | 0 | Quantitative | Expulsion fuse replacement
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.464 | Quantitative | HLCs | 400 | 775 | 962 | 126 | 188 | 250 |  |  | 0 | Quantitative | Maintenance, repair, and replacement of connectors, including hotline clamps
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.550 | Quantitative | Arrestors | 1375 | 1896 | 2216 | 1531 | 1715 | 1848 |  |  | 1848 | Quantitative | Lightning arrester removal and replacement
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.972 | Quantitative | Poles | 263 | 517 | 657 | 50 | 150 | 200 |  |  | 0 | Quantitative | Avian protection
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.449 | Quantitative | WFIs |  |  |  | 0 | 300 | 300 |  |  | 0 | Quantitative | Wireless Fault Indicators
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.1189 | Quantitative | Poles | 0 | 0 | 1 | 98 | 150 | 267 |  |  | 200 | Quantitative | Strategic pole replacement program
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.461 | Quantitative | Switches | 1 | 8 | 10 | 8 | 10 | 10 |  |  | 10 | Quantitative | PSPS sectionalizing enhancements
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.462 | Quantitative | Microgrid | NA | NA | NA | 0 | 0 | 4 |  |  | 0 | Quantitative | Microgrids
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.468 | Quantitative | Generators | 128 | 302 | 362 | 100 | 150 | 300 |  |  | 300 | Quantitative | Standby power (fixed power backup)
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.466 | Qualitative | Generators | NA | NA | NA | NA | NA | NA | NA | NA | NA | Qualitative | Generator grant program
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.467 | Qualitative | Generators | NA | NA | NA | NA | NA | NA | NA | NA | NA | Qualitative | Generator assistance program
Grid Design, Operations, and Maintenance | Asset inspections | WMP.478 | Quantitative | Structures | 8405 | 10601 | 11755 | 14850 | 15350 | 15450 | 6632 | 9948 | 13275 | Quantitative | Distribution overhead detailed inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.479 | Quantitative | Structures | 723 | 1533 | 1928 | 1121 | 1442 | 1960 | 1239 | 1899 | 1979 | Quantitative | Transmission overhead detailed inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.481 | Quantitative | Structures | 7279 | 10270 | 11900 | 4766 | 7149 | 9532 | 150 | 300 | 9532 | Quantitative | Distribution infrared inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.482 | Quantitative | Structures | 0 | 6077 | 6077 | 0 | 0 | 6179 | 0 | 0 | 6179 | Quantitative | Transmission infrared inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.483 | Quantitative | Structures | 527 | 726 | 1038 | 0 | 0 | 0 | 0 | 0 | 0 | Quantitative | Distribution wood pole intrusive inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.1190 | Quantitative | Structures | 38 | 38 | 90 | 0 | 0 | 0 | 50 | 75 | 141 | Quantitative | Transmission wood pole intrusive inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.552 | Quantitative | Structures | 7599 | 15311 | 15311 | 6753 | 10127 | 13500 | 4500 | 9000 | 13500 | Quantitative | Drone assessments
Grid Design, Operations, and Maintenance | Asset inspections | WMP.488 | Quantitative | Structures | 60986 | 83041 | 85857 | 71047 | 83247 | 86197 | 70756 | 83236 | 86535 | Quantitative | Distribution overhead patrol inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.489 | Quantitative | Structures | 5985 | 6200 | 6200 | 6008 | 6008 | 6337 | 3766 | 5650 | 6337 | Quantitative | Transmission overhead patrol inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.555 | Quantitative | Structures | 0 | 1602 | 1602 | 0 | 1632 | 1632 | 0 | 1632 | 1632 | Quantitative | Transmission 69kV tier 3 visual inspections
Grid Design, Operations, and Maintenance | Asset inspections | WMP.492 | Quantitative | Substations | 198 | 290 | 396 | 192 | 281 | 384 | 189 | 277 | 384 | Quantitative | Substation patrol inspections
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1191 | Quantitative | Findings | 100% | 100% | 97% | 100% | 100% | 100% | 100% | 100% | 100% | Quantitative | Quality assurance / quality control of transmission inspections
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.491 | Quantitative | Structures | 68 | 111 | 150 | 0 | 0 | 77 | 66 | 66 | 66 | Quantitative | Quality assurance / quality control of distribution detailed inspections
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1192 | Quantitative | Structures | 7599 | 15311 | 15311 | 6753 | 10127 | 13500 | 4500 | 9000 | 13500 | Quantitative | Quality assurance / quality control of distribution drone assessments
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1193 | Quantitative | Structures | 93 | 111 | 111 | 0 | 0 | 0 | 14 | 14 | 14 | Quantitative | Quality assurance / quality control of wood pole intrusive (transmission and distribution)
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1194 | Quantitative | Structures | 11 | 11 | 23 | 9 | 9 | 18 | 9 | 9 | 18 | Quantitative | Quality assurance / quality control of substation inspections
Situational Awareness and Forecasting | Enviornmental monitoring System | WMP.970 | Quantitative | Sensors | 0 | 0 | 6 | 3 | 6 | 6 | 0 | 0 | 6 | Quantitative | Air quality index
Vegetation Management and Inspection | Vegetation management inspection program | WMP.494 | Quantitative | Inspections | 239800 | 364122 | 514626 | 241800 | 374200 | 485400 | 241800 | 374200 | 485400 | Quantitative | Detailed inspections
Vegetation Management and Inspection | Vegetation management inspection program | WMP.508 | Quantitative | VMAs | 44 | 92 | 106 | 9 | 106 | 106 | 9 | 106 | 106 | Quantitative | Off-cycle patrol
Vegetation Management and Inspection | Fuels management | WMP.497 | Quantitative | Poles Cleared | 71 | 123 | 514 | 100 | 200 | 500 | 100 | 200 | 500 | Quantitative | Fuels management
Vegetation Management and Inspection | Pole Clearing | WMP.512 | Quantitative | Poles Brushed | 25591 | 31762 | 35258 | 25150 | 27890 | 33010 | 25150 | 27890 | 33010 | Quantitative | Pole clearing (brushing)
Vegetation Management and Inspection | Clearance | WMP.501 | Quantitative | Trees Trimmed or Removed | 5372 | 9551 | 13419 | 5890 | 8780 | 11200 | 5710 | 8600 | 11200 | Quantitative | Clearance
Vegetation Management and Inspection | Quality assurance / quality control | WMP.505 | Quantitative | Inspections | 47, 533 | 66517 | 18% | 15% | 15% | 15% | 15% | 15% | 15% | Quantitative | Quality assurance / quality control vegetation management

## Table 13
Utility | SDGE |  | Note: Provide a listing (as rows) of all work orders / notifications for corrective work on electric circuits that were open as of the end of the quarter.
Table No. | 13
Date Modified | 2024-11-01
Table 13: Open work orders / notifications
a. Work order number | b. Equipment Type | c. HFTD Tier | d. Line type | e. Date the work order was originally opened | f. Due date of the original work order | g. GO 95 rule 18 priority level of the original work order | h. Optional utility-specific repair priority | i. Date(s) the work order was reinspected or modified (if applicable) | j. Due date of the work order after it was reinspected or modified (if applicable) | k. Priority of the work order after it was reinspected or modified (if applicable) | l. Reason for reinspection (if applicable)
125650 | Complete Wood Pole | Tier 2 | Transmission | 2021-09-01 | 2023-08-02 | Level 2 | N/A
132312 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-10-28 | 2024-10-24 | Level 2 | N/A
132368 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-10-28 | 2024-10-24 | Level 2 | N/A
131463 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-12-12 | 2024-12-11 | Level 3 | N/A
132705 | Ground Connection | Tier 3 | Transmission | 2023-12-12 | 2024-12-11 | Level 2 | N/A
132706 | Guy Wire - Anchor | Tier 3 | Transmission | 2023-12-12 | 2024-12-11 | Level 2 | N/A
134161 | Area Around Structure | Tier 2 | Transmission | 2023-12-14 | 2024-12-13 | Level 2 | N/A
131614 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 3 | N/A
131634 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 3 | N/A
132831 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
132857 | Cold End Cotter Key(s) | Tier 3 | Transmission | 2023-12-18 | 2024-12-14 | Level 2 | N/A
132858 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2023-12-18 | 2024-12-14 | Level 2 | N/A
132871 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
132873 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
132875 | Bolted Spacer | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
132901 | Jumper (Complete) | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
133521 | Shoe Nut(s) | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
133522 | Hot End Cotter Key(s) | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
133523 | Cold End Clevis-Shackle | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
136229 | Member (Steel Tower) | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
133153 | Nuts | Tier 3 | Transmission | 2023-12-18 | 2024-12-16 | Level 2 | N/A
131951 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-12-19 | 2024-12-17 | Level 2 | N/A
131952 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
132855 | Jumper (Complete) | Tier 3 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
132976 | Cold End Cotter Key(s) | Tier 3 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
132995 | Tower-Bridge | Tier 3 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
133531 | Bolt(s) | Tier 3 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
133554 | Cold End Cotter Key(s) | Tier 3 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
132107 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2023-12-27 | 2024-12-26 | Level 3 | N/A
132108 | Insulators-Post, NCI, 69kv, Short | Tier 3 | Transmission | 2023-12-27 | 2024-12-26 | Level 2 | N/A
132311 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-12-29 | 2024-12-28 | Level 2 | N/A
132394 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-12-29 | 2024-12-28 | Level 2 | N/A
132412 | Cold End Cotter Key(s) | Tier 3 | Transmission | 2023-12-29 | 2024-12-28 | Level 2 | N/A
132424 | Jumper Bolt(S)-Nut(s) | Tier 3 | Transmission | 2023-12-29 | 2024-12-28 | Level 2 | N/A
129416 | Footings (Complete) | Tier 2 | Transmission | 2023-10-04 | 2025-01-03 | Level 2 | N/A
133245 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2024-01-10 | 2025-01-09 | Level 2 | N/A
133247 | Shieldwire Attachment Point | Tier 2 | Transmission | 2024-01-10 | 2025-01-09 | Level 2 | N/A
133248 | Damper (Complete) | Tier 2 | Transmission | 2024-01-10 | 2025-01-09 | Level 2 | N/A
135930 | Concrete | Tier 2 | Transmission | 2023-01-10 | 2025-01-09 | Level 2 | N/A
135931 | Footings (Complete) | Tier 2 | Transmission | 2023-01-10 | 2025-01-09 | Level 2 | N/A
133341 | Armor Rod - Shieldwire | Tier 3 | Transmission | 2024-01-11 | 2025-01-10 | Level 2 | N/A
133342 | Bolt(s) | Tier 3 | Transmission | 2024-01-11 | 2025-01-10 | Level 2 | N/A
133382 | Fiberglass Rod | Tier 3 | Transmission | 2024-01-20 | 2025-01-19 | Level 2 | N/A
136746 | Pole Butt | Tier 2 | Transmission | 2024-01-20 | 2025-01-19 | Level 2 | N/A
136747 | Shoe Pin-Bolt | Tier 2 | Transmission | 2024-01-20 | 2025-01-19 | Level 2 | N/A
133412 | Footings (Complete) | Tier 2 | Transmission | 2024-01-29 | 2025-01-28 | Level 2 | N/A
121727 | Insulators-Ceramic, Standard, 50K | Tier 3 | Transmission | 2020-12-15 | 2025-02-06 | Level 2 | N/A
134137 | Complete Steel Pole | Tier 2 | Transmission | 2024-02-15 | 2025-02-13 | Level 2 | N/A
134153 | Bolted Spacer | Tier 2 | Transmission | 2024-02-25 | 2025-02-24 | Level 2 | N/A
134157 | Cold End Cotter Key(s) | Tier 3 | Transmission | 2024-03-05 | 2025-02-24 | Level 2 | N/A
132516 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132517 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132519 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132534 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132535 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132536 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132537 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132538 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132539 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132587 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132596 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132623 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132624 | Pole Butt | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
134188 | Other(Specify) | Tier 3 | Transmission | 2024-02-29 | 2025-02-28 | Level 2 | N/A
132480 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132481 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132482 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132502 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132503 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132504 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132520 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132600 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132601 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132613 | Complete Wood Pole | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132614 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
132616 | Pole Butt | Tier 3 | Transmission | 2024-03-01 | 2025-03-01 | Level 2 | N/A
130462 | Complete Tower | Tier 2 | Transmission | 2024-03-11 | 2025-03-10 | Level 2 | N/A
130488 | Complete Tower | Tier 2 | Transmission | 2024-03-11 | 2025-03-10 | Level 2 | N/A
130537 | Anti-Climb Barrier | Tier 2 | Transmission | 2023-06-20 | 2025-03-12 | Level 2 | N/A
130538 | Jumper (Complete) | Tier 2 | Transmission | 2023-06-20 | 2025-03-12 | Level 2 | N/A
130539 | Complete Tower | Tier 2 | Transmission | 2023-06-20 | 2025-03-12 | Level 2 | N/A
130540 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-06-20 | 2025-03-12 | Level 2 | N/A
130541 | Conductor Strand(s) | Tier 2 | Transmission | 2023-06-20 | 2025-03-12 | Level 2 | N/A
133529 | Complete Tower | Tier 2 | Transmission | 2023-07-07 | 2025-03-12 | Level 2 | N/A
130460 | Damper (Complete) | Tier 2 | Transmission | 2024-03-14 | 2025-03-13 | Level 2 | N/A
133279 | Footings (Complete) | Tier 2 | Transmission | 2024-03-31 | 2025-03-31 | Level 2 | N/A
133947 | Shieldwire Attachment Point | Tier 2 | Transmission | 2024-04-06 | 2025-04-05 | Level 2 | N/A
133881 | X Marker | Tier 2 | Transmission | 2024-04-08 | 2025-04-07 | Level 2 | N/A
133882 | X Marker | Tier 2 | Transmission | 2024-04-08 | 2025-04-07 | Level 2 | N/A
134342 | Switch - Contacts | Tier 2 | Transmission | 2024-04-08 | 2025-04-07 | Level 2 | N/A
134349 | Switch Handle | Tier 2 | Transmission | 2024-04-08 | 2025-04-07 | Level 2 | N/A
134350 | Switch - Contacts | Tier 2 | Transmission | 2024-04-08 | 2025-04-07 | Level 2 | N/A
130573 | Footings (Complete) | Tier 2 | Transmission | 2023-04-10 | 2025-04-09 | Level 2 | N/A
132647 | Footings (Complete) | Tier 3 | Transmission | 2023-10-12 | 2025-04-11 | Level 2 | N/A
137016 | Stub Pole - Steel | Tier 2 | Transmission | 2024-04-16 | 2025-04-16 | Level 2 | N/A
133293 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2024-04-19 | 2025-04-18 | Level 2 | N/A
133294 | Bolt(s) | Tier 2 | Transmission | 2024-04-19 | 2025-04-18 | Level 2 | N/A
133295 | Shieldwire Attachment Point | Tier 2 | Transmission | 2024-04-19 | 2025-04-18 | Level 2 | N/A
133296 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2024-04-19 | 2025-04-18 | Level 2 | N/A
133297 | Shieldwire Attachment Point | Tier 2 | Transmission | 2024-04-19 | 2025-04-18 | Level 2 | N/A
133298 | Shieldwire Attachment Point | Tier 2 | Transmission | 2024-04-19 | 2025-04-18 | Level 2 | N/A
134666 | Footings (Complete) | Tier 2 | Transmission | 2024-04-23 | 2025-04-23 | Level 2 | N/A
130986 | Anti-Climb Barrier | Tier 2 | Transmission | 2024-04-25 | 2025-04-24 | Level 2 | N/A
133378 | Damper (Complete) | Tier 2 | Transmission | 2024-04-26 | 2025-04-25 | Level 2 | N/A
133152 | Footings (Complete) | Tier 3 | Transmission | 2023-10-29 | 2025-04-28 | Level 2 | N/A
133970 | Hot End Cotter Key(s) | Tier 2 | Transmission | 2024-04-29 | 2025-04-28 | Level 2 | N/A
131117 | Armor Rod - Shieldwire | Tier 2 | Transmission | 2024-05-09 | 2025-05-08 | Level 2 | N/A
134521 | Armor Rod - Shieldwire | Tier 2 | Transmission | 2024-05-09 | 2025-05-08 | Level 2 | N/A
130556 | Footings (Complete) | Tier 2 | Transmission | 2023-05-11 | 2025-05-10 | Level 2 | N/A
130574 | Footings (Complete) | Tier 2 | Transmission | 2023-05-17 | 2025-05-16 | Level 2 | N/A
130700 | Area Around Footer(s) | Tier 2 | Transmission | 2023-05-17 | 2025-05-16 | Level 2 | N/A
134408 | Bond Wire | Tier 2 | Transmission | 2024-05-21 | 2025-05-21 | Level 2 | N/A
134693 | Guy Wire - OH | Tier 2 | Transmission | 2024-05-24 | 2025-05-23 | Level 2 | N/A
134428 | Anchor Rods | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134429 | Cross Arms | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134430 | Fiberglass Rod | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134431 | Pole Ground (Wire) | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134432 | Jumper Strand(s) | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134436 | Anchor Rods | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134447 | Armor Rod Strand(s) | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134692 | Bond Wire | Tier 2 | Transmission | 2024-05-29 | 2025-05-28 | Level 2 | N/A
134415 | Bond Wire | Tier 2 | Transmission | 2024-05-30 | 2025-05-29 | Level 2 | N/A
134420 | Hardware | Tier 2 | Transmission | 2024-05-30 | 2025-05-29 | Level 2 | N/A
134777 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2024-05-31 | 2025-05-30 | Level 2 | N/A
134779 | Pole Butt | Tier 2 | Transmission | 2024-05-31 | 2025-05-30 | Level 2 | N/A
134780 | Bond Wire | Tier 2 | Transmission | 2024-05-31 | 2025-05-30 | Level 2 | N/A
134451 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2024-06-05 | 2025-06-04 | Level 2 | N/A
134452 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2024-06-05 | 2025-06-04 | Level 2 | N/A
134622 | Shoe Pin-Bolt | Tier 2 | Transmission | 2024-06-18 | 2025-06-18 | Level 2 | N/A
134634 | Pole Top | Tier 2 | Transmission | 2024-06-18 | 2025-06-18 | Level 2 | N/A
134635 | Bolt(s) | Tier 2 | Transmission | 2024-06-18 | 2025-06-18 | Level 2 | N/A
134637 | Shoe Pin-Bolt | Tier 2 | Transmission | 2024-06-18 | 2025-06-18 | Level 2 | N/A
134748 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2024-06-21 | 2025-06-21 | Level 2 | N/A
136998 | Complete Wood Pole | Tier 2 | Transmission | 2024-06-25 | 2025-06-25 | Level 2 | N/A
136999 | Complete Wood Pole | Tier 2 | Transmission | 2024-06-25 | 2025-06-25 | Level 2 | N/A
134397 | Complete Steel Pole | Tier 2 | Transmission | 2024-07-03 | 2025-07-03 | Level 2 | N/A
130050 | Other(Specify) | Tier 2 | Transmission | 2023-07-10 | 2025-07-08 | Level 2 | N/A
130055 | Conductor Weight(s) | Tier 2 | Transmission | 2023-07-10 | 2025-07-08 | Level 2 | N/A
134403 | Complete Steel Pole | Tier 2 | Transmission | 2024-07-09 | 2025-07-09 | Level 2 | N/A
134555 | Pole Butt | Tier 2 | Transmission | 2024-07-17 | 2025-07-17 | Level 2 | N/A
132325 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132326 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132328 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132329 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132336 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132343 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132344 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132345 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132360 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132361 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
132362 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2024-08-02 | 2025-08-02 | Level 3 | N/A
136093 | Shoe (Complete) | Tier 2 | Transmission | 2024-08-07 | 2025-08-06 | Level 2 | N/A
134154 | Aerial Light(s) | Tier 2 | Transmission | 2024-08-21 | 2025-08-21 | Level 2 | N/A
135531 | Conductor Strand(s) | Tier 2 | Transmission | 2024-08-21 | 2025-08-21 | Level 2 | N/A
134417 | Insulators-NCI, 69kv | Tier 2 | Transmission | 2024-09-03 | 2025-09-02 | Level 2 | N/A
134418 | Cross Arms | Tier 2 | Transmission | 2024-09-03 | 2025-09-02 | Level 2 | N/A
135965 | Pole Butt | Tier 2 | Transmission | 2024-09-04 | 2025-09-04 | Level 2 | N/A
136832 | Complete Wood Pole | Tier 2 | Transmission | 2024-09-04 | 2025-09-04 | Level 2 | N/A
136252 | Insulators-Post, NCI, 69kv, Long | Tier 3 | Transmission | 2024-09-11 | 2025-09-11 | Level 2 | N/A
136709 | Sign Warning (With Man) | Tier 2 | Transmission | 2024-09-18 | 2025-09-18 | Level 3 | N/A
136710 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2024-09-18 | 2025-09-18 | Level 2 | N/A
136711 | Hardware | Tier 2 | Transmission | 2024-09-18 | 2025-09-18 | Level 2 | N/A
136713 | Sign Warning (With Man) | Tier 2 | Transmission | 2024-09-18 | 2025-09-18 | Level 3 | N/A
137081 | Complete Wood Pole | Tier 2 | Transmission | 2024-09-18 | 2025-09-18 | Level 2 | N/A
137090 | Complete Wood Pole | Tier 2 | Transmission | 2024-09-18 | 2025-09-18 | Level 2 | N/A
130990 | Aerial Marker Sphere(s) | Tier 2 | Transmission | 2023-10-08 | 2025-10-07 | Level 2 | N/A
130991 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2025-10-07 | Level 2 | N/A
131178 | Shoe Nut(s) | Tier 2 | Transmission | 2023-10-08 | 2025-10-07 | Level 2 | N/A
133565 | Footings (Complete) | Tier 2 | Transmission | 2023-12-13 | 2025-12-12 | Level 2 | N/A
100023628727 | Pole | Tier 3 | Distribution | 2023-04-03 | 2023-10-31 | Level 2 | N/A
100023095820 | Pole | Tier 2 | Distribution | 2022-12-28 | 2023-12-31 | Level 2 | N/A
100023177889 | Cross Arm | Tier 2 | Distribution | 2023-01-09 | 2024-01-30 | Level 2 | N/A
100023178177 | Pole | Tier 2 | Distribution | 2023-01-09 | 2024-01-30 | Level 2 | N/A
100023277261 | Cross Arm | Tier 2 | Distribution | 2023-01-24 | 2024-01-30 | Level 2 | N/A
100023693412 | Pole | Tier 2 | Distribution | 2023-04-17 | 2024-04-29 | Level 2 | N/A
100023749695 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023762351 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023762365 | Cross Arm | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100024672843 | Pole | Tier 3 | Distribution | 2023-10-04 | 2024-04-30 | Level 2 | N/A
100023822497 | Anchor/Guy | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023851910 | Pole | Tier 2 | Distribution | 2023-05-16 | 2024-05-31 | Level 2 | N/A
100024788796 | Cross Arm | Tier 3 | Distribution | 2023-11-09 | 2024-05-31 | Level 2 | N/A
100024788811 | Cross Arm | Tier 3 | Distribution | 2023-11-09 | 2024-05-31 | Level 2 | N/A
100024788813 | Pole | Tier 3 | Distribution | 2023-11-09 | 2024-05-31 | Level 2 | N/A
100024809344 | Other | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024809346 | Pole | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024809347 | Cross Arm | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024809853 | Other | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024813880 | Cross Arm | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024845465 | Pole | Tier 3 | Distribution | 2023-11-20 | 2024-05-31 | Level 2 | N/A
100024848154 | Pole | Tier 3 | Distribution | 2023-11-21 | 2024-05-31 | Level 2 | N/A
100024848155 | Pole | Tier 3 | Distribution | 2023-11-21 | 2024-05-31 | Level 2 | N/A
100024848156 | Pole | Tier 3 | Distribution | 2023-11-21 | 2024-05-31 | Level 2 | N/A
100024851889 | Pole | Tier 3 | Distribution | 2023-11-22 | 2024-05-31 | Level 2 | N/A
100024892414 | Pole | Tier 3 | Distribution | 2023-11-06 | 2024-05-31 | Level 2 | N/A
100024895468 | Pole | Tier 3 | Distribution | 2023-11-27 | 2024-05-31 | Level 2 | N/A
100024895469 | Pole | Tier 3 | Distribution | 2023-11-27 | 2024-05-31 | Level 2 | N/A
100024108960 | Cross Arm | Tier 2 | Distribution | 2023-06-28 | 2024-06-30 | Level 2 | N/A
100025307352 | Pole | Tier 3 | Distribution | 2024-01-10 | 2024-07-31 | Level 2 | N/A
100025307353 | Pole | Tier 3 | Distribution | 2024-01-10 | 2024-07-31 | Level 2 | N/A
100025307355 | Pole | Tier 3 | Distribution | 2024-01-10 | 2024-07-31 | Level 2 | N/A
100025314025 | Pole | Tier 3 | Distribution | 2024-01-11 | 2024-07-31 | Level 2 | N/A
100025321324 | Pole | Tier 3 | Distribution | 2024-01-12 | 2024-07-31 | Level 2 | N/A
100025337691 | Cross Arm | Tier 3 | Distribution | 2024-01-17 | 2024-07-31 | Level 2 | N/A
100025337692 | Pole | Tier 3 | Distribution | 2024-01-17 | 2024-07-31 | Level 2 | N/A
100025337693 | Pole | Tier 3 | Distribution | 2024-01-17 | 2024-07-31 | Level 2 | N/A
100025367649 | Pole | Tier 3 | Distribution | 2024-01-23 | 2024-07-31 | Level 2 | N/A
100025395534 | Pole | Tier 3 | Distribution | 2024-01-24 | 2024-07-31 | Level 2 | N/A
100025398738 | Cross Arm | Tier 3 | Distribution | 2024-01-24 | 2024-07-31 | Level 2 | N/A
100025398740 | Pole | Tier 3 | Distribution | 2024-01-24 | 2024-07-31 | Level 2 | N/A
100025408674 | Insulator and Bushing | Tier 3 | Distribution | 2024-01-25 | 2024-07-31 | Level 2 | N/A
100025408831 | Pole | Tier 3 | Distribution | 2024-01-25 | 2024-07-31 | Level 2 | N/A
100025432622 | Conductor | Tier 3 | Distribution | 2024-01-30 | 2024-07-31 | Level 2 | N/A
100024316358 | Pole | Tier 2 | Distribution | 2023-08-09 | 2024-08-30 | Level 2 | N/A
100024494030 | Pole | Tier 2 | Distribution | 2023-08-23 | 2024-08-30 | Level 2 | N/A
100025472514 | Pole | Tier 3 | Distribution | 2024-02-04 | 2024-08-31 | Level 2 | N/A
100025480166 | Cross Arm | Tier 3 | Distribution | 2024-02-06 | 2024-08-31 | Level 2 | N/A
100025517314 | Pole | Tier 3 | Distribution | 2024-02-14 | 2024-08-31 | Level 2 | N/A
100025521730 | Cross Arm | Tier 3 | Distribution | 2024-02-15 | 2024-08-31 | Level 2 | N/A
100025526925 | Pole | Tier 3 | Distribution | 2024-02-16 | 2024-08-31 | Level 2 | N/A
100024546546 | Pole | Tier 2 | Distribution | 2023-09-21 | 2024-09-30 | Level 2 | N/A
100024546547 | Cross Arm | Tier 2 | Distribution | 2023-09-21 | 2024-09-30 | Level 2 | N/A
100024552866 | Cross Arm | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024553655 | Pole | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024553902 | Pole | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024553903 | Pole | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024578317 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024578767 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024578768 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024578769 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100025625985 | Pole | Tier 3 | Distribution | 2024-03-05 | 2024-09-30 | Level 2 | N/A
100025630183 | Pole | Tier 3 | Distribution | 2024-03-06 | 2024-09-30 | Level 2 | N/A
100025643232 | Pole | Tier 3 | Distribution | 2024-03-08 | 2024-09-30 | Level 2 | N/A
100025648109 | Pole | Tier 3 | Distribution | 2024-03-11 | 2024-09-30 | Level 2 | N/A
100025656582 | Pole | Tier 3 | Distribution | 2024-03-12 | 2024-09-30 | Level 2 | N/A
100025663846 | Pole | Tier 3 | Distribution | 2024-03-13 | 2024-09-30 | Level 2 | N/A
100025684742 | Pole | Tier 3 | Distribution | 2024-03-18 | 2024-09-30 | Level 2 | N/A
100025684743 | Pole | Tier 3 | Distribution | 2024-03-18 | 2024-09-30 | Level 2 | N/A
100025684837 | Pole | Tier 3 | Distribution | 2024-03-18 | 2024-09-30 | Level 2 | N/A
100025684906 | Other | Tier 3 | Distribution | 2024-03-18 | 2024-09-30 | Level 2 | N/A
100025692199 | Pole | Tier 3 | Distribution | 2024-03-19 | 2024-09-30 | Level 2 | N/A
100025692240 | Pole | Tier 3 | Distribution | 2024-03-19 | 2024-09-30 | Level 2 | N/A
100025704444 | Cross Arm | Tier 3 | Distribution | 2024-03-20 | 2024-09-30 | Level 2 | N/A
100025704595 | Pole | Tier 3 | Distribution | 2024-03-20 | 2024-09-30 | Level 2 | N/A
100025707503 | Other | Tier 3 | Distribution | 2024-03-21 | 2024-09-30 | Level 2 | N/A
100025707504 | Pole | Tier 3 | Distribution | 2024-03-21 | 2024-09-30 | Level 2 | N/A
100025707507 | Pole | Tier 3 | Distribution | 2024-03-21 | 2024-09-30 | Level 2 | N/A
100025713595 | Pole | Tier 3 | Distribution | 2024-03-22 | 2024-09-30 | Level 2 | N/A
100025713597 | Other | Tier 3 | Distribution | 2024-03-22 | 2024-09-30 | Level 2 | N/A
100025744000 | Pole | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025744002 | Cross Arm | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025744343 | Pole | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025744344 | Other | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025744349 | Pole | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025744681 | Pole | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025744682 | Pole | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025745386 | Pole | Tier 3 | Distribution | 2024-03-25 | 2024-09-30 | Level 2 | N/A
100025754958 | Pole | Tier 3 | Distribution | 2024-03-27 | 2024-09-30 | Level 2 | N/A
100024607585 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607586 | Insulator and Bushing | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607587 | Cross Arm | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607654 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607655 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024636631 | Pole | Tier 2 | Distribution | 2023-10-10 | 2024-10-31 | Level 2 | N/A
100024636991 | Pole | Tier 2 | Distribution | 2023-10-10 | 2024-10-31 | Level 2 | N/A
100024636992 | Pole | Tier 2 | Distribution | 2023-10-10 | 2024-10-31 | Level 2 | N/A
100025782841 | Cross Arm | Tier 3 | Distribution | 2024-04-01 | 2024-10-31 | Level 2 | N/A
100025788025 | Pole | Tier 3 | Distribution | 2024-04-02 | 2024-10-31 | Level 2 | N/A
100025788046 | Pole | Tier 3 | Distribution | 2024-04-02 | 2024-10-31 | Level 2 | N/A
100025788596 | Pole | Tier 3 | Distribution | 2024-04-02 | 2024-10-31 | Level 2 | N/A
100025796064 | Other | Tier 3 | Distribution | 2024-04-04 | 2024-10-31 | Level 2 | N/A
100025796067 | Pole | Tier 3 | Distribution | 2024-04-04 | 2024-10-31 | Level 2 | N/A
100025796068 | Anchor/Guy | Tier 3 | Distribution | 2024-04-04 | 2024-10-31 | Level 2 | N/A
100025796069 | Pole | Tier 3 | Distribution | 2024-04-04 | 2024-10-31 | Level 2 | N/A
100025797917 | Pole | Tier 3 | Distribution | 2024-04-04 | 2024-10-31 | Level 2 | N/A
100025797918 | Cross Arm | Tier 3 | Distribution | 2024-04-04 | 2024-10-31 | Level 2 | N/A
100025801338 | Other | Tier 3 | Distribution | 2024-04-05 | 2024-10-31 | Level 2 | N/A
100025801751 | Pole | Tier 3 | Distribution | 2024-04-05 | 2024-10-31 | Level 2 | N/A
100025802230 | Cross Arm | Tier 3 | Distribution | 2024-04-05 | 2024-10-31 | Level 2 | N/A
100025802231 | Pole | Tier 3 | Distribution | 2024-04-05 | 2024-10-31 | Level 2 | N/A
100025807232 | Pole | Tier 3 | Distribution | 2024-04-08 | 2024-10-31 | Level 2 | N/A
100025807812 | Anchor/Guy | Tier 3 | Distribution | 2024-04-08 | 2024-10-31 | Level 2 | N/A
100025808514 | Cross Arm | Tier 3 | Distribution | 2024-04-08 | 2024-10-31 | Level 2 | N/A
100025812295 | Pole | Tier 3 | Distribution | 2024-04-09 | 2024-10-31 | Level 2 | N/A
100025812296 | Pole | Tier 3 | Distribution | 2024-04-09 | 2024-10-31 | Level 2 | N/A
100025812297 | Cross Arm | Tier 3 | Distribution | 2024-04-09 | 2024-10-31 | Level 2 | N/A
100025812299 | Pole | Tier 3 | Distribution | 2024-04-09 | 2024-10-31 | Level 2 | N/A
100025814930 | Pole | Tier 3 | Distribution | 2024-04-10 | 2024-10-31 | Level 2 | N/A
100025815298 | Other | Tier 3 | Distribution | 2024-04-10 | 2024-10-31 | Level 2 | N/A
100025815351 | Anchor/Guy | Tier 3 | Distribution | 2024-04-10 | 2024-10-31 | Level 2 | N/A
100025815527 | Pole | Tier 3 | Distribution | 2024-04-10 | 2024-10-31 | Level 2 | N/A
100025815651 | Other | Tier 3 | Distribution | 2024-04-10 | 2024-10-31 | Level 2 | N/A
100025821758 | Pole | Tier 3 | Distribution | 2024-04-11 | 2024-10-31 | Level 2 | N/A
100025833388 | Pole | Tier 3 | Distribution | 2024-04-15 | 2024-10-31 | Level 2 | N/A
100025835223 | Pole | Tier 3 | Distribution | 2024-04-15 | 2024-10-31 | Level 2 | N/A
100025835227 | Pole | Tier 3 | Distribution | 2024-04-15 | 2024-10-31 | Level 2 | N/A
100025835228 | Other | Tier 3 | Distribution | 2024-04-15 | 2024-10-31 | Level 2 | N/A
100025837776 | Other | Tier 3 | Distribution | 2024-04-16 | 2024-10-31 | Level 2 | N/A
100025846326 | Anchor/Guy | Tier 3 | Distribution | 2024-04-17 | 2024-10-31 | Level 2 | N/A
100025847482 | Cross Arm | Tier 3 | Distribution | 2024-04-17 | 2024-10-31 | Level 2 | N/A
100025847483 | Pole | Tier 3 | Distribution | 2024-04-17 | 2024-10-31 | Level 2 | N/A
100025861956 | Cross Arm | Tier 3 | Distribution | 2024-04-19 | 2024-10-31 | Level 2 | N/A
100025875112 | Cross Arm | Tier 3 | Distribution | 2024-04-23 | 2024-10-31 | Level 2 | N/A
100025875113 | Pole | Tier 3 | Distribution | 2024-04-23 | 2024-10-31 | Level 2 | N/A
100025875114 | Pole | Tier 3 | Distribution | 2024-04-23 | 2024-10-31 | Level 2 | N/A
100025904630 | Pole | Tier 3 | Distribution | 2024-04-25 | 2024-10-31 | Level 2 | N/A
100025910778 | Pole | Tier 3 | Distribution | 2024-04-26 | 2024-10-31 | Level 2 | N/A
100025920496 | Pole | Tier 3 | Distribution | 2024-04-29 | 2024-10-31 | Level 2 | N/A
100025924820 | Cross Arm | Tier 3 | Distribution | 2024-04-30 | 2024-10-31 | Level 2 | N/A
100025924821 | Pole | Tier 3 | Distribution | 2024-04-30 | 2024-10-31 | Level 2 | N/A
100025925903 | Cross Arm | Tier 3 | Distribution | 2024-04-30 | 2024-10-31 | Level 2 | N/A
100024783489 | Pole | Tier 2 | Distribution | 2023-11-06 | 2024-11-30 | Level 2 | N/A
100024814992 | Pole | Tier 2 | Distribution | 2023-11-15 | 2024-11-30 | Level 2 | N/A
100024815172 | Pole | Tier 2 | Distribution | 2023-11-15 | 2024-11-30 | Level 2 | N/A
100024830829 | Pole | Tier 2 | Distribution | 2023-11-17 | 2024-11-30 | Level 2 | N/A
100024892056 | Pole | Tier 2 | Distribution | 2023-11-20 | 2024-11-30 | Level 2 | N/A
100024892418 | Pole | Tier 2 | Distribution | 2023-11-20 | 2024-11-30 | Level 2 | N/A
100025941092 | Cross Arm | Tier 3 | Distribution | 2024-05-01 | 2024-11-30 | Level 2 | N/A
100025947076 | Anchor/Guy | Tier 3 | Distribution | 2024-05-02 | 2024-11-30 | Level 2 | N/A
100025947776 | Pole | Tier 3 | Distribution | 2024-05-02 | 2024-11-30 | Level 2 | N/A
100025947781 | Cross Arm | Tier 3 | Distribution | 2024-05-02 | 2024-11-30 | Level 2 | N/A
100025948014 | Anchor/Guy | Tier 3 | Distribution | 2024-05-02 | 2024-11-30 | Level 2 | N/A
100025951302 | Cross Arm | Tier 3 | Distribution | 2024-05-03 | 2024-11-30 | Level 2 | N/A
100025952223 | Cross Arm | Tier 3 | Distribution | 2024-05-03 | 2024-11-30 | Level 2 | N/A
100025952224 | Pole | Tier 3 | Distribution | 2024-05-03 | 2024-11-30 | Level 2 | N/A
100025953009 | Pole | Tier 3 | Distribution | 2024-05-03 | 2024-11-30 | Level 2 | N/A
100025964194 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964350 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964351 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964638 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964639 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964640 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964779 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964800 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964801 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964913 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025964998 | Insulator and Bushing | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025966088 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025966164 | Pole | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025966165 | Cross Arm | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100025966166 | Anchor/Guy | Tier 3 | Distribution | 2024-05-07 | 2024-11-30 | Level 2 | N/A
100026036334 | Cross Arm | Tier 3 | Distribution | 2024-05-20 | 2024-11-30 | Level 2 | N/A
100026036335 | Cross Arm | Tier 3 | Distribution | 2024-05-20 | 2024-11-30 | Level 2 | N/A
100026090922 | Cross Arm | Tier 3 | Distribution | 2024-05-28 | 2024-11-30 | Level 2 | N/A
100026090923 | Pole | Tier 3 | Distribution | 2024-05-28 | 2024-11-30 | Level 2 | N/A
100026095102 | Cross Arm | Tier 3 | Distribution | 2024-05-28 | 2024-11-30 | Level 2 | N/A
100026095235 | Pole | Tier 3 | Distribution | 2024-05-28 | 2024-11-30 | Level 2 | N/A
100026114504 | Cross Arm | Tier 3 | Distribution | 2024-05-31 | 2024-11-30 | Level 2 | N/A
100026114569 | Cross Arm | Tier 3 | Distribution | 2024-05-31 | 2024-11-30 | Level 2 | N/A
100026138815 | Pole | Tier 3 | Distribution | 2024-06-04 | 2024-12-31 | Level 2 | N/A
100026140179 | Pole | Tier 3 | Distribution | 2024-06-04 | 2024-12-31 | Level 2 | N/A
100026180782 | Pole | Tier 3 | Distribution | 2024-06-12 | 2024-12-31 | Level 2 | N/A
100026184431 | Pole | Tier 3 | Distribution | 2024-06-13 | 2024-12-31 | Level 2 | N/A
100026184432 | Pole | Tier 3 | Distribution | 2024-06-13 | 2024-12-31 | Level 2 | N/A
100026184433 | Pole | Tier 3 | Distribution | 2024-06-13 | 2024-12-31 | Level 2 | N/A
100026194967 | Pole | Tier 3 | Distribution | 2024-06-10 | 2024-12-31 | Level 2 | N/A
100026201169 | Cross Arm | Tier 3 | Distribution | 2024-06-18 | 2024-12-31 | Level 2 | N/A
100026201301 | Cross Arm | Tier 3 | Distribution | 2024-06-18 | 2024-12-31 | Level 2 | N/A
100026206121 | Pole | Tier 3 | Distribution | 2024-06-19 | 2024-12-31 | Level 2 | N/A
100026206124 | Pole | Tier 3 | Distribution | 2024-06-19 | 2024-12-31 | Level 2 | N/A
100026206125 | Pole | Tier 3 | Distribution | 2024-06-19 | 2024-12-31 | Level 2 | N/A
100026206126 | Anchor/Guy | Tier 3 | Distribution | 2024-06-19 | 2024-12-31 | Level 2 | N/A
100026206129 | Cross Arm | Tier 3 | Distribution | 2024-06-19 | 2024-12-31 | Level 2 | N/A
100026220037 | Cross Arm | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026220039 | Pole | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026220061 | Pole | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026220438 | Pole | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026220439 | Pole | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026220770 | Other | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026220771 | Pole | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026223188 | Pole | Tier 3 | Distribution | 2024-06-21 | 2024-12-31 | Level 2 | N/A
100026230576 | Pole | Tier 3 | Distribution | 2024-06-24 | 2024-12-31 | Level 2 | N/A
100026230579 | Pole | Tier 3 | Distribution | 2024-06-24 | 2024-12-31 | Level 2 | N/A
100026230580 | Pole | Tier 3 | Distribution | 2024-06-24 | 2024-12-31 | Level 2 | N/A
100026230581 | Other | Tier 3 | Distribution | 2024-06-24 | 2024-12-31 | Level 2 | N/A
100026230583 | Pole | Tier 3 | Distribution | 2024-06-24 | 2024-12-31 | Level 2 | N/A
100026252252 | Pole | Tier 3 | Distribution | 2024-06-25 | 2024-12-31 | Level 2 | N/A
100026252253 | Cross Arm | Tier 3 | Distribution | 2024-06-25 | 2024-12-31 | Level 2 | N/A
100026252256 | Pole | Tier 3 | Distribution | 2024-06-25 | 2024-12-31 | Level 2 | N/A
100026252260 | Cross Arm | Tier 3 | Distribution | 2024-06-25 | 2024-12-31 | Level 2 | N/A
100026252797 | Pole | Tier 3 | Distribution | 2024-06-25 | 2024-12-31 | Level 2 | N/A
100026253048 | Pole | Tier 3 | Distribution | 2024-06-25 | 2024-12-31 | Level 2 | N/A
100026253049 | Pole | Tier 3 | Distribution | 2024-06-25 | 2024-12-31 | Level 2 | N/A
100026257677 | Cross Arm | Tier 3 | Distribution | 2024-06-26 | 2024-12-31 | Level 2 | N/A
100026257678 | Pole | Tier 3 | Distribution | 2024-06-26 | 2024-12-31 | Level 2 | N/A
100025268566 | Pole | Tier 2 | Distribution | 2024-01-02 | 2025-01-30 | Level 2 | N/A
100025422227 | Pole | Tier 2 | Distribution | 2024-01-24 | 2025-01-30 | Level 2 | N/A
100025434325 | Pole | Tier 2 | Distribution | 2024-01-30 | 2025-01-30 | Level 2 | N/A
100026283662 | Pole | Tier 3 | Distribution | 2024-07-01 | 2025-01-31 | Level 2 | N/A
100026313811 | Other | Tier 3 | Distribution | 2024-07-10 | 2025-01-31 | Level 2 | N/A
100026330560 | Pole | Tier 3 | Distribution | 2024-07-15 | 2025-01-31 | Level 2 | N/A
100026330562 | Conductor | Tier 3 | Distribution | 2024-07-15 | 2025-01-31 | Level 2 | N/A
100026359405 | Pole | Tier 3 | Distribution | 2024-07-18 | 2025-01-31 | Level 2 | N/A
100026359409 | Conductor | Tier 3 | Distribution | 2024-07-18 | 2025-01-31 | Level 2 | N/A
100025465847 | Cross Arm | Tier 2 | Distribution | 2024-02-02 | 2025-02-28 | Level 2 | N/A
100025465849 | Pole | Tier 2 | Distribution | 2024-02-02 | 2025-02-28 | Level 2 | N/A
100025469240 | Pole | Tier 2 | Distribution | 2024-02-02 | 2025-02-28 | Level 2 | N/A
100025489608 | Pole | Tier 2 | Distribution | 2024-02-05 | 2025-02-28 | Level 2 | N/A
100025506495 | Pole | Tier 2 | Distribution | 2024-02-10 | 2025-02-28 | Level 2 | N/A
100025506496 | Pole | Tier 2 | Distribution | 2024-02-10 | 2025-02-28 | Level 2 | N/A
100025521543 | Pole | Tier 2 | Distribution | 2024-02-15 | 2025-02-28 | Level 2 | N/A
100025521546 | Pole | Tier 2 | Distribution | 2024-02-15 | 2025-02-28 | Level 2 | N/A
100025522942 | Pole | Tier 2 | Distribution | 2024-02-15 | 2025-02-28 | Level 2 | N/A
100025526928 | Pole | Tier 2 | Distribution | 2024-02-16 | 2025-02-28 | Level 2 | N/A
100025543550 | Pole | Tier 2 | Distribution | 2024-02-21 | 2025-02-28 | Level 2 | N/A
100025544916 | Pole | Tier 2 | Distribution | 2024-02-21 | 2025-02-28 | Level 2 | N/A
100025544917 | Cross Arm | Tier 2 | Distribution | 2024-02-21 | 2025-02-28 | Level 2 | N/A
100025544918 | Pole | Tier 2 | Distribution | 2024-02-21 | 2025-02-28 | Level 2 | N/A
100025544950 | Pole | Tier 2 | Distribution | 2024-02-21 | 2025-02-28 | Level 2 | N/A
100025544951 | Pole | Tier 2 | Distribution | 2024-02-21 | 2025-02-28 | Level 2 | N/A
100025596658 | Insulator and Bushing | Tier 2 | Distribution | 2024-02-29 | 2025-02-28 | Level 2 | N/A
100025598865 | Pole | Tier 2 | Distribution | 2024-02-29 | 2025-02-28 | Level 2 | N/A
100025620387 | Pole | Tier 2 | Distribution | 2024-02-09 | 2025-02-28 | Level 2 | N/A
100025613304 | Cross Arm | Tier 2 | Distribution | 2024-03-01 | 2025-03-31 | Level 2 | N/A
100025614393 | Other | Tier 2 | Distribution | 2024-03-01 | 2025-03-31 | Level 2 | N/A
100025643243 | Pole | Tier 2 | Distribution | 2024-03-08 | 2025-03-31 | Level 2 | N/A
100025643246 | Other | Tier 2 | Distribution | 2024-03-08 | 2025-03-31 | Level 2 | N/A
100025643249 | Pole | Tier 2 | Distribution | 2024-03-08 | 2025-03-31 | Level 2 | N/A
100025656487 | Pole | Tier 2 | Distribution | 2024-03-12 | 2025-03-31 | Level 2 | N/A
100025656501 | Cross Arm | Tier 2 | Distribution | 2024-03-12 | 2025-03-31 | Level 2 | N/A
100025656502 | Cross Arm | Tier 2 | Distribution | 2024-03-12 | 2025-03-31 | Level 2 | N/A
100025656503 | Other | Tier 2 | Distribution | 2024-03-12 | 2025-03-31 | Level 2 | N/A
100025656507 | Cross Arm | Tier 2 | Distribution | 2024-03-12 | 2025-03-31 | Level 2 | N/A
100025664753 | Other | Tier 2 | Distribution | 2024-03-13 | 2025-03-31 | Level 2 | N/A
100025664757 | Cross Arm | Tier 2 | Distribution | 2024-03-13 | 2025-03-31 | Level 2 | N/A
100025664759 | Insulator and Bushing | Tier 2 | Distribution | 2024-03-13 | 2025-03-31 | Level 2 | N/A
100025664760 | Cross Arm | Tier 2 | Distribution | 2024-03-13 | 2025-03-31 | Level 2 | N/A
100025664762 | Pole | Tier 2 | Distribution | 2024-03-13 | 2025-03-31 | Level 2 | N/A
100025670568 | Pole | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025670714 | Pole | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025670718 | Pole | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025671463 | Anchor/Guy | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025673672 | Pole | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025673673 | Other | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025673674 | Cross Arm | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025673675 | Pole | Tier 2 | Distribution | 2024-03-14 | 2025-03-31 | Level 2 | N/A
100025679598 | Conductor | Tier 2 | Distribution | 2024-03-15 | 2025-03-31 | Level 2 | N/A
100025679973 | Pole | Tier 2 | Distribution | 2024-03-15 | 2025-03-31 | Level 2 | N/A
100025679977 | Pole | Tier 2 | Distribution | 2024-03-15 | 2025-03-31 | Level 2 | N/A
100025679978 | Pole | Tier 2 | Distribution | 2024-03-15 | 2025-03-31 | Level 2 | N/A
100025680173 | Pole | Tier 2 | Distribution | 2024-03-15 | 2025-03-31 | Level 2 | N/A
100025684401 | Pole | Tier 2 | Distribution | 2024-03-18 | 2025-03-31 | Level 2 | N/A
100025684407 | Pole | Tier 2 | Distribution | 2024-03-18 | 2025-03-31 | Level 2 | N/A
100025684883 | Other | Tier 2 | Distribution | 2024-03-18 | 2025-03-31 | Level 2 | N/A
100025686576 | Conductor | Tier 2 | Distribution | 2024-03-18 | 2025-03-31 | Level 2 | N/A
100025690362 | Pole | Tier 2 | Distribution | 2024-03-19 | 2025-03-31 | Level 2 | N/A
100025691622 | Pole | Tier 2 | Distribution | 2024-03-19 | 2025-03-31 | Level 2 | N/A
100025691623 | Cross Arm | Tier 2 | Distribution | 2024-03-19 | 2025-03-31 | Level 2 | N/A
100025691725 | Cross Arm | Tier 2 | Distribution | 2024-03-19 | 2025-03-31 | Level 2 | N/A
100025701635 | Pole | Tier 2 | Distribution | 2024-03-20 | 2025-03-31 | Level 2 | N/A
100025701637 | Cross Arm | Tier 2 | Distribution | 2024-03-20 | 2025-03-31 | Level 2 | N/A
100025701639 | Cross Arm | Tier 2 | Distribution | 2024-03-20 | 2025-03-31 | Level 2 | N/A
100025701641 | Other | Tier 2 | Distribution | 2024-03-20 | 2025-03-31 | Level 2 | N/A
100025702637 | Other | Tier 2 | Distribution | 2024-03-20 | 2025-03-31 | Level 2 | N/A
100025702638 | Pole | Tier 2 | Distribution | 2024-03-20 | 2025-03-31 | Level 2 | N/A
100025706888 | Conductor | Tier 2 | Distribution | 2024-03-21 | 2025-03-31 | Level 2 | N/A
100025707253 | Pole | Tier 2 | Distribution | 2024-03-21 | 2025-03-31 | Level 2 | N/A
100025707261 | Other | Tier 2 | Distribution | 2024-03-21 | 2025-03-31 | Level 2 | N/A
100025707374 | Anchor/Guy | Tier 2 | Distribution | 2024-03-21 | 2025-03-31 | Level 2 | N/A
100025711862 | Cross Arm | Tier 2 | Distribution | 2024-03-22 | 2025-03-31 | Level 2 | N/A
100025711863 | Cross Arm | Tier 2 | Distribution | 2024-03-22 | 2025-03-31 | Level 2 | N/A
100025743996 | Pole | Tier 2 | Distribution | 2024-03-25 | 2025-03-31 | Level 2 | N/A
100025743998 | Cross Arm | Tier 2 | Distribution | 2024-03-25 | 2025-03-31 | Level 2 | N/A
100025745041 | Cross Arm | Tier 2 | Distribution | 2024-03-25 | 2025-03-31 | Level 2 | N/A
100025745043 | Pole | Tier 2 | Distribution | 2024-03-25 | 2025-03-31 | Level 2 | N/A
100025745745 | Cross Arm | Tier 2 | Distribution | 2024-03-25 | 2025-03-31 | Level 2 | N/A
100025745746 | Pole | Tier 2 | Distribution | 2024-03-25 | 2025-03-31 | Level 2 | N/A
100025745747 | Other | Tier 2 | Distribution | 2024-03-25 | 2025-03-31 | Level 2 | N/A
100025749918 | Other | Tier 2 | Distribution | 2024-03-26 | 2025-03-31 | Level 2 | N/A
100025750416 | Other | Tier 2 | Distribution | 2024-03-26 | 2025-03-31 | Level 2 | N/A
100025750812 | Other | Tier 2 | Distribution | 2024-03-26 | 2025-03-31 | Level 2 | N/A
100025750814 | Other | Tier 2 | Distribution | 2024-03-26 | 2025-03-31 | Level 2 | N/A
100025751963 | Pole | Tier 2 | Distribution | 2024-03-26 | 2025-03-31 | Level 2 | N/A
100025759597 | Pole | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025759598 | Anchor/Guy | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025759599 | Cross Arm | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025760031 | Cross Arm | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025760034 | Anchor/Guy | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025760035 | Cross Arm | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025760519 | Cross Arm | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025762540 | Other | Tier 2 | Distribution | 2024-03-28 | 2025-03-31 | Level 2 | N/A
100025765374 | Pole | Tier 2 | Distribution | 2024-03-29 | 2025-03-31 | Level 2 | N/A
100026555434 | Cross Arm | Tier 3 | Distribution | 2024-09-03 | 2025-03-31 | Level 2 | N/A
100026555435 | Cross Arm | Tier 3 | Distribution | 2024-09-03 | 2025-03-31 | Level 2 | N/A
100026555436 | Cross Arm | Tier 3 | Distribution | 2024-09-03 | 2025-03-31 | Level 2 | N/A
100026558716 | Pole | Tier 3 | Distribution | 2024-09-04 | 2025-03-31 | Level 2 | N/A
100026560975 | Pole | Tier 3 | Distribution | 2024-09-05 | 2025-03-31 | Level 2 | N/A
100026577215 | Conductor | Tier 3 | Distribution | 2024-09-11 | 2025-03-31 | Level 2 | N/A
100026603996 | Conductor | Tier 3 | Distribution | 2024-07-17 | 2025-03-31 | Level 2 | N/A
100026603999 | Conductor | Tier 3 | Distribution | 2024-09-19 | 2025-03-31 | Level 2 | N/A
100025783681 | Cross Arm | Tier 2 | Distribution | 2024-04-01 | 2025-04-28 | Level 2 | N/A
100025783683 | Cross Arm | Tier 2 | Distribution | 2024-04-01 | 2025-04-28 | Level 2 | N/A
100025786319 | Pole | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025786510 | Anchor/Guy | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025787909 | Pole | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025788080 | Cross Arm | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025788081 | Cross Arm | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025788082 | Pole | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025788628 | Pole | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025790810 | Pole | Tier 2 | Distribution | 2024-04-02 | 2025-04-28 | Level 2 | N/A
100025791857 | Pole | Tier 2 | Distribution | 2024-04-03 | 2025-04-28 | Level 2 | N/A
100025792759 | Anchor/Guy | Tier 2 | Distribution | 2024-04-03 | 2025-04-28 | Level 2 | N/A
100025793054 | Conductor | Tier 2 | Distribution | 2024-04-03 | 2025-04-28 | Level 2 | N/A
100025793753 | Conductor | Tier 2 | Distribution | 2024-04-03 | 2025-04-28 | Level 2 | N/A
100025793754 | Conductor | Tier 2 | Distribution | 2024-04-03 | 2025-04-28 | Level 2 | N/A
100025793757 | Other | Tier 2 | Distribution | 2024-04-03 | 2025-04-28 | Level 2 | N/A
100025793880 | Conductor | Tier 2 | Distribution | 2024-04-03 | 2025-04-28 | Level 2 | N/A
100025796184 | Pole | Tier 2 | Distribution | 2024-04-04 | 2025-04-28 | Level 2 | N/A
100025798115 | Conductor | Tier 2 | Distribution | 2024-04-04 | 2025-04-28 | Level 2 | N/A
100025798117 | Conductor | Tier 2 | Distribution | 2024-04-04 | 2025-04-28 | Level 2 | N/A
100025798710 | Pole | Tier 2 | Distribution | 2024-04-04 | 2025-04-28 | Level 2 | N/A
100025798712 | Pole | Tier 2 | Distribution | 2024-04-04 | 2025-04-28 | Level 2 | N/A
100025798713 | Pole | Tier 2 | Distribution | 2024-04-04 | 2025-04-28 | Level 2 | N/A
100025799012 | Pole | Tier 2 | Distribution | 2024-04-04 | 2025-04-28 | Level 2 | N/A
100025801253 | Pole | Tier 2 | Distribution | 2024-04-05 | 2025-04-28 | Level 2 | N/A
100025801255 | Conductor | Tier 2 | Distribution | 2024-04-05 | 2025-04-28 | Level 2 | N/A
100025801256 | Pole | Tier 2 | Distribution | 2024-04-05 | 2025-04-28 | Level 2 | N/A
100025805769 | Pole | Tier 2 | Distribution | 2024-04-08 | 2025-04-28 | Level 2 | N/A
100025806180 | Pole | Tier 2 | Distribution | 2024-04-08 | 2025-04-28 | Level 2 | N/A
100025806181 | Pole | Tier 2 | Distribution | 2024-04-08 | 2025-04-28 | Level 2 | N/A
100025806182 | Pole | Tier 2 | Distribution | 2024-04-08 | 2025-04-28 | Level 2 | N/A
100025806184 | Pole | Tier 2 | Distribution | 2024-04-08 | 2025-04-28 | Level 2 | N/A
100025806185 | Pole | Tier 2 | Distribution | 2024-04-08 | 2025-04-28 | Level 2 | N/A
100025806186 | Pole | Tier 2 | Distribution | 2024-04-08 | 2025-04-28 | Level 2 | N/A
100025810830 | Pole | Tier 2 | Distribution | 2024-04-09 | 2025-04-28 | Level 2 | N/A
100025810831 | Pole | Tier 2 | Distribution | 2024-04-09 | 2025-04-28 | Level 2 | N/A
100025811090 | Pole | Tier 2 | Distribution | 2024-04-09 | 2025-04-28 | Level 2 | N/A
100025811091 | Pole | Tier 2 | Distribution | 2024-04-09 | 2025-04-28 | Level 2 | N/A
100025811092 | Pole | Tier 2 | Distribution | 2024-04-09 | 2025-04-28 | Level 2 | N/A
100025811298 | Pole | Tier 2 | Distribution | 2024-04-09 | 2025-04-28 | Level 2 | N/A
100025816909 | Conductor | Tier 2 | Distribution | 2024-04-10 | 2025-04-28 | Level 2 | N/A
100025817167 | Conductor | Tier 2 | Distribution | 2024-04-10 | 2025-04-28 | Level 2 | N/A
100025822708 | Conductor | Tier 2 | Distribution | 2024-04-11 | 2025-04-28 | Level 2 | N/A
100025834506 | Other | Tier 2 | Distribution | 2024-04-15 | 2025-04-28 | Level 2 | N/A
100025835331 | Anchor/Guy | Tier 2 | Distribution | 2024-04-15 | 2025-04-28 | Level 2 | N/A
100025838453 | Pole | Tier 2 | Distribution | 2024-04-16 | 2025-04-28 | Level 2 | N/A
100025838454 | Pole | Tier 2 | Distribution | 2024-04-16 | 2025-04-28 | Level 2 | N/A
100025838456 | Pole | Tier 2 | Distribution | 2024-04-16 | 2025-04-28 | Level 2 | N/A
100025840127 | Conductor | Tier 2 | Distribution | 2024-04-16 | 2025-04-28 | Level 2 | N/A
100025842115 | Pole | Tier 2 | Distribution | 2024-04-16 | 2025-04-28 | Level 2 | N/A
100025845314 | Pole | Tier 2 | Distribution | 2024-04-17 | 2025-04-28 | Level 2 | N/A
100025850496 | Cross Arm | Tier 2 | Distribution | 2024-04-18 | 2025-04-28 | Level 2 | N/A
100025850701 | Pole | Tier 2 | Distribution | 2024-04-18 | 2025-04-28 | Level 2 | N/A
100025851394 | Cross Arm | Tier 2 | Distribution | 2024-04-18 | 2025-04-28 | Level 2 | N/A
100025867593 | Pole | Tier 2 | Distribution | 2024-04-22 | 2025-04-28 | Level 2 | N/A
100025869604 | Other | Tier 2 | Distribution | 2024-04-22 | 2025-04-28 | Level 2 | N/A
100025869686 | Pole | Tier 2 | Distribution | 2024-04-22 | 2025-04-28 | Level 2 | N/A
100025871214 | Cross Arm | Tier 2 | Distribution | 2024-04-22 | 2025-04-28 | Level 2 | N/A
100025871297 | Pole | Tier 2 | Distribution | 2024-04-22 | 2025-04-28 | Level 2 | N/A
100025874343 | Cross Arm | Tier 2 | Distribution | 2024-04-23 | 2025-04-28 | Level 2 | N/A
100025874345 | Cross Arm | Tier 2 | Distribution | 2024-04-23 | 2025-04-28 | Level 2 | N/A
100025874454 | Anchor/Guy | Tier 2 | Distribution | 2024-04-23 | 2025-04-28 | Level 2 | N/A
100025875059 | Cross Arm | Tier 2 | Distribution | 2024-04-23 | 2025-04-28 | Level 2 | N/A
100025875059 | Cross Arm | Tier 2 | Distribution | 2024-04-23 | 2025-04-28 | Level 2 | N/A
100025875064 | Pole | Tier 2 | Distribution | 2024-04-23 | 2025-04-28 | Level 2 | N/A
100025875064 | Pole | Tier 2 | Distribution | 2024-04-23 | 2025-04-28 | Level 2 | N/A
100025882090 | Pole | Tier 2 | Distribution | 2024-04-24 | 2025-04-28 | Level 2 | N/A
100025882454 | Pole | Tier 2 | Distribution | 2024-04-24 | 2025-04-28 | Level 2 | N/A
100025882455 | Pole | Tier 2 | Distribution | 2024-04-24 | 2025-04-28 | Level 2 | N/A
100025883029 | Other | Tier 2 | Distribution | 2024-04-24 | 2025-04-28 | Level 2 | N/A
100025883031 | Other | Tier 2 | Distribution | 2024-04-24 | 2025-04-28 | Level 2 | N/A
100025904432 | Pole | Tier 2 | Distribution | 2024-04-25 | 2025-04-28 | Level 2 | N/A
100025904433 | Pole | Tier 2 | Distribution | 2024-04-25 | 2025-04-28 | Level 2 | N/A
100025904486 | Pole | Tier 2 | Distribution | 2024-04-25 | 2025-04-28 | Level 2 | N/A
100025905277 | Pole | Tier 2 | Distribution | 2024-04-25 | 2025-04-28 | Level 2 | N/A
100025905431 | Conductor | Tier 2 | Distribution | 2024-04-25 | 2025-04-28 | Level 2 | N/A
100025905847 | Pole | Tier 2 | Distribution | 2024-04-25 | 2025-04-28 | Level 2 | N/A
100025905851 | Conductor | Tier 2 | Distribution | 2024-04-25 | 2025-04-28 | Level 2 | N/A
100025910559 | Pole | Tier 2 | Distribution | 2024-04-09 | 2025-04-28 | Level 2 | N/A
100025911539 | Other | Tier 2 | Distribution | 2024-04-26 | 2025-04-28 | Level 2 | N/A
100025911585 | Insulator and Bushing | Tier 2 | Distribution | 2024-04-26 | 2025-04-28 | Level 2 | N/A
100025911586 | Conductor | Tier 2 | Distribution | 2024-04-26 | 2025-04-28 | Level 2 | N/A
100025919289 | Conductor | Tier 2 | Distribution | 2024-04-29 | 2025-04-28 | Level 2 | N/A
100025926232 | Anchor/Guy | Tier 2 | Distribution | 2024-04-30 | 2025-04-28 | Level 2 | N/A
100025926233 | Pole | Tier 2 | Distribution | 2024-04-30 | 2025-04-28 | Level 2 | N/A
100025926874 | Pole | Tier 2 | Distribution | 2024-04-30 | 2025-04-28 | Level 2 | N/A
100025942071 | Pole | Tier 2 | Distribution | 2024-05-01 | 2025-05-31 | Level 2 | N/A
100025945668 | Conductor | Tier 2 | Distribution | 2024-05-02 | 2025-05-31 | Level 2 | N/A
100025945669 | Pole | Tier 2 | Distribution | 2024-05-02 | 2025-05-31 | Level 2 | N/A
100025953145 | Cross Arm | Tier 2 | Distribution | 2024-05-03 | 2025-05-31 | Level 2 | N/A
100025959207 | Other | Tier 2 | Distribution | 2024-05-06 | 2025-05-31 | Level 2 | N/A
100025959603 | Pole | Tier 2 | Distribution | 2024-05-06 | 2025-05-31 | Level 2 | N/A
100025959623 | Other | Tier 2 | Distribution | 2024-05-06 | 2025-05-31 | Level 2 | N/A
100025969053 | Pole | Tier 2 | Distribution | 2024-05-08 | 2025-05-31 | Level 2 | N/A
100025979542 | Pole | Tier 2 | Distribution | 2024-05-10 | 2025-05-31 | Level 2 | N/A
100025979543 | Anchor/Guy | Tier 2 | Distribution | 2024-05-10 | 2025-05-31 | Level 2 | N/A
100025979544 | Pole | Tier 2 | Distribution | 2024-05-10 | 2025-05-31 | Level 2 | N/A
100025979546 | Pole | Tier 2 | Distribution | 2024-05-10 | 2025-05-31 | Level 2 | N/A
100025979548 | Pole | Tier 2 | Distribution | 2024-05-10 | 2025-05-31 | Level 2 | N/A
100025979549 | Anchor/Guy | Tier 2 | Distribution | 2024-05-10 | 2025-05-31 | Level 2 | N/A
100025990639 | Other | Tier 2 | Distribution | 2024-05-13 | 2025-05-31 | Level 2 | N/A
100025993153 | Pole | Tier 2 | Distribution | 2024-05-13 | 2025-05-31 | Level 2 | N/A
100025996124 | Cross Arm | Tier 2 | Distribution | 2024-05-14 | 2025-05-31 | Level 2 | N/A
100025996418 | Pole | Tier 2 | Distribution | 2024-05-14 | 2025-05-31 | Level 2 | N/A
100025996630 | Cross Arm | Tier 2 | Distribution | 2024-05-14 | 2025-05-31 | Level 2 | N/A
100025996632 | Conductor | Tier 2 | Distribution | 2024-05-14 | 2025-05-31 | Level 2 | N/A
100025996636 | Conductor | Tier 2 | Distribution | 2024-05-14 | 2025-05-31 | Level 2 | N/A
100026009131 | Pole | Tier 2 | Distribution | 2024-05-15 | 2025-05-31 | Level 2 | N/A
100026018163 | Pole | Tier 2 | Distribution | 2024-05-16 | 2025-05-31 | Level 2 | N/A
100026018165 | Pole | Tier 2 | Distribution | 2024-05-16 | 2025-05-31 | Level 2 | N/A
100026034806 | Anchor/Guy | Tier 2 | Distribution | 2024-05-20 | 2025-05-31 | Level 2 | N/A
100026044689 | Pole | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026044721 | Pole | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026045484 | Other | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026045486 | Pole | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026049943 | Pole | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026049944 | Cross Arm | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026049945 | Pole | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026049946 | Cross Arm | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026049947 | Cross Arm | Tier 2 | Distribution | 2024-05-21 | 2025-05-31 | Level 2 | N/A
100026053659 | Pole | Tier 2 | Distribution | 2024-05-23 | 2025-05-31 | Level 2 | N/A
100026054305 | Cross Arm | Tier 2 | Distribution | 2024-05-23 | 2025-05-31 | Level 2 | N/A
100026054308 | Anchor/Guy | Tier 2 | Distribution | 2024-05-23 | 2025-05-31 | Level 2 | N/A
100026104581 | Other | Tier 2 | Distribution | 2024-05-29 | 2025-05-31 | Level 2 | N/A
100026107812 | Pole | Tier 2 | Distribution | 2024-05-30 | 2025-05-31 | Level 2 | N/A
100026108720 | Anchor/Guy | Tier 2 | Distribution | 2024-05-30 | 2025-05-31 | Level 2 | N/A
100026109117 | Conductor | Tier 2 | Distribution | 2024-05-30 | 2025-05-31 | Level 2 | N/A
100026110101 | Anchor/Guy | Tier 2 | Distribution | 2024-05-30 | 2025-05-31 | Level 2 | N/A
100026110102 | Other | Tier 2 | Distribution | 2024-05-30 | 2025-05-31 | Level 2 | N/A
100026110106 | Cross Arm | Tier 2 | Distribution | 2024-05-30 | 2025-05-31 | Level 2 | N/A
100026117517 | Conductor | Tier 2 | Distribution | 2024-05-31 | 2025-05-31 | Level 2 | N/A
100026132409 | Cross Arm | Tier 2 | Distribution | 2024-06-03 | 2025-06-30 | Level 2 | N/A
100026132564 | Cross Arm | Tier 2 | Distribution | 2024-06-03 | 2025-06-30 | Level 2 | N/A
100026132566 | Conductor | Tier 2 | Distribution | 2024-06-03 | 2025-06-30 | Level 2 | N/A
100026133581 | Pole | Tier 2 | Distribution | 2024-06-03 | 2025-06-30 | Level 2 | N/A
100026137885 | Pole | Tier 2 | Distribution | 2024-06-04 | 2025-06-30 | Level 2 | N/A
100026138084 | Conductor | Tier 2 | Distribution | 2024-06-04 | 2025-06-30 | Level 2 | N/A
100026138089 | Cross Arm | Tier 2 | Distribution | 2024-06-04 | 2025-06-30 | Level 2 | N/A
100026138090 | Conductor | Tier 2 | Distribution | 2024-06-04 | 2025-06-30 | Level 2 | N/A
100026138091 | Pole | Tier 2 | Distribution | 2024-06-04 | 2025-06-30 | Level 2 | N/A
100026140134 | Pole | Tier 2 | Distribution | 2024-06-04 | 2025-06-30 | Level 2 | N/A
100026142929 | Other | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026143282 | Other | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026143413 | Other | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026143654 | Pole | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026144330 | Conductor | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026144331 | Cross Arm | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026144333 | Cross Arm | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026144553 | Other | Tier 2 | Distribution | 2024-06-05 | 2025-06-30 | Level 2 | N/A
100026170137 | Other | Tier 2 | Distribution | 2024-06-11 | 2025-06-30 | Level 2 | N/A
100026170138 | Cross Arm | Tier 2 | Distribution | 2024-06-11 | 2025-06-30 | Level 2 | N/A
100026170139 | Pole | Tier 2 | Distribution | 2024-06-11 | 2025-06-30 | Level 2 | N/A
100026170877 | Insulator and Bushing | Tier 2 | Distribution | 2024-06-11 | 2025-06-30 | Level 2 | N/A
100026171300 | Pole | Tier 2 | Distribution | 2024-06-11 | 2025-06-30 | Level 2 | N/A
100026174776 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026174777 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026175279 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026175680 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026176230 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026176350 | Cross Arm | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026176351 | Other | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026176352 | Other | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026176880 | Other | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026176883 | Cross Arm | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026177016 | Cross Arm | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026181577 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026181578 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026181607 | Pole | Tier 2 | Distribution | 2024-06-12 | 2025-06-30 | Level 2 | N/A
100026185289 | Anchor/Guy | Tier 2 | Distribution | 2024-06-13 | 2025-06-30 | Level 2 | N/A
100026185360 | Pole | Tier 2 | Distribution | 2024-06-13 | 2025-06-30 | Level 2 | N/A
100026185361 | Other | Tier 2 | Distribution | 2024-06-13 | 2025-06-30 | Level 2 | N/A
100026185364 | Anchor/Guy | Tier 2 | Distribution | 2024-06-13 | 2025-06-30 | Level 2 | N/A
100026185369 | Other | Tier 2 | Distribution | 2024-06-13 | 2025-06-30 | Level 2 | N/A
100026196492 | Pole | Tier 2 | Distribution | 2024-06-13 | 2025-06-30 | Level 2 | N/A
100026200701 | Pole | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026200779 | Conductor | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026200870 | Pole | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026200872 | Conductor | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026200873 | Conductor | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026201559 | Pole | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026201763 | Other | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026205394 | Conductor | Tier 2 | Distribution | 2024-06-19 | 2025-06-30 | Level 2 | N/A
100026205986 | Conductor | Tier 2 | Distribution | 2024-06-19 | 2025-06-30 | Level 2 | N/A
100026205988 | Pole | Tier 2 | Distribution | 2024-06-19 | 2025-06-30 | Level 2 | N/A
100026205989 | Cross Arm | Tier 2 | Distribution | 2024-06-19 | 2025-06-30 | Level 2 | N/A
100026207104 | Pole | Tier 2 | Distribution | 2024-06-19 | 2025-06-30 | Level 2 | N/A
100026219997 | Pole | Tier 2 | Distribution | 2024-06-21 | 2025-06-30 | Level 2 | N/A
100026228966 | Pole | Tier 2 | Distribution | 2024-06-18 | 2025-06-30 | Level 2 | N/A
100026257679 | Cross Arm | Tier 2 | Distribution | 2024-06-26 | 2025-06-30 | Level 2 | N/A
100026258072 | Cross Arm | Tier 2 | Distribution | 2024-06-26 | 2025-06-30 | Level 2 | N/A
100026258073 | Pole | Tier 2 | Distribution | 2024-06-26 | 2025-06-30 | Level 2 | N/A
100026258598 | Pole | Tier 2 | Distribution | 2024-06-26 | 2025-06-30 | Level 2 | N/A
100026266358 | Cross Arm | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026266359 | Conductor | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267708 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267781 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267784 | Cross Arm | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267786 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267790 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267793 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267796 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267799 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267899 | Cross Arm | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026267963 | Pole | Tier 2 | Distribution | 2024-06-28 | 2025-06-30 | Level 2 | N/A
100026317004 | Pole | Tier 2 | Distribution | 2024-06-25 | 2025-06-30 | Level 2 | N/A
100026289760 | Pole | Tier 2 | Distribution | 2024-07-02 | 2025-07-31 | Level 2 | N/A
100026309123 | Conductor | Tier 2 | Distribution | 2024-07-09 | 2025-07-31 | Level 2 | N/A
100026309380 | Conductor | Tier 2 | Distribution | 2024-07-09 | 2025-07-31 | Level 2 | N/A
100026309825 | Pole | Tier 2 | Distribution | 2024-07-09 | 2025-07-31 | Level 2 | N/A
100026309828 | Anchor/Guy | Tier 2 | Distribution | 2024-07-09 | 2025-07-31 | Level 2 | N/A
100026312941 | Cross Arm | Tier 2 | Distribution | 2024-07-10 | 2025-07-31 | Level 2 | N/A
100026312945 | Pole | Tier 2 | Distribution | 2024-07-10 | 2025-07-31 | Level 2 | N/A
100026312950 | Other | Tier 2 | Distribution | 2024-07-10 | 2025-07-31 | Level 2 | N/A
100026313787 | Conductor | Tier 2 | Distribution | 2024-07-10 | 2025-07-31 | Level 2 | N/A
100026313788 | Conductor | Tier 2 | Distribution | 2024-07-10 | 2025-07-31 | Level 2 | N/A
100026318150 | Pole | Tier 2 | Distribution | 2024-07-11 | 2025-07-31 | Level 2 | N/A
100026322603 | Other | Tier 2 | Distribution | 2024-07-12 | 2025-07-31 | Level 2 | N/A
100026322806 | Anchor/Guy | Tier 2 | Distribution | 2024-07-12 | 2025-07-31 | Level 2 | N/A
100026328273 | Anchor/Guy | Tier 2 | Distribution | 2024-07-15 | 2025-07-31 | Level 2 | N/A
100026328275 | Anchor/Guy | Tier 2 | Distribution | 2024-07-15 | 2025-07-31 | Level 2 | N/A
100026329591 | Anchor/Guy | Tier 2 | Distribution | 2024-07-15 | 2025-07-31 | Level 2 | N/A
100026334277 | Other | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334278 | Cross Arm | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334279 | Pole | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334300 | Other | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334301 | Pole | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334306 | Anchor/Guy | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334307 | Pole | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334744 | Cross Arm | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334746 | Cross Arm | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026334900 | Other | Tier 2 | Distribution | 2024-07-16 | 2025-07-31 | Level 2 | N/A
100026338714 | Anchor/Guy | Tier 2 | Distribution | 2024-07-17 | 2025-07-31 | Level 2 | N/A
100026339019 | Other | Tier 2 | Distribution | 2024-07-17 | 2025-07-31 | Level 2 | N/A
100026339040 | Other | Tier 2 | Distribution | 2024-07-17 | 2025-07-31 | Level 2 | N/A
100026362230 | Anchor/Guy | Tier 2 | Distribution | 2024-07-22 | 2025-07-31 | Level 2 | N/A
100026362232 | Cross Arm | Tier 2 | Distribution | 2024-07-22 | 2025-07-31 | Level 2 | N/A
100026372669 | Cross Arm | Tier 2 | Distribution | 2024-07-24 | 2025-07-31 | Level 2 | N/A
100026372721 | Pole | Tier 2 | Distribution | 2024-07-24 | 2025-07-31 | Level 2 | N/A
100026373019 | Conductor | Tier 2 | Distribution | 2024-07-24 | 2025-07-31 | Level 2 | N/A
100026373060 | Cross Arm | Tier 2 | Distribution | 2024-07-24 | 2025-07-31 | Level 2 | N/A
100026373190 | Pole | Tier 2 | Distribution | 2024-07-24 | 2025-07-31 | Level 2 | N/A
100026373571 | Pole | Tier 2 | Distribution | 2024-07-24 | 2025-07-31 | Level 2 | N/A
100026374171 | Pole | Tier 2 | Distribution | 2024-07-23 | 2025-07-31 | Level 2 | N/A
100026381509 | Pole | Tier 2 | Distribution | 2024-07-25 | 2025-07-31 | Level 2 | N/A
100026404801 | Other | Tier 2 | Distribution | 2024-07-29 | 2025-07-31 | Level 2 | N/A
100026404802 | Cross Arm | Tier 2 | Distribution | 2024-07-29 | 2025-07-31 | Level 2 | N/A
100026404803 | Pole | Tier 2 | Distribution | 2024-07-29 | 2025-07-31 | Level 2 | N/A
100026407664 | Anchor/Guy | Tier 2 | Distribution | 2024-07-30 | 2025-07-31 | Level 2 | N/A
100026408976 | Pole | Tier 2 | Distribution | 2024-07-30 | 2025-07-31 | Level 2 | N/A
100026409620 | Pole | Tier 2 | Distribution | 2024-07-30 | 2025-07-31 | Level 2 | N/A
100026409625 | Other | Tier 2 | Distribution | 2024-07-30 | 2025-07-31 | Level 2 | N/A
100026413197 | Pole | Tier 2 | Distribution | 2024-07-31 | 2025-07-31 | Level 2 | N/A
100026413199 | Pole | Tier 2 | Distribution | 2024-07-31 | 2025-07-31 | Level 2 | N/A
100026428384 | Anchor/Guy | Tier 2 | Distribution | 2024-07-15 | 2025-07-31 | Level 2 | N/A
100026428237 | Anchor/Guy | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026428718 | Other | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026428950 | Other | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026428954 | Other | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026428955 | Other | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026429749 | Cross Arm | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026429750 | Cross Arm | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026429751 | Anchor/Guy | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026429753 | Other | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026429845 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026430231 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026430323 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026430324 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026430341 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026430342 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026430344 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026430807 | Pole | Tier 2 | Distribution | 2024-08-01 | 2025-08-30 | Level 2 | N/A
100026431617 | Pole | Tier 2 | Distribution | 2024-08-02 | 2025-08-30 | Level 2 | N/A
100026432911 | Other | Tier 2 | Distribution | 2024-08-02 | 2025-08-30 | Level 2 | N/A
100026434088 | Pole | Tier 2 | Distribution | 2024-08-02 | 2025-08-30 | Level 2 | N/A
100026434089 | Pole | Tier 2 | Distribution | 2024-08-02 | 2025-08-30 | Level 2 | N/A
100026435946 | Anchor/Guy | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026435947 | Anchor/Guy | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026436139 | Other | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026436241 | Cross Arm | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026436242 | Other | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026436498 | Conductor | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026436705 | Conductor | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026436706 | Conductor | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026436707 | Other | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437049 | Conductor | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437105 | Pole | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437107 | Cross Arm | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437295 | Conductor | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437296 | Conductor | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437297 | Pole | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437353 | Pole | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437414 | Cross Arm | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026437473 | Pole | Tier 2 | Distribution | 2024-08-05 | 2025-08-30 | Level 2 | N/A
100026441611 | Pole | Tier 2 | Distribution | 2024-08-06 | 2025-08-30 | Level 2 | N/A
100026444148 | Insulator and Bushing | Tier 2 | Distribution | 2024-08-07 | 2025-08-30 | Level 2 | N/A
100026444149 | Pole | Tier 2 | Distribution | 2024-08-07 | 2025-08-30 | Level 2 | N/A
100026445090 | Pole | Tier 2 | Distribution | 2024-08-07 | 2025-08-30 | Level 2 | N/A
100026450093 | Other | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026450093 | Other | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026451224 | Pole | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026451225 | Pole | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026451226 | Conductor | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026451227 | Conductor | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026451966 | Pole | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026452806 | Cross Arm | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026452863 | Cross Arm | Tier 2 | Distribution | 2024-08-08 | 2025-08-30 | Level 2 | N/A
100026455267 | Other | Tier 2 | Distribution | 2024-08-09 | 2025-08-30 | Level 2 | N/A
100026455703 | Insulator and Bushing | Tier 2 | Distribution | 2024-08-09 | 2025-08-30 | Level 2 | N/A
100026455704 | Cross Arm | Tier 2 | Distribution | 2024-08-09 | 2025-08-30 | Level 2 | N/A
100026456007 | Other | Tier 2 | Distribution | 2024-08-09 | 2025-08-30 | Level 2 | N/A
100026456328 | Insulator and Bushing | Tier 2 | Distribution | 2024-08-09 | 2025-08-30 | Level 2 | N/A
100026456329 | Pole | Tier 2 | Distribution | 2024-08-09 | 2025-08-30 | Level 2 | N/A
100026456480 | Cross Arm | Tier 2 | Distribution | 2024-08-09 | 2025-08-30 | Level 2 | N/A
100026460815 | Pole | Tier 2 | Distribution | 2024-08-12 | 2025-08-30 | Level 2 | N/A
100026463928 | Other | Tier 2 | Distribution | 2024-08-13 | 2025-08-30 | Level 2 | N/A
100026464336 | Pole | Tier 2 | Distribution | 2024-08-13 | 2025-08-30 | Level 2 | N/A
100026464838 | Pole | Tier 2 | Distribution | 2024-08-13 | 2025-08-30 | Level 2 | N/A
100026464839 | Pole | Tier 2 | Distribution | 2024-08-13 | 2025-08-30 | Level 2 | N/A
100026473698 | Pole | Tier 2 | Distribution | 2024-08-15 | 2025-08-30 | Level 2 | N/A
100026474695 | Other | Tier 2 | Distribution | 2024-08-15 | 2025-08-30 | Level 2 | N/A
100026474976 | Other | Tier 2 | Distribution | 2024-08-15 | 2025-08-30 | Level 2 | N/A
100026475531 | Other | Tier 2 | Distribution | 2024-08-15 | 2025-08-30 | Level 2 | N/A
100026475664 | Other | Tier 2 | Distribution | 2024-08-15 | 2025-08-30 | Level 2 | N/A
100026479115 | Cross Arm | Tier 2 | Distribution | 2024-08-16 | 2025-08-30 | Level 2 | N/A
100026479327 | Other | Tier 2 | Distribution | 2024-08-16 | 2025-08-30 | Level 2 | N/A
100026479860 | Conductor | Tier 2 | Distribution | 2024-08-16 | 2025-08-30 | Level 2 | N/A
100026480136 | Conductor | Tier 2 | Distribution | 2024-08-16 | 2025-08-30 | Level 2 | N/A
100026480137 | Other | Tier 2 | Distribution | 2024-08-16 | 2025-08-30 | Level 2 | N/A
100026482756 | Other | Tier 2 | Distribution | 2024-08-19 | 2025-08-30 | Level 2 | N/A
100026484664 | Pole | Tier 2 | Distribution | 2024-08-19 | 2025-08-30 | Level 2 | N/A
100026489237 | Other | Tier 2 | Distribution | 2024-08-20 | 2025-08-30 | Level 2 | N/A
100026490193 | Cross Arm | Tier 2 | Distribution | 2024-08-20 | 2025-08-30 | Level 2 | N/A
100026490194 | Cross Arm | Tier 2 | Distribution | 2024-08-20 | 2025-08-30 | Level 2 | N/A
100026492588 | Conductor | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026492589 | Conductor | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026492777 | Other | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026492778 | Other | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026492972 | Conductor | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026492973 | Pole | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026492974 | Cross Arm | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026492977 | Pole | Tier 2 | Distribution | 2024-08-21 | 2025-08-30 | Level 2 | N/A
100026495821 | Cross Arm | Tier 2 | Distribution | 2024-08-22 | 2025-08-30 | Level 2 | N/A
100026499041 | Cross Arm | Tier 2 | Distribution | 2024-08-23 | 2025-08-30 | Level 2 | N/A
100026518733 | Pole | Tier 2 | Distribution | 2024-08-26 | 2025-08-30 | Level 2 | N/A
100026518961 | Insulator and Bushing | Tier 2 | Distribution | 2024-08-26 | 2025-08-30 | Level 2 | N/A
100026519491 | Other | Tier 2 | Distribution | 2024-08-26 | 2025-08-30 | Level 2 | N/A
100026519492 | Pole | Tier 2 | Distribution | 2024-08-26 | 2025-08-30 | Level 2 | N/A
100026520298 | Other | Tier 2 | Distribution | 2024-08-26 | 2025-08-30 | Level 2 | N/A
100026523245 | Other | Tier 2 | Distribution | 2024-08-27 | 2025-08-30 | Level 2 | N/A
100026523692 | Insulator and Bushing | Tier 2 | Distribution | 2024-08-27 | 2025-08-30 | Level 2 | N/A
100026523694 | Conductor | Tier 2 | Distribution | 2024-08-27 | 2025-08-30 | Level 2 | N/A
100026524682 | Other | Tier 2 | Distribution | 2024-08-27 | 2025-08-30 | Level 2 | N/A
100026524684 | Other | Tier 2 | Distribution | 2024-08-27 | 2025-08-30 | Level 2 | N/A
100026534984 | Other | Tier 2 | Distribution | 2024-08-29 | 2025-08-30 | Level 2 | N/A
100026538350 | Pole | Tier 2 | Distribution | 2024-08-30 | 2025-08-30 | Level 2 | N/A
100026539464 | Cross Arm | Tier 2 | Distribution | 2024-08-30 | 2025-08-30 | Level 2 | N/A
100026539465 | Pole | Tier 2 | Distribution | 2024-08-30 | 2025-08-30 | Level 2 | N/A
100026565829 | Conductor | Tier 2 | Distribution | 2024-09-06 | 2025-09-30 | Level 2 | N/A
100026572708 | Other | Tier 2 | Distribution | 2024-09-10 | 2025-09-30 | Level 2 | N/A
100026572750 | Cross Arm | Tier 2 | Distribution | 2024-09-10 | 2025-09-30 | Level 2 | N/A
100026572963 | Pole | Tier 2 | Distribution | 2024-09-10 | 2025-09-30 | Level 2 | N/A
100026577338 | Anchor/Guy | Tier 2 | Distribution | 2024-09-11 | 2025-09-30 | Level 2 | N/A
100026577791 | Pole | Tier 2 | Distribution | 2024-09-11 | 2025-09-30 | Level 2 | N/A
100026582099 | Pole | Tier 2 | Distribution | 2024-09-12 | 2025-09-30 | Level 2 | N/A
100026582580 | Anchor/Guy | Tier 2 | Distribution | 2024-09-11 | 2025-09-30 | Level 2 | N/A
100026585051 | Other | Tier 2 | Distribution | 2024-09-13 | 2025-09-30 | Level 2 | N/A
100026591506 | Pole | Tier 2 | Distribution | 2024-09-16 | 2025-09-30 | Level 2 | N/A
100026591812 | Other | Tier 2 | Distribution | 2024-09-16 | 2025-09-30 | Level 2 | N/A
100026600118 | Other | Tier 2 | Distribution | 2024-09-19 | 2025-09-30 | Level 2 | N/A
100026601298 | Other | Tier 2 | Distribution | 2024-09-19 | 2025-09-30 | Level 2 | N/A
100026601387 | Pole | Tier 2 | Distribution | 2024-09-19 | 2025-09-30 | Level 2 | N/A
100026625664 | Cross Arm | Tier 2 | Distribution | 2024-09-24 | 2025-09-30 | Level 2 | N/A
100026640599 | Anchor/Guy | Tier 2 | Distribution | 2024-09-30 | 2025-09-30 | Level 2 | N/A
100023598897 | Other | Tier 2 | Distribution | 2023-03-28 | N/A | N/A | N/A
100023644150 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644152 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023653912 | Cross Arm | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653914 | Other | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653916 | Pole | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653919 | Cross Arm | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023683980 | Other | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023683982 | Pole | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023683983 | Other | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684001 | Pole | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023697438 | Cross Arm | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023721064 | Pole | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721112 | Insulator and Bushing | Tier 3 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721113 | Cross Arm | Tier 3 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721114 | Anchor/Guy | Tier 3 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721585 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023721652 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023721706 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722111 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023761860 | Cross Arm | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761863 | Pole | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761864 | Pole | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761872 | Cross Arm | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761874 | Other | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023808802 | Cross Arm | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023820119 | Pole | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023848393 | Cross Arm | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023854997 | Cross Arm | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855061 | Anchor/Guy | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855062 | Cross Arm | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023885018 | Other | Tier 2 | Distribution | 2023-05-23 | N/A | N/A | N/A
100023885059 | Cross Arm | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885062 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885064 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885083 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885084 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885134 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885156 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885163 | Other | Tier 2 | Distribution | 2023-05-23 | N/A | N/A | N/A
100023885171 | Other | Tier 2 | Distribution | 2023-05-23 | N/A | N/A | N/A
100023885173 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023910982 | Pole | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023925581 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925607 | Pole | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925665 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023931625 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023932254 | Other | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932259 | Other | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932301 | Cross Arm | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023938540 | Cross Arm | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938564 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938565 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023957393 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023965246 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965247 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965248 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965310 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965320 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983041 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983042 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983075 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023985705 | Other | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985707 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100024009478 | Pole | Tier 2 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024016993 | Pole | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024028124 | Pole | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024032815 | Pole | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024044729 | Other | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044823 | Other | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044824 | Cross Arm | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024106743 | Pole | Tier 3 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024147689 | Other | Tier 2 | Distribution | 2023-07-07 | N/A | N/A | N/A
100024168166 | Other | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168167 | Cross Arm | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168168 | Cross Arm | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168210 | Anchor/Guy | Tier 2 | Distribution | 2023-07-12 | N/A | N/A | N/A
100024173425 | Cross Arm | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173429 | Cross Arm | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173440 | Cross Arm | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173443 | Pole | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173462 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173463 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173465 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173469 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024178672 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024180601 | Pole | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180607 | Cross Arm | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024208614 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208776 | Anchor/Guy | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208832 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024225993 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226059 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226061 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226069 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226087 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226090 | Pole | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024243901 | Pole | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243946 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244052 | Pole | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244056 | Cross Arm | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024267192 | Other | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024315851 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315854 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315856 | Cross Arm | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316022 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316033 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024321211 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321239 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321425 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024328247 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328261 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328503 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024333940 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333941 | Transformer | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333993 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333994 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333996 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333997 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334105 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334107 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334108 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334112 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334114 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334163 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334171 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334173 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334174 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334175 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334178 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334180 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334199 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335233 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335234 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335350 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335584 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335594 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024343789 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343790 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343862 | Cross Arm | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343913 | Cross Arm | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343924 | Cross Arm | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024351538 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351583 | Pole | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024351584 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024351591 | Pole | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351592 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351595 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024351701 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351703 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024364160 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364235 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364255 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024369030 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369053 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369054 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369061 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369066 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369067 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369068 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369072 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369140 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369141 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369143 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369146 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369159 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024380231 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380258 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380295 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380296 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024394526 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396401 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396402 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396439 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396591 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396596 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396597 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396601 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396606 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396610 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396638 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396647 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396648 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396649 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024409671 | Anchor/Guy | Tier 2 | Distribution | 2023-08-25 | N/A | N/A | N/A
100024409672 | Anchor/Guy | Tier 2 | Distribution | 2023-08-25 | N/A | N/A | N/A
100024434765 | Pole | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434821 | Cross Arm | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434845 | Pole | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434897 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024445368 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445375 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445382 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445384 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445385 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445386 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445388 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024481523 | Conductor | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482165 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482166 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482212 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487249 | Pole | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024489189 | Pole | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024497211 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497216 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497217 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497236 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497245 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497323 | Cross Arm | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497324 | Other | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497325 | Other | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024501993 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502004 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502005 | Pole | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502026 | Pole | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502028 | Pole | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024505466 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507184 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507272 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507286 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507288 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507294 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512451 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512455 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512473 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512478 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512479 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024519842 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521070 | Pole | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521087 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521099 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024533341 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533342 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533354 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533355 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533359 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024539684 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539685 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539687 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539694 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539697 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539712 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539734 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539756 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539758 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539782 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539802 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539847 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024545146 | Cross Arm | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100026595647 | Cross Arm | Tier 3 | Distribution | 2024-09-17 | N/A | N/A | N/A
100026595648 | Transformer | Tier 3 | Distribution | 2024-09-17 | N/A | N/A | N/A
100026595660 | Cross Arm | Tier 3 | Distribution | 2024-09-17 | N/A | N/A | N/A
100026595667 | Pole | Tier 3 | Distribution | 2024-09-17 | N/A | N/A | N/A
100026595669 | Pole | Tier 3 | Distribution | 2024-09-17 | N/A | N/A | N/A
100026613426 | Cross Arm | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026613427 | Cross Arm | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026613429 | Cross Arm | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026613561 | Insulator and Bushing | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026613563 | Other | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026613564 | Cross Arm | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026613565 | Cross Arm | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026613566 | Pole | Tier 3 | Distribution | 2024-09-23 | N/A | N/A | N/A
100026630390 | Pole | Tier 3 | Distribution | 2024-09-25 | N/A | N/A | N/A
100026638950 | Other | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638952 | Pole | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638955 | Anchor/Guy | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638959 | Other | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638961 | Pole | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638963 | Pole | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638964 | Pole | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638965 | Other | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638968 | Conductor | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638969 | Pole | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638971 | Other | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638972 | Conductor | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026638973 | Anchor/Guy | Tier 3 | Distribution | 2024-09-27 | N/A | N/A | N/A
100026645002 | Pole | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026645003 | Other | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026645004 | Other | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026645005 | Other | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026645007 | Other | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026649470 | Other | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026649472 | Conductor | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026649474 | Pole | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026649476 | Other | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
100026649479 | Insulator and Bushing | Tier 3 | Distribution | 2024-09-30 | N/A | N/A | N/A
P100379 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100380 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100383 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100383 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100609 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P100754 | Anchor/Guy | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P100922 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P101106 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P101230 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P101331 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P101614 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P10182 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P102142 | Pole | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P102518 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P102519 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P102597 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P103149 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P103249 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P10331 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P10341 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P10350 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P103630 | Other | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P103671 | Pole | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P103782 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P10394 | Fuse | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P10394 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P10394 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P10394 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P104031 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P104031 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P104031 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P104031 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P10412 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P104982 | Other | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P104982 | Cross Arm | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P104982 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P105077 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P106139 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P106139 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P106547 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P107327 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P10746 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P10747 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P107564 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P107652 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107655 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107659 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107714 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107715 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107716 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107716 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107719 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107728 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107875 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P107975 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P108130 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P108134 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P108139 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P108153 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P108381 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P108542 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P108919 | Pole | Tier 2 | Distribution | 2022-03-09 | N/A | N/A | N/A
P109000 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P109459 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P109611 | Pole | Tier 2 | Distribution | 2022-10-04 | N/A | N/A | N/A
P109705 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P109812 | Pole | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P109851 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P110202 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P110202 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P110206 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P110320 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P110394 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P110414 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P110414 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P110433 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P110511 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P110511 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P110609 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P110783 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P110783 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P110954 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111113 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111113 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111170 | Transformer | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P111188 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111245 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P111275 | Other | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P111340 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P111345 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P111378 | Cross Arm | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P111380 | Pole | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P111381 | Other | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P111470 | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111470 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111474 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111477 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P111482 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111483 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111486 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111507 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P111613 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111625 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P111778 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P111809 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P112028 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P112067 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112072 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112080 | Pole | Tier 2 | Distribution | 2022-06-10 | N/A | N/A | N/A
P112081 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112085 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112086 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112107 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P112107 | Other | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P112115 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P112183 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P112306 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P112394 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P112539 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P112542 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P112547 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P112893 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P112893 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P112893 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P112951 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P113017 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113126 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P113356 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P113385 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P113386 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P113400 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P113400 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P113400 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P113443 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113462 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P113491 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P113566 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P113566 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P113699 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113700 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113985 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P114203 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P114309 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P114310 | Other | Tier 2 | Distribution | 2022-10-28 | N/A | N/A | N/A
P114668 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P114668 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P114906 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P114906 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P114906 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P115319 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P115355 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P115355 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P115355 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P115622 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P115635 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P115635 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P115792 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P115792 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P115849 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P116046 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P116053 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P116074 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P116331 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P116372 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116372 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116373 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116373 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116548 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P116639 | Transformer | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P116712 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P116712 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P11683 | Cross Arm | Tier 3 | Distribution | 2022-10-12 | N/A | N/A | N/A
P11683 | Other | Tier 3 | Distribution | 2022-10-12 | N/A | N/A | N/A
P116887 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P116887 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P116891 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P116894 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P116900 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P116938 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P116962 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P117119 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P117132 | Anchor/Guy | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P117145 | Pole | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P117154 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P117257 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Transformer | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117486 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P117521 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P117559 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P117587 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117588 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117589 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117629 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117629 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117641 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P117656 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117656 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117656 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117668 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P117804 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P117807 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P117859 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P117878 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P117952 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P118754 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P118761 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P118873 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P118940 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P118954 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P118955 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P118961 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P118972 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P118972 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P118973 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P119144 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P119155 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P119155 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P119255 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P119255 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P119258 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P119280 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P119492 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P119492 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P119519 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P119686 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P119686 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P119728 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P119728 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P119839 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P120814 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P121060 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P121060 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P121647 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P121649 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P121934 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P122211 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P122212 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P122573 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P124118 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P124119 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P124941 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P124942 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P124942 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P124947 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P125025 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P126052 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P126063 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P12609 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P127214 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P12790 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P128403 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P128441 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128450 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128450 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128450 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128451 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128454 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128455 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128456 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128456 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128463 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128463 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128871 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P128871J | Pole | Tier 2 | Distribution | 2022-05-13 | N/A | N/A | N/A
P128906 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P130439 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P130553 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P130711 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P130711 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P130773 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P130773 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P13081 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P13081 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P130839 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P13087 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P13092 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P130943 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P130943 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P13101 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P13102 | Other | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P131156 | Cross Arm | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P131177 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P131178 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P13131 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P13131 | Other | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P13132 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P131402 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P131413 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P131413 | Transformer | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P13145 | Other | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P13145 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P13145 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P13145 | Other | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P13145 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P13145 | Cross Arm | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P13160 | Other | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P13160 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P13165 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P13175 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P13212 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P13212 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P13285 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P132911 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P13294 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P132945 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P132945 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P13296 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P132977 | Transformer | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P132979 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P13309 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P13310 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P133417 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P133456 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P13416 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P13465 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P134684 | Cross Arm | Tier 2 | Distribution | 2022-07-11 | N/A | N/A | N/A
P134687 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P134687 | Pole | Tier 2 | Distribution | 2022-08-11 | N/A | N/A | N/A
P134687 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P134836 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134855 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134856 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134858 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134864 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134865 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P135067 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P135075 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P135086 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P135086 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P135325 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P136166 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P136166 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P136199 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P136200 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P136273 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P136601 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P137967 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P137972 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P138009 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P138010 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P138010 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P138693 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P139091 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P139135 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P139511 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P13992 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P14413 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P14742 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P14743 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P14766 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14771 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14791 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14792 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14901 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P14985 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P15084 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P15087 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P15137 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P15137 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P15285 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15375 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P15460 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15461 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15462 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15463 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15477 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15479 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15480 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15548 | Other | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P15548 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P15569 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15570 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15574 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15804 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P15947 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P160114 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P16027 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P16027 | Fuse | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P160512 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P16058 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P16058 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P160603 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P16131 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P161347 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P161457 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P161528 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P16163 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16163 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16173 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16174 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16174 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P161837 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P161948 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P162131 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P162131 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P162131 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P162131 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P162131 | Other | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P162131 | Pole | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P162577 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P162793 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P163166 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P163362 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P163400 | Pole | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P163566 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P164100 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164112 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164159 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P164187 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164188 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164218 | Anchor/Guy | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164218 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164225 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P164263 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164263 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164469 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16471 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P164764 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P164857 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P164936 | Pole | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P165029 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P165158 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P165163 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P165166 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P165189 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P165190 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P165201 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P165203 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P165216 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P165224 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165225 | Other | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165225 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165236 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165272 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P165440 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P165454 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P165454 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P165603 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P165724 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P165743 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P165743 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P165821 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P165821 | Anchor/Guy | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P165850 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P165961 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P166116 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P166128 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P166245 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P166469 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P166527 | Anchor/Guy | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166529 | Pole | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166530 | Pole | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166530 | Other | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166531 | Pole | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P16699 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P16699 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P16703 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P16703 | Insulator and Bushing | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P167162 | Switch | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P167223 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167224 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167696 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P167719 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P167863 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167863 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167953 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P168057 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P168137 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P168137 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P168223 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P168594 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P16872 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P168743 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P168809 | Pole | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P168904 | Pole | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P169126 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P16930 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16930 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16938 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16938 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16938 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P169385 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P16939 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16947 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P169516 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P169550 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P16975 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P170171 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P170502 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P170504 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P17057 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17059 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17067 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17067 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17081 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P17081 | Insulator and Bushing | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P17081 | Conductor | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P170883 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P171426 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P172048 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P172246 | Pole | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P172246 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P172255 | Transformer | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P172263 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P172268 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P172452 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172453 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172466 | Other | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P172470 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172470 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172477 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172479 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172481 | Cross Arm | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P172484 | Other | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P172498 | Other | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P172499 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P172499 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P172508 | Pole | Tier 2 | Distribution | 2022-05-27 | N/A | N/A | N/A
P172514 | Pole | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P172516 | Cross Arm | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P172525 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172527 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172527 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172762 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P173315 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173315 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173316 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173316 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173316 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173722 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P173722 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P173856 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P17396 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P174255 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P174693 | Cross Arm | Tier 2 | Distribution | 2022-02-11 | N/A | N/A | N/A
P174695 | Cross Arm | Tier 2 | Distribution | 2022-02-11 | N/A | N/A | N/A
P174798 | Transformer | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P174808 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P17493 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P175013 | Cross Arm | Tier 2 | Distribution | 2022-08-31 | N/A | N/A | N/A
P175016 | Cross Arm | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P175198 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P175199 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P175296 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P175296 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P175384 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P175399 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P17540 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P175417 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P175537 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P175537 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P17561 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P176022 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P176074 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P177248 | Other | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177248 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177248 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Other | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Cross Arm | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Other | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177252 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177340 | Conductor | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P177857 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P177886J | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P177897 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P177897 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P177956 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P177960 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P178320 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P178521 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P178522 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P178595 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P178647 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P178650 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P179870 | Other | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P179876 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P18083 | Transformer | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P182005 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P182005 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P183607 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P183607 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P18389 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P18401 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P18402 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P18404 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P18411 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P18442 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P18446 | Conductor | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P18446 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P184755 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P18504 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P18614 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P18642 | Cross Arm | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P18688 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P18695 | Anchor/Guy | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P18696 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P18734 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P18734 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P190007 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P190193 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P190927 | Pole | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P190939 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P190977 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P190981 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P190982 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P191121 | Cross Arm | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P19122 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P19126 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P19126 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P19128 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P191636 | Anchor/Guy | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P191636 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P192111 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P192111 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P192115 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P193139 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P193245 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P193394 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P19362 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P19362 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P194136 | Anchor/Guy | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P194136 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P194136 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P194228 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P195368 | Pole | Tier 2 | Distribution | 2022-07-28 | N/A | N/A | N/A
P196251 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P196531 | Pole | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P196531 | Other | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P196545 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P196546 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P196549 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P19655 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P19655 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P196551 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P19683 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P197638 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P19807 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P198176 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P198453 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P198865 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P198919 | Pole | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P198942 | Cross Arm | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P198942 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P199111 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P199377 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P199399 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P199815 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P199831 | Anchor/Guy | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P199888 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P200143 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P200150 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P200225 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P200284 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P200317 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P200319 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P200460 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P200533 | Pole | Tier 3 | Distribution | 2022-12-12 | N/A | N/A | N/A
P201740 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P202052 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P202500 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P202593 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P202593 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P202789 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P202813 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P203597 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P204384 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P205196 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P205387 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P205443 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P205483 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P205491 | Pole | Tier 2 | Distribution | 2022-11-16 | N/A | N/A | N/A
P206096 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206096 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206147 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P206712 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P206758 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P206918 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P206918 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P206967 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206967 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206967 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P207282 | Pole | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P207282 | Other | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P208524 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P209041 | Anchor/Guy | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P209042 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P210299 | Pole | Tier 2 | Distribution | 2022-05-18 | N/A | N/A | N/A
P210303 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P210344 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P210344 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P210366 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P210406 | Pole | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P210433 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P210456 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210457 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210488 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P210617 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P210771 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210776 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P210777 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P211047 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P211073 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P211074 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P211076 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P211153 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P211289 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P211336 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P211344 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P211547 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P211567 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P211730 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P211806 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P211974 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P212011 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P212014 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P212073 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P212124 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P212353 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212398 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P212398 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P212476 | Transformer | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P212494 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212497 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212498 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212546 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P212629 | Other | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P212651 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P212691 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P212693 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P212798 | Other | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P21284 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P21284 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P213041 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P213049 | Transformer | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P213116 | Anchor/Guy | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213118 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213119 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213119 | Other | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213126 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213296 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P213398 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213399 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213399 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213445 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213445 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213454 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P213461 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P213531 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P213531 | Other | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P213531 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P213799 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P213850 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P213933 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P213935 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P214000 | Other | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P214013 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P214015 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P214104 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P214104 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P214104 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P214118 | Anchor/Guy | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P214118 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P214135 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P214250 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P214282 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P214576 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P214576 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P214757 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P214765 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P214767 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P214952 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P214952 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P215041 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P215262 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P215262 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P215516 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P215647 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215647 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215649 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215650 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215721 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P215879 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P215879 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P215948 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P216152 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P216153 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P216156 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P216180 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P216181 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P216205 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P216205 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P216391 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P216400 | Transformer | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P216400 | Cross Arm | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P216620 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P216692 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P216698 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P216698 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P216761 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P216773 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P216834 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P216834 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P216836 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P216841 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P217016 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P217117 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P217117 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P217117 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P217122 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P217218 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P217258 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217259 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217304 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P217319 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217319 | Other | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217319 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217320 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217400 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217400 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217728 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P217757 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P21786 | Switch | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P217909 | Other | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P217909 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P21806 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P218186 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P218187 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P218242 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P218262 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P218266 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P218267 | Pole | Tier 2 | Distribution | 2022-10-14 | N/A | N/A | N/A
P218461 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P218684 | Cross Arm | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P218689 | Pole | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P218736 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P218848 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P218848 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P218879 | Cross Arm | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P218879 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P219035 | Other | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219035 | Cross Arm | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219035 | Transformer | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219452 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P219453 | Fuse | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P219485 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P219492 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P219611 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P219683 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P220434 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P220530 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P220600 | Conductor | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P220951 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P220951 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P220984 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P221407 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P221407 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P221603 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P224242 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P224330 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P224884 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P225174 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P225408 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P225930 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P225932 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P226793 | Conductor | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P227979 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P228082 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P228169 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P228274 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P228276 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P228888 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P233517 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P233518 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P233617 | Cross Arm | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P233816 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P235901 | Conductor | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P237475 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P237729 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P237856 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P237856 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P237969 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P238016 | Anchor/Guy | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P238758 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P238759 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P238774 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238774 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238929 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238929 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238975 | Pole | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P239111 | Cross Arm | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P239111 | Pole | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P239114 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P239196 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P239218 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P239257 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P239281 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P239785 | Other | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P245093 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P245100 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P245104 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P245111 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P245499 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P245667 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P247434 | Anchor/Guy | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P24981 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25068 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P25224 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25303 | Other | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P25307 | Pole | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P25308 | Pole | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P25315 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25319 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25323 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P253370 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P253649 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P253754 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P254172 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P254174 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P254174 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P254677 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P254897 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P254906 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P254906 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P25589 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P26011 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P26442 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P26690 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P270022 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P270022 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P270190 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P270547 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P270547 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P27088 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P271013 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P271392 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P271400 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P27302 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P273446 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P273605 | Pole | Tier 3 | Distribution | 2022-11-28 | N/A | N/A | N/A
P273613 | Cross Arm | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P273622 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273622 | Other | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273623 | Pole | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273625 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273626 | Pole | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273629 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273631 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273631 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273634 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273635 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273637 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273638 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273638 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273649 | Pole | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273654 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273655 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273658 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273658 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P27377 | Other | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P273802 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P274146 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P27439 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P274677 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P274848 | Anchor/Guy | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P275125 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P276202 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P276245 | Cross Arm | Tier 2 | Distribution | 2022-02-11 | N/A | N/A | N/A
P276283 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P276284 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P276432 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P276969 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P277300 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P277753 | Conductor | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P277753 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P277807 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P277808 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P278079 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P278079 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P278270 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P278346 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P278346 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P278346 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P278871 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P27896 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P27902 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P27912 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P27995 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P27996 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P280407 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P28105 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P28105 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P28214 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P28301 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P28314 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P283531 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P28377 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P28417 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P294291 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P30163 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30234 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30234 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30234 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30244 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P30307 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P30792 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P30815 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P310171 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P310605 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P310648 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P310654 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P310970 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P311024 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P311027 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P3111460 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P311161 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311162 | Other | Tier 2 | Distribution | 2022-07-20 | N/A | N/A | N/A
P311163 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P31123 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P311360 | Pole | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P311360 | Cross Arm | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P311361 | Cross Arm | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P311374 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311374 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311375 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311375 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311384 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311384 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311436 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P311618 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311619 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311619 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311620 | Pole | Tier 2 | Distribution | 2022-05-09 | N/A | N/A | N/A
P311621 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311621 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311670 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P311670 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P311689 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P31169 | Pole | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P31169 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P31169 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P31169 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P31171 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P31171 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P31174 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P31177 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P311811 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311817 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311818 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311823 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311823 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311828 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P312057 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P312334 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P312334 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P312447 | Pole | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P312476 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P312569 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P312587 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P312587 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P312638 | Cross Arm | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P313146 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P313147 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P313399 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P313399 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P313564 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P313564 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P316199 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P316603 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P316893 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P316969 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P317008 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P317146 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P317760 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P317762 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P318073 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P318073 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P318079 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P318087 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P318243 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P318633 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P318666 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P318666 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P318667 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P318667 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P318805 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P318870 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P318871 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P319010 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P319010 | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P319045 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P319047 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P319272 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P319283 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P319473 | Pole | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P319520 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P319633 | Pole | Tier 2 | Distribution | 2022-06-30 | N/A | N/A | N/A
P319634 | Cross Arm | Tier 2 | Distribution | 2022-06-30 | N/A | N/A | N/A
P320776 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P321097 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P32216 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P323123 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P324144 | Other | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P324293 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P32785 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P32813 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P32813 | Other | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P32842 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P32842 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P32940 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P32940 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P32941 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P32941 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P32941 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P32941 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P33611 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P33763 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P33794 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P33813 | Pole | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P33814 | Pole | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P33869 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P34174 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P34872 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P35036 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P35982 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P36015 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P36068 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P36068 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P36208 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P36625 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P36715 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P36715 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P36794 | Pole | Tier 2 | Distribution | 2022-11-18 | N/A | N/A | N/A
P36794 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P36982 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P370037 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P370044 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P370057 | Cross Arm | Tier 2 | Distribution | 2021-11-10 | N/A | N/A | N/A
P370804 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P370805 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P370806 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P370944 | Conductor | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P371076 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P371202 | Conductor | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371202 | Conductor | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371202 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371204 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371925 | Cross Arm | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P373013 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P373106 | Pole | Tier 2 | Distribution | 2022-10-10 | N/A | N/A | N/A
P373107 | Transformer | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P373713 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P374193 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P374319 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P374930 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P375248 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P375272 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P375273 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P376165 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P376255 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P376280 | Conductor | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P376280 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P376920 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P377028 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P377349 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P377349 | Transformer | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P38798 | Pole | Tier 2 | Distribution | 2022-07-28 | N/A | N/A | N/A
P38799 | Other | Tier 2 | Distribution | 2022-07-28 | N/A | N/A | N/A
P38961 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P38992 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P38992 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P40754 | Other | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P40757 | Anchor/Guy | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P40759 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P410104 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P410104 | Conductor | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P410105 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P410119 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P410124 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P41052 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P41054 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P41054 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P410558 | Cross Arm | Tier 2 | Distribution | 2022-03-24 | N/A | N/A | N/A
P410606 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P410606 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P410636 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P410636 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P410747 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P410747 | Pole | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P410782 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P410782 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P411024 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P411160 | Other | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P411164 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P411426 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P411475 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P411475 | Pole | Tier 2 | Distribution | 2022-08-19 | N/A | N/A | N/A
P411594 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P412165 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P412368 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P412368 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P412373 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P412378 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P412699 | Cross Arm | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P412699 | Other | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P412941 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P412965 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P412969 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P412989 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P412996 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P413502 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P413502 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P413678 | Transformer | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P413724 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P413724 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P413725 | Other | Tier 2 | Distribution | 2022-12-05 | N/A | N/A | N/A
P413938 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P413981 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P414156 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P414198 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P414326 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P414381 | Transformer | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P414490 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P414490 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P414495 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P414552 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P414552 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P41456 | Anchor/Guy | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41458 | Anchor/Guy | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41459 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41460 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41461 | Cross Arm | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41462 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41463 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41464 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41466 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41467 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41469 | Cross Arm | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P41471 | Cross Arm | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P41478 | Cross Arm | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P41478 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P41479 | Other | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P414839 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P41485 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P414858 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P414971 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P41518 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41518 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41520 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41522 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P415228 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P415228 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P41525 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41526 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41526 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41527 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P41528 | Cross Arm | Tier 2 | Distribution | 2022-01-24 | N/A | N/A | N/A
P41530 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P41531 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P41532 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P415334 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P41535 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P41539 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P415485 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P415938 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P416002 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P416246 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P416266 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P416266 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P416288 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P416288 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P416441 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P416442 | Other | Tier 2 | Distribution | 2022-07-18 | N/A | N/A | N/A
P416443 | Pole | Tier 2 | Distribution | 2022-05-12 | N/A | N/A | N/A
P416444 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P416447 | Pole | Tier 2 | Distribution | 2022-05-09 | N/A | N/A | N/A
P416448 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P416748 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P417006 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P417062 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P417062 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P417177 | Cross Arm | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P417177 | Other | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P417220 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P417239 | Conductor | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P417239 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P41728 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41729 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41729 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P417290 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P417290 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P41733 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P41733 | Cross Arm | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P417457 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P417457 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P417492 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P417493 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P41759 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41759 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41759 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41761 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P417716 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P417723 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P417731 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P417782 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P417916 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P418157 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P418351 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P41839 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P418442 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P418443 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P418732 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P418845 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P418873 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P418873 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P419059 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P419135 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P419160 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P419160 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P41925 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P419379 | Transformer | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P419380 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P419380 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P419549 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P42000 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P42001 | Anchor/Guy | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P42001 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P42268 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P42269 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42270 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42272 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42292 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42294 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P42296 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42297 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P42298 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42299 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P42300 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42301 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P42560 | Other | Tier 3 | Distribution | 2020-05-11 | N/A | N/A | N/A
P44311 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P44315 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P44315 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P44315 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P44637 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44647 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44816 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44821 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44821 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44821 | Conductor | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44836 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44843 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44845 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44848 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44849 | Pole | Tier 2 | Distribution | 2022-04-24 | N/A | N/A | N/A
P44859 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44870 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44874 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44874 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44879 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44879 | Anchor/Guy | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44884 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44884 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44884 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44890 | Cross Arm | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P44891 | Other | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P44907 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44911 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44911 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44914 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44914 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44920 | Cross Arm | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P44922 | Cross Arm | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P44922 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P44930 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44938 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44942 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44946 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44946 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P44947 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P45006 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45008 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45011 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45012 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45034 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45034 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45034 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45035 | Other | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P45035 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P45035 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P45128 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45135 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45153 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45153 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45154 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45189 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45333 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45333 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45334 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45336 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45336 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45460 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45460 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45530 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45681 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P45726 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45739 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45740 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45740 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45740 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45837 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45839 | Other | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45842 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45852 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45866 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45866 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45892 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45893 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45918 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45931 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45933 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45933 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45938 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46002 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P46003 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P46003 | Other | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P46047 | Other | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P46047 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P46048 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46074 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46075 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46075 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46077 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46077 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46078 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46078 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46079 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46080 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46082 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46083 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46083 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46084 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46084 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46086 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46088 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46088 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46094 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46099 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P46132 | Cross Arm | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P46133 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P46137 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46139 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46141 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46141 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46143 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46176 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46210 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46210 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46213 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P46213 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P46432 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P46543 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P46560 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P470081 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P470081 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P470088 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P470601 | Transformer | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P471261 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P471261 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P471274J | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P471899 | Pole | Tier 3 | Distribution | 2021-12-20 | N/A | N/A | N/A
P473812 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P473840 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474084 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474084 | Other | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474095 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474171 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P474485 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P474535 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P474537 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P474936 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P475568 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P475572 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P475994 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P476188 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P476711 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P477971 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P478017 | Transformer | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P478022 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P478388 | Other | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P510310 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P510310 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P510609 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P510640 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P510748 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P510748 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P510914 | Conductor | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P510934 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P511046 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P511046 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P511099 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P511122 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P511163 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P511281 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P511324 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P511327 | Anchor/Guy | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P511334 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P511335 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P511428 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P511474 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P511474 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P511476 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P511856 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P511862 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P511897 | Fuse | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P512003 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P512094 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P512297 | Anchor/Guy | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P512297 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P512300 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P512420 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P512420 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P512472 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P512966 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P512995 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P512997 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P513106 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P513106 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P513148 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P513148 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P513187 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P513187 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P513405 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P513415 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P513454 | Cross Arm | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P513467 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P513788 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P513918 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P514022 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P514044 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P514368 | Cross Arm | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P514368 | Other | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P514368 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P514434 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P514435 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P514449 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P514535 | Pole | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P514696 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P514697 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P514697 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P514713 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P514760 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P514761 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P514787 | Transformer | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P514843 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P515037 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515161 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515212 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P515359 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P515359 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P515364 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515365 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515365 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515368 | Transformer | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515371 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515371 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515372 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515595 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P515597 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P515604 | Anchor/Guy | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P515604 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P515862 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P516125 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P516145 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P516145 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P516145 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P516184 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P516184 | Transformer | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P516325 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P516325 | Anchor/Guy | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P516522 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516523 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516523 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516638 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P516779 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P516887 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P516901 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P516911 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P516911 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P516957 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P516957 | Cross Arm | Tier 2 | Distribution | 2022-06-13 | N/A | N/A | N/A
P516958 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P516958 | Cross Arm | Tier 2 | Distribution | 2022-06-13 | N/A | N/A | N/A
P516959 | Cross Arm | Tier 2 | Distribution | 2022-06-13 | N/A | N/A | N/A
P516959 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P516961 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P516961 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P516962 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P517127 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P517129 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P517129 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P517183 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P517448 | Pole | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P517453 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P517781 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P517782 | Pole | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P517962 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P517981J | Pole | Tier 2 | Distribution | 2022-09-02 | N/A | N/A | N/A
P518012 | Pole | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P518023 | Pole | Tier 2 | Distribution | 2022-04-28 | N/A | N/A | N/A
P518158 | Conductor | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P518158 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P518202 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P518202 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P518210 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518211 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518211 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518213 | Anchor/Guy | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518213 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518546 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P518575 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P518670 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P518725 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P518780 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P518781 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P518783 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P518783 | Other | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P518783 | Other | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518783 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518785 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518785 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P518785 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518785 | Other | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518785 | Other | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P518785 | Cross Arm | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P518786 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518786 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P518787 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518787 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P518799 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P518889 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P518918 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P519061 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P519325 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P519325 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P519327 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P519365 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P519456 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519456 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519456 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519495 | Transformer | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P519811 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P519838 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P519838 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P519851 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P519854 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P519941 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519941 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P570135 | Transformer | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P570135 | Cross Arm | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P570171 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P570546 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P570928 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P570928 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P570928 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P570929 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P571380 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P571595 | Pole | Tier 2 | Distribution | 2022-10-20 | N/A | N/A | N/A
P571665 | Pole | Tier 2 | Distribution | 2022-03-18 | N/A | N/A | N/A
P571695 | Cross Arm | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P572015 | Anchor/Guy | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P572178 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572179 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572538 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572974 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P574572 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P575216 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P575222 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P575428 | Pole | Tier 2 | Distribution | 2021-11-08 | N/A | N/A | N/A
P576331 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P576675 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P576745 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P576747 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P576749 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P577067 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P577335 | Transformer | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P577335 | Other | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P577335 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P578769 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P578769 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P579767 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P610038 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P610054 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P610054 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P610106 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P610256 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P610381 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P610381 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P610382 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P610497 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P610525 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P610786 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P610786 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P610841 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P610841 | Insulator and Bushing | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P610912 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P611037 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P611479 | Cross Arm | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P611480 | Pole | Tier 2 | Distribution | 2021-08-09 | N/A | N/A | N/A
P611522 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P611754 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P611872 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P612022 | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P612120 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P612158 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P612159 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P612333 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P612333 | Cross Arm | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P612426 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P612489 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P612541 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P612541 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P612541 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P612772 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P612980 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P613182 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P613252 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P613252 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P613321 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P613542 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P613615 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P613643 | Cross Arm | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P613643 | Pole | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P613716 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P613716 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P613723 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P613724 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P613900 | Cross Arm | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P613994 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P614170 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P614520J | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P614777 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P614790 | Pole | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P615062 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P615074 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P615216 | Pole | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P615234 | Pole | Tier 2 | Distribution | 2022-12-01 | N/A | N/A | N/A
P615235 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P615501 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P615501 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P615526 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P615526 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P615527 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P615528 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P615528 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P615609 | Cross Arm | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615611 | Cross Arm | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615611 | Other | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615612 | Pole | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615612 | Other | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615761 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P615867 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P615922 | Transformer | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P616063 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P616235 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P616416 | Other | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P616416 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P616702 | Cross Arm | Tier 2 | Distribution | 2022-10-04 | N/A | N/A | N/A
P616769 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P616770 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P616877 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P616886 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P617546 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P617551 | Other | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P617551 | Conductor | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P617551 | Insulator and Bushing | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P617898 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P617964 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P617966 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P617967 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P617979 | Anchor/Guy | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P617980 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P618053 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P618195 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P618261 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P618261 | Other | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P618278 | Pole | Tier 2 | Distribution | 2022-11-04 | N/A | N/A | N/A
P618293 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618293 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618519 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P618522 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P618728 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P618736 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618736 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618739 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P618753 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P618785 | Other | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P618838 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P618987 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619127 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P619152 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P619276 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P619276 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P619319 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619319 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619321 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619476 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P619476 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P619546 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P619578 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P619756 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P619863 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P619893 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P619915 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P670057 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P671410 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P671690 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P671690 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P671696 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P672639 | Other | Tier 2 | Distribution | 2022-10-25 | N/A | N/A | N/A
P672640 | Other | Tier 2 | Distribution | 2022-10-25 | N/A | N/A | N/A
P672676 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P674283 | Conductor | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P674283 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P675047 | Transformer | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P675328 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P675330 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P676515 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P676515 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P676547 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P676869 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P676870 | Conductor | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P677097 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P677546 | Cross Arm | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P678679 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P679565 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P679762 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P707069 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P707069 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P710257 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710259 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710260 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P710270 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P710270 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P710282 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P710295 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P710305 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P710330 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P710333 | Transformer | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P710336 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P710353 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P710361 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P710449 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P710453 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P710543 | Transformer | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P710590 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P710702 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P710702 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P710731 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P710760 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710761 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710762 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710763 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710764 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710764 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710766 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710767 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710837 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710896 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P711354 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P711355 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P711445 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P711449 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P711450 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P711777 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P711808 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P711972 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P711974 | Anchor/Guy | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P712001 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P712058 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P712144 | Cross Arm | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P712144 | Other | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P712243 | Pole | Tier 2 | Distribution | 2022-06-16 | N/A | N/A | N/A
P712282 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P712344 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P712344 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P712344 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P712382 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P712384 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P712437 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712437 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712438 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712471 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P712573 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P712704 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P712734 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P712742 | Other | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P712742 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P712766 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P712887 | Anchor/Guy | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P712966 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P713162 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P713162 | Other | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P713175 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P713175 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P713267 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713267 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713268 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713270 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713271 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713378 | Pole | Tier 2 | Distribution | 2022-11-04 | N/A | N/A | N/A
P713379 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P713379 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P713412 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P713535 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P713708 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P713719 | Transformer | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P713811 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P713811 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P713934 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713934 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713971 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P713971 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P714026 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P714030 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P714034 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P714045 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P714059 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P714191 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P714216 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P714238 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P714566 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P714566 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P714778 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P714801 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P714848 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P714975 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P714994 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P714995 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P715097 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P715289 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P715308 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P715526 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P715531 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P715532 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P715534 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P715676 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P715872 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P716012 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P716017 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P716052 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P716089 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P716291 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P716309 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P716309 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P716353 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P716364 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P716371 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P716461 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P716582 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P716746 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P716746 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P716827 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P716961 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P716989 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P717218 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P717431 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P717480 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P717481 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P717495 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P717495 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P717496 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P717622 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P717780 | Transformer | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P717781 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P717884 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P717885 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P718033 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P718039 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P718078 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P718107 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P718230 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P718445 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P718573 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P718631 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P718734 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P718781 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P718796 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P718824 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P718995 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P718995 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P719072 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P719072 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P719083 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P719301 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P719301 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P719302 | Other | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P719324 | Pole | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P719327 | Pole | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P719327 | Other | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P719336 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P719336 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P719365 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P719365 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P719400 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P719401 | Other | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P719478 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719478 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719479 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719479 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719480 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719599 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P719599 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P719616 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P719749 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P719770 | Cross Arm | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P719778 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P719778 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P719779 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P719814 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P719899 | Other | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P719900 | Other | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P719901 | Other | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P719902 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P719902 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P73709 | Transformer | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P73879 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P74169 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P74310 | Pole | Tier 2 | Distribution | 2022-02-15 | N/A | N/A | N/A
P74312 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P74314 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P74315 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P75088 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P75489 | Other | Tier 2 | Distribution | 2021-11-08 | N/A | N/A | N/A
P770248 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P770248 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P770269 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P770282 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P770474 | Pole | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P770475 | Pole | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P770475 | Conductor | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P771224 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P771533 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P771923 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P771941 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P771942 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P772394 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P772523 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P772524 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P772524 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P772766 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P772884 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P773213 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P773225 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P773295 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P773566 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P773644 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P773645 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P773713 | Conductor | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P773713 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P773969 | Other | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P774385 | Conductor | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P774385 | Other | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P774391 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P775020 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P775097 | Conductor | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P775097 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P775345 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P775414 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P775612J | Pole | Tier 2 | Distribution | 2022-10-10 | N/A | N/A | N/A
P775643 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P775652 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P776191 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P776191 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P776416 | Insulator and Bushing | Tier 2 | Distribution | 2022-02-15 | N/A | N/A | N/A
P777027 | Pole | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P777265 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P777477 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P778741 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P810077 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P810081 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P810081 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P810392 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P810562 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P810583 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P810654 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P810710 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P810876 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811017 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P811018 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P811019 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P811169 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811200 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P811447 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P811471 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P811506 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811506 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811625 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P811647 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P811648 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P811740 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P811934 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P811950 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811951 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811995 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811995 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811995 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P812189 | Insulator and Bushing | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P812189 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P812192 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P812192 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P812202 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P812202 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P812214 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P812214 | Pole | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P812216 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P812323 | Pole | Tier 2 | Distribution | 2022-07-20 | N/A | N/A | N/A
P812348 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P812368 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P812374 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P812423 | Other | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P812527 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P812541 | Anchor/Guy | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P812612 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P812612 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P812762 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P812767 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P812815 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P812815 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P812915 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P812960 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P812960 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P812960 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P813013 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P813228 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813231 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813231 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813298 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P813298 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P813312 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P813513 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P813635 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P813635 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P813699 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P813791 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P813904 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P813971 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813971 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813971 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814118 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814118 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814295 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P814344 | Other | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P814364 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814364 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814404 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814404 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814410 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P814488 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P814488 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P814594 | Transformer | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P814594 | Other | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P814624 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P814636 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P814736 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P814736 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P814737 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P814809 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P814821 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P814950 | Other | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P815037 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P815142 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815144 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815145 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815203 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P815206 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P815293 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P815295 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P815433 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P815433 | Other | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P815463 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P815463 | Conductor | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P815512 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P815557 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P815739 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P815766 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P815987 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815987 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P816093 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816093 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816178 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P816181 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P816181 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P816245 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P816368 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P816370 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P816373 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P816414 | Pole | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P816414 | Cross Arm | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P816465 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P816465 | Other | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P816465 | Other | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P816471 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P816510 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P816510 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P816544 | Cross Arm | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P816592 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816592 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816593 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816593 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816594 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816594 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816615 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P816615 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P816615 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P816642 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P816654 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P816708 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P816916 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P816974 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P817036 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P817036 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P817074 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P817218 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P817254 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P817333 | Other | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P817583 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P817591 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P817623 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P818045 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P818045 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P818188 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P818198 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P818373 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P818373 | Insulator and Bushing | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P818373 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P818429 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P818474 | Other | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P818474 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P818474 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P818754 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P818754 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P818800 | Pole | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P819071 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P819071 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P819187 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P819188 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P819435 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P819678 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P819845 | Other | Tier 2 | Distribution | 2022-07-28 | N/A | N/A | N/A
P831226 | Cross Arm | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P839764 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86042 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86045 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86051 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86054 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86056 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P870041 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870060 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870079 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870355 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P870356 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P870396 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P870520 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P870522 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P870946 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P871189 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P871560 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P871970 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P872004 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P872498 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P872511 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P872511 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P872530 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P872532 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P872866 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P873021 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P873063 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P873282 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P873370 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P873539 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P873540 | Pole | Tier 2 | Distribution | 2022-05-29 | N/A | N/A | N/A
P873551 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873591 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P873787 | Anchor/Guy | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P873898 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873898 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P874034 | Pole | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P874046 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P874438 | Pole | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P874538 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P874596 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P874648 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P874695 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874696 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874696 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874795 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P874808 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874950 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P875166 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875166 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875374 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P875374 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P875411 | Pole | Tier 2 | Distribution | 2021-09-02 | N/A | N/A | N/A
P875488 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875507 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P875520 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P875622 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P875645 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P875779 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P875924 | Pole | Tier 2 | Distribution | 2022-11-30 | N/A | N/A | N/A
P876243 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P876244 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P876355 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P876424 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P876445 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876562 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876562 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876636 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P876682 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P876729 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P876854 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876928 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877036 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P877083 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P877390 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877394 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P877447 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877655 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877901 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P877901 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P878117 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P878342 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P878857 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P878857 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P878859 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P878938 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P878938 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P878939 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90098 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90147 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90147 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P910020 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P91438 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P91442 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P970147 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P970187 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P970419 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P970419 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P970731 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P970786 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P970809 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P971093 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P971176 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P971211 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P971559 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P972009 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P972342 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P972386 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P972699 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972740 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972749 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P977008 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P977008 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P977085 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P977152 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P977153 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
Z10216 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
Z118300 | Cross Arm | Tier 2 | Distribution | 2021-08-30 | N/A | N/A | N/A
Z118300 | Cross Arm | Tier 2 | Distribution | 2021-08-30 | N/A | N/A | N/A
Z16579 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
Z16579 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
Z181660 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
Z181660 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
Z188630 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z188630 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z219781 | Cross Arm | Tier 2 | Distribution | 2022-03-10 | N/A | N/A | N/A
Z219792 | Cross Arm | Tier 2 | Distribution | 2022-03-09 | N/A | N/A | N/A
Z31759 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z31760 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z31761 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z31762 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A

## Table 14
Utility | SDGE
Table No. | 14
Date Modified | 2024-11-01
Table 14: HFTD Area Risk Summary
*EC to add all other risk categories to right of last required category.
HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
Non-HFTD Distribution
HFTD 2 Distribution | 0.047538 | 0.031982 | 0.015556 | 0.013222 | 0.03454 | 0.025 | 0.02837 |  | 4.0466 | 542.8529 |  |  |  | 412.8923
HFTD 3 Distribution | 0.1547 | 0.13119 | 0.023512 | 0.03971 | 0.06088 | 0.02857 | 0.05228 |  | 8.7489 | 719.6897 |  |  |  | 192.7886
Non-HFTD Transmission
HFTD 2 Transmission
HFTD 3 Transmission

## Table 15
Utility | SDGE
Table No. | 15
Date Modified | 2024-11-01
Table 15: Top Risk Circuit Scores
*EC to add all other risk categories to right of last required category.
Top- Risk Circuit/ Segment/ Span ID | Risk Granularity | Line Class | Circuit/ Segment/ Span Length (mi) | Inclusion Reason | HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
237-30R | Segment Level | Primary Overhead Conductor | 31.7027 | Top 5% highest risk | 3 | 0.0071378 | 0.0070124 | 0.00012549 | 0.0015737 | 0.05575 | 0 | 0.0361 |  | 0.038501 | 4.456 |  |  |  | 0.77479
909-805R | Segment Level | Primary Overhead Conductor | 17.9655 | Top 5% highest risk | 3 | 0.0070517 | 0.0069859 | 6.5722e-05 | 0.0011743 | 0.03717 | 0.00533 | 0.02166 |  | 0.024392 | 5.9492 |  |  |  | 0.64051
222-1401R | Segment Level | Primary Overhead Conductor | 24.7428 | Top 5% highest risk | 3 | 0.0069137 | 0.006763 | 0.00015078 | 0.0011834 | 0.04646 | 0.00533 | 0.02166 |  | 0.061625 | 5.7151 |  |  |  | 0.58163
524-69R | Segment Level | Primary Overhead Conductor | 30.7449 | Top 5% highest risk | 3 | 0.0054614 | 0.0053589 | 0.00010255 | 0.00069999 | 0.06504 | 0 | 0.0361 |  | 0.027883 | 7.6557 |  |  |  | 0.87426
222-1364R | Segment Level | Primary Overhead Conductor | 29.0487 | Top 5% highest risk | 3 | 0.0048739 | 0.0045724 | 0.0003015 | 0.0012567 | 0.05575 | 0.00533 | 0.02166 |  | 0.048496 | 3.6384 |  |  |  | 1.4779
448-11R | Segment Level | Primary Overhead Conductor | 26.0403 | Top 5% highest risk | 3 | 0.0034275 | 0.0030746 | 0.00035286 | 0.001268 | 0.02787 | 0.00533 | 0.01444 |  | 0.11151 | 2.4248 |  |  |  | 0.75224
217-983R | Segment Level | Primary Overhead Conductor | 6.8258 | Top 5% highest risk | 3 | 0.0029979 | 0.0029499 | 4.8037e-05 | 0.0004178 | 0 | 0 | 0 |  | 0.046607 | 7.0605 |  |  |  | 0.24501
222-1370R | Segment Level | Primary Overhead Conductor | 13.7777 | Top 5% highest risk | 3 | 0.003084 | 0.0028076 | 0.00027642 | 0.00055786 | 0.01858 | 0 | 0.02888 |  | 0.061625 | 5.0329 |  |  |  | 1.0663
358-682F | Segment Level | Primary Overhead Conductor | 10.4536 | Top 5% highest risk | 3 | 0.0029468 | 0.0027387 | 0.00020816 | 0.00057108 | 0.00929 | 0.01067 | 0.02888 |  | 0.094315 | 4.7956 |  |  |  | 0.52467
157-81R | Segment Level | Primary Overhead Conductor | 28.2803 | Top 5% highest risk | 3 | 0.0025865 | 0.0024851 | 0.00010138 | 0.00055707 | 0.01858 | 0 | 0.04331 |  | 0.027883 | 4.4611 |  |  |  | 0.86429
1030-989R | Segment Level | Primary Overhead Conductor | 18.3203 | Top 5% highest risk | 3 | 0.0025165 | 0.0024432 | 7.3369e-05 | 0.00093193 | 0.01858 | 0 | 0.01444 |  | 0.050816 | 2.6216 |  |  |  | 0.34322
79-808R | Segment Level | Primary Overhead Conductor | 10.257 | Top 5% highest risk | 3 | 0.0022855 | 0.002219 | 6.6476e-05 | 0.00058203 | 0.01858 | 0 | 0.00722 |  | 0.085084 | 3.8126 |  |  |  | 0.18573
73-643R | Segment Level | Primary Overhead Conductor | 12.4727 | Top 5% highest risk | 3 | 0.002406 | 0.0022098 | 0.00019624 | 0.000619 | 0.00929 | 0 | 0.00722 |  | 0.032283 | 3.5699 |  |  |  | 1.445
237-1765R | Segment Level | Primary Overhead Conductor | 7.3028 | Top 5% highest risk | 3 | 0.0022577 | 0.0021647 | 9.3007e-05 | 0.00034129 | 0.03717 | 0 | 0.00722 |  | 0.053686 | 6.3428 |  |  |  | 0.41183
214-1122R | Segment Level | Primary Overhead Conductor | 17.9733 | Top 5% highest risk | 3 | 0.0022373 | 0.0021261 | 0.00011124 | 0.00094677 | 0.03717 | 0 | 0.00722 |  | 0.036683 | 2.2456 |  |  |  | 0.72083
1215-32R | Segment Level | Primary Overhead Conductor | 11.565 | Top 5% highest risk | 3 | 0.002094 | 0.0019926 | 0.00010146 | 0.00071302 | 0.00929 | 0 | 0.02166 |  | 0.1303 | 2.7946 |  |  |  | 0.1851
237-17R | Segment Level | Primary Overhead Conductor | 13.629 | Top 5% highest risk | 2 | 0.0021463 | 0.0018932 | 0.00025313 | 0.00031356 | 0.06504 | 0 | 0.0361 |  | 0.023005 | 6.0376 |  |  |  | 2.6157
220-298R | Segment Level | Primary Overhead Conductor | 32.6462 | Top 5% highest risk | 3 | 0.0020342 | 0.0018868 | 0.00014736 | 0.0016389 | 0 | 0 | 0.04331 |  | 0.085634 | 1.1513 |  |  |  | 0.40906
217-837R | Segment Level | Primary Overhead Conductor | 11.5797 | Top 5% highest risk | 3 | 0.0019793 | 0.0017697 | 0.00020954 | 0.0005441 | 0.00929 | 0 | 0.0361 |  | 0.02377 | 3.2526 |  |  |  | 2.0955
73-683R | Segment Level | Primary Overhead Conductor | 9.9674 | Top 5% highest risk | 3 | 0.0018435 | 0.0017472 | 9.6297e-05 | 0.00047296 | 0 | 0 | 0.00722 |  | 0.032283 | 3.6942 |  |  |  | 0.70908
157-232R | Segment Level | Primary Overhead Conductor | 10.3659 | Top 5% highest risk | 3 | 0.0019805 | 0.0017153 | 0.00026522 | 0.00056298 | 0.03717 | 0 | 0.02166 |  | 0.057225 | 3.0468 |  |  |  | 1.1018
445-1311R | Segment Level | Primary Overhead Conductor | 11.4862 | Top 5% highest risk | 3 | 0.0017235 | 0.001547 | 0.0001765 | 0.00069027 | 0 | 0 | 0.01444 |  | 0.1303 | 2.2412 |  |  |  | 0.32199
235-899R | Segment Level | Primary Overhead Conductor | 9.8138 | Top 5% highest risk | 2 | 0.0017584 | 0.0015266 | 0.00023184 | 0.00022114 | 0.01858 | 0 | 0.02888 |  | 0.023005 | 6.9033 |  |  |  | 2.3957
222-2013R | Segment Level | Primary Overhead Conductor | 15.1184 | Top 5% highest risk | 3 | 0.0015989 | 0.0014909 | 0.00010806 | 0.00079337 | 0.02787 | 0 | 0.00722 |  | 0.049883 | 1.8792 |  |  |  | 0.51494
521-14R | Segment Level | Primary Overhead Conductor | 11.8083 | Top 5% highest risk | 3 | 0.0016341 | 0.0014883 | 0.00014577 | 0.00027393 | 0.01858 | 0 | 0.01444 |  | 0.053136 | 5.4331 |  |  |  | 0.65215
970-1341R | Segment Level | Primary Overhead Conductor | 4.1301 | Top 5% highest risk | 3 | 0.0015913 | 0.0013957 | 0.00019561 | 0.00021206 | 0.02787 | 0 | 0 |  | 0.053686 | 6.5818 |  |  |  | 0.86613
217-835R | Segment Level | Primary Overhead Conductor | 17.6886 | Top 5% highest risk | 3 | 0.0014356 | 0.0013957 | 3.9966e-05 | 0.00027313 | 0.00929 | 0 | 0 |  | 0.028361 | 5.1099 |  |  |  | 0.33499
216-1857 | Segment Level | Primary Overhead Conductor | 6.5295 | Top 5% highest risk | 3 | 0.001424 | 0.0013795 | 4.4488e-05 | 0.0004345 | 0 | 0 | 0.00722 |  | 0.026353 | 3.1749 |  |  |  | 0.40131