## Tab 1 - Overview tab
IE ARC Attachments
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | SDGE
Legends
Tab 1 | Overview Tab - Instructions and overview
Tab 2 | Catalog of Initiatives - Initiative review and funding compliance of all initiatives
Tab 3 | Data Requests - Comprehensive list of documents reviewed
Tab 4 | SME Interviews - Summary of interviews conducted
Tab 5 | List of Failed-to-Fund Initiatives - All initiatives funded less than 100%

## Tab 2 - Catalog of Initiatives
Catalog of Initiatives
Independent Evaluator: |  | Bureau Veritas
Electrical Corporation: |  | SDGE
WMP Category | Initiative Tracking ID | WMP Section Number | Initiative Name | Initiative Type | WMP - Initiative Description | WMP - Initiative Target | EC-Claimed Progress (Q4 QDR) | EC-Claimed Progress (EC ARC) | EC-Claimed Progress | EC-Claimed Initiative Status | Target Not Met - Rationale | Sample Size (#) | Sample Validation Rate (%) | Verification Method | Initiative Validation Rate (%) | IE Finding on Initiative | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%) | Funding discrepancy - finding | Funding discrepancy - detail | Satisfied Risk Reduction Goal - finding | Satisfied Risk Reduction Goal - detail
Grid Design Operations and Maintenance | WMP.449 | 8.1.8.2 | Wireless Fault Indicators | Non-focus & non-field verifiable | 300 Wireless Fault Indicators | 300 | 0 | 0 | 0 | Target not met | Program was paused due to manufacturer upgrades requiring different communications specifications not currently employed. | N/A | N/A | SDG&E Written Response (DR029) | 0% | Initiative not validated | 0 | 0 | 0% | No discrepancy |  | Yes | N/A
Grid Design Operations and Maintenance | WMP.453 | 8.1.4.3 | Capacitor Maintenance and Replacement Program (SCADA) | Non-focus & non-field verifiable | No Target | 0 | 1 | 1 | 1 | Target met | N/A | 1 | 100% | Capacitor GIS Data (DR005b) Project As-Builts (DR030) | 100% | Initiative validated | 287 | 204 | -28.9% | Underspend | Reduced unit costs and minimal expenditures for residual trailing costs. | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | WMP.455 | 8.1.2.1 | Distribution Overhead Hardening (Covered Conductor) | Focus & field verifiable | 60 Miles | 60 | 35.9 | 35.9 | 35.9 | Target not met | Workplan for this initiative anticipated a reduction in target. Initiative faced delays related to land acquisition, final engineering, permitting, environmental permitting, customer negotiations, material availability, and Santa Ana Wind Events. | 42 | 100% | Field Inspection Distribution Overhead Hardening GIS Data (DR005b) As-Builts (DR011b, DR011c) | 60% | Initiative not validated | 79890 | 78642 | -1.6% | Underspend | Less than 10% variance | No | EC did not meet its target by 40% and did not meet its intended risk reduction
Grid Design Operations and Maintenance | WMP.459 | 8.1.4.4 | Expulsion Fuse Replacement | Non-focus & non-field verifiable | No Target | 0 | 188 | 188 | 188 | Target met | N/A | 23 | 100% | Expulsion Fuse Replacement GIS Data (DR005b) As-Builts (DR031) | 100% | Initiative validated | 1463 | 207 | -85.9% | Underspend | Cost reductions achieved through direct cost savings and bundling work with other programs. | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | WMP.461 | 8.1.2.11.1 | PSPS Sectionalizing Enhancements | Non-focus & non-field verifiable | Install 10 Switches | 10 | 18 | 18 | 18 | Target met | N/A | 9 | 100% | PSPS Sectionalizing List (DR012) As-Builts/Redline Submission (DR012.b) | 180% | Initiative validated | 1786 | 2135 | 19.5% | Overspend | Installation of additional devices beyond the initial plan. | Yes | N/A
Grid Design Operations and Maintenance | WMP.462 | 8.1.2.7 | Microgrids | Non-focus & non-field verifiable | 4 Microgrids | 4 | 0 | 0 | 0 | Target not met | Battery storage has not been completed for the Microgrids. Renewable generation has been put on hold for 3 sites due to SDG&E's 2024 GRC decision. | N/A | N/A | SDG&E Written Response (DR032) | 0% | Initiative not validated | 7715 | 7396 | -4.1% | Underspend | Less than 10% variance | Yes | N/A
Grid Design Operations and Maintenance | WMP.463 | 8.1.2.8.1 | Advanced Protection | Focus & field verifiable | 8 Circuits | 8 | 5 | 5 | 5 | Target not met | Crews were reallocated to work on Strategic Undergrounding and Covered Conductor initiatives in November and December. | 5 | 100% | Field Inspection GIS Data (DR005b, DR013c) As-Builts (DR013b) SME Interview (DR013c) | 63% | Initiative not validated | 15810 | 11130 | -29.6% | Underspend | Crews were reallocated to other priority wildfire mitigation programs. | No | EC did not meet its target by >30% and did not meet its intended risk reduction
Grid Design Operations and Maintenance | WMP.464 | 8.1.4.5 | Maintenance, Repair, and Replacement of Connectors, Including Hotline Clamps | Focus & field verifiable | 250 Hotline Clamps | 250 | 678 | 678 | 678 | Target met | N/A | 83 | 100% | Field Inspection Hotline Clamp GIS Data (DR005b) | 271% | Initiative validated | 1702 | 802 | -52.9% | Underspend | Achieved cost efficiencies through bundling maintenance activities with other scheduled work. | Yes
Grid Design Operations and Maintenance | WMP.466 | 8.1.2.11.3 | Generator Grant Program | Non-focus & non-field verifiable | Continue to provide portable backup power solutions to vulnerable, electricity dependent customers | Continue to provide portable backup power solutions to vulnerable, electricity dependent customers | Customer eligibility lists were updated and provided to contractor on a recurring basis. Contractor conducted scheduling, delivery, and product training to all eligible customers who enrolled in the program, and completing final 2024 report. | N/A | N/A | Target met | N/A | N/A | N/A | SDGE Written Response Generator Grant Program Annual 2024 (DR014) |  | Initiative validated | 3139 | 927 | -70.5% | Underspend | Delays attributed to battery market availability and General Rate Case (GRC) budget implications. | N/A | N/A
Grid Design Operations and Maintenance | WMP.467 | 8.1.2.11.4 | Generator Assistance Program | Non-focus & non-field verifiable | Continue to provide rebates on portable backup power solutions to customers who experience PSPS | Continue to provide rebates on portable backup power solutions to customers who experience PSPS | Customer eligibility list provided to vendor monthly. Year end letters sent to customers on 12/18/24. | N/A | N/A | Target met | N/A | N/A | N/A | SDGE Written Response Generator Assistance Program Final 2024 (DR015) |  | Initiative validated | 486 | 478 | -1.6% | Underspend | Less than 10% variance | N/A | N/A
Grid Design Operations and Maintenance | WMP.468 | 8.1.2.11.2 | Standby Power (Fixed Power Backup) | Non-focus & non-field verifiable | Install 300 Generators | 300 | 54 | 54 | 54 | Target not met | Nov. 1 2023 - Proposed change to reduce target from 300 to 58. Rejected May 13, 24. | 17 | 100% | List of Fixed Power Backup Installations (DR016) Fixed Power Backup Application/Work Flow (DR016.b) | 18% | Initiative not validated | 5377 | 5207 | -3.2% | Underspend | Less than 10% variance | No | SDG&E fell short of installing 300 generators therefore not meeting the risk reduction goal
Grid Design Operations and Maintenance | WMP.473 | 8.1.2.2 | Strategic Undergrounding | Focus & field verifiable | 125 Miles | 125 | 112 | 112 | 112 | Target met | N/A | 58 | 100% | Field Inspection Strategic Undergrounding GIS Data(DR005b) As-Builts (DR034) | 90% | Initiative not validated | 301729 | 217140 | -28% | Underspend | Underspend due to construction delays and cost efficiencies realized through competitive bidding. | Yes | N/A
Grid Design Operations and Maintenance | WMP.475 | 8.1.2.5.1 | Distribution Overhead System Hardening | Focus & field verifiable | No Target | 0 | 0.5 | 0.5 | 0.5 | Target met | N/A | 0.54 | 100% | Field Inspection Distribution Overhead System Hardening GIS Data (DR005b) As-Builts (DR035) | 100% | Initiative validated | 3281 | 6459 | 96.9% | Overspend | Additional unplanned construction was transferred into this initiative. | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | WMP.478 | 8.1.3.1 | Distribution Overhead Detailed Inspections | Focus & non-field verifiable | Complete 15,450 Overhead Distribution Inspections | 15450 | 16503 | 16503 | 16503 | Target met | N/A | 73 | 100% | Distribution Overhead Inspections List (DR017) Inspection Results List (DR017.b) | 106% | Initiative validated | 6841 | 8550 | 25% | Overspend | Greater-than-anticipated completion of corrective maintenance activities. | Yes | N/A
Grid Design Operations and Maintenance | WMP.479 | 8.1.3.2 | Transmission Overhead Detailed Inspections | Non-focus & non-field verifiable | Complete 1,960 Overhead Tranmission Inspections | 1960 | 2940 | 2940 | 2940 | Target met | N/A | 18 | 100% | Transmission Overhead Inspections List (DR018) SDGE Written Response (DR018.b) | 150% | Initiative validated | 1743 | 1030 | -40.9% | Underspend | Lower-than-anticipated repairs required based on historical equipment conditions. | Yes | N/A
Grid Design Operations and Maintenance | WMP.481 | 8.1.3.3 | Distribution infrared Inspections | Non-focus & non-field verifiable | Complete 9,532 Distribution Infrared Inspections | 9532 | 6398 | 6398 | 6398 | Target not met | Nov. 1 2023 - Proposed to change target from 9500 structures to 300 structures. Rejected May 13, 2024 | 18 | 100% | Distribution Infrared Inspection List 2023 Change Order Request 2025 Change Order Request 2025 Petition to Amend (DR036) | 67% | Initiative not validated | 10 | 145 | 1350% | Overspend | The budget was adjusted to align with the 2024 General Rate Case (GRC). | No | SDG&E did not fully complete distribution infrared inspections therefore not meeting the risk reduction goal
Grid Design Operations and Maintenance | WMP.482 | 8.1.3.4 | Transmission Infrared Inspections | Non-focus & non-field verifiable | Complete 6,179 Transmission Infrared Inspections | 6179 | 7161 | 7161 | 7161 | Target met | N/A | 18 | 100% | Transmission Infrared Inspection List (DR019) SDGE Written Response (DR019.b) | 115% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | Yes | N/A
Grid Design Operations and Maintenance | WMP.483 | 8.1.3.5 | Distribution Wood Pole Intrusive Inspections | Non-focus & non-field verifiable | Complete 0 Distribution Wood Pole Intrusive Inspections | 0 | 2225 | 2225 | 2225 | Target met | N/A | 18 | 100% | Distribution Wood Pole Inspection List (DR020) SDGE Written Response (DR020.b) |  | Initiative validated | 1025 | 296 | -71.1% | Underspend | Corrective actions were funded through other program budgets. | Yes | N/A
Grid Design Operations and Maintenance | WMP.488 | 8.1.3.8 | Distribution Overhead Patrol Inspections | Focus & non-field verifiable | Complete 86,197 Distribution Overhead Patrol Inspections | 86197 | 86140 | 86140 | 86140 | Target met | N/A | 73 | 100% | Distribution Overhead Patrol Inspection List (DR021)-SDGE Written Response (DR021.b) | 99% | Initiative validated | 857 | 2708 | 216% | Overspend | Overspend due to significantly more corrective maintenance than anticipated. | Yes | N/A
Grid Design Operations and Maintenance | WMP.489 | 8.1.3.9 | Transmission Overhead Patrol Inspections | Non-focus & non-field verifiable | Complete 6,337 Transmission Overhead Patrol Inspections | 6337 | 7366 | 7366 | 7366 | Target met | N/A | 18 | 100% | Transmission Overhead Patrol Inspection List (DR022) SDGE Written Response (DR022.b) | 116% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | Yes | N/A
Grid Design Operations and Maintenance | WMP.491 | 8.1.6.2 | Quality Assurance/Quality Control of Distribution Detailed Inspections | Non-focus & non-field verifiable | 77 Structures | 77 | 440 | 440 | 440 | Target met | N/A | 23 | 100% | QA/QC GIS Data (DR005b) | 100% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | WMP.492 | 8.1.3.11 | Substation Patrol Inspections | Non-focus & non-field verifiable | Complete 384 Substation Inspections | 384 | 379 | 379 | 379 | Target met | N/A | 17 | 100% | Substation Patrol Inspection List (DR023) SDGE Written Response (DR023.b) Substation Inspection Reports (DR023.b) | 98% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | Yes | N/A
Grid Design Operations and Maintenance | WMP.543 | 8.1.2.5.2 | Transmission Overhead Hardening | Non-focus & field verifiable | 10.2 Miles | 10.2 | 9.08 | 9.08 | 9.08 | Target met | N/A | 9.08 | 100% | Field Inspection Transmission Overhead Hardening GIS Data (DR005b) As-Builts (DR024) | 89% | Initiative not validated | 0 | 0 | 0% | No discrepancy |  | No | EC did not meet its target by >10% and did not meet its intended risk reduction.
Grid Design Operations and Maintenance | WMP.545 | 8.1.2.5.2 | Transmission Overhead Hardening (Distribution Underbuild) | Non-focus & field verifiable | 1 Mile | 1 | 7 | 7 | 7 | Target met | N/A | 7 | 100% | Field Inspection Transmission Overhead Hardening (Distribution Underbuild) GIS Data(DR005b) As-Builts (DR044) | 700% | Initiative validated | 12464 | 12039 | -3.4% | Underspend | Less than 10% variance | Yes
Grid Design Operations and Maintenance | WMP.549 | 8.1.2.8.3 | Distribution Communications Reliability Improvements | Focus & field verifiable | 60 Base Stations | 60 | 3 | 3 | 3 | Target not met | SDG&E revised this program to align WMP costs with the 2024 General Rate Case | 3 | 100% | Field Inspection Distribution Communications Reliability Improvements GIS Data (DR005b) | 5% | Initiative not validated | 31686 | 22506 | -29% | Underspend | Budget reductions due to anticipated outcomes from the General Rate Case (GRC). | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | WMP.550 | 8.1.4.6 | Lightning Arrester Removal and Replacement | Focus & field verifiable | 1848 Lightning Arresters | 1848 | 1654 | 1654 | 1654 | Target met | N/A | 88 | 100% | Field Inspections Lightning Arrester GIS Data (DR005b) | 90% | Initiative not validated | 2983 | 2719 | -8.9% | Underspend | Less than 10% variance | No | EC did not meet its target by 10% and did not meet its intended risk reduction.
Grid Design Operations and Maintenance | WMP.552 | 8.1.3.7 | Drone Assessments | Focus & non-field verifiable | 13500 Structures | 13500 | 6529 | 6529 | 6529 | Target not met | SDG&E revised this program to align WMP costs with the 2024 General Rate Case | 92 | 100% | Drone Inspection GIS Data (DR005b) SDG&E Written Response (DR046) Inspection Reports (DR046) | 48% | Initiative not validated | 95493 | 106265 | 11.3% | Overspend | Higher-than-planned volume of corrective work identified through drone inspections. | No | EC did not meet its target by >50% and did not meet its intended risk reduction.
Grid Design Operations and Maintenance | WMP.555 | 8.1.3.10 | Transmission 69kV Tier 3 Visual Inspections | Non-focus & non-field verifiable | Complete 1,632 Transmission 69kV Tier 3 Visual Inspections | 1632 | 1605 | 1605 | 1605 | Target met | N/A | 18 | 100% | Transmission 69kV T3 Visual Inspections (DR026) SDGE Written Response (DR026.b) | 98% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | Yes | N/A
Grid Design Operations and Maintenance | WMP.972 | 8.1.2.10.1 | Avian Protection | Focus & field verifiable | 200 Poles | 200 | 774 | 774 | 774 | Target met | N/A | 84 | 100% | Field Inspections Avian Protection GIS Data (DR005b) | 387% | Initiative validated | 1113 | 1108 | -0.4% | Underspend | Less than 10% variance | Yes
Grid Design Operations and Maintenance | WMP.1189 | 8.1.2.10.2 | Strategic Pole Replacement Program | Focus & field verifiable | 267 Poles | 267 | 40 | 40 | 40 | Target not met | Delays in the bid for engineering and design for the 2024 work plan. | 40 | 100% | Field Inspections Pole Replacement GIS Data (DR005b) | 15% | Initiative not validated | 7019 | 2605 | -62.9% | Underspend | Project delays due to design firm transitions, material supply challenges, and weather-related disruptions. | No | EC did not meet its target by 85% and did not meet its intended risk reduction.
Grid Design Operations and Maintenance | WMP.1190 | 8.1.3.6 | Transmission Wood Pole Intrusive Inspections | Non-focus & non-field verifiable | Complete 0 Transmission Wood Pole Intrusive Inspections | 0 | 164 | 164 | 164 | Target met | N/A | 17 | 100% | Transmission Wood Pole Intrusive Inspection List (DR006) SDGE Written Response (DR006.b) |  | Initiative validated | 0 | 0 | 0% | No discrepancy |  | N/A | N/A
Grid Design Operations and Maintenance | WMP.1191 | 8.1.6.1 | Quality Assurance/Quality Control of Transmission Inspections | Non-focus & non-field verifiable | Complete 100% QA/QC of Transmission Inspections | 100% | 100% | 100% | 100% | Target met | N/A | 1 | 100% | QAQC Transmission Inspection List (DR007) |  | Initiative validated | 0 | 0 | 0% | No discrepancy |  | N/A | N/A
Grid Design Operations and Maintenance | WMP.1192 | 8.1.6.3 | Quality Assurance/Quality Control of Distribution Drone Assessments | Non-focus & non-field verifiable | 13500 Structures | 13500 | 6529 | 6529 | 6529 | Target met |  | 23 | 100% | Drone Assessment QA/QC GIS Data (DR005b) Drone Inspection Audit Documentation (DR028) | 100% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | WMP.1193 | 8.1.6.4 | Quality Assurance/Quality Control of Wood Pole Intrusive (Transmission and Distribution) | Non-focus & non-field verifiable | Complete 0 QA/QC Wood Pole Intrusive Inspections | 0 | 150 | 150 | 150 | Target met | N/A | 37 | 100% | QAQC Wood Pole Intrusive List (DR008) Inspection Details List (DR008.b) |  | Initiative validated | 0 | 0 | 0% | No discrepancy |  | N/A | N/A
Grid Design Operations and Maintenance | WMP.1194 | 8.1.6.5 | Quality Assurance/Quality Control of Substation Inspections | Non-focus & non-field verifiable | Complete 18 QA/QC Substation Inspections | 18 | 22 | 22 | 22 | Target met | N/A | 10 | 100% | QAQC Substation Inspection List (DR009) QAQC Substation Inspection Reports (DR009.b) | 122% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | N/A | N/A
Grid Design Operations and Maintenance | WMP.1195 | 8.1.2.8.2 | Early Fault Detection | Non-focus & field verifiable | 60 Nodes | 60 | 62 | 62 | 62 | Target met |  | 18 | 100% | Field Inspections Early Fault Detection GIS Data (DR005b) | 103% | Initiative validated | 4170 | 3600 | -13.7% | Underspend | Resource shifts in Q4 and forecasting challenges leading to reduced spending. | Yes
Vegetation Management and Inspections | WMP.494 | 8.2.2.1 | Detailed inspections | Focus & field verifiable | 485,400 Inspections | 485400 | 523949 | 523949 | 523949 | Target met |  | 92 | 100% | Detailed Inspections GIS Data (DR005b) SME Interview (DR038) | 108% | Initiative validated | 60084 | 76305 | 27% | Overspend | Increased contractor costs resulting from new service agreements. | Yes
Vegetation Management and Inspections | WMP.497 | 8.2.3 | Fuels Management | Focus & non-field verifiable | Manage 500 Poles Fuel | 500 | 147 | 147 | 147 | Target not met | SDG&E elected to reduce this program. Informed by the knowledge that the remaining poles in the fuels management inititaitves would be addressed by other risk-reducing vegetation managements measures such as pole clearing. | 64 | 100% | Fuels Management List (DR039) Fuels Management Fulcrum (DR039.b) | 29% | Initiative not validated | 5833 | 3159 | -45.8% | Underspend | Reduction in expenditures due to strategic planning aligned with anticipated General Rate Case (GRC) outcomes and cost savings from tribal collaboration efforts. | Yes | By the overcompletion of WMP.512
Vegetation Management and Inspections | WMP.501 | 8.2.3.3 | Clearance | Non-focus & non-field verifiable | Clear 11,200 Trees | 11200 | 11788 | 11788 | 11788 | Target met | N/A | 18 | 100% | Clearance List (DR040) Clearance Work Dispatch (DR040.b) | 105% | Initiative validated | 10235 | 0 | -100% | Underspend | Costs were integrated into Initiative WMP.494 (Detailed Inspections). | Yes | N/A
Vegetation Management and Inspections | WMP.505 | 8.2.5 | Quality Assurance/Quality Control Vegetation Management | Non-focus & non-field verifiable | 15% of inspections | 15 | 37 | 37 | 37 | Target met |  | 23 | 100% | QA/QC GIS Data (DR005b) SME Interview (SMEXXX) | 120% | Initiative validated | 0 | 0 | 0% | No discrepancy |  | N/A | No risk reduction goal identified for this initiative.
Vegetation Management and Inspections | WMP.508 | 8.2.2.2 | Off-Cycle Patrol | Non-focus & non-field verifiable | Complete 106 Off-Cycle Patrol of VMAs | 106 | 105 | 105 | 105 | Target met | N/A | 16 | 100% | Off-Cycle Patrol List (DR042) Off-Cycle Patrol Work Order (DR042.b) | 100% | Initiative validated | 0 | 0 | 0% | No discrepancy |  |  | N/A
Vegetation Management and Inspections | WMP.512 | 8.2.3.1 | Pole Clearing (Brushing) | Focus & non-field verifiable | Clear 33,010 Poles | 33010 | 36500 | 36500 | 36500 | Target met | N/A | 73 | 100% | Pole Clearing List (DR043) Pole Clearing Dispatch (DR043.b) | 110% | Initiative validated | 7893 | 7097 | -10.1% | Underspend | Halting the clearing of exempt poles as a cost efficiency measure. | Yes | N/A
Situational Awareness and Forecasting | WMP.970 | 4.1.2 | Air Quality Index | Non-focus & non-field verifiable | 6 Sensors | 6 | 0 | 0 | 0 | Target not met | Installations were completed in 2023 | 0 | 0% | SDG&E Written Response (DR047) | 0% | Initiative not validated | 0 | 45 | 100% | Overspend | Expenses were for maintenance and calibration of sensors installed in the previous year (2023). | N/A | No risk reduction goal identified for this initiative.
Note on K11: Number of "actuals" from which samples are selected

## Tab 3 - Data Requests
Data Requests
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | SDGE
Date Sent | Date Response Received | Section / Initiative | Data Request Number | List of Documents Received
2025-05-20 | 2025-05-23 | QAQC Questions | SDG&E_DR001 | SDGE Response IE-2025-DR001
2025-05-06 | 2025-05-08 | All | SDG&E_DR005 | SDGE Response IE-2025-DR005 SDGE_2024_Q2_NonConfidential.gdb SDGE_2024_Q4_NonConfidential.gdb
2025-05-15 | 2025-05-19 | All | SDG&E_DR005.b | SME Interview: QDRYearlyCombined.gdb RE_ Data Request DR005_b - SDGE SME Interview-email with files provided
2025-04-22 | 2025-04-25 | WMP.1190 | SDG&E_DR006 | SDGE Response IE-2025-DR006
2025-05-05 | 2025-05-08 | WMP.1190 | SDG&E_DR006.b | SDGE Response IE-2025-DR006.b SDGE Response IE-2025-DR006.b
2025-04-22 | 2025-04-29 | WMP.1191 | SDG&E_DR007 | SDGE Response IE-2025-DR007.pdf SDGE Response IE-2025-DR007.xlsx
2025-06-05 | 2025-06-09 | WMP.1191 | SDG&E_DR007.b | SDGE Response IE-2025-DR007.b
2025-04-22 | 2025-04-25 | WMP.1193 | SDG&E_DR008 | SDGE Response IE-2025-DR008
2025-04-22 | 2025-04-25 | WMP.1194 | SDG&E_DR009 | SDGE Response IE-2025-DR009
2025-05-05 | 2025-05-08 | WMP.1194 | SDG&E_DR009.b | SDGE Response IE-2025-DR009.b IE-2025-DR009.b_Inspection Reports
2025-04-22 | 2025-04-30 | WMP.1195 | SDG&E_DR010 | SDGE Response IE-2025-DR010
2025-04-22 | 2025-04-29 | WMP.455 | SDG&E_DR011 | SDGE Response IE-2025-DR011.pdf SDGE Response IE-2025-DR011.xlsx
2025-05-15 | 2025-05-23 | WMP.455 | SDG&E_DR011.b | SDGE Response IE-2025-DR011.b.pdf SDG&E Response IE-2025-DR011.b Confidentiality Declaration Will Speer signed.pdf SDGE Response IE-2025-DR011.b_Q1_Attachments.zip (41 documents)
2025-05-27 | 2025-05-30 | WMP.455 | SDG&E_DR011.c | SDGE Response IE-2025-DR011c.pdf ESH C0073 P CC OH 530000335621 Construction Redlines Redacted 20252905.pdf
2025-04-22 | 2025-04-25 | WMP.461 | SDG&E_DR012 | SDGE Response IE-2025-DR012
2025-05-27 | 2025-05-29 | WMP.461 | SDG&E_DR012.b | SDGE Response IE-2025-DR012.b.pdf SDGE Response IE-2025-DR012.b_Attachments.zip (19 documents)
2025-04-22 | 2025-04-30 | WMP.463 | SDG&E_DR013 | SDGE Response IE-2025-DR013
2025-05-15 | 2025-05-20 | WMP.463 | SDG&E_DR013.b | SDGE Response IE-2025-DR013.b.pdf SDGE Response IE-2025-DR013.b Confidentiality Declaration Will Speer.pdf FIRM C222 SS ASD SCOPE WO#530000314632 FINAL AS-BUILT_2 of 2_CONFIDENTIAL.pdf ESH C521 A APP WO#530000364743 FINAL AS-BUILT_CONFIDENTIAL.pdf ESH_C0907_A_APP_WO 530000370511_ASBUILT_CONFIDENTIAL.pdf FCP_C78_53X281822 ASBUILT_CONFIDENTIAL.pdf FIRM C222 SS ASD SCOPE WO#530000314632 FINAL AS-BUILT_1 of 2_CONFIDENTIAL.pdf
2025-05-23 | 2025-05-29 | WMP.463 | SDG&E_DR013.c | SDGE Response IE-2025-DR013.c.pdf SDGE Response IE-2025-DR013.c - Advanced Protection.xlx
2025-04-22 | 2025-04-30 | WMP.466 | SDG&E_DR014 | SDGE Response IE-2025-DR014.pdf; Generator Grant Program (WMP.466)_Annual report_PY 2024.pdf
2025-04-22 | 2025-04-30 | WMP.467 | SDG&E_DR015 | SDGE Response IE-2025-DR015.pdf; Generator Assistance Program-Final_2024.pdf
2025-04-22 | 2025-04-29 | WMP.468 | SDG&E_DR016 | SDGE Response IE-2025-DR016.pdf SDGE Response IE-2025-DR016.xlsx
2025-05-27 | 2025-05-30 | WMP.468 | SDG&E_DR016.b | SDGE Response IE-2025-DR016.b.pdf SDGE Response IE-2025-DR016.b Confidentiality Declaration.pdf SDGE Response IE-2025-DR016.b_Attachments file (16 doucments)
2025-04-22 | 2025-04-25 | WMP.478 | SDG&E_DR017 | SDGE Response IE-2025-DR017
2025-05-05 | 2025-05-08 | WMP.478 | SDG&E_DR017.b | SDGE Response IE-2025-DR017.b SDGE Response IE-2025-DR017.b
2025-04-22 | 2025-04-25 | WMP.479 | SDG&E_DR018 | SDGE Response IE-2025-DR018
2025-05-20 | 2025-05-22 | WMP.479 | SDG&E_DR018.b | SDGE Response IE-2025-DR018.b.pdf SDGE Response IE-2025-DR018.b.xlsx
2025-04-22 | 2025-04-25 | WMP.482 | SDG&E_DR019 | SDGE Response IE-2025-DR019
2025-05-20 | 2025-05-22 | WMP.482 | SDG&E_DR019.b | SDGE Response IE-2025-DR019.b
2025-04-22 | 2025-04-25 | WMP.483 | SDG&E_DR020 | SDGE Response IE-2025-DR020
2025-05-20 | 2025-05-22 | WMP.483 | SDG&E_DR020.b | SDGE Response IE-2025-DR020.b.pdf SDGE Response IE-2025-DR020.b.xlsx
2025-04-22 | 2025-04-25 | WMP.488 | SDG&E_DR021 | SDGE Response IE-2025-DR021
2025-05-05 | 2025-05-08 | WMP.488 | SDG&E_DR021.b | SDGE Response IE-2025-DR021.b SDGE Response IE-2025-DR021.b
2025-04-22 | 2025-04-25 | WMP.489 | SDG&E_DR022 | SDGE Response IE-2025-DR022
2025-05-20 | 2025-05-22 | WMP.489 | SDG&E_DR022.b | SDGE Response IE-2025-DR022.b.pdf SDGE Response IE-2025-DR022.b.xlsx
2025-04-22 | 2025-04-29 | WMP.492 | SDG&E_DR023 | SDGE Response IE-2025-DR023.pdf SDGE Response IE-2025-DR023.xlsx
2025-05-05 | 2025-05-08 | WMP.492 | SDG&E_DR023.b | SDGE Response IE-2025-DR023.b IE-2025-DR023.b_Inspection Reports
2025-04-22 | 2025-04-30 | WMP.543 | SDG&E_DR024 | SDGE Response IE-2025-DR024.pdf; SDGE Response IE-2025-DR024.xlsx
2025-05-15 | 2025-05-20 | WMP.543 | SDG&E_DR024.b | SDGE Response IE-2025-DR024.b.pdf SDG&E Response IE-2025-DR024.b Confidentiality Declaration Will Speer.pdf File 1 - 2019-0268 IFC: 2019-0268_IFC_CONFIDENTIAL.pdf 2019-0268_EPIC_CONFIDENTIAL.pdf File 2 - 2019-0255 IFC: 2019-0255_IFC_CONFIDENTIAL.pdf File 3 - 2014-00051-ZZ IFC: 2014-00051-ZZ_IFC-WO2981470_CONFIDENTIAL.pdf
2025-06-05 | 2025-06-09 | WMP.543 | SDG&E_DR024.c | SDGE Response IE-2025-DR024.c.pdf
2025-04-22 | 2025-04-30 | WMP.549 | SDG&E_DR025 | SDGE Response IE-2025-DR025 CONFIDENTIAL_SDGE-Closeout_Package_Division_Substation_PPT SDG&E Response IE-2025-DR025 Confidentiality Declaration Will Speer CONFIDENTIAL_82052_Division_Substation_Drive_and_LTE_Verification_Test_Results
2025-04-22 | 2025-04-25 | WMP.555 | SDG&E_DR026 | SDGE Response IE-2025-DR026
2025-05-05 | 2025-05-08 | WMP.555 | SDG&E_DR026.b | SDGE Response IE-2025-DR026.pdf SDGE Response IE-2025-DR026.xlx
2025-05-20 | 2025-05-23 | WMP.1192 | SDG&E_DR028 | SDGE Response IE-2025-DR028.pdf SDGE Response IE-2025-DR028.xlsx
2025-05-15 | 2025-05-20 | WMP.473 | SDG&E_DR034 | SDG&E Response IE-2025-DR032 Confidentiality Declaration Will Speer.pdf SDGE Response IE-2025-DR034.pdf SDGE Response IE-2025-DR034_Q1 Attachments.zip
2025-05-29 | 2025-05-30 | WMP.473 | SDG&E_DR034.b | SDGE Response IE-2025-DR034b.pdf
2025-06-05 | 2025-06-09 | WMP.473 | SDG&E_DR034.c | SDGE Response IE-2025-DR034.c.pdf
2025-05-15 | 2025-05-21 | WMP.475 | SDG&E_DR035 | SDGE Response IE-2025-DR035.pdf ESHC0445VASD_WO#530000248958_FinalAs-Built_20250519145645.011_X_Redacted.pdf FiRMC0217ZWO#530000350672FinalAs-Built_20250519055955.933_X-Redacted.pdf
2025-05-13 | 2025-05-16 | WMP.481 | SDG&E_DR036 | SDGE Response IE-2025-DR036.xlx SDGE Response IE-2025-DR036 SDGE_2025_Petition_To_Amend_R0 2025-01-27_SDGE_2025_Change Order Report_R0 2023-12-19_SDGE_2023_Change Order Report_R1
2025-06-05 | 2025-06-09 | WMP.481 | SDG&E_DR036.b | SDGE Response IE-2025-DR036.b.pdf
2025-05-20 | 2025-05-23 | WMP.491 | SDG&E_DR037 | SDGE Response IE-2025-DR037.pdf SDGE Response IE-2025-DR037_Inspection Reports_Redacted.zip: IE-2025-DR37 Eastern 1st QTR 2024 OH QA_Redacted.pdf IE-2025-DR37 Northeast 1st QTR 2024 OH QA_Redacted.pdf IE-2025-DR37 Northeast 2nd QTR 2024 OH QA_Redacted.pdf IE-2025-DR37 Northeast 3rd QTR 2024 OH QA_Redacted.pdf IE-2025-DR37 Northeast 4th QTR 2023 OH QA_Redacted.pdf IE-2025-DR37 Orange County 2nd QTR 2024 OH QA_Redacted.pdf IE-2025-DR37 Ramona 1st QTR 2024 OH QA_Redacted.pdf IE-2025-DR37 Ramona 2nd QTR 2024 OH QA_Redacted.pdf
2025-05-20 | 2025-05-22 | WMP.494 | SDG&E_DR038 | SDGE Response IE-2025-DR038 SDG&E DR038; DR041 Meeting Minutes 05.22.25 (SME Interview)
2025-05-13 | 2025-05-15 | WMP.497 | SDG&E_DR039 | SDGE Response IE-2025-DR039_Q01 SDGE Response IE-2025-DR039
2025-05-27 | 2025-05-30 | WMP.497 | SDG&E_DR039.b | SDGE Response IE-2025-DR039.b.pdf SDGE Response IE-2025-DR039.b_Q01.xlx
2025-05-13 | 2025-05-15 | WMP.501 | SDG&E_DR040 | SDGE Response IE-2025-DR040_Q01 SDGE Response IE-2025-DR040
2025-05-27 | 2025-05-29 | WMP.501 | SDG&E_DR040.b | SDGE Response IE-2025-DR040.b.pdf SDGE Response IE-2025-DR040.b.xlx
2025-05-20 | 2025-05-22 | WMP.505 | SDG&E_DR041 | SDGE Response IE-2025-DR041 SDG&E DR038; DR041 Meeting Minutes 05.22.25 (SME Interview)
2025-05-29 | 2025-05-30 | WMP.505 | SDG&E_DR041.b | SDGE Response IE-2025-DR041b.pdf
2025-05-13 | 2025-05-15 | WMP.508 | SDG&E_DR042 | SDGE Response IE-2025-DR042_Q01 SDGE Response IE-2025-DR042
2025-05-27 | 2025-05-29 | WMP.508 | SDG&E_DR042.b | SDGE Response IE-2025-DR042.b.pdf IE-2025-DR042.b.Q01_Redacted.pdf
2025-05-13 | 2025-05-15 | WMP.512 | SDG&E_DR043 | SDGE Response IE-2025-DR043_Q01 SDGE Response IE-2025-DR043
2025-05-27 | 2025-05-29 | WMP.512 | SDG&E_DR043.b | SDGE Response IE-2025-DR043.b.pdf SDGE Response IE-2025-DR043.b.xlx
2025-05-15 | 2025-05-20 | WMP.545 | SDG&E_DR044 | SDGE Response IE-2025-DR044.pdf SDG&E Response IE-2025-DR044 Confidentiality Declaration Will Speer.pdf File 1 - 2019-0268 Dist IFC: 2019-0268_IFC-WO53-356446_CONFIDENTIAL.pdf 2019-0268_IFC-WO53-356838_CONFIDENTIAL.pdf 2019-0268_IFC-WO53-356294_CONFIDENTIAL.pdf File 2 - 2014-00051-ZZ Dist IFC: 2014-00051-ZZ_IFC-WO53-303415_CONFIDENTIAL.pdf 2014-00051-ZZ_IFC-WO53-303441_CONFIDENTIAL.pdf 2014-00051-ZZ_IFC-WO53-302559_CONFIDENTIAL.pdf 2014-00051-ZZ_IFC-WO53-303271_CONFIDENTIAL.pdf 2014-00051-ZZ_IFC-WO53-303412_CONFIDENTIAL.pdf 2014-00051-ZZ_IFC-WO53-303412_CONFIDENTIAL.pdf 2014-00051-ZZ_IFC-WO53-303414_CONFIDENTIAL.pdf File 3 - 2014-00009-ZZ Dist IFC: 2014-00009-ZZ_IFC-WO53-330493_CONFIDENTIAL.pdf 2014-00009-ZZ_IFC-WO53-330512_CONFIDENTIAL.pdf
2025-06-05 | 2025-06-09 | WMP.550 | SDG&E_DR045 | SDGE Response IE-2025-DR045.pdf
2025-05-20 | 2025-05-22 | WMP.552 | SDG&E_DR046 | SDGE Response IE-2025-DR046.pdf SDGE_2025_Petition_To_Amend_R0.pdf 2025-01-27_SDGE_2025_Change Order Report_R0.pdf SDGE Response IE-2025-DR046_Q1_Drone Assessments_Inspection Reports.zip (17 documents)
2025-05-19 | 2025-05-22 | WMP.1193 | SDGE_DR008.b | SDGE Response IE-2025-DR008.b.pdf SDGE Response IE-2025-DR008.b_Q01.xlsx SDGE Response IE-2025-DR008.b_Q02.xlsx SDGE Response IE-2025-DR008.b_Q03.xlsx
2025-05-19 | 2025-05-21 | WMP. 449 | SDGE_DR029 | SDGE Response IE-2025-DR029.pdf
2025-05-19 | 2025-05-21 | WMP.453 | SDGE_DR030 | SDGE Response IE-2025-DR030.pdf HFTD_Cap_53x267992_Asbuilt_Redacted.pdf HFTD_Cap_53x267992_SCADA.pdf HFTD_Cap_53x267992.pdf
2025-05-19 | 2025-05-22 | WMP.459 | SDGE_DR031 | SDGE Response IE-2025-DR031.pdf SDGE Response IE-2025-DR031_Attachments.zip (11 documents)
2025-05-19 | 2025-05-22 | WMP.462 | SDGE_DR032 | SDGE Response IE-2025-DR032.pdf
2025-05-19 | 2025-05-21 | WMP.970 | SDGE_DR047 | SDGE Response IE-2025-DR047.pdf

## Tab 4 - SME Interviews
SME Interviews
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | SDGE
Interview date | Section / Initiative | SME interview number | Positions interviewed | Summary of interview
2025-05-19 | NA - DR005.b - Geodatabase | SME001 |  | Overview of demonstration of geodatabase to verify team is interpreting it correctly and getting the right data. SDGE shared screen of latest tempate from Energy Safety GDB V4.0. SDGE reiterated the process the C2 team is performing is correct and could zip files to send to match up quarter by quarter. Layers from 2024 are combined for grid hardening point and grid hardening line.
2025-05-20 | NA - Drone Coordination | SME002 |  | Drone team of C2 explains that imagery will be easier for areas that are inaccessible, pilot certifications can be provided as well as insurance and that sampling requirements need to be fulfilled. SDGE has strict policies in place for military, FAA, sensitivity and privacy, etc. and that this is a unique situation and request for approvals of items, already has drone imagery and can provide photos. Will have to look at contract and IE scope by Energy Safety to make call. C2 ensured SDGE that team is looking at as-builts and SDGE agrees this is best. C2 will adjust sample sizing to make adjustments to locations.
2025-05-22 | DR038 - WMP.494 & DR041 - WMP.505 | SME003 |  | Overview of process for both initiatives, verificatoin and validation, lessons learned, any other points. Screen shared for database showing the interface that contractors have when working and data is captured in various records, mobile app is Epoch Work Managment System. Inventories trees, veg. mgmt. areas are displayed, based on master schedule, field team of inspectors, if in HFTD scondary activity would be added for required work, different data captured for inspector. Validation in conjunction with QAQC is run by different contractor/auditor but in same system.
2025-05-29 | DR013.c - WMP.463 | SME004 |  | Discussion of Advanced Protection initiative involving what equipment is installed, communications, use of field devices, non-field components, data monitoring, substation has central computer - RTAC - Real Time Automation Controller. SDGE mentioned a response is forthcominmg for the data request for structure locations of field devices that are not included in geodatabase QDR data.
2025-05-30 | DR041.b - WMP.505 | SME005 |  | Understanding the calculations for Veg. Mgmt.QA/QC initiative used for QDR reporting and in ARC with reports completoin at 37% of inspections. Target for 2024 was 12-15% of inspections for each individual initiative; SDGE looks at the programs to determine whether the QA/QC is met and exceeded sample target for each in 2024. Calculation is different in ARC than reported is an average of the completion of the individual initiatives represented as a percentage.
2025-06-09 | DR024.c - WMP.543 DR034.c - WMP.473 DR045 - WMP.505 | SME006 |  | Discussion of the criteria for classification of initiative status, what are they and how were they developed. Statuses were defined by Energy Safety and left to the EC to determine. SDGE uses 90%-110% for Completed, less than 90% for Delayed, and Greater than 110% for exeeded. Discussion of how risk impact is calculated for initiatives. SDGE takes the difference between the pre and post mitigation risk likelihood and consequence and allocate between the years of the WMP cycle.

## Tab 5 - List of "Fail-to-Fund"
List of Failed-to-Fund Initiatives
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | SDGE
WMP Category | WMP Section Number | WMP Page Number | Initiative Tracking ID | Initiative Name | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%)
Grid Design Operations and Maintenance | 8.1.4.3 | 214 | WMP.453 | Capacitor Maintenance and Replacement Program (SCADA) | 287 | 204 | 28.92%
Grid Design Operations and Maintenance | 8.1.2.1 | 152 | WMP.455 | Distribution Overhead Hardening (Covered Conductor) | 79890 | 78642 | 1.562%
Grid Design Operations and Maintenance | 8.1.4.4 | 215 | WMP.459 | Expulsion Fuse Replacement | 1463 | 207 | 85.85%
Grid Design Operations and Maintenance | 8.1.2.7 | 162 | WMP.462 | Microgrids | 7715 | 7396 | 4.135%
Grid Design Operations and Maintenance | 8.1.2.8.1 | 164 | WMP.463 | Advanced Protection | 15810 | 11130 | 29.6%
Grid Design Operations and Maintenance | 8.1.4.5 | 217 | WMP.464 | Maintenance, Repair, and Replacement of Connectors, Including Hotline Clamps | 1702 | 802 | 52.88%
Grid Design Operations and Maintenance | 8.1.2.11.3 | 178 | WMP.466 | Generator Grant Program | 3139 | 927 | 70.47%
Grid Design Operations and Maintenance | 8.1.2.11.4 | 180 | WMP.467 | Generator Assistance Program | 486 | 478 | 1.646%
Grid Design Operations and Maintenance | 8.1.2.11.2 | 176 | WMP.468 | Standby Power (Fixed Power Backup) | 5377 | 5207 | 3.162%
Grid Design Operations and Maintenance | 8.1.2.2 | 154 | WMP.473 | Strategic Undergrounding | 301729 | 217140 | 28.03%
Grid Design Operations and Maintenance | 8.1.3.2 | 186 | WMP.479 | Transmission Overhead Detailed Inspections | 1743 | 1030 | 40.91%
Grid Design Operations and Maintenance | 8.1.3.5 | 193 | WMP.483 | Distribution Wood Pole Intrusive Inspections | 1025 | 296 | 71.12%
Grid Design Operations and Maintenance | 8.1.2.5.2 | 160 | WMP.545 | Transmission Overhead Hardening (Distribution Underbuild) | 12464 | 12039 | 3.41%
Grid Design Operations and Maintenance | 8.1.2.8.3 | 171 | WMP.549 | Distribution Communications Reliability Improvements | 31686 | 22506 | 28.97%
Grid Design Operations and Maintenance | 8.1.4.6 | 219 | WMP.550 | Lightning Arrester Removal and Replacement | 2983 | 2719 | 8.85%
Grid Design Operations and Maintenance | 8.1.2.10.1 | 172 | WMP.972 | Avian Protection | 1113 | 1108 | 0.4492%
Grid Design Operations and Maintenance | 8.1.2.10.2 | 174 | WMP.1189 | Strategic Pole Replacement Program | 7019 | 2605 | 62.89%
Grid Design Operations and Maintenance | 8.1.2.8.2 | 167 | WMP.1195 | Early Fault Detection | 4170 | 3600 | 13.67%
Vegetation Management and Inspections | 8.2.3 | 269 | WMP.497 | Fuels Management | 5833 | 3159 | 45.84%
Vegetation Management and Inspections | 8.2.3.3 | 275 | WMP.501 | Clearance | 10235 | 0 | 100%
Vegetation Management and Inspections | 8.2.3.1 | 271 | WMP.512 | Pole Clearing (Brushing) | 7893 | 7097 | 10.08%
Note on E11: Kopunova, Sara: If applicable since some commitments occur outside of initiatives