## Tab 1 - Overview tab
IE ARC Attachments
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | PG&E
Legends
Tab 1 | Overview Tab - Instructions and overview
Tab 2 | Catalog of Initiatives - Initiative review and funding compliance of all initiatives
Tab 3 | Data Requests - Comprehensive list of documents reviewed
Tab 4 | SME Interviews - Summary of interviews conducted
Tab 5 | List of Failed-to-Fund Initiatives - All initiatives funded less than 100%

## Tab 2 - Catalog of Initiatives
Catalog of Initiatives
Independent Evaluator: |  | Bureau Veritas
Electrical Corporation: |  | PG&E
WMP Category | Initiative Tracking ID | WMP Section Number | Initiative Name | Initiative Type | WMP - Initiative Description | WMP - Initiative Target | EC-Claimed Progress (Q4 QDR) | EC-Claimed Progress (EC ARC) | EC-Claimed Progress | EC-Claimed Initiative Status | Target Not Met - Rationale | Sample Size (#) | Sample Validation Rate (%) | Verification Method | Initiative Validation Rate (%) | IE Finding on Initiative | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%) | Funding discrepancy - finding | Funding discrepancy - detail | Satisfied Risk Reduction Goal - finding | Satisfied Risk Reduction Goal - detail
Grid Design Operations and Maintenance | AI-02 | 8.1.3.1.1 | Detailed Inspection Transmission – Ground | Non-focus & non-field verifiable | Complete 20,000 Ground Inspections on Transmission | 20000 | 21713 | 21684 | 21684 | Target met | N/A | 18 | 100% | Detailed Inspection List Inspection Reports (DR006) | 108% | Initiative validated | 13959067.34 | 11494112.42 | 17.66% | Overspend | The underspend resulted primarily from reduced contractor overtime, achieved by maintaining a standard 5-day workweek, along with efficiencies gained by prioritizing inspections by circuit lines and better utilizing internal inspectors. | N/A | N/A
Grid Design Operations and Maintenance | AI-04 | 8.1.3.1.2 | Detailed Inspection Transmission – Aerial | Non-focus & non-field verifiable | Complete 20,000 Aerial Inspections on Transmission | 20000 | 22865 | 22757 | 22757 | Target met | N/A | 18 | 100% | Detailed Aerial Inspection List Inspection Reports (DR007) | 113% | Initiative validated | 32446300.16 | 32529109.11 | 0.2552% | Overspend | Less than 10% variance | N/A | N/A
Grid Design Operations and Maintenance | AI-05 | 8.1.3.1.3 | Detailed Inspection Transmission – Climbing | Non-focus & non-field verifiable | Complete 1,200 Climbing Inspections on Transmission | 1200 | 1216 | 0 | 1216 | Target met | N/A | 18 | 100% | Detailed Climbing Inspection List Inspection Reports (DR008) | 101% | Initiative validated | 3757940.82 | 2825240.76 | 24.82% | Overspend | Cost savings were attributed to efficiencies from simultaneously inspecting multiple circuit corridors, reducing resource requirements. | N/A | N/A
Grid Design Operations and Maintenance | AI-06 | 8.1.3.1.4 | Perform transmission infrared inspections | Non-focus & non-field verifiable | Perform 4,000 Transmission Infrared Inspections | 4000 | 4339 | 0 | 4339 | Target met | N/A | 18 | 100% | Infrared Inspection List Inspection Reports (DR009) | 108% | Initiative validated | 2798124.86 | 2678268.09 | 4.283% | Overspend | Less than 10% variance | N/A | N/A
Grid Design Operations and Maintenance | AI-07 | 8.1.3.2.1 | Detailed Ground Inspections – Distribution | Focus & non-field verifiable | Complete 220,016 Ground & Aerial Distribution Inspections | 220016 | 223146 | 223122 | 223122 | Target met | N/A | 73 | 100% | Detailed Ground Inspection List (x3) Inspection Reports (DR010) | 101% | Initiative validated | 53312391.85 | 51098645.1 | 4.152% | Overspend | Less than 10% variance | Yes | N/A
Grid Design Operations and Maintenance | AI-08 | 8.1.3.3.1 | Supplemental Inspections - Substation Distribution | Non-focus & non-field verifiable | Complete 76 Substation Distribution Inspections | 76 | 76 | 76 | 76 | Target met | N/A | 15 | 100% | Substation Distribution Inspection List Inspection Reports (DR011) | 100% | Initiative validated | 2649376.07 | 2378156.72 | 10.24% | Overspend | Reduced spending resulted from improved efficiency in ground, infrared, and aerial inspections due to process enhancements | N/A | N/A
Grid Design Operations and Maintenance | AI-09 | 8.1.3.3.1 | Supplemental Inspections - Substation Transmission | Non-focus & non-field verifiable | Complete 36 Substation Transmission Inspections | 36 | 36 | 36 | 36 | Target met | N/A | 12 | 100% | Substation Transmission Inspection List Inspection Reports (DR012) | 100% | Initiative validated | 2647189.28 | 2361971.73 | 10.77% | Overspend | The underspend was attributed to improved efficiency in ground, infrared, and aerial inspections, similar to those achieved in Initiative AI-08, due to process improvements. | N/A | N/A
Grid Design Operations and Maintenance | AI-10 | 8.1.3.3.1 | Supplemental Inspections - Hydroelectric Substations and Powerhouses | Non-focus & non-field verifiable | Complete 46 Hydroelectric Substation & Powerhouse Inspections | 46 | 46 | 46 | 46 | Target met | N/A | 13 | 100% | Hydroelectric Substation Inspection List Inspection Reports (DR013) | 100% | Initiative validated | 1016666.6667 | 2245689.3 | 120.9% | Overspend | The overspend was primarily due to two factors: 1. Correction of prior year accounting: Drone inspection costs incurred in 2023 were mistakenly charged to Substation orders and were corrected by charging them to Power Generation in 2024, and 2. Use of contract resources: The internal workforce was unavailable for ground inspections, necessitating reliance on more expensive contracted resources. | N/A | N/A
Grid Design Operations and Maintenance | GH-01 | 8.1.2.1 | System Hardening – Distribution | Focus & field verifiable | Complete 280 Circuit Miles of Distribution System Hardening | 280 | 348.3 | 348.29 | 348 | Target met | N/A | 75 | 100% | Field Inspection System Hardening -Distribution Documentation (DR018) As-Builts (DR018b) | 124% | Initiative validated | 97014000 | 134200897.69 | 38.33% | Underspend | PG&E attributed the budget variance to the completion of 108 miles of overhead system hardening, compared to the originally planned 70 miles. Costs associated with undergrounding were reported separately under Initiative GH-04 for clarity and accurate financial tracking. | Yes | N/A
Grid Design Operations and Maintenance | GH-02 | 8.1.2.1 | Evaluate Covered Conductor Effectiveness | Non-focus & non-field verifiable | Update the covered conductor recorded effectiveness calculation using 2023 and 2024 outage data on the lines that have Covered Conductors for consideration in future system hardening workplans. | Update the covered conductor recorded effectiveness calculation using 2023 and 2024 outage data on the lines that have Covered Conductors for consideration in future system hardening workplans. | The 2023 outage data--on the lines that have covered conductors for consideration in future system hardening workplans--was downloaded and we adjusted the recorded effectiveness calculation using this data. The documented results were shared with stakeholders to gain buy-in on any adjustments proposed to the covered conductor recorded effectiveness value. | The Program updated the covered conductor estimated effectiveness calculation using 2023 outage data on the lines that have Covered Conductors for consideration in future system hardening workplans. The program was able to provide a Whitepaper showing the updated covered conductor effectiveness calculation. | The Program updated the covered conductor estimated effectiveness calculation using 2023 outage data on the lines that have Covered Conductors for consideration in future system hardening workplans. The program was able to provide a Whitepaper showing the updated covered conductor effectiveness calculation. | Target met | N/A | 1 | 100% | Covered Conductor Effectiveness Whitepaper (Front Load Data Request) Covered Conductor Effectiveness Data – CONFIDENTIAL (Front Load Data Request) | 100% | Initiative validated | 0 | 0 | 0% | Underspend | Specific costs associated with GH-02 are not tracked however the objective/target was met for 2024. | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | GH-04 | 8.1.2.2 | 10K Undergrounding | Focus & field verifiable | Complete 250 Circuit Miles of Undergrounding | 250 | 257.8 | 257.84 | 257.84 | Target met | N/A | 72 | 100% | Field Inspection Undergrounding Documentation (DR020) As-Builts (DR020b, DR020c) | 103% | Initiative validated | 960417824.38 | 999783169.97 | 4.099% | Overspend | Less than 10% variance | Yes | N/A
Grid Design Operations and Maintenance | GH-06 | 8.1.2.5.1 | System Hardening - Transmission Shunt Splices | Non-focus & field verifiable | Install Shunt Splices on 22 Transmission Lines | 22 | 23 | 23 | 23 | Target met | N/A | 13 | 100% | Field Inspection Shunt Splice Documentation (Front Load Data Request) | 105% | Initiative validated | 4900000 | 4042319 | 17.5% | Underspend | PG&E reported achieving cost savings primarily through efficient coordination with tagging crews and the optimal use of existing clearances during scheduled operational activities. | Yes | N/A
Grid Design Operations and Maintenance | GH-09 | 8.1.2.10.3 | Distribution Line Motor Switch Operator (MSO) – Replacements | Non-focus & non-field verifiable | Replace 26 MSOs | 26 | 26 |  | 26 | Target met | N/A | 11 | 100% | Distribution Line MSO List As-Built/SCADA (DR022/.b) | 100% | Initiative validated | 5835035 | 2993993.19 | 48.69% | Overspend | Lower costs resulted from scope refinement, including deferral of legacy MSO work not part of the WMP commitment and shifting some projects from replacement to simpler removal-only, avoiding costs related to installing SCADA-enabled devices. | Yes | N/A
Grid Design Operations and Maintenance | GH-10 | 8.1.2.10.5 | Non-Exempt Expulsion Fuse – Removal | Focus & field verifiable | Remove Non-Exempt Expulsion Fuses/Cutouts From 3,000 Fuse Locations | 3000 | 3106 | 3112 | 3112 | Target met | N/A | 89 | 100% | Field Inspection Non-Exempt Expulsion Fuse Documentation (Front Load Data Request) | 104% | Initiative validated | 19800024 | 16866849.22 | 14.81% | Overspend | Cost savings resulted from increased use of internal labor, reducing reliance on more expensive contractor labor. | Yes | N/A
Grid Design Operations and Maintenance | GM-01 | 8.1.6.1 | Asset Inspections - Quality Assurance | Focus & non-field verifiable | Perform system inspection QA audits on QC completed locations and achieve the associated quality pass rates for each asset inspection program as specified below: Transmission Ground Inspection – HFTD/HFRA (Field): 500 audit locations*; 94% pass rate Distribution Ground Inspections – HFTD/HFRA (Field): 1,500 audit locations*; 90% pass rate *Audit locations are subject to change and dependent on completed execution work and constraints. The number of audit locations will be identified using a statistically valid approach with a 95% confidence level (CL) and 5% margin of error. | Transmission – 500 audit locations; 94% pass rate Distribution – 1,500 audit locations; 90% pass rate | QA System Inspection Transmission Pass Rate -> 99.97% Total # of Locations Audited -> 2970 Total # of Locations Passed -> 2969 Total # of Locations Failed -> 1 QA System Inspection Distribution Pass Rate -> 99.69% Total # of Locations Audited -> 7098 Total # of Locations Passed -> 7076 Total # of Locations Failed -> 12 | Transmission – 2,970 audit locations; 99.97% pass rate Distribution – 7,098 audit locations; 99.69% pass rate | Transmission – 2,970 audit locations; 99.97% pass rate Distribution – 7,098 audit locations; 99.69% pass rate | Target met | N/A | Transmission Inspections –80 Distribution Inspections –88 | Transmission – 100% Distribution – 100% | Asset Inspection QA Distribution Raw Data (Front Load Data Request) Asset Inspection QA Transmission Raw Data (Front Load Data Request) Distribution Quality Assurance Audits - CONFIDENTIAL (DR024) Transmission Quality Assurance Audits - CONFIDENTIAL (DR024) Distribution Audit Checklist (DR024) Transmission Audit Checklist (DR024) | Transmission – 594% Distribution – 473% | Initiative validated | 2751000 | 8052354.29 | 192.7% | Overspend | The substantial overspend was corrected by prior-year under-accounting for the Quality Assurance Sampling and Inspection (QASI) program, including comprehensive costs of sampling, dispatch, data collection, and reporting that were previously omitted. | N/A | No risk reduction goal identified for this initiative.
Grid Design Operations and Maintenance | GM-03 | 8.1.7.2 | Eliminate HFTD-HFRA Distribution Backlog | Focus & non-field verifiable | Reduce HFTD/HFRA Open Tag Backlog by 64,000 | 64000 | 96141 | 0 | 96141 | Target met | N/A | 73 | 100% | Open Tag Backlog List Aerial Inspections (DR025) Notification Source (DR025) | 150% | Initiative validated | 0 | 0 | 0% | Underspend | Specific costs associated with GM-03 are not tracked however the objective/target was met for 2024. | Yes | N/A
Grid Design Operations and Maintenance | GM-06 | 8.1.2.10.1 | EPSS - Down Conductor Detection (DCD) | Focus & field verifiable | Make capable for Down Conductor Detection (DCD) 400 protective device controllers or relays | 400 | 705 | 705 | 705 | Target met | N/A | 83 | 100% | Field Inspection EPSS – Down Conductor Detection (DCD) Documentation (Front Load Data Request) | 176% | Initiative validated | 9800039.19 | 11569517.72 | 18.06% | Overspend | Additional costs were associated with incremental Remote Access work, enabling improved cellular and radio communications for field operations, thereby enhancing the operational effectiveness of the DCD program. | Yes | N/A
Grid Design Operations and Maintenance | GM-07 | 8.1.8.1.1 | Updates on EPSS Reliability Study | Non-focus & non-field verifiable | Provide Updated EPSS Reliability Study | Provide annually an updated EPSS reliability impact study per ACI 22-32 | This commitment was completed in Q1. | Submitted Feb. 15, 2024 | N/A | Target met | N/A | N/A | N/A | DR027 Response EPSS Reliability Study | 0% | Initiative validated | 0 | 0 | 0% | Underspend | Specific costs associated with GM-07 are not tracked however the objective/target was met for 2024. | N/A | N/A
Grid Design Operations and Maintenance | GM-09 | 8.1.6.1 | Asset Inspection – Quality Control | Focus & non-field verifiable | System Inspection Transmission – HFTD (Field): 1,300 audit locations*; 92 percent pass rate System Inspection Distribution – HFTD (Desktop): 140,000 audit locations*; 88 percent pass rate System Inspection Distribution – HFTD (Field): 30,000 audit locations*; 88 percent pass rate | Transmission – 23,012 audit locations; 99.95% pass rate Distribution – 175,376 audit locations; 99.83% pass rate | Transmission – 23,012 audit locations; 99.95% pass rate Distribution – 175,376 audit locations; 99.83% pass rate | Transmission – 23,012 audit locations; 99.95% pass rate Distribution – 175,376 audit locations; 99.83% pass rate | Transmission – 23,012 audit locations; 99.95% pass rate Distribution – 175,376 audit locations; 99.83% pass rate | Target met | N/A | Transmission – 92 Distribution – 92 | Transmission – 100% Distribution – 100% | Asset Inspection QC Distribution Documentation (Front Load Data Request) Asset Inspection QC Transmission Documentation (Front Load Data Request) QC Distribution WMP Commitment Submission (Front Load Data Request) QC Transmission WMP Commitment Submission (Front Load Data Request) | Transmission – 141% Distribution – 103% | Initiative validated | 29737562.21 | 31434012.11 | 5.705% | Overspend | Less than 10% variance | N/A | No risk reduction goal identified for this initiative.
Vegetation Management and Inspections | VM-01 | 8.2.2.1.1 | LiDAR Data Collection - Transmission | Non-focus & non-field verifiable | Lidar Inspection of 17,500 Circuit Miles | 17500 | 17989 | 17953 | 17953 | Target met | N/A | 25 | 100% | Lidar Documentation (Front Load Data Request, DR035) Lidar Contractor Work Complete Attestation (DR035) | 103% | Initiative validated | 6633942 | 5150984.9 | 22.35% | Overspend | Cost reductions resulted from using internal PG&E helicopter resources instead of contracted helicopter services for LiDAR data collection. | N/A | No risk reduction goal identified for this initiative.
Vegetation Management and Inspections | VM-02 | 8.2.3.1 | Pole Clearing Program | Focus & non-field verifiable | Pole Clearing of 63,000 Distribution Poles | 63000 | 79988 | 77152 | 77152 | Target met | N/A | 92 | 100% | Pole Clearing Documentation (Front Load Data Request) | 122% | Initiative validated | 28803000 | 68512359.94 | 137.9% | Overspend | The overspend resulted from PG&E expanding the program to address newly identified risks. They decided to increase pole-clearing work in areas where the fire risk was higher. This included extra work in regions experiencing more fires and areas requiring increased safety measures. | Yes | N/A
Vegetation Management and Inspections | VM-03 | 8.2.2.2.5 | Focused Tree Inspection Program | Focus & non-field verifiable | Inspect 1,500 Circuit Miles | 1500 | 1568.2 | 1557.09 | 1557.09 | Target met | N/A | 88 | 100% | Focused Tree Inspection Documentation (Front Load Data Request) | 104% | Initiative validated | 209050000 | 61359169.66 | 70.65% | Overspend | PG&E strategically reallocated resources from this initiative toward higher-risk vegetation management areas identified through risk assessments, resulting in a reduced scope for this specific initiative. | Yes | N/A
Vegetation Management and Inspections | VM-04 | 8.2.2.2.4 | Tree Removal Inventory | Focus & non-field verifiable | Remove 20,000 Trees | 20000 | 32480 | 32091 | 32091 | Target met | N/A | 92 | 100% | Tree Removal Inventory Documentation (Front Load Data Request) | 160% | Initiative validated | 77911000 | 26655532.94 | 65.79% | Overspend | Funds were strategically reallocated from this program to address higher-priority vegetation management risks identified during the year. | Yes | N/A
Vegetation Management and Inspections | VM-05 | 8.2.2.3.1 | Defensible Space Inspections - Distribution Substation | Non-focus & non-field verifiable | Inspect 131 Distribution Substations | 131 | 131 | 131 | 131 | Target met | N/A | 20 | 100% | Defensible Space Inspection – Distribution Documentation (Front Load Data Request) Distribution Substation Defensible Space Inspection Reports (DR039) | 100% | Initiative validated | 2500000 | 2389946.88 | 4.402% | Underspend | Less than 10% variance | Yes | N/A
Vegetation Management and Inspections | VM-06 | 8.2.2.3.1 | Defensible Space Inspections - Transmission Substation | Non-focus & field verifiable | Inspect 55 Transmission Substations | 55 | 54 | 54 | 54 | Target met | N/A | 18 | 100% | Defensible Space Inspection – Transmission Documentation (Front Load Data Request) Transmission Substation Defensible Space Inspection Reports (DR040) Substation Transfer Documentation (DR040) | 98% | Initiative validated | 1282495 | 1048954.94 | 18.21% | Underspend | The underspend was due to challenges in obtaining approvals from agencies and neighboring property owners, which prevented planned additional defensible space improvements. | Yes | N/A
Vegetation Management and Inspections | VM-07 | 8.2.2.3.1 | Defensible Space Inspections - Hydroelectric Substations and Powerhouses | Non-focus & non-field verifiable | Inspect 61 Hydroelectric Substations and Powerhouses | 59 | 59 | 59 | 59 | Target met | N/A | 18 | 100% | Defensible Space Inspection – Hydroelectric Substations and Powerhouses Documentation (Front Load Data Request) Hydroelectric Substations and Powerhouses Defensible Space Inspection Reports (DR041) Substation Transfer Documentation (DR041) | 97% | Initiative validated | 1916670 | 1558473.35 | 18.69% | Underspend | The underspend resulted from lower-than-anticipated vegetation growth, reducing the need for mitigation work, and the divestiture of two facilities, which lowered the overall scope of the initiative. | No | PG&E identifies that the reported risk impact is less than the risk impact goal because two powerhouses were divested reducing the total count of inspections.
Vegetation Management and Inspections | VM-08 | 8.2.5 | Vegetation Management - Quality Verification | Non-focus & non-field verifiable | Distribution Routine VM - HFTD: 2,675 Audit Locations; 95% Pass Rate Transmission Routine VM - HFTD: 1,284 Audit Locations; 95% Pass Rate Vegetation Control Pole Clearing - HFTD: 1,926 Audit Locations; 95% Pass Rate | Distribution 4,477 Audit Locations; 99.95 % Pass Rate Transmission 2,728 Audit Locations; 99.95% Pass Rate Pole Clearing 3,466 Audit Locations; 99.86% Pass Rate | Distribution 4,477 Audit Locations; 99.95 % Pass Rate Transmission 2,728 Audit Locations; 99.95% Pass Rate Pole Clearing 3,466 Audit Locations; 99.86% Pass Rate | Distribution 4,477 Audit Locations; 99.95 % Pass Rate Transmission 2,728 Audit Locations; 99.95% Pass Rate Pole Clearing 3,466 Audit Locations; 99.86% Pass Rate | Distribution 4,477 Audit Locations; 99.95 % Pass Rate Transmission 2,728 Audit Locations; 99.95% Pass Rate Pole Clearing 3,466 Audit Locations; 99.86% Pass Rate | Target met | N/A | Distribution - 23 Transmission - 23 Pole Clearing - 23 | Distribution – 100% Transmission – 100% Pole Clearing – 100% | VM Distribution QV Documentation (Front Load Data Request, DR042) VM Transmission QV Documentation (Front Load Data Request, DR042) Pole Clearing QV Documentation (Front Load Data Request, DR042) Distribution QV Survey (DR042) Transmission QV Survey (DR042) Pole Clearing QV Survey (DR042) | Distribution - Initiative Validated (167%) Transmission - Initiative Validated (212%) Pole Clearing - Initiative Validated (180%) | Initiative validated | 14710000 | 13104145.03 | 10.92% | Overspend | The underspend was primarily due to cost-sharing with Electric Operations, which helped reduce overall program costs. | N/A | No risk reduction goal identified for this initiative.
Vegetation Management and Inspections | VM-13 | 8.2.2.1.1 | Routine Ground - Transmission | Non-focus & non-field verifiable | Routine Ground Transmission Inspection of 17,740 Circuit Miles | 17740 | 17954 | 17953 | 17953 | Target met | N/A | 27.8 | 100% | Routine Ground – Transmission Documentation (Front Load Data Request, DR043) | 101% | Initiative validated | 25666626 | 26433898.17 | 2.989% | Overspend | Less than 10% variance | Yes | N/A
Vegetation Management and Inspections | VM-14 | 8.2.2.1.2 | Transmission Second Patrol | Non-focus & non-field verifiable | Transmission Second Patrol of 5,625 Circuit Miles | 5625 | 5848 | 5697.6 | 5697.6 | Target met | N/A | 29.2 | 100% | Transmission Second Patrol Documentation (Front Load Data Request, DR044) | 101% | Initiative validated | 1192271 | 3695206.96 | 209.9% | Overspend | The overspend was due to unplanned costs associated with inspections and data collection using LiDAR, a specific technology used to enhance the patrol process. | Yes | N/A
Vegetation Management and Inspections | VM-15 | 8.2.2.1.3 | Integrated Vegetation Management - Transmission | Focus & non-field verifiable | Complete Integrated Vegetation Management and Fee Inspections of 6,504 acres | 6504 | 7907 | 7907 | 7907 | Target met | N/A | 134 | 100% | Integrated Vegetation Management – Transmission Documentation (Front Load Data Request, DR045) Vendor Attestation (DR045) | 122% | Initiative validated | 14576814 | 9164393.31 | 37.13% | Overspend | PG&E met the inspection target by completing the planned number of inspections in the required areas. However, they performed less tree removal work than initially planned, which was part of the broader vegetation management program. The reason for this is that some of the tree work was not necessary, either due to lower vegetation growth or because the most critical areas had already been addressed. As a result, PG&E was able to complete the inspections successfully while spending less on the tree removal portion, resulting in an underspend. | Yes | N/A
Vegetation Management and Inspections | VM-16 | 8.2.2.2.1 | Distribution Routine Patrol | Focus & non-field verifiable | Complete Distribution Routine Annual Patrol Inspection of 78,650 Circuit Miles | 78650 | 78307 | 78310.8 | 78310.8 | Target met | N/A | 95.98 | 100% | Distribution Routine Patrol Documentation (Front Load Data Request, DR046) | 100% | Initiative validated | 744607000 | 890506999.49 | 19.59% | Overspend | The overspend resulted from an increase in completed units due to a reallocation of work based on a risk-informed assessment, prioritizing higher-risk areas. | Yes | N/A
Vegetation Management and Inspections | VM-17 | 8.2.2.2.2 | Distribution Second Patrol | Focus & non-field verifiable | Complete Distribution Second Patrol Inspection of 25,685 Circuit Miles | 25685 | 27259.8 | 25519 | 25519 | Target met | N/A | 97.85 | 100% | Distribution Second Patrol Documentation (Front Load Data Request, DR047) | 99% | Initiative validated | 80124000 | 132743388.64 | 65.67% | Overspend | The overspend was due to an increase in units completed, resulting from a reallocation of funds to higher-risk areas, which focused on addressing more critical vegetation management work. | Yes | N/A
Vegetation Management and Inspections | VM-18 | 8.2.2.2.3 | VM for Operational Mitigations (VMOM) | Non-focus & non-field verifiable | Mitigate 6,500 Trees | 6500 | 6937 | 6935 | 6935 | Target met | N/A | 18 | 100% | VMD/OneVM List | 106% | Initiative validated | 20904000 | 8418883.69 | 59.73% | Overspend | The underspend was primarily due to a shift in focus, reallocating funds from VMOM to other vegetation work in higher-risk areas. This resulted in fewer units being completed under this initiative than originally planned. | N/A | N/A
Vegetation Management and Inspections | VM-19 | 8.2.4 | One VM Application Record Keeping Enhancement (Routine, Second Patrol) | Non-focus & non-field verifiable | Enhance the One VM application for Routine, and Second Patrol to include capability to capture factors for prescribing trees for removal. | Enhance the One VM application for Routine, and Second Patrol to include capability to capture factors for prescribing trees for removal. | This commitment was completed in Q1. | VM Completed the enhancement of the One-VM application for Routine, and Second Patrol to include capability to capture factors for prescribing trees for removal on Jan. 30, 2024. | N/A | Target met | N/A | N/A | N/A | DR048 Utility Response (DR048) Photo Evidence (DR048) OneVM Enhancement to Align (DR048) | 0% | Initiative validated | 27000000 | 29511717.05 | 9.303% | Overspend | Less than 10% variance | N/A | N/A
Vegetation Management and Inspections | VM-20 | 8.2.4 | Record Keeping Enhancement (VMOM, TRI) | Non-focus & non-field verifiable | Enhance the application for the Vegetation Management for Operational Mitigations (VMOM) - VMPI2 and Tree Removal Inventory (TRI) | Enhance the application for the Vegetation Management for Operational Mitigations (VMOM) - VMPI2 and Tree Removal Inventory (TRI) | This commitment was completed in Q3. | VM enhanced the application for the Vegetation Management for Operational Mitigations (VMOM), One VM, and Tree Removal Inventory (TRI) Field Maps program to include capability to capture factors for prescribing trees for removal. In 2024, the VMOM system of record migrated to One-VM. | N/A | Target met | N/A | N/A | N/A | DR050 Utility Response (DR050) TRI Reason (DR050) One VM Enhancement to Align (DR050) | 0% | Initiative validated | 0 | 0 | 0% | Overspend | Specific costs associated with VM-20 are not tracked however the objective/target was met for 2024. | N/A | N/A
Vegetation Management and Inspections | VM-21 | 8.2.2.2.5 | FTI Record Keeping Enhancement | Non-focus & non-field verifiable | Enhance record keeping practices for the Focused Tree Inspection program (FTI) by creating records of all potential strike trees inspected using a digitized Tree Risk Assessment form. | Enhance record keeping practices for the Focused Tree Inspection program (FTI) by creating records of all potential strike trees inspected using a digitized Tree Risk Assessment form. | This commitment was completed in Q1. | This commitment was completed in 2024. The Tree Risk Assessment Form was digitized and provides the reason for tree removal. A Job Aid demonstrating record keeping of digitized Tree Risk Assessment Form was published. | N/A | Target met | N/A | N/A | N/A | Potential Strike Tree Lists (x3) Digital TRAQ Form | 0% | Initiative validated | 0 | 1310936 | 100% | Overspend | PG&E indicated that specific costs associated with VM-21 were not separately tracked at the initiative level. Instead, these expenses are aggregated within a larger financial reporting group. PG&E has confirmed that despite this variance, the overall operational objective for VM-21 was successfully met in 2024. | N/A | N/A
Vegetation Management and Inspections | VM-22 | 8.2.5.2 | Vegetation Management - Quality Control | Non-focus & non-field verifiable | Distribution Routine VM - HFTD: 80,000 Audit Locations; 88% Pass Rate Transmission Routine VM - HFTD: 13,500 Audit Locations; 92% Pass Rate Vegetation Control Pole Clearing - HFTD: 10,500 Audit Locations; 80% Pass Rate | Distribution - 80,931 Audit Locations; 97.38 % Pass Rate Transmission - 15,897 Audit Locations; 99.08% Pass Rate Pole Clearing - 21,740 Audit Locations; 88.30% Pass Rate | Distribution - 80,931 Audit Locations; 97.38 % Pass Rate Transmission - 15,897 Audit Locations; 99.08% Pass Rate Pole Clearing - 21,740 Audit Locations; 88.30% Pass Rate | Distribution - 80,931 Audit Locations; 97.38 % Pass Rate Transmission - 15,897 Audit Locations; 99.08% Pass Rate Pole Clearing - 21,740 Audit Locations; 88.30% Pass Rate | Distribution - 80,931 Audit Locations; 97.38 % Pass Rate Transmission - 15,897 Audit Locations; 99.08% Pass Rate Pole Clearing - 21,740 Audit Locations; 88.30% Pass Rate | Target met | N/A | Distribution - 23 Transmission - 23 Pole Clearing - 23 | Distribution – 100% Transmission – 100% Pole Clearing – 100% | VM Distribution QC Documentation (Front Load Data Request, DR052) VM Transmission QC Documentation (Front Load Data Request, DR052) Pole Clearing QC Documentation (Front Load Data Request,DR052) VM QC Distribution Survey (DR052) VM QC Missed Veg Survey (DR052) VM QC Transmission Survey (DR052) VM QC Pole Clearing Survey (DR052) | Distribution – Initiative Validated (101%) Transmission – Initiative Validated (118%) Pole Clearing – Initiative Validated (207%) | Initiative validated | 41025000 | 40138500.52 | 2.161% | Overspend | Less than 10% variance | N/A | No risk reduction goal identified for this initiative.
Situational Awareness and Forecasting | SA-02 | 8.3.3.1 | Line Sensor - Installations | Non-focus & non-field verifiable | Install 40 Line Sensors | 40 | 45 | 0 | 45 | Target met | N/A | 13 | 100% | Line Sensor Installations Inspection Reports (DR032) | 100% | Initiative validated | 4445198 | 3817637.29 | 14.12% | Underspend | The underspend primarily resulted from reducing the program scope by removing non-WMP circuits, correcting initial over-planning at the start of the year. | N/A | N/A
Situational Awareness and Forecasting | SA-10 | 8.3.3.3 | Distribution Fault Anticipation (DFA) Installations | Focus & non-field verifiable | Install 15 DFAs | 15 | 17 | 0 | 17 | Target met | N/A | 14 | 100% | DFA HFTD Circuit Designation Report DFA First Comms (DR033) DFA Portal Screenshots (DR033) | 113% | Initiative validated | 3000001 | 2390286.92 | 20.32% | Underspend | The underspend was primarily due to deferred engineering work, as seven planned readiness projects for 2025 did not begin in 2024. | No | Moved 6 circuits from 2025 work plan to meet 2024 goal. These circuits were of lower wildfire risk
Situational Awareness and Forecasting | SA-11 | 8.3.3.3 | Early Fault Detection (EFD) Installations | Non-focus & non-field verifiable | Install 2 EFDs | 2 | 2 | 0 | 2 | Target met | N/A | 2 | 100% | EFD Installations Job Package Camp Evers (DR034) Job Package Miwuk (DR034) | 100% | Initiative validated | 7000000 | 2802426.7 | 59.97% | Underspend | The underspend was attributed to work deferrals resulting from resource and scheduling issues, as well as lower-than-expected unit costs. | Yes | N/A
Emergency Preparedness | EP-01 | 8.4.2.3.1 | Complete PSPS and Wildfire Tabletop and Functional Exercises | Non-focus & non-field verifiable | Complete PSPS and Wildfire Tabletop and Functional Exercise annually in compliance with the guiding principles of the Homeland Security Exercise Evaluation Program (HSEEP) | Complete PSPS and Wildfire Tabletop Functional Exercises | The 2024 Wildfire and PSPS Tabletop and Functional exercises are complete | The 2024 Wildfire and PSPS Tabletop and Functional exercises are complete | The 2024 Wildfire and PSPS Tabletop and Functional exercises are complete | Target met | N/A | 3 | 100% | Wildfire Tabletop Exercise After-Action Report (DR016) PSPS Tabletop Exercise After-Action Report (DR016) PSPS and Wildfire Full Scale Exercise After-Action Report (DR016) | 100% | Initiative validated | 0 | 0 | 0% | Overspend | Specific costs associated with EP-01 are not tracked however the objective/target was met for 2024. | N/A | No risk reduction goal identified for this initiative.
Emergency Preparedness | EP-06 | 8.4.3.1 | Review, and revise the CERP and 2 Wildfire Related Annexes on a yearly basis | Non-focus & non-field verifiable | Review & Revise 3 Documents: The CERP and the Two Wildfire-Related Annexes | 3 | 3 | 0 | 3 | Target met | N/A | 3 | 100% | PSPS Annex CERP Wildfire Annex Company Emergency Response Plan Standard | 100% | Initiative validated | 0 | 0 | 0% | Underspend | Specific costs associated with EP-06 are not tracked however the objective/target was met for 2024. | N/A | N/A
Emergency Preparedness | PS-06 | 8.5.3 | Provide portable batteries to PG&E customers | Non-focus & non-field verifiable | Provide 4,000 Portable Batteries to Customers | 4000 | 4376 | 4357 | 4357 | Target met | N/A | 18 | 100% | Batteries Delivered Summaries Agreement to Accept Equipment Forms (DR029) | 108% | Initiative validated | 13064000 | 13197419.6 | 1.021% | Underspend | Less than 10% variance | N/A | N/A
Emergency Preparedness | PS-07 | 9.1.5 | PSPS Customer Impact Reduction | Non-focus & non-field verifiable | Reduce PSPS Impacts by 9,980 Customer Events | 9980 | 10529 | 10491 | 10491 | Target met | N/A | 18 | 100% | Customer Impact Summary GH-04 Customer Impact GH-09 Customer Impact | 105% | Initiative validated | 0 | 0 | 0% | Underspend | Specific costs associated with PS-07 are not tracked however the objective/target was met for 2024. | N/A | N/A
Emergency Preparedness | PS-11 | 9.1.2 | Pilot using drones for PSPS restoration | Non-focus & non-field verifiable | Pilot and Review Drones for PSPS Restoration | Pilot using drones for PSPS restoration and/or damage assessment to improve PSPS outage restoration time. | PG&E has completed the objective to evaluate whether drones can be used to support PSPS restoration efforts. The findings were presented in PG&E’s WRGSC on November 14, 2024. | PG&E has completed the objective to evaluate whether drones can be used to support PSPS restoration efforts. The findings were presented in PG&E’s WRGSC on November 14, 2024. | N/A | Target met | N/A | N/A | N/A | PG&E Written Response UAS PSPS Patrols Report (DR031) | 0% | Initiative validated | 0 | 0 | 0% | Underspend | Specific costs associated with PS-11 are not tracked however the objective/target was met for 2024. | N/A | N/A
Community Outreach and Engagement | CO-01 | 8.5.2 | Community Engagement - Meetings | Non-focus & non-field verifiable | Complete 22 Community Engagement Meetings | 22 | This initiative was completed in Q3. | 25 Events | 25 | Target met | N/A | 10 | 100% | Post-Event Reports (DR014) | 113% | Initiative validated | 0 | 0 | 0% | Overspend | PG&E does not track detailed internal and external labor costs associated with CO-01 at a process level. However the objective/target was met for 2024. | N/A | N/A
Community Outreach and Engagement | CO-02 | 8.5.2 | Community Engagement - Surveys | Non-focus & non-field verifiable | Complete 2 Community Engagement Surveys | 2 | 2 | 0 | 2 | Target met | N/A | 2 | 100% | Pre-Season Survey Analysis Report Post-Season Survey Analysis Report | 100% | Initiative validated | 0 | 0 | 0% | Overspend | PG&E does not track detailed internal and external labor costs associated with CO-02 at a process level. However the objective/target was met for 2024. | N/A | N/A
Note on K11: Number of "actuals" from which samples are selected

## Tab 3 - Data Requests
Data Requests
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | PG&E
Date Sent | Date Response Received | Section / Initiative | Data Request Number | List of Documents Received
2025-05-20 | 2025-05-28 | QAQC Questions | PG&E_DR001 | DRU15781_Q01_Atch01_QA_QC_Progam Categories_SMEs_PG&E_Notes_CONF.xlx DRU15781_Q01_Atch01_QA_QC_Progam Categories_SMEs_PG&E_Notes_Redacted.xlx DRU15781_Audit_DR_Independent Evaluator_D001_CONF.pdf DRU15781_Audit_DR_Independent Evaluator_D001_Redacted.pdf DRU15781_OEIS Confidentiality Declaration.pdf
2025-05-21 | 2025-05-28 | Financials | PG&E_DR005 | DRU15784_Q01_Atch01_DR005_Attachment_Updates_CONF.xlx DRU15784_Q01_Atch01_DR005_Attachment_Updates_Redacted.xlx DRU15784_OEIS Confidentiality Declaration.pdf DRU15784_Q01_Atch01_DR005_Attachment_Updates_CONF - V2supplemental.xlsx
NA | 2025-06-04 | Financials - GH05_GH11 Only Updates | PG&E_DR005 | DRU15784_Q01_Atch01_DR005_Attachment_Updates_CONF - V2supplemental
2025-05-02 | 2025-05-06 | AI-02 | PG&E_DR006 | PG&E DR006 - AI-02 Response 05.06.25.zip (38 documents)
2025-05-05 | 2025-05-08 | AI-04 | PG&E_DR007 | DRU15670_DR007_AI-04_20250508.zip (148 documents)
2025-05-05 | 2025-05-07 | AI-05 | PG&E_DR008 | DR008_AI-05.zip (38 documents)
2025-05-14 | 2025-05-19 | AI-06 | PG&E_DR009 | DRU15743_Q01_Atch01_PARKWAY-MORAGA_46099751_121824_CONF.pdf DRU15743_Q01_Atch01_PARKWAY-MORAGA_46099751_121824_Redacted.pdf DRU15743_Q01_Atch02_JEFFERSON_46099779_093024_Redacted.pdf DRU15743_Q01_Atch02_JEFFERSON_46099779_093024_CONF.pdf DRU15743_Audit_DR_Independent Evaluator_D001.pdf DRU15743_OEIS Confidentiality Declaration.pdf
2025-05-06 | 2025-05-09 | AI-07 | PG&E_DR010 | DRU15672_DR010_AI-07_20250509.zip (151 documents)
2025-05-27 | 2025-05-30 | AI-08 | PG&E_DR011 | DRU15806_DR011_AI-08_20250530 (185 documents)
2025-05-27 | 2025-05-30 | AI-09 | PG&E_DR012 | DRU15808_DR012_AI-09_20250530 (153 documents)
2025-05-27 | 2025-05-30 | AI-10 | PG&E_DR013 | DRU15809_DR013_AI-10_20250530 (175 documents)
2025-05-27 | 2025-05-29 | CO-01 | PG&E_DR014 | DRU15810_DR014_CO-01_20250529 (23 documents)
2025-05-07 | 2025-05-12 | EP-01 | PG&E_DR016 | DRU15692_Audit_DR_Independent Evaluator_D001 DRU15692_OEIS Confidentiality Declaration DRU15692_Q01_Atch01_2024 WF Tabletop AAR_CONF DRU15692_Q01_Atch01_2024 WF Tabletop AAR_Redacted DRU15692_Q01_Atch02_2024 PSPS Tabletop AAR_CONF DRU15692_Q01_Atch02_2024 PSPS Tabletop AAR_Redacted DRU15692_Q01_Atch03_2024 PSPS_WF FSE AAR_CONF DRU15692_Q01_Atch03_2024 PSPS_WF FSE AAR_Redacted
2025-05-05 | 2025-05-08 | GH-01 | PG&E_DR018.b | PG&E_DR018.b_GH-01 Response.zip (88 documents)
2025-05-05 | 2025-05-09 | GH-04 | PG&E_DR020.b | DRU15651_DR020_GH-04_20250508.zip (70 documents)
2025-05-27 | 2025-05-29 | GH-04 | PG&E_DR020.c | DRU15813_Audit_DR_Independent Evaluator_D001.pdf DRU15813_OEIS Confidentiality Declaration.pdf DRU15813_Q01_Atch01_35279181_AS Built_CONF.pdf DRU15813_Q01_Atch01_35279181_AS Built_Redacted.pdf
2025-04-30 | 2025-05-05 | GH-06 | PG&E_DR021 | DRU15652_Audit_DR_Independent Evaluator_D001 DRU15652_Atch01_GH-06_ShuntSplice_2024
2025-05-02 | 2025-05-06 | GH-09 | PG&E_DR022 | PG&E DR Response DR022.zip (46 documents)
2025-05-08 | 2025-05-13 | GH-09 | PG&E_DR022.b | DRU15697_Audit_DR_Independent Evaluator_D001 DRU15697_OEIS Confidentiality Declaration DRU15697_Q01a_Atch01_35276372_ASBUILTDWG_CONF DRU15697_Q01a_Atch01_35276372_ASBUILTDWG_Redacted DRU15697_Q01a_Atch02_35276372_ASBUILT_CMCS_CONF DRU15697_Q01a_Atch02_35276372_ASBUILT_CMCS_Redacted DRU15697_Q01a_Atch03_35276372_13529_SCADA Release_20241014_CONF DRU15697_Q01a_Atch03_35276372_13529_SCADA Release_20241014_Redacted DRU15697_Q01b_Atch01_35205297_AS BUILT DWG_CONF DRU15697_Q01b_Atch01_35205297_AS BUILT DWG_Redacted DRU15697_Q01b_Atch02_35205297_AsBuilt CMCS_CONF DRU15697_Q01b_Atch02_35205297_AsBuilt CMCS_Redacted DRU15697_Q01b_Atch03_35205297_832991_SCADA Release_CONF DRU15697_Q01b_Atch03_35205297_832991_SCADA Release_Redacted
2025-05-09 | 2025-05-14 | GM-01 | PG&E_DR024 | DRU15704_Audit_DR_Independent Evaluator_D001 DRU15704_OEIS Confidentiality Declaration DRU15704_Q01_Transmission_CONF.zip DRU15704_Q02_Distribution_CONF.zip DRU15704_Q03_Atch01_GM-01_TRANS_Checklist and cause codes DRU15704_Q03_Atch02_GM-01_DIST_Checklist and cause codes
2025-05-08 | 2025-05-13 | GM-03 | PG&E_DR025 | DRU15674_Audit_DR_Independent Evaluator_D001 DRU15674_OEIS Confidentiality Declaration DRU15674_Q01_Atch03_Notification Source Summary.xlx DRU15674_Q01_Atch01_WMP Aerial Insp_CONF.zip DRU15674_Q01_Atch02_EPSS Aerial Insp_CONF.zip
2025-05-13 | 2025-05-16 | GM-07 | PG&E_DR027 | DRU15737_Audit_DR_Independent Evaluator_D001.pdf
2025-05-09 | 2025-05-14 | GM-09 | PG&E_DR028 | DRU15710_Audit_DR_Independent Evaluator_D001.pdf GM-09 BCONF letter.pdf DRU15710_Q02_GM-09_DIST_CompletedAudits_BCONF.zip (92 documents) DRU15710_Q01_GM-09_TRANS_CompletedAudits_BCONF.zip (92 documents)
2025-05-05 | 2025-05-07 | PS-06 | PG&E_DR029 | DR029_PS-06.zip (41 documents)
2025-05-13 | 2025-05-16 | PS-11 | PG&E_DR031 | DRU15735_Q01_Atch02_UAS_PS-11-2023-2024_CONF DRU15735_Q01_Atch02_UAS_PS-11-2023-2024_Redacted DRU15735_OEIS Confidentiality Declaration DRU15735_Q01_Atch01_PGE Response PS-11_CONF DRU15735_Q01_Atch01_PGE Response PS-11_Redacted DRU15735_Audit_DR_Independent Evaluator_D001
2025-05-02 | 2025-05-07 | SA-02 | PG&E_DR032 | DR032_SA-02.zip (118 documents)
2025-05-05 | 2025-05-08 | SA-10 | PG&E_DR033 | DRU15677_Audit_DR_Independent Evaluator_D001 DRU15677_OEIS Confidentiality Declaration DRU15677_Q01_Atch01_PGE_DRE033_SA-10 DFA First Comms-112224 DRU15677_Q01_Atch02_PGE_DRE033_SA-10 DFA Portal Screenshots_CONF DRU15677_Q01_Atch02_PGE_DRE033_SA-10 DFA Portal Screenshots_Redacted
2025-05-05 | 2025-05-07 | SA-11 | PG&E_DR034 | DRU15680_Audit_DR_Independent Evaluator_D001 DRU15680_OEIS Confidentiality Declaration DRU15680_Q01_Atch01_CAMP EVERS 2106 Node 13_CONF DRU15680_Q01_Atch01_CAMP EVERS 2106 Node 13_Redacted DRU15680_Q01_Atch02_MIWUK 1702 NODE1_CONF DRU15680_Q01_Atch02_MIWUK 1702 NODE1_Redacted
2025-05-12 | 2025-05-15 | VM-01 | PG&E_DR035 | DRU15716_Audit_DR_Independent Evaluator_D001 DRU15716_Q01_Atch02_PGE_NV5_2024 LiDAR Mileage Attest_CONF DRU15716_Q01_Atch01_VM-01_ROE Attestation DRU15716_OEIS Confidentiality Declaration DRU15716_Q01_Atch02_PGE_NV5_2024 LiDAR Mileage Attest_Redacted
2025-05-12 | 2025-05-15 | VM-02 | PG&E_DR036 | DRU15718_OEIS Confidentiality Declaration.pdf DRU15718_Q01_Atch01_VM-02 Pole Clearing Program_Response_CONF.xlsx DRU15718_Q01_Atch01_VM-02 Pole Clearing Program_Response_Redacted.xlsx DRU15718_Audit_DR_Independent Evaluator_D001.pdf
2025-05-12 | 2025-05-15 | VM-03 | PG&E_DR037 | DRU15719_Q01_Atch01_VMDR-3812_DR037_FTI_20250513_CONF.xlsx DRU15719_Q01_Atch01_VMDR-3812_DR037_FTI_20250513_Redacted.xlsx DRU15719_OEIS Confidentiality Declaration.pdf DRU15719_Audit_DR_Independent Evaluator_D001.pdf
2025-05-12 | 2025-05-15 | VM-04 | PG&E_DR038 | DRU15720_Audit_DR_Independent Evaluator_D001
2025-05-12 | 2025-05-15 | VM-05 | PG&E_DR039 | DRU15721_DR039_VM-05_20250515 (40 files)
2025-05-12 | 2025-05-15 | VM-06 | PG&E_DR040 | DRU15722_DR040_VM-06_20250515 (41 files)
2025-05-12 | 2025-05-15 | VM-07 | PG&E_DR041 | DRU15723_DR041_VM-07_20250515 (40 files)
2025-05-12 | 2025-05-15 | VM-08 | PG&E_DR042 | DRU15724_Q001_Atch01_QV Distribution 2024.xlsx DRU15724_Q002_Atch01_QV Transmission_CONFxlsx DRU15724_Q002_Atch01_QV Transmission_Redacted.xlsx DRU15724_Q003_Atch01_QV VC Pole Clearing.xlsx DRU15724_Audit_DR_Independent Evaluator_D001.pdf DRU15724_OEIS Confidentiality Declaration.pdf DRU15724_Q001_Atch02_REVISED-QAP Distribution Survey.pdf DRU15724_Q002_Atch02_REVISED-QAP Transmission Survey.pdf DRU15724_Q003_Atch02_REVISED-QAP VC Pole Clearing Survey.pdf
2025-05-12 | 2025-05-15 | VM-13 | PG&E_DR043 | DRU15725_Q01_Atch01_VM13_Routine Ground-Transmission Response DRU15725_Audit_DR_Independent Evaluator_D001
2025-05-12 | 2025-05-15 | VM-14 | PG&E_DR044 | DRU15726_Audit_DR_Independent Evaluator_D001 DRU15726_Q01_Atch01_VM-14 Transmission Second Patrol Response
2025-05-27 | 2025-05-30 | VM-15 | PG&E_DR045 | DRU15816_DR045_VM-15_20250530 (16 documents)
2025-05-27 | 2025-05-30 | VM-16 | PG&E_DR046 | DRU15817_Audit_DR_Independent Evaluator_D001.pdf DRU15817_OEIS Confidentiality Declaration.pdf DRU15817_Q01_Atch01_OneVM Tree Prescriptions_CONF.xlx DRU15817_Q01_Atch01_OneVM Tree Prescriptions_Redacted.xlx
2025-05-30 | 2025-06-04 | VM-16 | PG&E_DR046.b | DRU15837_Audit_DR_Independent Evaluator_D001
2025-05-27 | 2025-05-30 | VM-17 | PG&E_DR047 | DRU15818_Audit_DR_Independent Evaluator_D001.pdf DRU15818_OEIS Confidentiality Declaration.pdf DRU15818_Q01_Atch01_OneVM Prescriptions_CONF.xlx DRU15818_Q01_Atch01_OneVM Prescriptions_Redacted.xlx
2025-05-30 | 2025-06-04 | VM-17 | PG&E_DR047.b | DRU15837_Audit_DR_Independent Evaluator_D001
2025-05-13 | 2025-05-16 | VM-19 | PG&E_DR049 | DRU15734_Audit_DR_Independent Evaluator_D001.pdf DRU15734_Q01_Atch01_Screenshot_094503.pdf DRU15734_Q01_Atch02_One VM enhancement to align with VM-19.pdf
2025-05-13 | 2025-05-16 | VM-20 | PG&E_DR050 | DRU15733_Q01_Atch01_Tri reason_Redacted.pdf DRU15733_Q01_Atch01_Tri reason_CONF.pdf DRU15733_Q01_Atch02_Tri reason.pdf DRU15733_Q01_Atch03_One VM enhancement to align with VM-19.pdf DRU15733_Audit_DR_Independent Evaluator_D001.pdf DRU15733_OEIS Confidentiality Declaration.pdf
2025-05-13 | 2025-05-20 | VM-21 | PG&E_DR051 | DRU15731_Audit_DR_Independent Evaluator_D001.pdf DRU15731_Q01_Atch04_VM-21 Digital TRAQ Form.pdf DRU15731_Q01_Atch01_VMDR-3826_OneVM_FTI2024_20250519_NC,BA,CC,CV.xlsx DRU15731_Q01_Atch02_VMDR-3826_OneVM_FTI2024_20250519_SI.xlsx DRU15731_Q01_Atch03_VMDR-3826-OneVM_FTI2024_20250519_NV.xlsx
2025-05-12 | 2025-05-15 | VM-22 | PG&E_DR052 | DRU15728_Q001_Atch01_VM QC Distribution.xlsx DRU15728_Q002_Atch01_VM QC Transmission_CONF.xlsx DRU15728_Q002_Atch01_VM QC Transmission_Redacted.xlsx DRU15728_Q003_Atch01_QC VC Pole Clearing.xlsx DRU15728_Audit_DR_Independent Evaluator_D001.pdf DRU15728_OEIS Confidentiality Declaration.pdf DRU15728_Q001_Atch02_01A_VMQC Distribution Survey.pdf DRU15728_Q001_Atch03_01C_VMQC Distribution Missed Veg Survey.pdf DRU15728_Q002_Atch02_01D_VMQC Transmission Survey.pdf DRU15728_Q003_Atch02_01G_VMQC VC Pole Clearing Survey.pdf
Formulas:
Date Response Received = WORKDAY(Table48[[#This Row],[Date Sent]],3)

## Tab 4 - SME Interviews
SME Interviews
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | PG&E
Interview date | Section / Initiative | SME interview number | Positions interviewed | Summary of interview
No Interviews conducted | No Interviews conducted | No Interviews conducted | No Interviews conducted | No Interviews conducted

## Tab 5 - List of "Fail-to-Fund"
List of Failed-to-Fund Initiatives
Independent Evaluator: | Bureau Veritas
Electrical Corporation: | PG&E
WMP Category | WMP Section Number | WMP Page Number | Initiative Tracking ID | Initiative Name | WMP - Planned Spend ($) | EC-Claimed Actual Spend ($) | Variance (%)
Grid Design Operations and Maintenance | 8.1.3.1.1 | 477 | AI-02 | Detailed Inspection Transmission – Ground | 13959067.34 | 11494112.42 | 17.66%
Grid Design Operations and Maintenance | 8.1.3.1.3 | 479 | AI-05 | Detailed Inspection Transmission – Climbing | 3757940.82 | 2825240.76 | 24.82%
Grid Design Operations and Maintenance | 8.1.3.1.4 | 480 | AI-06 | Perform transmission infrared inspections | 2798124.86 | 2678268.09 | 4.283%
Grid Design Operations and Maintenance | 8.1.3.2.1 | 487 | AI-07 | Detailed Ground Inspections - Distribution | 53312391.85 | 51098645.1 | 4.152%
Grid Design Operations and Maintenance | 8.1.3.3.1 | 498 | AI-08 | Supplemental Inspections - Substation Distribution | 2649376.07 | 2378156.72 | 10.24%
Grid Design Operations and Maintenance | 8.1.3.3.1 | 498 | AI-09 | Supplemental Inspections - Substation Transmission | 2647189.28 | 2361971.73 | 10.77%
Grid Design Operations and Maintenance | 8.1.2.5.1 | 441 | GH-06 | System Hardening - Transmission Shunt Splices | 4900000 | 4042319 | 17.5%
Grid Design Operations and Maintenance | 8.1.2.8.1 | 456 | GH-07 | Distribution Protective Devices | 6907369 | 3398420.1 | 50.8%
Grid Design Operations and Maintenance | 8.1.2.10.3 | 463 | GH-09 | Distribution Line Motor Switch Operator (MSO) - Replacements | 5835035 | 2993993.19 | 48.69%
Grid Design Operations and Maintenance | 8.1.2.10.5 | 465 | GH-10 | Non-Exempt Expulsion Fuse - Removal | 19800024 | 16866849.22 | 14.81%
Vegetation Management and Inspections | 8.2.2.1.1 | 663 | VM-01 | LiDAR Data Collection - Transmission | 6633942 | 5150984.9 | 22.35%
Vegetation Management and Inspections | 8.2.2.2.5 | 681 | VM-03 | Focused Tree Inspection Program | 209050000 | 61359169.66 | 70.65%
Vegetation Management and Inspections | 8.2.2.2.4 | 680 | VM-04 | Tree Removal Inventory | 77911000 | 26655532.94 | 65.79%
Vegetation Management and Inspections | 8.2.2.3.1 | 683 | VM-05 | Defensible Space Inspections - Distribution Substation | 2500000 | 2389946.88 | 4.402%
Vegetation Management and Inspections | 8.2.2.3.1 | 683 | VM-06 | Defensible Space Inspections - Transmission Substation | 1282495 | 1048954.94 | 18.21%
Vegetation Management and Inspections | 8.2.2.3.1 | 683 | VM-07 | Defensible Space Inspections - Hydroelectric Substations and Powerhouses | 1916670 | 1558473.35 | 18.69%
Vegetation Management and Inspections | 8.2.5 | 701 | VM-08 | Vegetation Management – Quality Verification | 14710000 | 13104145.03 | 10.92%
Vegetation Management and Inspections | 8.2.2.1.3 | 668 | VM-15 | Integrated Vegetation Management - Transmission | 14576814 | 9164393.31 | 37.13%
Vegetation Management and Inspections | 8.2.2.2.3 | 678 | VM-18 | VM for Operational Mitigations (VMOM) | 20904000 | 8418883.69 | 59.73%
Vegetation Management and Inspections | 8.2.5.2 | 706 | VM-22 | Vegetation Management - Quality Control | 41025000 | 40138500.52 | 2.161%
Situational Awareness and Forecasting | 8.3.3.1 | 746 | SA-02 | Line Sensor - Installations | 4445198 | 3817637.29 | 14.12%
Situational Awareness and Forecasting | 8.3.6.3 | 781 | SA-05 | Evaluate FPI and IPW Modeling enhancements in 2023 - 2025(a) | 5302577.3 | 4899613.97 | 7.599%
Situational Awareness and Forecasting | 8.3.3.3 | 747 | SA-10 | Distribution Fault Anticipation (DFA) Installations | 3000001 | 2390286.92 | 20.32%
Situational Awareness and Forecasting | 8.3.3.3 | 747 | SA-11 | Early Fault Detection (EFD) Installations | 7000000 | 2802426.7 | 59.97%
Note on E11: Kopunova, Sara: If applicable since some commitments occur outside of initiatives