## OEIS Table 6-3
Initiative Activity | Initiative Activity Section # | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness- Outage Program Riska | Cost-Benefit Score - Overall Risk | Cost-Benefit Score - Wildfire Risk | Cost-Benefit Score – Outage Program Riskb | % HFTD Covered | % HFTD/HFRA Coveredc | Expected % Risk Reduction | Model(s) Used to Calculate Risk Impact
Combined Covered Conductor (WMP.0455) | 8.2.1 | 58% | 58% | n/ad | 1.55 | 4.49 | n/a | 3.85% | n/a | 0.69% | WiNGS-Planning v4.0
PSPS Sectionalizing Enhancements (WMP.461)e | 8.2.11.1 | n/a | n/a | n/a | n/a | n/a | n/a | 100% | n/a | n/a | WiNGS-Planning v4.0
Microgrids (WMP.462) | 8.2.7 | 100%f | 0% | 100%f | 0 | 0g | 0 | 0.18% | n/a | 100% | WiNGS-Planning v4.0
Advanced Protection (WMP.463) | 8.2.8.1 | 8% | 8% | n/a | 7.42 | 7.42 | n/a | 5.95% | n/a | 0.17% | WiNGS-Planning v4.0
Strategic Undergrounding (WMP.473) | 8.2.2 | 99% | 99% | 99%h | 11.53 | 11.73 | n/a | 0.01% | n/a | 9.07% | WiNGS-Planning v4.0
Distribution Overhead System Hardening (WMP.475) | 8.2.5.1 | 39% | 39% | n/a | 2.36 | 2.36 | n/a | 0.36% | n/a | 0.03% | WiNGS-Planning v4.0
Distribution Overhead Detailed Inspections (WMP.478) | 8.3.1 | 29% | 29% | n/a | 52.72 | 106.8 | n/a | 100% | n/a | 10.78% | WiNGS-Planning v4.0
Transmission Overhead Detailed Inspections (WMP.479) | 8.3.2 | 28% | 28% | n/a | n/ai | n/ai | n/ai | 100% | n/a | n/ai | WiNGS-Planning v4.0
Detailed Inspections (WMP.494) | 9.2.1 | 4.95% | 4.95% | n/a | 28.17 | 28.17 | n/a | 100% | n/a | 13.58% | WiNGS-Planning v4.0
Fuels Management (WMP.497) | 9.7 | 4.95% | 4.95% | n/a | 0.6 | 0.6 | n/a | 0.69% | n/a | 0.33% | WiNGS-Planning v4.0
Off-Cycle Patrol (WMP.508) | 9.2.2 | 4.95% | 4.95% | n/a | 65.16 | 65.16 | n/a | 100% | n/a | 13.57% | WiNGS-Planning v4.0
Pole Clearing (Brushing) (WMP.512) | 9.4 | 4.95% | 4.95% | n/a | 15.09 | 3.05 | n/a | 30.43% | n/a | 13.47% | WiNGS-Planning v4.0
Strategic Pole Replacement (WMP.1189) | 8.2.3.2 | 39% | 39% | n/a | 4.4 | 4.4 | n/a | 0.83% | n/a | 0.13% | WiNGS-Planning v4.0
Early Fault Detection (WMP.1195) | 10.3.1 | 16% | 16% | n/a | 76.35 | 76.35 | n/a | 32.99% | n/a | 1.01% | WiNGS-Planning v4.0
Distribution Overhead Patrol Inspections (WMP.488) | 8.3.7 | 10% | 10% | n/a | 190.89 | 190.89 | n/a | 100% | n/a | 20.74% | WiNGS-Planning v4.0
Distribution Wood Pole Intrusive Inspections (WMP.483) | 8.3.4 | 10% | 10% | n/a | 20.55 | 20.55 | n/a | 23.58% | n/a | 1.93% | WiNGS-Planning v4.0
Risk-Informed Drone Inspections (WMP.552) | 8.3.6 | 29% | 29% | n/a | 54.95 | 54.95 | n/a | 26.97% | n/a | 4.16% | WiNGS-Planning v4.0
[a]SDG&E does not currently calculate mitigation effectiveness for outage program risk except for WMP.462 and WMP.473.
[b]SDG&E's current methodology is designed to calculate the wildfire CBR and is not currently equipped to generate distinct CBR calculations for wildfire and outage program risks.
[c]SDG&E does not use HFRA boundaries.
[d]SDG&E does not directly calculate the effectiveness of PSPS and PEDS outage mitigations. However, the WiNGS-Planning model estimates risk reduction by simulating an increase in the alert wind gust thresholds.
[e]SDG&E does not calculate the CBR and risk reduction for this mitigation. See section 8.2.11.1.4 for details.
[f]Activity Effectiveness is when Microgrid is in operation.
[g]The Microgrid activity is not designed to mitigate wildfire risk directly. Therefore, CBR and effectiveness specific to wildfire risk are zero.
[h]Activity effectiveness percentage is based on subject matter expert assumption.
[i]Transmission programs are funded through FERC allocations and, as such, are not included in the calculation of CBR or risk reduction metrics within the WMP.

## OEIS Table 8-1
Initiative | Quantitative or Qualitative Target | Activity (Tracking ID #) | Previous Tracking ID (if applicable) | Target Unit | 2026 Target / Status | % Planned in HFTD for 2026 | % Planned in HFRA for 2026 | % risk reduction for 2026 | 2027 Target/Status | % Planned in HFTD for 2027 | % Planned in HFRA for 2027 | % risk reduction for 2027 | 2028 Target/Status | % Planned in HFTD for 2028 | % Planned in HFRA for 2028 | % risk reduction for 2028 | 3-year total | Section; Page number
Work Orders | Qualitative | Corrective Maintenance Program (CMP) (WMP.1433) - Repair wildfire-related conditions within established timeframes | n/a | n/a | By 12/31/2026, complete repairs within required timeframes | n/a | n/a | n/a | By 12/31/2027, complete repairs within required timeframes | n/a | n/a | n/a | By 12/31/2028, complete repairs within required timeframes | n/a | n/a | n/a | n/a | 8.6; p. 190
Equipment Maintenance and Repair | Qualitative | Transmission Asset Health (WMP.1458) - Analyze asset health for transmission shield wire, insulators, and hardware; explore proactive replacement strategies | n/a | n/a | By 12/31/2026, begin data analysis of asset health, current condition, and outage history of transmission equipment | n/a | n/a | n/a | By 12/31/2027, continue analysis of transmission equipment, and review and adjust replacement strategies | n/a | n/a | n/a | By 12/31/2028, continue analysis of transmission equipment, and review and adjust replacement strategies | n/a | n/a | n/a | n/a | 8.4; p. 173
Grid Ops and Procedures | Qualitative | Personnel Training (WMP.1452)- Examine electric line crew training and incorporate updates annually. | n/a | n/a | By 12/31/2026, update electric line crew training. | n/a | n/a | n/a | By 12/31/2027, update electric line crew training. | n/a | n/a | n/a | By 12/31/2028, update electric line crew training. | n/a | n/a | n/a | n/a | 8.7; 196
Workforce Planning | Qualitative | Workforce Planning (Asset Mgmt) - Consult with subject matter experts to update the Storm and PSPS curriculum.(WMP.1453) | n/a | n/a | By 12/31/2026, update Storm and PSPS training with lessons learned. | n/a | n/a | n/a | By 12/31/2027, update Storm and PSPS training with lessons learned. | n/a | n/a | n/a | By 12/31/2028, update Storm and PSPS training with lessons learned. | n/a | n/a | n/a | n/a | 8.8; p. 203
Other grid topology improvements to mitigate or reduce PSPS events | Qualitative | Standby Power Program: (WMP.468) Assess and enable resiliency and backup power solutions for eligible non-residential customers in the high fire threat district. | n/a | n/a | By 12/31/2026, enable backup power solutions of priority sites. | n/a | n/a | n/a | By 12/31/2027, enable backup power solutions of priority sites. | n/a | n/a | n/a | By 12/31/2028, enable backup power solutions of priority sites. | n/a | n/a | n/a | n/a | 8.2.11; p. 147
Other grid topology improvements to mitigate or reduce PSPS events | Qualitative | Customized Resiliency Assessments: (WMP.1432) Assess and enable resiliency and backup power solutions for eligible residential customers in the high fire threat district. | n/a | n/a | By 12/31/2026, offer resiliency support for eligible customers. | n/a | n/a | n/a | By 12/31/2027, offer resiliency support for eligible customers. | n/a | n/a | n/a | By 12/31/2028, offer resiliency support for eligible customers. | n/a | n/a | n/a | n/a | 8.2.11; p. 147
Other grid topology improvements to mitigate or reduce PSPS events | Qualitative | Generator Assistance Program: (WMP.467) Provide rebates on backup power solutions for eligible customers in the high fire threat district. | n/a | n/a | By 12/31/2026, enable rebates for backup power solutions for eligible customers. | n/a | n/a | n/a | By 12/31/2027, enable rebates for backup power solutions for eligible customers. | n/a | n/a | n/a | By 12/31/2028, enable rebates for backup power solutions for eligible customers. | n/a | n/a | n/a | n/a | 8.2.11; p. 147
Grid Design and System Hardening | Quantitative | Combined Covered Conductor (WMP.455) | n/a | Miles | 50 | 100% | n/a | 0.11% | 50 | 100% | n/a | 0.34% | 30 | 100% | n/a | 0.24% | 130 | 8.2.1; p. 133
Grid Design and System Hardening | Quantitative | PSPS Sectionalizing Enhancements (WMP.461) | n/a | Switches | 7 | 100% | n/a | n/a | 6 | 100% | n/a | n/a | 5 | 100% | n/a | n/a | 18 | 8.2.11; p. 147
Grid Design and System Hardening | Quantitative | Microgrids (WMP.462) | n/a | Microgrids | 0 | n/a | n/a | n/a | 0 | n/a | n/a | n/a | 1 | 100% | n/a | 100% | 1 | 8.2.7; p. 142
Grid Design and System Hardening | Quantitative | Advanced Protection (WMP.463) | n/a | Nodes | 30 | 100% | n/a | 0.06% | 30 | 100% | n/a | 0.06% | 30 | 100% | n/a | 0.06% | 90 | 8.2.8.1; p. 143
Grid Design and System Hardening | Quantitative | Strategic Undergrounding (WMP.473) | n/a | Miles | 0 | n/a | n/a | n/a | 0 | n/a | n/a | n/a | 50 | 100% | n/a | 9.07% | 50 | 8.2.2; p. 134
Grid Design and System Hardening | Quantitative | Distribution Overhead System Hardening (WMP.475) | n/a | Miles | 6.53 | 100% | n/a | 0.03% | 0 | n/a | n/a | n/a | 0 | n/a | n/a | n/a | 6.53 | 8.2.5.1; p. 139
Grid Design and System Hardening | Quantitative | Transmission Overhead Hardening (WMP.543) | n/a | Miles | 6.02 | 100% | n/a | n/a | 11.94 | 100% | n/a | n/a | 3 | 100% | n/a | 0.0022% | 20.96 | 8.2.5.2; p. 141
Grid Design and System Hardening | Quantitative | Transmission Overhead Hardening (Distribution Underbuild) (WMP.545) | n/a | Miles | 1.2 | 100% | n/a | 0.0003% | 7.1 | 100% | n/a | 0.0018% | 3 | 100% | n/a | n/a | 11.3 | 8.2.5.2; p. 141
Grid Design and System Hardening | Quantitative | Strategic Pole Replacement (WMP.1189) | n/a | Poles | 200 | 93% | n/a | 0.04% | 200 | 86% | n/a | 0.05% | 200 | 70% | n/a | 0.04% | 600 | 8.2.10; p. 146
Asset Inspections | Quantitative | Distribution Overhead Detailed Inspections (WMP.478) | n/a | Inspections | 21924 | 100% | n/a | 6.5% | 17779 | 100% | n/a | 2.58% | 11537 | 100% | n/a | 1.7% | 51240 | 8.3.1; p. 155
Asset Inspections | Quantitative | Transmission Overhead Detailed Inspections (WMP.479) | n/a | Inspections | 2447 | 83% | n/a | n/a | 2524 | 81% | n/a | n/a | 2545 | 87% | n/a | n/a | 7516 | 8.3.2; p. 157
Asset Inspections | Quantitative | Transmission Infrared Inspections (WMP.482) | n/a | Inspections | 7294 | 84% | n/a | n/a | 7294 | 84% | n/a | n/a | 7294 | 84% | n/a | n/a | 21882 | 8.3.3; p. 159
Asset Inspections | Quantitative | Distribution Wood Pole Intrusive Inspections (WMP.483) | n/a | Inspections | 1214 | 100% | n/a | 0.05% | 5477 | 100% | n/a | 0.35% | 11923 | 100% | n/a | 1.53% | 18614 | 8.3.4; p. 161
Asset Inspections | Quantitative | Transmission Wood Pole Intrusive Inspections (WMP.1190) | n/a | Inspections | 68 | 100% | n/a | n/a | 196 | 100% | n/a | n/a | 24 | 100% | n/a | n/a | 288 | 8.3.5; p. 163
Asset Inspections | Quantitative | Risk-Informed Drone Inspections (WM.552) | n/a | Inspections | 6500 | 85% | n/a | 1.08% | 6500 | 96% | n/a | 1.36% | 6500 | 98% | n/a | 1.73% | 19500 | 8.3.6; p. 164
Asset Inspections | Quantitative | Distribution Overhead Patrol Inspections (WMP.488) | n/a | Inspections | 84678 | 100% | n/a | 6.91% | 84678 | 100% | n/a | 6.91% | 84678 | 100% | n/a | 6.91% | 254034 | 8.3.7; p. 168
Asset Inspections | Quantitative | Transmission Overhead Patrol Inspections (WMP.489) | n/a | Inspections | 7454 | 84% | n/a | n/a | 7454 | 84% | n/a | n/a | 7454 | 84% | n/a | n/a | 22362 | 8.3.8; p. 169
Asset Inspections | Quantitative | Substation Patrol Inspections (WMP.492) | n/a | Inspections | 381 | 100% | n/a | n/a | 381 | 100% | n/a | n/a | 381 | 100% | n/a | n/a | 1143 | 8.3.9; p. 171

## OEIS Table 9-2
Activity (Program) | Tracking ID | Previous Tracking ID, if applicable | Target Unit | Cumulative (Cml.) Quarterly Target 2026, Q1 | Cml. Quarterly Target 2026, Q2 | Cml. Quarterly Target 2026, Q3 | Cml. Quarterly Target 2026, Q4 | Cml. Quarterly Target 2027, Q1 | Cml. Quarterly Target 2027, Q2 | Cml. Quarterly Target 2027, Q3 | Cml. Quarterly Target 2027, Q4 | Cml. Quarterly Target 2028, Q1 | Cml. Quarterly Target 2028, Q2 | Cml. Quarterly Target 2028, Q3 | Cml. Quarterly Target 2028, Q4 | % HFTD Covered in 2026 | % Risk Reduction for 2026 | % Risk Reduction for 2027 | % Risk Reduction for 2028 | 3- year Total | Activity Timeline Target | Section; Page Number
Detailed Inspection | WMP.494 | n/a | Inspections | 60080 | 140365 | 207680 | 255000 | 60080 | 140365 | 207680 | 255000 | 60080 | 140365 | 207680 | 255000 | 100% | 4.53% | 4.53% | 4.53% | 765000 | 2028-12-31 | 9.2; p. 211
Off-Cycle Patrol | WMP.508 | n/a | VMAs | 25 | 44 | 92 | 106 | 25 | 44 | 92 | 106 | 25 | 44 | 92 | 106 | 100% | 4.52% | 4.52% | 4.52% | 318 | 2028-12-31 | 9.2; p. 211
Pole Clearing | WMP.512 | n/a | Poles | 4479 | 12196 | 20875 | 22000 | 4479 | 12196 | 20875 | 22000 | 4479 | 12196 | 20875 | 22000 | 100% | 4.49% | 4.49% | 4.49% | 66000 | 2028-12-31 | 9.4; p. 214