## Discovery Log
**This Discovery Log reflects Data Requests completed as of 05:00PM each Wednesday
SDG&E 2026 WMP Discovery Log
Question Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Response | Requestor | Date Rec'd | Final Due Date | Date Sent | Link | Number of Atchs | NDA Required | WMP Section | Category | Sub Category
1 | OEIS | 2 | OEIS-2 | 1 | OEIS-2.1 | Regarding Vegetation Management Inspections: On page 209 of its 2026-2028 Base WMP, SDG&E lists the Area Inspected for all Vegetation Management Inspection programs as “HFTD.” On pages 57-60 of its 2026-2028 Base WMP, SDG&E describes evaluating high fire areas outside of the HFTD and explains why SDG&E has not proposed adding these areas to the HFTD. SDG&E states that some of these areas are of a lower priority for grid-hardening initiatives but does not mention other WMP activities. a. Explain SDG&E’s decision-making process for excluding the WUI and coastal canyons from SDG&E’s 2026-2028 WMP Vegetation Management Inspection Programs and associated targets. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). b. Does SDG&E plan to perform Detailed Inspection (WMP.494) in the WUI and coastal canyons during the 2026-2028 WMP cycle? i. If not, provide the estimated risk reduction achieved by performing Detailed Inspections to: 1. The WUI 2. Coastal canyons c. Does SDG&E plan to perform Off-Cycle Patrols (WMP.508) in the WUI and coastal canyons during the 2026-2028 WMP cycle? i. If not, provide the estimated risk reduction achieved by adding Off-Cycle Patrols to: 1. The WUI 2. Coastal canyons | a. The targets presented for Vegetation Management inspections are limited to the HFTD to remain consistent with the approach taken in SDG&E’s Test Year 2024 GRC Decision.1 SDG&E clarifies that Detailed Inspection (WMP.494) activities and Off-Cycle patrols, such as targeted species patrols, are performed outside the HFTD throughout its entire service territory, but these inspections are no longer in scope for WMP. b. Yes, as described above, SDG&E plans to perform Detailed Inspection in the WUI and coastal canyons during the 2026-2028 WMP cycle. b.i. N/A c. Yes, as described above, SDG&E plans to perform Off-Cycle Patrols in the WUI and coastal canyons during the 2026-2028 WMP cycle. c.i. N/A | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5 | 5 Risk Methodology and Assessment | 5.6.2 | 5.6.2 Model Controls, Design, and Review
2 | OEIS | 2 | OEIS-2 | 2 | OEIS-2.2 | Regarding Integrated Vegetation Management Activities: In SDG&E's 2023-2025 Base WMP (pages 284-286), sections 8.2.3.6 High-Risk Species and 8.2.3.7 Fire-Resilient Right-of-Ways SDG&E includes four integrated vegetation management activities: Right Tree, Right Place (WMP.1325), Community Tree Rebate Program (WMP.1326), Land Services Vegetation Abatement (WMP.1327) and Fire Coordination Fuels Reduction MOU & Grant (WMP.1328). On page 215 of its 2026-2028 Base WMP, SDG&E lists Fuels Management (WMP.497) as its only IVM activity. SDG&E states that “because of the relative lack of vegetation density along its major transmission corridors, SDG&E does not engage in these traditional integrated vegetation management activities.” a. Does SDG&E plan to perform all or some of the activities that its 2023-2025 Base WMP describes for WMP.1325, WMP.1326, WMP.1327, and WMP.1328 during the 2026-2028 WMP cycle? i. If yes, describe which activities SDG&E plans to perform and which it will discontinue during the 2026-2028 Base WMP cycle. ii. For each of these activities its plans to perform during the 2026-2028 WMP cycle, explain why SDG&E excludes these activities from its 2026-2028 Base WMP. iii. For each of these activities it will not perform during the 2026-2028 WMP cycle, explain SDG&E’s decision-making process for discontinuing the activity. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). | a. SDG&E does plan to perform some of the activities described for WMP.1325, WMP.1326, WMP.1327, and WMP.1328 during its 2023-2025 Base WMP during the 2026-2028 Base WMP cycle. i. SDG&E plans to perform Right Tree, Right Place; Land Services Vegetation Management Abatement; and Fire Coordination Fuels Reduction & Grant activities during the 2026-2028 Base WMP. SDG&E plans to discontinue the Community Tree Rebate Program during the 2026-2026 Base WMP cycle. ii. As stated in its 2023-2025 Base WMP, SDG&E’s Right Tree, Right Place (WMP.1325) is part of its tree removal program (see page 277). SDG&E primarily engages customers with the option to remove incompatible trees during the inspection activity or during the tree pruning activity. In its 2026-2028 Base WMP Guidelines, Energy Safety created two new initiatives for Vegetation Management: IVM and Pruning and Right Place within IVM, and instead to reserve IVM solely for the activity of Fuels Management. SDG&E will continue to engage customers on the option to remove incompatible trees using the concept of Right Tree, Right Place during the inspection and tree pruning and removal activities during the 2026-2028 Base WMP. Land Services Vegetation Management Abatement, and Fire Coordination Fuels Reduction & Grant are not categorized as activities within IVM in the 2026-2026 Base WMP. However, both activities are described under the new WMP section titled Partnerships 9.8 and will continue during the 2026-2028 Base WMP. iii. SDG&E’s Community Tree Rebate Program (WMP.1326) has been discontinued in 2025 to promote customer affordability and reflect SDG&E’s authorized revenue requirements. SDG&E also believes it has substantively met the overall goal of the program to engage those customers eligible to participate in the program. The cessation of the program does not negatively impact the company’s risk mitigation measures as the program is not primarily aimed at risk reduction. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 9 | 9 Vegetation Management and Inspections | 9.7.1 | 9.7.1 Overview
3 | OEIS | 2 | OEIS-2 | 3 | OEIS-2.3 | Regarding Vegetation Management Quality Assurance and Quality Control: On page 224 of its 2026-2028 WMP, SDG&E combines Detailed Inspections (WMP.494), Prune and Removal (Clearance)(WMP.501), and Pole Clearing (WMP.512) into a single quality check activity/row in Table 9-6: Vegetation Management QA and QC Activity Targets. a. Complete the table below with a separate row for each activity containing activityspecific quantitative values for population/sample unit, annual population size, annual sample size, confidence level, and margin of error (MOE). i. In the “Annual Sample Size” column, list the number of individual sample units that make up the sample rather than listing a percentage of the population. | SDG&E performs QA/QC throughout the calendar year following the completion of the scheduled vegetation management activities (Detailed Inspections; Pruning and Removal; Pole Clearing). SDG&E strives to complete a 15% audit for each activity. The sample population for each audit is dependent on the number of units completed for each respective activity, thus calculated based on historical averages. Note that Prune and Removal is dependent on the Detailed Inspection, therefore, an accurate method to calculate annual population size or sample size is not available. SDG&E includes in the table provided above an approximate value of the Annual Sample Size for each of the three activities. Initiative/Activity Being Audited Population / Sample Unit Annual Population Size Annual Sample Size Confide nce Level Margin of Error (MOE) Detailed Inspections (WMP.494) Number of Trees Inspected 255,000 38,250 99% 3% Initiative/Activity Being Audited Population / Sample Unit Annual Population Size Annual Sample Size Confide nce Level Margin of Error (MOE) Prune and Removal (Clearance) (WMP.501) Number of Trees Pruned/Remo ved N/A N/A N/A N/A Pole Clearing (WMP.512) Number of Poles Brushed 22,000 3,300 99% 3% | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 9 | 9 Vegetation Management and Inspections | OEIS Table 9-6 | Vegetation Management QA and QC Activity Targets
4 | OEIS | 2 | OEIS-2 | 4 | OEIS-2.4 | Regarding Larger QA/QC Sample Sizes for Enhanced Vegetation Management Activities in the HFTD: On page 289 of its 2023-2025 WMP, SDG&E indicates that "a higher sampling percentage is used for some enhanced vegetation management activities in the HFTD, including a 100 percent post-trim audit of all completed trim and removal work generated from the off-cycle patrol (WMP.508) activities… Additionally, audits are performed on 100 percent of all work completed on tree trim “Memo” work orders." SDG&E’s audit of a higher percentage of “some enhanced vegetation management activities in the HFTD” is absent from its 2026-2028 Base WMP. a. Does SDG&E plan to perform a post-trim audit of completed trim and removal work generated from off-cycle patrol activities during the 2026-2028 WMP cycle? i. If so, explain why SDG&E excludes this audit from its 2026-2028 Base WMP. ii. If not, explain SDG&E’s decision-making process for discontinuing this audit. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). b. Does SDG&E plan to audit work completed on tree trim “Memo” work orders during the 2026-2028 WMP cycle? i. If so, explain why SDG&E excludes this audit from its 2026-2028 Base WMP. ii. If not, explain SDG&E’s decision-making process for discontinuing this audit. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). | a. Yes, SDG&E plans to perform post-trim audits of completed pruning and removal work generated from off-cycle patrol activities during the 2026-2028 WMP cycle. i. For the 2026-2028 Base WMP, SDG&E will integrate a post-trim audit of work generated from the off-cycle patrols into its standard auditing processes. Doing so will align overall audit practices and provide procedural consistency. Upon further evaluation of its audit scope, SDG&E believes that utilizing a representative sample population to perform its audits is effective in determining contractor compliance and work quality. SDG&E may elect to conduct a higher percentage of audits on work generated from the off cycle HFTD patrol than the standard 15%. However, this may be the same VMA, and the most efficient and effective utilization of contractor resources. ii. Please see the response to i. above. b. Yes, SDG&E plans to audit work completed on tree trim “Memo” work orders during the 2026-2028 WMP cycle. i. For the 2026-2028 Base WMP, SDG&E will integrate a post-trim audit of work generated from the off-cycle patrols into its standard auditing processes. Doing so will align overall audit practices and provide procedural consistency. Upon further evaluation of its audit scope, SDG&E believes that utilizing a representative sample population to perform its audits is effective in determining contractor compliance and work quality. SDG&E may elect to conduct a higher percentage of audits on work generated from the off cycle HFTD patrol than the standard 15%. However, this may be influenced by other vegetation management activities concurrently in process within the same VMA, and the most efficient and effective utilization of contractor resources. ii. Please see the response to i. above. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | N/A | Absence Enhanced vegetation management activities in the HFTD in 2026-2028 Base WMP | N/A | N/A
5 | OEIS | 2 | OEIS-2 | 5 | OEIS-2.5 | Regarding Benchmarking Performance of Vegetation Management Operations Across Multiple VMAs: On page 290 of its 2023-2025 Base WMP, SDG&E states it “is considering the development of compliance-based audits as a measure of system status and reliability. Such audits may be performed across multiple VMAs and create benchmarking for the performance of vegetation management operations. The anticipated timeline to implement compliance-based audits is 2 to 3 years.” a. Provide an update on the progress of using audits to benchmark the performance of vegetation management operations across multiple VMAs. b. Provide a summary of findings, lessons learned, and improvements to vegetation operations that SDG&E has implemented as a result of considering compliance-based audits as a measure of system status and reliability. | a. SDG&E continues to explore the possibility of expanding its audit program to include a compliance-based component for the activity of tree pruning. In its current state the posttrim audit program is scaled and scoped to occur at the individual Vegetation Management Area (VMA) level focusing on contractor performance and work quality. A compliancebased audit would target instances of non-compliant tree clearances and incorporate rootcause analysis as part of the procedure. Compliance-based audits could be conducted throughout the year exclusive of the schedule for routine tree trimming activities. b. Developing a compliance audit would require enhancements to SDG&E’s current work management system (Cityworks) including the design, development, and testing of integrating multiple VMAs into the system’s randomization tool, creation of new electronic forms to support data entry, and back-end reporting to track audit results, among others. Other considerations in expanding the audit scope include the required increase in contractor staffing resources and additional costs for the program. SDG&E has also considered employing the use of remote sensing technology as a potential tool in a compliance-driven audit. For example, LiDAR could be used on a broad scale and as a mechanism in accurately identifying non-compliant trees. Cost and frequency of LiDAR capture and the timeliness of data processing are additional considerations for viability. SDG&E will continue to explore this issue and currently continues to anticipate a timeline of 2 to 3 years to complete its evaluation of possible implementation of a compliance-based audits in its vegetation management program. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 2023-2025 Base WMP | Benchmarking Performance of Vegetation Management Operations Across | N/A | N/A
6 | OEIS | 2 | OEIS-2 | 6 | OEIS-2.6 | Regarding Past Due Work Order Quantities and Constraint Types: On page 228 of its 2026-2028 Base WMP, SDG&E lists 9,916 past due work orders in Tables 9-7 and 9-8. On page 292 of its 2023-2025 Base WMP, SDG&E lists 981 past due work orders. a. Describe the factors that have primarily led to an approximately 900 percent increase in past due work orders from the time of 2023-2025 Base WMP submission to the time of the 2026-2028 Base WMP submission. | The difference in the number of past due work orders provided in the 2023-2025 Base WMP compared with the numbers of past due work orders provided in the 2026-2028 Base WMP can be attributed to the differences in the methodology of deriving the data, and not the result of a substantial increase in past due work orders. In its 2026-2028 Base WMP, SDG&E reported the total number of open work orders, not past due work orders. SDG&E makes the correction in tables provided below. SDG&E will additionally provide these corrected tables in its forthcoming errata. OEIS Table 9-7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier HFTD Area 0-30 days 31-90 days 91-180 days 181+ days HFTD Tier 2 75 225 5 1 HFTD Tier 3 300 29 1 0 OEIS Table 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels Priority Level 0-30 days 31-90 days 91-180 days 181+ days High Priority 40 12 2 0 Low Priority 335 242 4 1 | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 9.12.3 | 9.12.3 Trends . | Table 9-7 | Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier HTFD Area 0-30 Days 31-90 Days 91-180
7 | OEIS | 2 | OEIS-2 | 7 | OEIS-2.7 | Regarding Financial Attribute Components: On page 29 of SDG&E’s 2026-2028 Base WMP, SDG&E discusses two general components of the financial attribute: societal damage and utility repair costs. a. Provide information on the magnitude of these two components in comparison to one another, including the following individual portions for each component: i. Physical damage, lost wages, and relocation costs for societal damage ii. Labor and materials for utility repair b. Provide an example of how total cost is calculated showing the various societal damage and utility repair monetization components. | In accordance with CPUC Decision (D.) 22-12-027, SDG&E is shifting from its previous reliance on the Multi-Attribute Value Framework (MAVF) to a Cost-Benefit Analysis (CBA) approach. Section 5.1 introduces this new methodology, offering an initial outline that will be further developed in SDG&E’s upcoming 2025 Risk Assessment Mitigation Phase (RAMP) filing. This section serves to bridge the Wildfire Mitigation Plan (WMP) with broader enterprise risk management efforts. This section introduces the financial attribute and explains how it can be used to capture two general categories of costs: societal damage (e.g., including physical damages, lost wages, and relocation costs) and utility repair costs (e.g., labor, materials). This approach is intended to reflect how financial impacts may be consistently calculated and applied across SDG&E. Specifically for this WMP, SDG&E’s wildfire consequence model estimates societal damages by assigning monetary values to projected structure losses and acres burned, based on outputs from Technosylva wildfire simulations. SDG&E’s wildfire consequence model does not estimate utility repair costs, because of the difficulty of estimating the number of assets impacted and the severity of the impact and because the high-level dollar estimates for utility repairs would be relatively insignificant when compared to the more substantial costs associated with structural losses and acres burned. In the PSPS Risk Model, the financial impact of a de-energization event is estimated based on several key factors: the assumed duration of the PSPS event, the number and types of customers affected, and cost proxies informed by the federal per diem rates for lodging, meals, and incidentals applicable to San Diego County. a) Not applicable – see explanation above. b) The following is an example of how SDG&E quantifies wildfire risk. This example was originally shared during the Risk Modeling Working Group session held on March 26, 2025. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5.2 | 5.2 Risk Analysis Framework | N/A | N/A
8 | OEIS | 2 | OEIS-2 | 8 | OEIS-2.8 | Regarding Climate Change Projections: On page 30 of SDG&E’s 2026-2028 Base WMP, SDG&E notes that a system-wide climate adaptation vulnerability assessment (CAVA) is being analyzed to examine mid- and endcentury climate change projections. SDG&E notes that it plans to update its risk modeling methodology when new data becomes available. a. Provide a timeline for the completion of this examination and its implementation into the risk modeling methodology. This timeline must include: i. Discreet steps within the timeline for implementation ii. Expected completion dates for each step, down to quarter granularity (i.e., Q4 2025) | SDG&E is actively exploring multiple methodologies to model future wildfire risk, with particular emphasis on projecting potential increases in acres burned relative to historical baseline. A key objective is to align these projections as closely as possible with the latest climate science, specifically the CMIP6 (Coupled Model Intercomparison Project Phase 6) simulation outputs, which will inform California’s upcoming Fifth Climate Change Assessment, scheduled for release in 2026. Currently, the most recent wildfire projection dataset available on Cal-Adapt is based on earlier CMIP5 simulations, specifically the work by Westerling (2018). However, this dataset is now considered outdated. In response, the UC Merced research team is actively working to update wildfire projections using CMIP6 data. These updated projections will provide a more accurate and forward-looking foundation for assessing wildfire risk under future climate scenarios and will be incorporated into the 2026 Assessment. Once the CMIP6-based wildfire projections are made available, SDG&E will review, validate, and incorporate the data into its risk modeling framework, pending approval by its internal subject matter experts (SMEs). | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5.2 | 5.2 Risk Analysis Framework | N/A | N/A
9 | OEIS | 2 | OEIS-2 | 9 | OEIS-2.9 | Regarding Consequence Models: On page 36 of SDG&E’s 2026-2028 Base WMP, Figure 5-6 depicts the differences between the WiNGS-Ops and WiNGS-Planning consequence models. a. Provide a description of any additional differences between the two models not captured within Figure 5-6. b. Explain why egress is only included as a part of the WiNGS-Planning model. c. Explain how the egress factor is calculated. | a) Figure 5-6 depicts all major model source and process step differences between the consequence models across both the operational and planning versions of the WiNGS model. Additional differences of each model exist and are summarized within the model technical documentation. For more details, please refer to Appendix B: Supporting Documentation For Risk Methodology and Assessment, Section 2: Summary Documentation. The notable difference related to the consequence models not captured directly in Figure 5-6 between the two versions of the WiNGS is the risk unit utilized. WiNGS-Planning uses a cost-benefit ratio (CBR) framework unit as described in the up-coming filing for the 2025 Risk Assessment and Mitigation Phase (RAMP) report for its risk score, whereas WiNGS-Ops will upgrade to leverage the same framework in the future and currently uses a weighted risk score approach using a risk spend efficient (RSE) framework as described by SDGE’s 2021 Risk Assessment and Mitigation Phase (RAMP) report. WiNGS-Ops is expected to align with the cost-benefit framework by end of Q3-2025. b) As the WiNGS-Ops model is focused on PSPS and emergency decision making, SDG&E does not incorporate egress modeling into its WINGS-Ops model, based on the operational roles and responsibilities defined during wildfire and PSPS de-energization events. This decision reflects both the utility’s limited authority in evacuation matters and the established structure of emergency response coordination within California. Primarily, SDG&E does not intend to use egress model outputs during PSPS activations or active wildfire incidents. This is because utility personnel do not have the authority to initiate or request evacuations, nor are they part of the formal decision-making process regarding evacuation orders. These decisions are made by the Incident Commander, who operates within a Unified Command structure composed of first responder agencies, most notably fire and law enforcement authorities. Utilities, including SDG&E, typically serve as cooperators in these incidents, providing support with utility knowledge but not directing public safety actions. The decision to evacuate is multifaceted and considers a range of dynamic factors such as fire behavior, weather conditions, terrain, and population density. Utilities are generally not a significant factor in this analysis. Law enforcement agencies are the primary leads for executing evacuations, and their decisions are informed by real-time situational awareness and public safety priorities. While SDG&E recognizes the value of egress modeling as a tool for understanding potential evacuation challenges, it does not currently view it as a best practice for utility-led operational platforms. Instead, SDG&E focuses on strengthening partnerships with fire and law enforcement agencies to enhance coordination and public safety. This includes participating in joint training exercises, leveraging shared communication platforms, and supporting public messaging during emergencies. By maintaining clear boundaries around its operational role and deferring evacuation decisions to the appropriate authorities, SDG&E ensures that its wildfire and PSPS response efforts remain aligned with the broader emergency management framework in California. c) The Egress model is intended to be included in the wildfire consequence model (safety attribute) of WiNGS-Planning. The egress model is a relative ranking model that helps in identifying areas in SDG&E service territory that are most vulnerable to evacuation constraints during a wildfire event. SDG&E completed the first iteration of the model by the end of 2022 and adoption in WiNGS-Planning was completed in 2023. At any given location, the model simulates different (stochastic) potential scenarios of movements of people considering road capacity constraints during the evacuation process. Each scenario is triggered by a simulated match-drop ignition (spread, direction, duration), predefined evacuation routes, and evacuation travel times. Random scenarios are created based on a set of Subject Matter Expert assumptions, 8-hour unsuppressed wildfire simulations created by Technosylva, historical weather conditions, population information, and road-street networks and geometries. SDG&E’s egress model is predominantly influenced by these two papers: - Grajdura, Sarah, Sachraa Borjigin, and Deb Niemeier. "Fast-moving dire wildfire evacuation simulation." Transportation research part D: transport and environment 104 (2022): 103190. - Kim, Sangho, Betsy George, and Shashi Shekhar. "Evacuation route planning: scalable heuristics." Proceedings of the 15th annual ACM international symposium on Advances in geographic information systems. 2007. SDG&E emphasizes that this model is for mitigation planning and scoping only and is not intended to be used during an evacuation planning or during an active real-evacuation event. This model is not used to create a set of strategies or define best practices to ensure the safe and efficient evacuation of communities in the path of an advancing wildfire. In the event of a wildfire evacuation event, SDG&E will work closely with local authorities, emergency responders, law enforcement, and other stakeholders to assist with evacuation efforts based on known real time conditions and available information. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5.5.2 | 5.5.2 Top Risk-Contributing Circuits/Segments/Spans | Figure 5-6 | WiNGS-Planning and Ops Calculation Schematic
10 | OEIS | 2 | OEIS-2 | 10 | OEIS-2.10 | Regarding Attributes for Wildfire Consequence: a. On page 38 of SDG&E’s 2026-2028 Base WMP, SDG&E Table 5-4 provides estimates used to calculate various risk components. i. For the safety component, SDG&E states that it is using an assumption of a 0.00617 factor to estimate the total number of equivalent fatalities per structure destroyed. Provide documentation justifying the basis for this assumption, including the analysis conducted on the CAL FIRE data set as discussed within SDG&E Table 5-4. ii. For the financial component, SDG&E states that it is using an assumption of $2,350 per acre burned for suppression and restoration cost. Provide documentation justifying the basis for this assumption, including any analysis performed. b. On pages 39 and 40 of SDG&E’s 2026-2028 Base WMP, the financial attributes for PSPS and PEDS consequences are discussed in SDG&E Table 5-5 and SDG&E Table 5-6, respectively. Provide additional discussion and justification on the motivation and basis for the differences in financial attribute assumptions used for PSPS and PEDS.Include any supporting documentation and analysis that led to the financial attribute assumptions used. | a) i) Refer to “SDGE_Wildfire_Fatality_Structures_ratios_2025_05_12.xlsx” for details on how this assumption is calculated a) ii) Refer to “SDGE_Cost_per_acre_2025_05_09.xlsx” for details on how this assumption is calculated b) The differences in how financial estimates are calculated for PSPS and PEDS events are based on the assumption that PSPS events typically involve longer restoration times, with an assumed duration of approximately 24 hours per event. Due to this extended duration, a per-diem cost estimation method is applied. This approach accounts for additional customer impacts, including the need for meals and lodging during the de-energization period. In contrast, PEDS events are typically shorter in duration and occur with less predictability, often being characterized as “random” in nature. Due to their limited duration, it is assumed that these events are less likely to necessitate extended accommodations or meal provisions. As a result, the financial estimates for PEDS events do not include per-diem costs for meals and lodging, leading to lower overall cost assumptions. To estimate the financial impact of a PEDS event, SDG&E applies a simplified cost assumption equivalent to 10% of the expected reliability impact. This percentage is derived from a high-level approximation of post-patrol costs associated with overhead line inspections conducted during elevated or extreme fire weather conditions. While this estimate is not event-specific, SDG&E subject matter experts consider it as a reasonable proxy to reflect the variability in financial impacts across different PEDS events. This approach acknowledges that not all PEDS events incur the same level of cost. With this approach, the financial estimate is intended to scale proportionally with the simulated PEDS event duration and the number of customers affected by a given PEDS outage, providing a consistent approach for estimating financial impact in the absence of detailed event-level data. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE_Cost_per_acre_2025_05_09_0.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE_Wildfire_Fatality_Structures_ratios_2025_05_12_0.xlsx | 2 | No | 5.2.2.2.1 | Wildfire CoRE | Table 5-4 | Attributes for Wildfire Consequence
11 | MGRA | 3 | MGRA-3 | 1 | MGRA-3.1 | With regard to Figure 1-1: 2026-2028 Expected risk Reduction: a. Does the risk reduction indicated include SDG&E's convex risk weighting function/attitude? b. If the answer to a) is yes, please provide an equivalent figure using a neutral risk attitude. | a) No. Figure 1-1 does not include SDG&E’s risk aversion. b) Not applicable | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 1.2 | 1.2 Objectives | Figure 1-1 | 2026-2028 Expected Risk Reduction
12 | MGRA | 3 | MGRA-3 | 2 | MGRA-3.2 | With regard to “Wind Gust Weight” described on p. 13, how is this weighting determined and the driver normalized? | To distinguish and quantify the wildfire risk for a given risk driver that occurred at locations prone to wildfire conditions, the 99th percentile wind gust for a given location is compared to the 25th, 50th, 75th of the overall 99th percentile wind guests for all HFTD locations. The weight (WRwind) of the wind component for a risk event is calculated using 20, 21, 22, and 23, respectively. The frequency of the ignition events (Rfreq) is aggregated by the FPI level, wind gust category, and consequence category. For drivers that do not have CPUC reportable ignitions, this multiply factor (n_ignition_events_normalized) would be 1. For example, if 5 animal-contact caused ignitions occurred at locations where the 99th wind gust falls between 25th to 50th percentiles of the overall 99th wind gust (WRwind = 21) and where the 50th consequence is above the overall 50th percentile threshold, the Rfreq is calculated as follow: Rfreq = n_ignition_events_normalized × WRwind × Wcon × Σn Rcon The ignition events are normalized using the min-max scaling normalization formula: | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 3.4 | 3.4 Prioritized List of Wildfire Risks and Risk Drivers . | N/A | N/A
13 | MGRA | 3 | MGRA-3 | 3 | MGRA-3.3 | Please provide technical documentation for the risk driver statistical analysis and testing mentioned on page 14: “Topographical and climatological risk factors, which include factors include FPI, temperature, humidity, wind gust, elevation, slope, and aspect associated with the location where risk events were observed, were evaluated. Test statistics method Mann Whitney Test was used to compare the sample mean of a risk driver to the sample mean of the other risk drivers. If the difference was statistically significant, this risk factor is noted in OEIS Table 3-1 as influential for a risk driver. These factors are evaluated based on the historical climatological data and current topographical characteristics of the locations associated with each risk driver.” | SDG&E objects to the request to the extent is seeks information that is publicly available and equally available to the requestor. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not have technical documentation regarding this Mann Whitney Test but abundant explanations can be found online. The goal is to test the statistical significance of a risk factor for a given risk driver. Risk events for each diver category are not normally distributed, which is the main reason Mann Whitney Test is used to run the statistical test instead of using T test. The data used for this test are processed in python, mannwhitneyu() function under “scipy.stats” library. The underlying data have risk factors mapped to individual risk event observations. The data field, FPI value, is spatially and temporally mapped to each observation; whereas other risk factors, such as temperature and slope, are mapped spatially to the asset where the risk events were observed. The data are sampled into two groups, a given risk driver and all other observations before running this test. The OEIS table 3-1 shows the result of the test for each risk driver category when compared with all the other risk drivers. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 3.4 | 3.4 Prioritized List of Wildfire Risks and Risk Drivers . | N/A | N/A
14 | MGRA | 3 | MGRA-3 | 4 | MGRA-3.4 | With regard to SDG&E Table 5-7, p. 42, please provide the justification and modeling that leads to the P100 percentile of a potential $211B loss in the SDG&E service area. | As illustrated in Table 5-7, Wildfire risk constitutes the majority of the Overall Utility Risk, significantly outweighing the contributions from PSPS and PEDS risks. Over the course of the 5 million simulated years, the most extreme wildfire scenario, resulting in an estimated cost of approximately $211 billion, was driven by two ignition events that coincidentally occurred under the same simulation seed ID. The table below shows how the maximum values are derived based on the Monte Carlo simulation: Ignition 1 Ignition 2 Total Sim Weather Conditions Date 11/12/2018 11/17/2014 --- Ignition ID 403589 1012407 --- Seed ID 11792465 11792465 --- Total Acres Burned 43,703 35,934 79,637 Total Structures Destroyed 6,029 4,042 10,071 Sim Max Wind Gust Conditions 62 55 --- SCADA Sect. Device 907-1562AE 909-451 --- Feeder ID 907 909 --- Wildfire Total Risk (with Risk Aversion) [M$] $136,729.33 $74,237.73 $210,967.06 Wildfire Total Risk (without Risk Aversion) [M$] $7,559.78 $4,989.72 $12,549.50 Wildfire Safety Risk (without Risk Aversion) [M$] $1,427.77 $863.42 $2,291.19 Wildfire Financial Risk (without Risk Aversion) [M$] $6,132.00 $4,126.24 $10,258.25 Wildfire Reliability Risk (without Risk Aversion) [M$] $0.01 $0.05 $0.06 | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 5.2.2.3 | 5.2.2.3 Risk | SDGE Table 5-7 | 5-7: Pre-Mitigation Wildfire, PSPS, PEDS, and Overall Utility Risk estimates for the Service Territory . 42
15 | MGRA | 3 | MGRA-3 | 5 | MGRA-3.5 | Please provide a list of the 125 worst fire weather days (p. 45) and associated wildfire hazard intensity data. | Please see attached spreadsheet titled “SDGE Response MGRA-2026-8- 03_Q5_SDGE_125_worst_fire_days_stats_2025_05_15.xlsx” for the list of 125 days and percentile values of acres burned and structure destroyed for each day. This is the data as referenced on page 45 of SDG&E’s 2026-2028 WMP. This list is currently under review by the Meteorology and Risk Analytics teams. Given the extreme fire weather conditions experienced within SDG&E’s service territory between November 2024 and January 2025, SDG&E is evaluating the inclusion of these recent dates in future analyses. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03_Q5_SDGE_125_worst_fire_days_stats_2025_05_15.xlsx | 1 | No | 5.2.3 | 5.2.3 Key Assumptions and Limitations . | N/A | N/A
16 | MGRA | 3 | MGRA-3 | 6 | MGRA-3.6 | With regard to OEIS Table 4-3, and corresponding Excel table (MGRA-3-9 b), please break out customers into Residential, Small C&I, and Medium/Large C&I. | SDG&E objects to the request to the extent it is unduly burdensome and calls on SDG&E to perform studies or analysis that do not currently exist. Subject to and without waving the foregoing objections, SDG&E responds as follows: Commercial and Industrial customers are split based on their kW demand. SDG&E does not have C&I broken down by small, medium or large. The documentation provided includes customer hours broken out into Residential and C&I. Please see the attached spreadsheet titled “SDGE Response MGRA-2026-8-03_Q06-OEIS-Table- 4-3.xlsx.” | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03_Q06-OEIS-Table-4-3.xlsx | 1 | No | OEIS Table 4-3 | 4-3: Frequently De-energized Circuits 23 | N/A | N/A
17 | MGRA | 3 | MGRA-3 | 7 | MGRA-3.7 | WiNGS-Planning still incorporate a decision tree that will default to underground if the Cost/benefit characteristics meet certain criteria, as was described in the SDG&E GRC? Or are all combinations evaluated as options prior to the decision tree? a. If the answer is yes decision tree is prior to CBR calculation does the CBR use SDG&E’s convex risk function/attitude for the decision tree? | SDG&E objects to the request to the extent it is argumentative and mischaracterizes SDG&E’s modeling functions. SDG&E further objects to the request to the extent it is vague and ambiguous, and fails to identify with specificity the information requested. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not default to undergrounding as the preferred mitigation strategy. For each feeder segment, SDG&E evaluates risk reduction and cost-benefit ratios for both Combined Covered Conductor and Strategic Undergrounding mitigation options. As stated in the 2026-2028 WMP filing, mitigations are selected by considering their Cost Benefit Ratio (CBR) estimates which encompass risk reduction estimates, as well as both upfront installation and lifecycle costs. Lifecycle costs are essential to making informed and cost-effective decisions in infrastructure investments. They encompass not only the initial investment in mitigation measures but also the ongoing costs of maintenance, operations, and potential upgrades. See section 6.1.3 of the 2026-2028 WMP filing for further details. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | N/A | WiNGS-Planning | N/A | N/A
18 | MGRA | 3 | MGRA-3 | 8 | MGRA-3.8 | SDG&E describes significant changes to the covered conductor management structure that are now ongoing (p. 98). Will covered conductor deployment continue unabated while SDG&E reorganizes the management process? | Yes, the covered conductor deployment is expected to continue unabated while SDG&E reorganizes the Project Management Office (PMO) services. There will be some overlap between the incumbent PMO service provider and the new PMO service provider to ensure a smooth transition. The new PMO service provider may also subcontract some of their services with the incumbent to ensure there are no disruptions in the program. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 6.1.3.2 | 6.1.3.2 Activity Prioritization . | 6.1.3.2.3 | Resource Optimization
19 | MGRA | 3 | MGRA-3 | 9 | MGRA-3.9 | Please provide tabular data in Excel spreadsheet format for the following figures: a. OEIS Table 3-1: List of Risks and Risk Drivers to Prioritize b. OEIS Table 4-3: Frequently De-energized Circuits c. OEIS Table 6-1 and Appendix F, List of Prioritized Areas d. SDG&E Table 6-1 Potential Mitigation Activities for Risk Drivers e. OEIS Table 6-3 Risk Impact of Activities f. Appendix G refers to a dead web link. Please provide the data in Excel spreadsheet as well as fix the weblink. | For a-f all the requested tables are available on SDG&E’s website at https://www.sdge.com/2026- 2028-wildfire-mitigation-plan | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | OEIS Table 3-1 | 3-1: List of Risks and Risk Drivers to Prioritize 11 | N/A | N/A
20 | MGRA | 3 | MGRA-3 | 10 | MGRA-3.10 | Please provide GIS data in the form of shapefiles or geodatabases that support the following figures (if these have not already been provided). a. Figure 4-3: Frequently De-energized circuits, p. 22. | Please see the attached gdb titled, “SDGE_Frequently_De-energized_circuits.gdb.” | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE_Frequently_De-energized_circuits.gdb_.zip | 1 | No | Figure 4-3 | 4-3: Frequently De-energized Circuits . 22 | N/A | N/A
21 | MGRA | 3 | MGRA-3 | 11 | MGRA-3.11 | Is FPI historic geographic data available, if so is it available through a public interface and if not how difficult would it to be to produce? a. If SDG&E were asked to produce FPI estimates given a set of geographic points and date/time, how far back into history could SDG&E provide FPI data? | SDGE divides the service territory into 8 operational districts. The FPI is computed daily for each operational district using live fuel moisture values, dead fuel moisture values, grass NDVI values, dewpoint depression and sustained wind speed forecast. The output is not gridded, and each district receives an FPI value from 1-17. Historical values are archived in a spreadsheet and are not posted publicly. a. For operational FPI values, SDGE started keeping daily records of the data in April 2013 but there exists intermittent values as far back as late September 2012. Again, the FPI values are calculated per district and not for a set of otherwise specified geographic points. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | N/A | FPI historic geographic data | N/A | N/A
22 | OEIS | 3 | OEIS-3 | 1 | OEIS-3.1 | Regarding Contractor Employees with Minimum Qualifications On pages 229 through 231 of its 2026-2028 Base WMP, SDG&E lists the worker titles, qualifications, and training associated with its vegetation management workforce. SDG&E indicates that for several positions (Pre-Inspector, Tree Trim General Foreperson/Supervisor, and Tree Trimmer), the total number of employees with each position is greater than the number of minimally qualified employees. This suggests that some employees holding the Pre-Inspector, Tree Trim General Foreperson/Supervisor, or Tree Trimmer title do not possess minimum qualifications. a. Are there employees with each of the above worker titles who do not hold the minimum qualifications for their position? i. If yes, list other factors associated with each worker title that contribute to a hiring decision for an employee who does not possess minimum qualifications. ii. If no, explain why there is a difference between the number of employees with minimum qualifications and the total number of employees. | After further investigation with its contractors, SDG&E has determined that it erred in its initial reporting of the number of contracted employees who possess minimum qualifications compared to the total number of employees. SDG&E can confirm that all contracted employee positions including Pre-Inspector, Tree Trim General Foreperson/Supervisor, and Tree Trimmer possess the minimum qualifications. The error was related to the number of employees who possess specific certifications, which are not a requirement of employment. SDG&E will update the number of contracted employees in Revision 1 of the 2026-2028 WMP. | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 0 | No | 9.13 | 9.13 Workforce Planning (WMP.506) | N/A | N/A
23 | OEIS | 3 | OEIS-3 | 2 | OEIS-3.2 | Regarding Fire Potential Index for Action Initiation On page 252 of its 2026-2028 Base WMP SDG&E states that, “The FPI reflects key variables such as the state of native grasses across the service territory (‘green-up’), fuels (ratio of DFM component to LFM component), and weather (sustained wind speed and dew point depression). Each of these variables is assigned to a numeric value. Those numeric values are summed up to generate a Fire Potential Index value from 0 to 17 that expresses the degree of fire threat expected for each of the seven days in the forecast. The numeric values are grouped as ‘Normal’, ‘Elevated’, or ‘Extreme’.” a. Provide the following information regarding the Fire Potential Index (FPI) breakpoints and how each is used in the initiation of PSPS events. i. A detailed description of the weather conditions associated with each level of the FPI breakpoint (i.e., Normal, Elevated, and Extreme). ii. The initiation criteria for PSPS events for FPI breakpoint (i.e., Normal, Elevated, and Extreme). b. Provide the following information regarding the FPI breakpoints and how they are used for actions taken in the field. i. A detailed description of actions taken in the field that are associated with each FPI breakpoint (i.e., Normal, Elevated, and Extreme). | a.i. Please reference the attached document titled “SDGE Response OEIS-P-WMP_2025-SDGE-03_Q2_Fire Potential Index (FPI).pdf.” Weather conditions are a function of dewpoint depression and sustained wind speeds. Since each break point is a function of dead fuel moisture, live fuel moisture, grass NDVI, dewpoint depression and sustained wind speeds, no single value of wind or dewpoint depression defines each breakpoint - they are defined by the combination of all variables and are based on a backcast against historical fires as shown in the figures below. a.ii. The FPI is a consideration for PSPS but not the only one. The following outlines the procedure for initializing a PSPS from a Meteorology perspective: 1. Has the National Weather Service (NWS) provided any indication in their forecast discussion, forecast products or social media communications that a Red Flag Warning or critical fire weather conditions may be possible during the forecast period? 2.Has the GACC in Riverside, CA given any indication in their forecast discussion/products or social media communications of a “High Risk Day” or any Santa Ana Wildfire Threat Index rating may be issued? 3. Does the SDG&E Fire Potential Index show that a combination of fuel dryness and Santa Ana winds may lead to the potential for large wildfire (FPI 14 or above)? 4. Do initial wind speed forecasts generated by SDG&E meteorology models (WRF and AI forecasting) indicate a reasonable probability of reaching alert speeds for any of the SDG&E weather stations? 5. Do the forecasted weather conditions warrant a convening of executive leadership to discuss the potential for PSPS Protocols? b.i. SDG&E has several procedures that outline company responsibilities and action required for each breakpoint. Electric Distribution Operations (EDO) has procedures during SDG&E fire conditions that outline the distribution operating restrictions and notifications required for overhead facilities during various operating condition levels, to include operating under NORMAL conditions (1-11), ELEVATED Conditions (12-14), and EXTREME Conditions (15-17).Electric Grid Operations at SDG&E has fire preparedness and transmission restrictions that outline the transmission operating restrictions and notifications required for overhead facilities during various operating condition levels, to include operating under NORMAL conditions (1-11), ELEVATED Conditions (12-14) , and EXTREME Conditions (15-17). SDG&E operations and maintenance has a wildland fire prevention plan that outlines the minimum wildland fire prevention standards for all system Operations & Maintenance work conducted in wildland areas of our service territory. The plan provides a wildland fire risk and mitigation matrix based on work activity within Fire Potential Index (FPI) or Project Activity Level (PAL) areas to set a level for minimum fire prevention and suppression tools. The Fire Potential Index (FPI) (1-17) is a comprehensive assessment of fire risk, used as a tool for making operation & maintenance decisions related to fire prevention. The tool converts environmental, statistical, and scientific data into an easily understood forecast of short-term fire threat. The 7-day forecast is used for planning purposes, while the daily FPI is used for work activities. The FPI is used to determine the fire potential for each day (Normal, Elevated, or Extreme). | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_Q2_Fire%20Potential%20Index%20%28FPI%29.pdf | 1 | No | 10.6 | 10.6 Fire Potential Index (WMP.450) | 10.6.1 | 10.6.1 Existing Calculation Approach and Use
24 | OEIS | 3 | OEIS-3 | 3 | OEIS-3.3 | Regarding SDG&E’s Response to SDGE-25U-01 In Appendix D, pages 1-2, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-25U-01. Calculating Risk Scores Using Maximum Consequence Values. a. In its response, SDG&E states that “Moving forward, the new risk event probability distribution outputs, along with statistical distribution metrics such as mean and various percentiles, will be used to inform future optimal mitigation prioritization decisions.” i. When does SDG&E intend to start using the new outputs? ii. If the new outputs have been implemented already, provide a detailed description of how the new risk event probability distributions impacted SDG&E’s risk model scores. This must include, at a minimum: (1) A list showing any shifts to risk ranking prioritizations. (2) Heatmaps of risk distributions across SDG&E’s territory showing changes in risk scores. b. In its response, SDG&E states that “the wildfire risk modeling approach will continue to be updated” and that “assumptions and inputs used in the models will be continuously reviewed and enhanced.” i. What frequency does SDG&E plan on updating its risk models? ii. What frequency does SDG&E plan on reviewing and enhancing assumptions and inputs? iii. Provide SDG&E’s timeline including concrete milestones and associated dates for future risk modeling updates. | a. i. SDG&E has begun adopting risk event probability distribution outputs from its WiNGS-Planning model as of Q1 2025 and first reported on them in the 2026-2028 WMP base filing. ii. The new risk event probability distributions, derived from the WiNGS-Planning model, have been implemented in alignment with the Cost-Benefit Ratio (CBR) framework outlined in SDG&E’s forthcoming 2025 Risk Assessment and Mitigation Phase (RAMP) filing. This represents a significant methodological shift from the Risk Spend Efficiency (RSE) framework used in the 2021 RAMP filing—as required by the CPUC. Under the new framework, risk is quantified in monetary terms, replacing the Multi-Attribute Value Framework (MAVF) previously used. The updated model outputs include comprehensive statistical distribution metrics—such as mean, P95, P99, and maximum values—providing a probabilistic view of risk events. This contrasts with the earlier approach, which relied on a single deterministic risk score per asset. Key impacts of this upgrade include: - The probabilistic modeling approach offers greater transparency into the range and likelihood of potential risk events, rather than a single-point estimate. - The use of trained predictive models to estimate ignition events introduces a more data-driven and forward-looking risk assessment capability. - Technosylva simulation data used in the old model uses a 8 hour run simulation, whereas the new model uses a 24 hour run simulation Due to the change in risk units and modeling methodology, direct comparisons of risk scores between the old and new frameworks are not feasible. Instead, changes in risk rankings could provide a lens through which to assess the impact of the new model. However, comparing ranking outputs from the two models is further complicated due to differences in GIS data snapshots associated with the official model runs dates, which reflect changes in the electric infrastructure over time, such as installation of new sectionalizing devices, undergrounding of overhead lines, covered conductor of existing bare wires, thereby introducing variability unrelated to the modeling framework change itself. For a list of segment ranking comparisons, please see attached file titled “SDGE Response OEIS-P-WMP_2025-SDGE-03__Q3_rank_summary.xlsx.” (2) SDG&E does not currently have a comparison between risk scores generated under the previous MAVF methodology and those produced using the new Cost-Benefit framework. Developing a meaningful comparison would require substantial resources and the application of several assumptions. However, SDG&E could generate heatmaps illustrating shifts in risk rankings across feeder segments within its service territory, but it would take several weeks to complete. SDG&E can begin this work, once OEIS confirms that it would like SDG&E to spend weeks creating these heatmaps. b. i. SDG&E’s risk models are continuously in the process of development and review for potential enhancements and currently follow a minimum yearly cadence of release of new production versions. ii. SDG&E’s review and enhancement of assumptions and inputs for its risk models coincide with the release of each new production version. iii. SDG&E maintains a proactive and iterative approach to enhancing its risk modeling capabilities. As part of our commitment to continuous improvement, SDG&E reviews its risk models annually. This process includes a thorough evaluation of model performance, integration of new data, and consideration of feedback from both intervenors and the Office of Energy Infrastructure Safety (OEIS). SDG&E prioritizes and execute updates based on this feedback to ensure our models remain robust, transparent, and aligned with evolving risk landscapes. Looking ahead, SDG&E’s roadmap for future risk modeling enhancements is guided by the Risk Modeling Improvement Plan outlined in the 2026–2028 WMP, Section 5, OEIS Table 5-6: Utility Risk Assessment Improvement Plan, as well as any feedback collected in the Risk Modeling Working Groups where SDG&E is actively participating | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03__Q3_rank_summary.xlsx | 1 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
25 | OEIS | 3 | OEIS-3 | 4 | OEIS-3.4 | Regarding SDG&E’s Response to SDGE-23B-04 In Appendix D, pages 3-4, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-23B-04. Incorporation of Extreme Weather Scenarios into Planning Models. a. In SDG&E’s response, SDG&E states that its latest model methodology estimates “upper tail risk, which includes rare and extreme scenarios.” On page 51 of SDG&E’s 2026-2028 Base WMP, SDG&E states that it “does not currently analyze extreme events or highly uncertain scenarios” and that “the WiNGS-Planning model is designed to incorporate historical weather conditions experienced within the service territory.” i. Describe how “rare and extreme scenarios” differ from “extreme events or highly uncertain scenarios” in these two instances. b. On page 51 of SDG&E’s 2026-2028 Base WMP, SDG&E states that “the potential incorporation of climate change scenarios based on the latest climate modeling projection datasets that are being produced with the support from California Energy Commission are currently being evaluated.” i. Provide a timeline with concrete milestones and dates for SDG&E’s evaluation for integration of climate change scenarios. c. In SDG&E’s response, SDG&E states that the framework allows SDG&E to “generate statistical estimates of potential wind events over the maximum asset life of its system.” i. What estimates did SDG&E use for maximum asset life, given that the fire behavior scenarios used span the years 2013 to 2021? ii. Describe how SDG&E integrated and estimated the maximum asset life into risk modeling. | a) i. In the context of the reference on page 3 of Appendix D, SDGE-23B-04. Incorporation of Extreme Weather Scenarios into Planning Models, “rare and extreme scenarios” is referring to the upper tail risk interval of the probabilistic distribution that accounts for rare but catastrophic risk events. The full probabilistic distribution of risk events leveraging Technosylva’s outputs calculated under extreme fire weather days are currently accounted for in SDG&E’s risk modeling framework. The reference on page 51 of the 2026-2028 Base WMP, from Section 5.3.2 Extreme-Event/High Uncertainty Scenarios, is in the context of rare and extreme risk event hazards that are not accounted for in SDG&E’s current risk modeling, including black swan events such as acts of terrorism, multi-hazard scenarios such as ignitions from another source during a PSPS, extended drought, etc. b) i. SDG&E is exploring multiple methodologies to model future wildfire risk, with particular emphasis on projecting potential increases in acres burned relative to historical baseline. A key objective is to align these projections with the latest climate science, specifically the CMIP6 (Coupled Model Intercomparison Project Phase 6) simulation outputs, which will inform California’s upcoming Fifth Climate Change Assessment, scheduled for release in 2026. Currently, the most recent wildfire projection dataset available on Cal-Adapt is based on earlier CMIP5 simulations, specifically the work by Westerling (2018). However, this dataset is now considered outdated. In response, the UC Merced research team is actively working to update wildfire projections using CMIP6 data. These updated projections will aim to reflect a more accurate and forward-looking foundation for assessing wildfire risk under future climate scenarios and will be incorporated into the 2026 Assessment. Once the CMIP6-based wildfire projections are made available, SDG&E will review, validate, and incorporate the data into its risk modeling framework, pending approval by its internal subject matter experts (SMEs). c) i. A 5 million simulation run was performed leveraging Probability of Ignition (POI) model outputs and fire behavior scenarios from Technosylva’s WRRM model that include weather conditions observed from 2013 to 2021 to simulate annual wildfire risk event scenarios, effectively equating 5 million years being simulated. The maximum asset life is modeled for Combined Covered Conductor and Undergrounding with an assumed lifespan of 55 years in alignment with guidance from the with the Electric Undergrounding Program (EUP) risk modeling reporting requirements established by Energy Safety pursuant to Senate Bill 884. ii. Maximum asset life is utilized to estimate projected risk reduction benefits over the life of the asset as part of the calculation of Cost Benefit Ratio (CBR) metrics for each mitigation type, which account for annual inflation and various benefit discount rates scenarios over that lifetime. For further details on how CBR metrics are calculated, see Section 6.2.1.2 Risk Impact of Activities in SDG&E’s 2026-2028 WMP report. | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 0 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
26 | OEIS | 3 | OEIS-3 | 5 | OEIS-3.5 | Regarding SDG&E’s response to SDGE-25U-02 In Appendix D, pages 5-6, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-25U-02 Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety. In SDG&E’s response, SDG&E describes monthly meetings held focusing on WMP activities and topics. Provide the dates and topics associated with each meeting held. | Please see attached document titled, “SDGE Response OEIS-P-WMP_2025-SDGE-03_Q5.pdf.” | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 1 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
27 | OEIS | 3 | OEIS-3 | 6 | OEIS-3.6 | Regarding SDG&E’s response to SDGE-25U-03 In Appendix D, pages 7-29, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-25U-03. Third-Party Recommendations for Model Improvements. In Table 4-1: WiNGS-Planning Risk Model Updates, SDG&E provides a status of “Not Applicable” for the following recommendations: CHI Update and Mean Value Assessment. Explain why these recommendations are listed as “Not Applicable.” | In Table 4-1: WiNGS-Planning Risk Model Updates, SDG&E initially marked the CHI Update and Mean Value Assessment recommendations as “Not Applicable” incorrectly. These entries will be corrected to reflect their true status: - The CHI update has been completed and subsequently removed from the WiNGS-Planning model, as the integration of WiNGS-Ops into WiNGS-Planning now captures this information. - The Mean Value Assessment is currently underway, with completion anticipated before 2027. With the transition to a probabilistic risk assessment framework, SDG&E considers this requirement to be almost completed through the enhanced modeling approach. | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 0 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
28 | OEIS | 4 | OEIS-4 | 1 | OEIS-4.1 | Regarding reduction in 2025 targets/expenditure for Lightning Arrestor Removal/Replacement (WMP.550) and Avian Protection (WMP.972) In its Petition to Amend, SDG&E requests to reduce its 2025 targets for Lightning Arrestor Removal/Replacement (WMP.550) from 1,848 to 90 and for Avian Protection (WMP.972) from 200 to 95 poles.1 SDG&E revised its projected 2025 capital expenditure for Lightning Arrestor Removal/Replacement (WMP.550) from $3.483 million to $0, and for Avian Protection (WMP.972) from $1.512 million to $0.2 In its General Rate Case (GRC) decision, the California Public Utilities Commission (CPUC) adopted a capital forecast of $3.2 million for SDG&E’s lightning arrestor replacement and avian protection programs.3,4 The CPUC adopted forecast is $0.357 million lower than SDG&E’s proposal in the GRC application. a. Explain why its projected expenditure in its Petition to Amend for the Lightning Arrestor Removal/Replacement (WMP.550) and Avian Protection (WMP.972) initiatives are $0 even though the CPUC adopted a capital forecast of $3.2 million. b. Provide the unit cost of lightning arrestor removal and replacement in High Fire Threat district (HFTD) Tier 2 and Tier 3 and the number of lightning arrestors SDG&E plans to remove/replace in Tier 2 and Tier 3, respectively. i. If the total annual cost is higher than that adopted by the CPUC, provide justification for the higher unit cost. c. Explain why SDG&E’s 2025 Avian Protection (WMP.972) target is reduced even though the category is uncontested in the GRC decision. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
29 | OEIS | 4 | OEIS-4 | 2 | OEIS-4.2 | Regarding reduction in 2025 targets/expenditure for Detailed Vegetation Inspections (WMP.494) In its Petition to Amend, SDG&E seeks to reduce its 2025 Detailed Vegetation Inspections (WMP.494) target from 485,400 inspections to 255,000 inspections in the HFTD.5 Correspondingly, SDG&E requested to reduce its HFTD expenditure from $32.639 million to $30.854 million.6 For the category of Vegetation Management and Inspection – Tree Trimming only, the GRC decision authorized $26.612 million for the work in the HFTD, which is $0.62 million lower than SDG&E’s proposal ($27.232 million) due to lower unit ($97 in Tier 2 and Tier 3) cost adopted.7 CPUC also authorized $15.269 million in the non-HFTD for the 2024 test year, which is consistent with SDG&E’s proposal.8 For the category of Vegetation Management and Inspection, the GRC decision authorized $ 12.481 million, which is $3.552 million less than SDG&E’s request ($ 16.033 million, post-Update Testimony forecast).9 The GRC decision did not discuss the number of inspections for this category.10 a. Provide the number of inspections SDG&E planned in its GRC application that formed the basis for the $41.881 million CPUC authorization in both HFTD and non-HFTD.11 Include a reference (from its GRC filing, include the URL and page number) for the number of inspections. i. If the number of inspections SDG&E plans to conduct in its GRC application is not consistent with the target changes in the Petition to Amend, provide justification for the difference in the scope of work. b. Explain why inspections are only performed in the HFTD when there is an authorized non-HFTD forecast. c. Provide unit costs for Detailed Vegetation Inspections (WMP.494) in the HFTD and non- HFTD. i. If SDG&E’s unit cost calculates to a higher total cost than $26.612 million (HFTD) and $15.269 million (non-HFTD) authorized by the CPUC, provide justification for the higher unit costs. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
30 | OEIS | 4 | OEIS-4 | 3 | OEIS-4.3 | Regarding reduction in 2025 targets/expenditure for Pole Clearing (WMP.512) In its Petition to Amend, SDG&E seeks to reduce its 2025 Pole Clearing (WMP.512) target from 33,010 poles to 22,000 poles.12 SDG&E requests to reduce its operations expenditure for Pole Clearing (WMP.512) from $8.13 million to $6.427 million.13 The GRC decision adopts a 2024 forecast of $5.369 million for Pole Brushing/Clearing with the same number of poles SDG&E stated in its GRC application.14 CPUC’s authorization is $2.524 million less than SDG&E’s request ($7.893 million) in its GRC application.15 a. From its GRC application, provide the number of poles SDG&E planned to clear that formed the basis for the $7.893 million requested by SDG&E.16 Include a reference (from its GRC filing, include the URL and page number) for the number of poles. b. Provide the unit cost for Pole Clearing (WMP.512) in HFTD Tier 2 and Tier 3, and the number of poles SDG&E plans to brush in each tier. i. If the unit cost amounts to a total cost higher than the $5.369 million authorized by the CPUC, provide justification for the higher unit cost. c. Provide justification for reduced target request given that the GRC decision does not discuss the scope of pole brushing/clearing. The acceptance of Cal Advocate’s recommendation implicitly endorses workloads per year; the workloads forecast by SDGE and recommended by Cal Advocates are equal – it’s only the unit cost that differs.17 i. If the number of poles SDG&E plans to clear is not consistent with the number provided in its GRC application, provide justification for the difference in the scope of work. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
31 | OEIS | 4 | OEIS-4 | 4 | OEIS-4.4 | Regarding reduction in 2024 targets for Fuels Management (WMP.497) In its Petition to Amend, SDG&E seeks to reduce its 2024 Fuel Management (WMP.497) target from 500 poles to 150 poles.18 The GRC decision adopts a 2024 forecast of $5.246 million with the same number of structures SDG&E stated in its GRC application. CPUC’s authorization is $1.028 million less than SDG&E’s request ($6.274 million) in its GRC application. a. From SDG&E’s GRC application, provide the number of structures SDG&E planned to clear in 2024 that formed the basis for the $6.274 million forecast proposed by the SDG&E.19 SDG&E must include a reference to a GRC filing (including URL and page number) for the number of structures. b. Provide the unit cost for Fuels Management (WMP.497) in HFTD Tier 2 and Tier 3, , and the number of structures SDG&E cleared in each Tier from its GRC application. i. If the unit cost amounts to a total annual cost higher than the $5.246 million authorized by the CPUC, provide justification for the higher unit cost. c. Provide justification for reducing its 2024 target given that the GRC decision did not reduce the scope of the program. i. If the request to reduce its target to 150 poles for 2024 is not consistent with the number provided in the GRC application, provide justification to the difference in the scope of work. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
32 | OEIS | 4 | OEIS-4 | 5 | OEIS-4.5 | Regarding reduction in 2025 targets and expenditures for Distribution Vegetation Inspections (WMP.494) and Pole Clearing (WMP.512) a. Complete the table below by listing the proposed target in SDG&E’s Petition to Amend, unit costs, and total costs in 2021 dollars. i. If any of the expenditures in the “2025 Total Cost” column are different from the expenditures in the “GRC Authorized Cost” column explain why. Data Request OEIS-P-WMP_2025-SDGE-04 7 Initiative Location Unit 2025 Target in Petition to Amend 2025 Unit Cost (2021 $/unit) 2025 Total Cost (millions of 2021 $) GRC Authorized Cost (millions of 2021 $) Distribution Vegetation Inspections (WMP.494) Non-HFTD Inspections 15.269 Distribution Vegetation Inspections (WMP.494) HFTD Inspections 26.612 Pole Clearing (WMP.512) HFTD Poles 5.369 |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
33 | OEIS | 4 | OEIS-4 | 6 | OEIS-4.6 | Regarding reduction in 2024 targets and expenditure for Fuels Management (WMP.497) a. Complete the table below by listing the proposed target in SDG&E’s Petition to Amend, unit costs, and total costs in 2021 dollars. i. If any of the expenditures in the “2024 Total Cost” column are different from the expenditures in the “GRC Authorized Cost” column explain why. Initiative Location Unit 2024 Target in Petition to Amend 2024 Unit Cost (2021 $/unit) 2024 Total Cost (millions of 2021 $) GRC Authorized Cost (millions of 2021 $) Fuels Management (WMP.497) HFTD Poles 5.264 |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
34 | OEIS | 4 | OEIS-4 | 7 | OEIS-4.7 | Regarding reduction in 2025 target for Covered Conductor (WMP.455) In its Petition to Amend, SDG&E seeks to increase its 2025 target from 40 miles to 50 miles with the capital expenditure increased from $67.63 million to $81.43 million.20 SDG&E’s petition produces a unit cost of $1.623 million per mile. In the GRC decision, the CPUC adopted $71.9 million for 100 miles of covered conductor, for an average cost of less than $1 million per mile.21 Explain the $1.623 million unit cost for covered conductor. Present the historic unit cost data and itemize the key expenses included when estimating the unit cost for covered conductor. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
35 | OEIS | 4 | OEIS-4 | 8 | OEIS-4.8 | Regarding reduction in 2025 targets/expenditure for Strategic Pole Replacement Program (WMP.1189) In its Petition to Amend, SDG&E seeks to decrease its 2025 target from 291 poles to 200 poles while requesting to increase its capital expenditure from $6.948 million to $7.923 million. As provided in SDG&E’s response to Data Request OEIS-P-WMP_2025-SDGE-01,22 the Strategic Pole Replacement Program initiative (WMP.1189) is part of the High Risk Pole Replacement Program in the GRC decision, which is an uncontested category in the GRC decision.23 a. Provide an explanation for the reduced target and increased expenditure. b. Provide an explanation for increased unit cost for the initiative, given the increased expenditure and decrease in target. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
36 | OEIS | 4 | OEIS-4 | 9 | OEIS-4.9 | Regarding reduction in targets for uncontested initiatives and for initiatives that the GRC decision adopted SDG&E’s proposal In its Petition to Amend, SDG&E requested target changes for nine initiatives and accompanying expenditure reductions for initiatives that were not contested in the GRC.24 • 2024 target changes o Distribution Communications Reliability Improvements (WMP.549) o Distribution Infrared Inspections (WMP.481) o Standby Power Program (WMP.468)  The GRC decision adopted SDG&E’s proposal.25 • 2024 and 2025 target changes o Drone Assessments (WMP.552) • 2025 target changes o Strategic Pole Replacement Program (WMP.1189) o Transmission OH Hardening (WMP.543) o Distribution Communications Reliability Improvements (WMP.549) o Connectors, including hotline clamps (WMP.464) o Expulsion Fuse Replacement (WMP.459) Provide explanations for each of the target and expenditure reductions for the above initiatives. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
37 | OEIS | 4 | OEIS-4 | 10 | OEIS-4.10 | Regarding revenue requirement and capital expenditure In its Petition to Amend, SDG&E indicated that there is a “Revenue Requirement Shortfall” of $0.148 billion to complete the GRC-authorized capital expenditure (Capex).26 In addition, SDG&E stated the total “Actual/Forecasted Capex” is $1.045 billion while the total “Adjusted Capex Target” is $1.086 billion.27 The GRC decision stated that the CPUC adopted “…a base margin revenue (O&M and capital revenue requirement) increase of 3 percent each year for 2025, 2026, and 2027 plus certain wildfire mitigations, including undergrounding and covered conductor” which allows SDG&E to “fund incremental capital additions for wildfire mitigation programs that are important for infrastructure safety.”28 The GRC decision goes on to state that it provides “… both just and reasonable returns for the utilities and affordable rates for ratepayers.”29 a. Provide a reference from the GRC decision (include a URL and page number) for the in the “Authorized Capital Expenditures (Capex)” values SDG&E provides in its Petition to Amend.30 b. Provide explanations for the “Revenue Requirement Shortfall”. c. Provide high-level explanation on the calculation of “Adjusted Capex Target”. d. Provide explanations to the $41 million difference between the total “Actual/Forecasted Capex” and “Adjusted Capex.” 31 |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
38 | OEIS | 4 | OEIS-4 | 11 | OEIS-4.11 | Q11. Regarding memorandum accounts In the GRC decision, the CPUC decided not to modify the Wildfire Mitigation Plan Memorandum Account (WMPMA).32,33 The decision also converted the existing two-way Tree Trimming Balancing Account into a one-way Vegetation Management Balancing Account (WMBA) with an accompanying Vegetation Management Memorandum Account (VMMA) for spend above the VMBA authorization. Provide the table from pages 2 and 3 of the Petition to Amend listing the initiatives. For each, identify whether the initiative is eligible to be booked in the WMPMA, the VMBA, or the VMMA. |  | Zhenying Shao | 2025-05-15 | 2025-05-21 |  |  |  |  | N/A | SDGE 2025 Petition to Amend | N/A | N/A
39 | OEIS | 5 | OEIS-5 | 1 | OEIS-5.1 | Regarding Database(s) Used for Data Storage: On page 288 of its 2026-2028 Base WMP, SDG&E lists the different databases used for data storage among its various enterprise systems. SDG&E indicates several databases that are in use (Oracle, SAP Hana, Azure, AWS, Proprietary Databases, etc.). a. Provide an overview of any data governance plan that SDG&E has in place. b. Provide a description of SDG&E’s ability to migrate data across systems, such as between third-party software and internal proprietary databases, if any. i. If migration of data across systems is not possible, what internal plan does SDG&E have to ensure complete data migration in the future? | a. The Enterprise Data Governance Office provides strategies to promote clean, organized, and easily accessible data. Data governance processes and controls are documented for the enterprise systems leveraged in the WMP Data Platform. The Enterprise Data Catalog is comprised of two main components, SAP Hana and AWS. Collibra, DataZone, and Glue, are used for creating data asset inventories, data stewardship, metadata capture, and governance. The WMP Data Platform provides a centralized data repository that enables consistent, reliable, and automated reporting of mandated OEIS reporting requirements, along with other data consumption needs. Data is ingested into the Data Foundation from multiple Data Sources including asset systems, asset management systems, outage systems, vegetation management systems, and other internal and external systems, enabling one source of truth for the WMP Data Platform. Data Consumption includes regulatory reporting, internal reporting, efficacy studies, and advanced analytics. The Data Governance program ensures WMP data is governed by management oversight, policies and procedures, education, and tool standards. An overview of the WMP Data Platform is in Figure 1 shown below. b. SDG&E has successfully centralized its data from Oracle to SAP HANA. The data is organized using HANA Views, making it easily accessible. SAP HANA is utilized for producing SDG&E’s Quarterly Data Reports and for responding to data requests, demonstrating the system's efficiency and reliability. In addition, we have plans for cloud migration as shown by the annual goals below. This initiative is focused on creating high-quality, reusable solutions that support better, faster decision-making across the board. 2026 Goals: • Establish data migration patterns. • Successfully migrate data sets, including grid hardening, assets, and PSPS/risk events. • Implement data validation, integrity, and governance processes. 2027 Goals: • Execute data integration from the upgraded SAP S/4 HANA platform for ERP, transitioning from the legacy SAP ECC system. • Implement data ingestion processes for the new Transmission SAP S/4 HANA system. • Maintain enterprise data quality standards. 2028 Goals: • Integrate and ingest critical data from all newly implemented systems across the organization. • Establish data pipelines, security protocols, and ETL processes. • Prioritize data quality and system compatibility while maintaining compliance standards. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDG%26E%20Efficacy%20Studies%20Documentation.pdf | 1 | No | 12.2 | 12.2 Summary of Enterprise Systems . | N/A | N/A
40 | OEIS | 5 | OEIS-5 | 2 | OEIS-5.2 | Regarding SDG&E’s response to SDG&E-25U-08: In response to SDGE-25U-08, SDG&E lists findings resulting from its 2024 IR inspections in Table 9-1. In 2024, thermography findings were created on the structures listed in the table below. a. For each structure, indicate in the adjacent columns if the structure was observed by continuous monitoring technology as of April 1, 2024. For each structure that was monitored by any continuous monitoring technology (ARFS, PQ, or other) as of April 1, 2024, indicate whether any inspections were triggered as a result of the continuous monitoring technology, provide the type of inspection that was performed, and provide the date the inspection was performed. Structure ID Monitored By Advanced Radio Frequency Sensors (ARFS) April 1, 2024 (yes/no) Monitored By Power Quality (PQ) Sensors April 1, 2024 (yes/no) Monitored By Other Condition Monitoring Device/Technology as of April 1, 2024 (specify device or technology name) Inspection(s) Triggered By Continuous Monitoring Technology (yes/no) Triggered Inspection Date(s) P192125 P737707 P192259 P479712 P192287 P570385 P11850 P192306 P474064 P201281 P279981 P379031 Z245659 Z731331 P227944 Z118778 Z473088 Z229374 P839538 P734600 P933220 P2135672414 P313295 P2157171985 P174771 | Structure ID Monitored By Advanced Radio Frequency Sensors (ARFS) April 1, 2024 (yes/no) Monitored By Power Quality (PQ) Sensors April 1, 2024 (yes/no) Monitored By Other Condition Monitoring Device/Technology as of April 1, 2024 (specify device or technology name) Inspection(s) Triggered By Continuous Monitoring Technology (yes/no) Triggered Inspection Date(s) P192125 No Yes* No No N/A P737707 No Yes* No No N/A P192259 No Yes* No No N/A P479712 No Yes* No No N/A P192287 No Yes* No No N/A P570385 No Yes* No No N/A Structure ID Monitored By Advanced Radio Frequency Sensors (ARFS) April 1, 2024 (yes/no) Monitored By Power Quality (PQ) Sensors April 1, 2024 (yes/no) Monitored By Other Condition Monitoring Device/Technology as of April 1, 2024 (specify device or technology name) Inspection(s) Triggered By Continuous Monitoring Technology (yes/no) Triggered Inspection Date(s) P11850 No Yes* No No N/A P192306 No No No N/A N/A P474064 No Yes* No No N/A P201281 No Yes* No No N/A P279981 No Yes* No No N/A P379031 No Yes* No No N/A Z245659 No Yes* No No N/A Z731331 No Yes No No N/A P227944 No Yes No No N/A Z118778 No Yes* No No N/A Z473088 No Yes* No No N/A Z229374 No Yes* No No N/A P839538 No Yes* No No N/A P734600 No Yes* No No N/A P933220 No No No N/A N/A P2135672414 No Yes No No N/A P313295 No Yes* No No N/A P2157171985 No Yes* No No N/A P174771 No Yes* No No N/A * Monitor is at the substation bank or bus level and does not distinguish between circuits | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | SDG&E findings resulting from its 2024 IR inspections in Table 9-1 | N/A | N/A
41 | OEIS | 5 | OEIS-5 | 3 | OEIS-5.3 | Regarding Continuous Monitoring Technology Deployment: a. Provide the total number of structures in SDG&E’s HFTD/HFRA. b. Provide the number of structures in SDG&E’s HFTD/HRA continuously monitored by both PQ sensors and ARFS as of Jan 1, 2025. c. Provide the number of structures in SDG&E’s HFTD/HFRA continuously monitored by PQ sensors but not ARFS as of Jan 1, 2025. d. Provide the number of structures in SDG&E’s HFTD/HFRA continuously monitored by ARFS but not PQ sensors as of Jan 1, 2025. e. List any other continuous monitoring sensors or technologies deployed by SDG&E that have been used or are planned for use to inform grid inspections and/or corrective grid work. | a. 85,639 distribution structures in the HFTD b. 6,932 distribution structures in the HFTD monitored by both PQ and ARFS c. 59,445 distribution structures in the HFTD monitored by PQ but not ARFS d. 7,649 distribution structures in the HFTD monitored by ARFS but not PQ e. The EFD Program aims to utilize the PQ and ARFS monitoring technologies to detect and prevent significant equipment failures in order to address fire risk while also gaining the benefits of reducing customer forced outages. Sensors that are a part of this program have the potential to be used to inform grid inspections and/or corrective grid work. To accomplish this SDG&E is looking at the process changes needed to integrate the two processes that are currently separate. At this time the integration is still in its early stages. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | Continuous Monitoring Technology Deployment | N/A | N/A
42 | OEIS | 5 | OEIS-5 | 4 | OEIS-5.4 | Regarding Inspections Trigged by Continuous Monitoring Technology: a. Describe the process for initiating an inspection due to ARFS data. Include how assets are flagged for potential inspection, confirmed for inspection, the type of inspection is determined (i.e. patrol, infrared, detailed), and the inspection due date is determined. i. Provide supporting documentation including written processes, guidance, and/or job aids related to initiating and performing inspections as a result of ARFS data. b. Describe the process for initiating an inspection due to PQ sensor data. Include how assets are flagged for potential inspection, confirmed for inspection, the type of inspection is determined (i.e. patrol, infrared, detailed), and the inspection due date is determined. i. Provide supporting documentation including written processes, guidance, and/or job aids related to initiating and performing inspections as a result of PQ sensor data. c. Provide the total number of inspections initiated in 2024 as a result of ARFS data. i. Provide the number of such inspections that resulted in level 1 findings. ii. Provide the number of such inspections that resulted in level 2 findings. d. Provide the total number of inspections initiated in 2024 as a result of PQ sensor data. i. Provide the number of such inspections that resulted in level 1 findings. ii. Provide the number of such inspections that resulted in level 2 findings. | a. SDG&E receives a bi-monthly report from the manufacturer of ARFS equipment containing locations of interest with data showing RF energy dispersion signal groupings. After analyzing that data, SDG&E will issue a patrol for any locations with a concerning amount of disturbance energy. The patrol is performed by SDG&E’s drone pilots, who capture high-resolution images from all angles of the location in question. Additionally, the drone pilot may capture infrared images of the location in question. Images are reviewed, then the asset is field verified by an engineer and a qualified electrical worker to determine severity and remediation work needed. Drone inspections are typically completed within two weeks of issuance, depending on resource availability. Currently there is no formal documentation of this process as this is still in the R&D space and SDG&E is continually improving and altering the process. b. SDG&E received a weekly report of all new precursor events captured by PQ sensors. This data is then reviewed by engineers to determine severity and if a known location can be identified. For overhead-related assets, the same process described in item 4a is followed. For underground-related assets, the engineer will issue an underground patrol request to be completed by a qualified electrical worker. Underground patrols involve a visual inspection as well as an infrared camera to locate hot connections. Depending on findings, remediation work is determined by the field personnel. Underground patrols are requested to be completed within three days. Currently there is no formal documentation of this process as this is still in the R&D space and SDG&E is continually improving and altering the process. c. 40 inspections initiated in 2024 as a result of ARFS data i. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 1 findings. ii. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 2 findings. d. 20 inspections initiated in 2024 as a result of PQ data i. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 1 findings. ii. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 2 findings. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | Inspections Trigged by Continuous Monitoring Technology: | N/A | N/A
43 | OEIS | 5 | OEIS-5 | 5 | OEIS-5.5 | Regarding Transmission Inspection QA/QC a. Provide a copy of SDG&E document TCM 807, Section 5.2: Condition Assessment, Version 8G. | See attached document titled “TCM807 Version 8G Section 5.2-Condition Assessment.pdf.” | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/TCM807%20Version%208G%20Section%205.2-Condition%20Assessment.pdf | 1 | No |  | #N/A |  | #N/A
44 | OEIS | 5 | OEIS-5 | 6 | OEIS-5.6 | Regarding Weather Station Maintenance and Calibration In section 10.5.5 of the Wildfire Mitigation Plan Guidelines on page 136, the utility companies must provide an “acceptable percentage of weather station outages as defined by the electric corporation.” Page 252 of the 2026-2028 Base SDG&E WMP Submission states, “although SDG&E does not have a set acceptable outage percentage, the stations have consistently maintained a 99 percent communication rate.” a. Provide an acceptable percentage of weather station outages in which SDG&E will still be able to operate without an increase in risk or impact to the PSPS decision making as outlined in the Wildfire Mitigation Plan Guidelines. i. If SDG&E cannot provide what percentage of weather station outages is defined as acceptable, provide an explanation why it cannot. | SDGE weather stations have consistently maintained a 99 percent communication rate. SDG&E does not have a set acceptable outage percentage because it is nearly impossible to ascertain an acceptable percentage. All weather stations operate independently of distribution circuits and are powered by batteries that are recharged by solar panels. Each high-risk circuit has a weather station associated with that circuit. However, some circuits are very long and have multiple weather stations associated with that circuit. Additionally, not all areas of the HFTD are affected the same way during Santa Ana wind events. Thus, picking weather stations that are inconsequential because other circuit associated stations that could be used as a proxy is event and weather dependent and cannot be answered in a holistic manner. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 10.5 | 10.5 Weather Forecasting | 10.5 | 10.5 Weather Forecasting
45 | OEIS | 5 | OEIS-5 | 7 | OEIS-5.7 | Regarding Vegetation Inspections and Pole Clearing Targets: Page 104 of the Wildfire Mitigation Plan Guidelines states “Targets for inspection activities (programs) of overhead electrical assets must use circuit miles as the unit.” a. Provide all quarterly and year-end targets from Table 9-2 for the following programs in circuit miles: i. Detailed Inspection (WMP.494) ii. Off-Cycle Patrol (WMP.508) | Targets by circuit mile are provided below. Historically, Detailed Inspections have been reported by inspections complete, and Off-Cycle Patrol by Vegetation Management Area (VMA) complete. While able to pivot and report by circuit line mile, this unit of measure provides a less granular understanding of the work completed. SDG&E will comply with updating to the new unit requirement in the 2026-2028 WMP and associated QDR data tables when OEIS allows a mechanism to do so. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | Vegetation Inspections and Pole Clearing Targets | N/A | N/A
46 | OEIS | 5 | OEIS-5 | 8 | OEIS-5.8 | Regarding Vegetation Management QA/QC Pass Rate Targets: On page 224 of its 2026-2028 Base WMP, SDG&E targets a 90% pass rate for its “Quality assurance/quality control of Vegetation Management” (WMP.505) initiative. On page 290 of its 2023-2025 Base WMP, SDG&E targets a pass rate of 95% for all three of its QA/QC audits. SDG&E states that in 2022 it achieved a pass rate of 94% for pre-inspection, 99% for tree trimming, and 97% for pole clearing activities. a. Explain why SDG&E has lowered its pass rate target for QA/QC in its 2026-2028 Base WMP. b. Describe any obstacles to SDG&E increasing the QA/QC pass rate target each year from 2026-2028 (e.g., need for additional training, longer time to complete vegetation management work, human error, etc.). | a. After further review of historical QA/QC findings and pass rates, SDG&E determined that a 90% pass rate is a reasonable and representative target and threshold for work quality performance of the vegetation management contractors. b. SDG&E anticipates no obstacles to potentially increasing its QA/QC pass rate target in the future. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 9.11 | 9.11 Quality Assurance and Quality Control of Vegetation Management (WMP.505) | 9.11.1 | 9.11.1 Overview, Objectives, and Targets
47 | OEIS | 5 | OEIS-5 | 9 | OEIS-5.9 | Regarding the Granularity of Priority Levels in Past Due Vegetation Management Work Orders: On page 228 of its 2026-2028 Base WMP, SDG&E categorizes past due work orders by “Low Priority” and “High Priority.” On page 227 of its 2026-2028 WMP, SDG&E sets work completion timelines for routine pruning and removal of “60 to 120 days following inspections,” and “Memo” work order timelines of “the same day the condition is observed, the next day, or within 30 days.” a. Complete the table below, in the format of Table 9-8, to disaggregate low and high priority past due pruning and removal work into the following priority levels: 60-120 days, within 30 days, next day, same day. Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels Priority Level 0-30 Days 31-90 Days 91-180 Days 181+ Days 60-120 Days Within 30 Days Next Day Same Day | Priority Level 0-30 Days 31-90 Days 91-180 Days 181+ Days 60-120 Days 335 242 4 1 Within 30 Days 40 12 2 0 Next Day 0 0 0 0 Same Day 0 0 0 0 | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 9.12 | 9.12 Work Orders | 9.12.3 | 9.12.3 Trends .
48 | OEIS | 5 | OEIS-5 | 10 | OEIS-5.10 | Regarding SDG&E’s Pole Clearing Program: On page 213 of its 2026-2028 Base WMP, SDG&E states, "The determination to stop clearing poles with exempt equipment was made due to the evaluation of cost efficiencies,environmental impacts, impacts to customers, and the general absence of ignition data associated with exempt equipment." a. Did SDG&E consult with other electrical corporations before deciding to stop clearing vegetation around poles with Public Resource Code (PRC) 4292 exempt equipment? i. List all electrical corporations that SDG&E consulted in making this decision. ii. Provide summaries of any discussions with these electrical corporations that informed SDG&E’s evaluation and decision-making process. iii. Did SDG&E request ignition data associate with PRC 4292 exempt equipment from other electrical corporations? 1. If ignition data was requested, provide a summary of the ignition data received from each electrical corporation SDG&E consulted. iv. If SDG&E did not consult with other electrical corporations, explain why. b. Provide the ignition data that was used to support SDG&E's claim that there is a general absence of ignition data associated with PRC 4292 exempt equipment. i. What time period did the ignition data cover? ii. How many ignitions, if any, were identified as being associated with PRC 4292 exempt equipment? c. Were customer opinions solicited or considered when evaluating the customer impacts of clearing vegetation around poles with PRC 4292 exempt equipment? i. If so, provide a summary of the customer feedback received regarding this activity. ii. If customer input was not solicited, explain the basis of SDG&E’s determination that clearing vegetation around PRC 4292 exempt equipment has customer impacts. d. Were environmental experts or formal assessments used in evaluating the environmental impacts of clearing vegetation around poles with PRC 4292 exempt equipment? i. If so, provide a summary of the findings from those environmental assessments regarding this activity. ii. If environmental experts or assessments were not used, explain SDG&E’s decision-making process for determining that clearing around PRC 4292 exempt poles has environmental impacts. | a. SDG&E did not directly consult with other electrical corporations before deciding to stop clearing vegetation around poles with exempt PRC 4292 equipment. i. NA ii. NA iii. NA 1. NA iv. SDG&E did not consult with other electrical corporations on this decision based on the differences in the geography, topography and vegetation types between the service territories, and the internal considerations specific to SDG&E (e.g., cost efficiencies, no known prior ignitions associated with exempt hardware, additional environmental review). A primary driver for SDG&E stopping the clearing of vegetation around poles is based on Cal Fire’s classification of the equipment as exempt which was determined through field testing. b. As required by the CPUC, utilities must report ignitions involving their equipment that meet the criteria per D.14-02-015. Please see https://www.cpuc.ca.gov/industries-and-topics/wildfires for the ignition data related to SDG&E. i. The time-period the data ignition covers is 2014-2024. ii. There were no ignitions that were directly associated with PRC 4292 exempt equipment. c. Customers were not separately and specifically solicited when SDG&E evaluated the impacts of clearing vegetation around poles with PRC 4292 exempt equipment. However, customer impacts are derived through historical, anecdotal interactions with Vegetation Management, and are described further below in response to Question ii. i. NA ii. Customers can be impacted by vegetation clearing for PRC 4292 in multiple ways. 1) Customers often must provide physical access to a property for the contractor to perform pole clearing; 2) Pole clearing often requires two or more visits annually to a property for mechanical, herbicide, and/or re-clear activities; 3) Post-clearing audit activities may necessitate additional property visits by the contractor; 4) Pole clearing requires removal of vegetation down to bare mineral soil within a 10 foot radius, and the removal of tree branches within the radius up to the height of the conductors. Ground clearing could promote soil erosion at the base of the pole and would require the removal of healthy landscaping maintained by the customer. These impacts are a necessary result of pole clearing where required by law, however, they can be seen as an unnecessary burden to customers where it’s not required by law. d. Yes. All poles that receive pole brushing for PRC 4292 are annually screened for environmental and cultural review. i. Please see attached document titled, “OEIS-2025-05_Q10(d)(i)_Redacted.pdf”. SDG&E is providing an example of an annual environmental release for poles that are scheduled for pole brushing. SDG&E is providing a redacted version that contains personal names and phone numbers that are not directly relevant to the question. ii. N/A | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2025-05_Q10%28d%29%28i%29_Redacted.pdf | 1 | No | 9.4 | 9.4 Pole Clearing (WMP.512) | 9.4.4 | 9.4.4 Updates .
49 | OEIS | 5 | OEIS-5 | 11 | OEIS-5.11 | Regarding SDG&E’s Pole Clearing Target (WMP.512): On page 208 of its 2026-2028 Base WMP, SDG&E sets annual targets in 2026, 2027, and 2028 of 22,000 poles. On page 257 of its 2023-2025 Base WMP, SDG&E set annual targets for 2023, 2024, and 2025 of 33,010 poles. The delta between SDG&E’s targets in the 2026-2028 Base WMP and SDG&E’s 2023-2025 Base WMP is 11,010 poles. On page 211 of its 2026-2028 Base WMP, SDG&E states that “Since the 2023-2025 Base WMP, SDG&E has ceased performing pole clearing on poles with exempt equipment, such as hotline clamps (HLC).” a. Of the 11,010 poles that SDG&E no longer plans to clear, provide the number of those poles that hold exempt equipment and do not hold any non-exempt equipment. b. If some of the 11,010 poles that SDG&E no longer plans to clear hold non-exempt equipment, describe the other operational decisions that led to SDG&E’s plan to no longer clear these poles. c. Provide details of any risk reduction measures that will compensate for the reduced volume of pole clearing work. | a. All 11,010 of the poles SDG&E no longer plans to clear hold exempt equipment. b. N/A. See response to a. above. c. The risk reduction measures that compensate for the reduced volume of pole clearing work include locations where non-exempt hardware is replaced by exempt hardware. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 9.1 | 9.1 Targets. | 9.1.2 | 9.1.2 Quantitative Targets .
50 | OEIS | 5 | OEIS-5 | 12 | OEIS-5.12 | Regarding SDG&E’s Early Fault Detection Third Party Evaluation: In its response to the Early Fault Detection Implementation (SDGE-25U-05) ACI on page 32 of Appendix D in SDG&E's 2026-2028 WMP, SDG&E stated: "A third party was engaged to evaluate its effectiveness, and based on their analysis, several changes were implemented to accommodate system tracing and ensure the accurate coverage of the installed devices." a. Provide a copy of this third-party evaluation and analysis. b. Provide a summary of the types of issues missed that resulted in the ten false negatives. | A. See attached PDF document titled “EFD Study Document.pdf” for the early fault detection third-party evaluation and analysis. b. SDGE found the below 10 false negative with EFD devices. Issue# Outage ID Circuit Cause 1 220223E253449 211 Wire slap/pole down/wire down (severe weather) 2 230601E286128 350 Pole - contact/damage/broke/rotted/on fire 3 230316E280845 445 Arrester failure 4 230113E276229 448 Crossarm failure/contact 5 230111E276108 448 Hardware failure 6 230731E290189 448 Transformer (station) failure/contact 7 230607E286603 524 OH connector failure (jumper/splice/squeeze-on) 8 240613E313709 211 Pole - contact/damage/broke/rotted/on fire 9 240319E307337 350 Transformer (station) failure/contact 10 240109E301776 217 Cutout failure | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/EFD%20Study%20Document.pdf | 1 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
51 | OEIS | 5 | OEIS-5 | 13 | OEIS-5.13 | Regarding SDG&E’s Risk Reduction in OEIS Table 8-1: Energy Safety’s understanding of the expected risk reduction for the activities is Section 8 Grid Design & System Hardening and Grid Operations reported in OEIS Table 8-1 of SDG&E's 2026-2028 WMP is currently calculated at a segment/circuit level in which work is being completed. However, the expected risk reduction to be reported in Table 8-1 should reflect the reduction in SDG&E's overall wildfire and PSPS risk – in other words, the impact of each activity on the enterprise-wide risk. a. Is the expected risk reduction for activities reported in OEIS Table 8-1 calculated at a segment/circuit level in which work is being completed? If not, explain how SDG&E calculated the expected risk reduction values in Table 8-1. b. Provide the updated risk reduction percentages for each activity reported in OEIS Table 8-1 for the years 2026, 2027, and 2028, calculated at the overall enterprise level. c. Provide the updated expected risk reduction percentages for each activity reported in OEIS Table 6-3 using the same update to the calculation as Table 8-1 in part (b). | a) The expected risk reduction for activities reported in OEIS Table 8-1 are calculated at a segment level on which activity is going to be completed in the WMP years 2026-2028. b) Please refer to the attached spreadsheet titled “2026_OEIS Guideline Tables.xlsx” for updated table 8-1 risk reduction. c) Please refer to the attached spreadsheet titled “2026_OEIS Guideline Tables.xlsx” for updated table 6-3 risk reduction. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/2026_OEIS%20Guideline%20Tables.xlsx | 1 | No | OEIS Table 8-1 | 8-1: Grid Design, Operations, and Maintenance Targets by Year 126 | N/A | N/A
52 | OEIS | 5 | OEIS-5 | 14 | OEIS-5.14 | Regarding OEIS Table 6-4: a. Provide an updated version of OEIS Table 6-4 (SDG&E’s 2026-2028 Base WMP, p. 116; and Appendix F, pp. 58-73) via Excel with the following additional columns for each circuit/circuit segment: i. Total Circuit Mileage Undergrounded as of EOY 2025 ii. Total Circuit Mileage of Covered Conductor as of EOY 2025 iii. Total Circuit Mileage Planned for Undergrounding (for 2026, 2027, and 2028, respectively) iv. Total Circuit Mileage Planned for Covered Conductor (for 2026, 2027, and 2028, respectively) | Please refer to the attached spreadsheet titled “2026_OEIS Guideline Table 6-4.xlsx” for the updated OEIS 6-4 Table with the additional requested columns included. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/2026_OEIS%20Guideline%20Table%206-4.xlsx | 1 | No | OEIS Table 6-4 | 6-4: Summary of Risk Reduction for Top-Risk Circuits .. 116 | N/A | N/A
53 | OEIS | 5 | OEIS-5 | 15 | OEIS-5.15 | Regarding OEIS Table 6-1: a. Provide the total overall utility risk value used to calculate the percentage of overall utility risk percentages shown in OEIS Table 6-1 (SDG&E’s 2026-2028 Base WMP, p. 84 Appendix F, pp. 12-55) b. Provide an updated version of OEIS Table 6-1 via Excel with the following additional columns for each circuit/circuit segment: i. Safety Risk Score Component of Wildfire Risk Score ii. Reliability Risk Score Component of Wildfire Risk Score iii. Financial Risk Score Component of Wildfire Risk Score iv. PSPS Risk Score v. PEDS Risk Score | a) The percentage of overall utility risk is calculated from the total overall utility risk across the full territory, which includes circuit-segments that do not have overhead in the HFTD territory. These were not included in the OEIS 6-1 Table, since SDG&E’s risk prioritization is focused primarily in the HFTD territory. The total overall utility risk value calculated from the full list of circuit-segments in the territory is $3,032,480,966. b) Please refer to the attached spreadsheet titled “2026_OEIS Guideline Table 6-1.xlsx” for the updated OEIS 6-1 Table with the additional requested columns included. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/2026_OEIS%20Guideline%20Table%206-1.xlsx | 1 | No | OEIS Table 6-1 | 6-1: List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk 84 | N/A | N/A
54 | OEIS | 5 | OEIS-5 | 16 | OEIS-5.16 | Regarding OEIS Table 6-3: a. Provide a detailed explanation of the analysis used to calculate the activity effectiveness for each activity in OEIS Table 6-3 (SDG&E’s 2026-2028 Base WMP, pp. 111-112). Include copies of any relevant workpapers and supporting documentation used for this analysis. b. Provide a detailed explanation of the analysis used to calculate expected % risk reduction for each activity in OEIS Table 6-3. Include copies of any relevant workpapers (i.e. the “CCC Risk & Cost Benefit” Excel sheet) and supporting documentation used for this analysis. | a) Please see attached PDF titled “SDG&E Efficacy Study Documentation.pdf” for effectiveness calculation explanation. b) Please refer to Appendix G of WMP 2026-2028 for detail % risk reduction calculation, which is available on SDG&E’s 2026-2028 WMP website at: https://www.sdge.com/2026-2028-wildfire-mitigation-plan. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | OEIS Table 6-3 | 6-3: Risk Impact of Activities .. 111 | N/A | N/A
55 | OEIS | 5 | OEIS-5 | 17 | OEIS-5.17 | Regarding SDG&E’s Mitigation Initiative Prioritization On page 100 of SDG&E’s 2026-2028 Base WMP, in Figure 6-2, SDG&E depicts a flowchart showing its high-level mitigation prioritization. a. As part of the “develop draft hardening scope” portion, SDG&E includes a bullet point to “Optimize survey.” Describe what is included in this step of prioritization and provide any supporting documentation and procedures outlining this step. b. SDG&E includes a step to “prioritize Wildfire Risk reduction benefit” as part of developing its draft hardening scope. Describe what factors and thresholds are used as part SDG&E’s measuring and determining reduction benefit and provide any supporting documentation and procedures. c. SDG&E includes a step to determine whether “hardening scoping plan ready for release.” Describe what instances would lead to a “no” at this step and therefore run through development of a draft hardening scope and review again. | See updated Figure 6-2: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk as submitted in the WMP substantive and non-substantive errata, which is available on the OEIS docket as well as SDG&E’s website at https://www.sdge.com/2026-2028-wildfire-mitigation-plan. a. “Optimize survey” was removed from the figure as it is not a primary consideration in this step of prioritization. Rather, SDG&E evaluates the advantages of “bundling” the hardening of upstream feeder segments to optimize PSPS risk reduction and leverage economies of scale by reducing permitting and mobilization costs b. “Prioritize Wildfire Risk reduction benefit” was modified to be “Analyze Wildfire, PSPS, and PEDS risk reduction benefit.” The primary drivers for selecting a circuit-segment mitigation project are wildfire risk (a direct output from WiNGS-Planning) and the PSPS de-energization history and risk of the circuit. The PSPS review considers both upstream and downstream topography, wind speeds, and recommended mitigations to optimize the overall mitigation plan for the circuit. The WiNGS-Planning model is used to calculate wildfire, PSPS, and PEDS risk used in the aggregated overall wildfire and overall outage program risk components. The model estimates the baseline risk and quantifies the expected risk reduction for both Combined Covered Conductor and Strategic Undergrounding for each feeder segment. For more details around prioritization analysis and ranking of circuit-segments, see Section 6.1.2 Risk-Informed Prioritization. c. Subject matter expertise review may identify projects or components of projects that are infeasible. For example, covered conductor installation is not permitted above certain elevations due to the negative impacts of ice loading. Another example may include property ownership, land access, or environmental constraints that require significant revisions to the routing of a proposed SUG project. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 6.1.3.2.5 | Activity Prioritization | 6.1.3.2.6 | Mitigation Initiative Prioritization to Reduce Wildfire and PSPS Risk
56 | OEIS | 6 | OEIS-6 | 1 | OEIS-6.1 | Regarding Injuries/Fatalities Conversion: Page 53 of SDG&E's 2026-2028 Base WMP, “OEIS Table 5-4: Summary of Risk Models,” notes that SDG&E uses “number of acres burned conversion factors to estimate the number of serious injuries and fatalities from customers impacted.” However, page 38 of SDG&E’s 2026-2028 Base WMP, “SDGE Table 5-4: Attributes for Wildfire Consequence,” notes that SDG&E uses a fatalities per structure destroyed factor. a. Clarify if the injuries/fatalities conversion is based on acres burned (per OEIS Table 5-4) or structures destroyed (per SDGE Table 5-4). Explain the differences between the factors in each table. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.4 | 5.4 Summary of Risk Models . | N/A | N/A
57 | OEIS | 6 | OEIS-6 | 2 | OEIS-6.2 | Regarding Monte Carlo Simulations: On page 46 of SDG&E's 2026-2028 Base WMP, SDG&E notes that Monte Carlo simulations are used to assess risk outcomes on the grid. On page 3 of “Appendix D: Areas for Continued Improvement,” SDG&E describes the intent of the Monte Carlo simulations, but methods are not provided in “Appendix B: Supporting Documentation for Risk Methodology and Assessment.” a. Provide a detailed description of the methodology and framework for Monte Carlo simulations used within SDG&E’s risk modeling. Include any documentation, procedures, and policies which describe the methods. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.3 | 5.3 Risk Scenarios . | N/A | N/A
58 | OEIS | 6 | OEIS-6 | 3 | OEIS-6.3 | Regarding WiNGS-Ops Consequence Risk Metrics: On page 47 of SDG&E's 2026-2028 Base WMP, SDG&E notes that the WiNGS-Ops visualization platform displays the worst-case estimates of acres burned. a. Is the only consequence risk metric for WiNGS-Ops acres burned? i. If yes, discuss why other consequence risk metrics are not used. ii. If not, provide a list of other consequence risk metrics used. b. Provide a detailed description of how the safety, reliability, and financial attributes for consequence are displayed and analyzed for operations. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.3 | 5.3 Risk Scenarios . | N/A | N/A
59 | OEIS | 6 | OEIS-6 | 4 | OEIS-6.4 | Regarding Technical Documentation for Risk Models: a. On page 49 of SDG&E's 2026-2028 Base WMP, SDG&E mentions the “statistical and machine learning models detailed in Appendix B,” but Appendix B lacks documentation on these models. Provide technical documentation for the statistical and machine learning models used for Wings-Planning and Wings-Ops models. b. On page 61 and 62 of SDG&E's 2026-2028 Base WMP, SDG&E mentions usage of Amazon Web Services (AWS). Provide technical documentation showing how and where SDG&E uses AWS in its statistical and machine learning models used for Wings-Planning and Wings-Ops. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.3 | 5.3 Risk Scenarios . | 5.3.1 | 5.3.1 Design Basis Scenarios
60 | OEIS | 6 | OEIS-6 | 5 | OEIS-6.5 | Regarding Design Scenarios: a. On page 49 of SDG&E's 2026-2028 Base WMP, SDG&E mentions that it uses a 2-year history for historical weather and fuel data. Describe why a longer weather history is not used. Include any supporting analysis and documentation showing how and why SDG&E chose to use a 2-year history. b. Page 50 of SDG&E's 2026-2028 Base WMP, “OEIS Table 5-2: Summary of Design Scenarios,” mentions the "WV1" scenario ID. i. Specify if this WV1 scenario ID is intended to address "Weather Condition 1" from the WMP Guidelines. ii. If it is not, discuss: (1) Why SDG&E includes “WV1” as a design scenario. (2) How “WV1” differs from “Weather Condition 1.” (3) How “Weather Condition 1” is otherwise captured within the design scenarios in OEIS Table 5-2, or why it is excluded. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.3 | 5.3 Risk Scenarios . | 5.3.1 | 5.3.1 Design Basis Scenarios
61 | OEIS | 6 | OEIS-6 | 6 | OEIS-6.6 | Regarding AFN Scaling Factors: Page 53 of SDG&E's 2026-2028 Base WMP, “OEIS Table 5-4: Summary of Risk Models,” notes the input of "Scaling factors for AFN customer impacts." a. Clarify if SDG&E uses scaling based on AFN for PSPS consequences only, or for wildfire consequences as well. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.4 | 5.4 Summary of Risk Models . | N/A | N/A
62 | OEIS | 6 | OEIS-6 | 7 | OEIS-6.7 | Regarding Proposed Updates to the HFTD: On page 59 of SDG&E's 2026-2028 Base WMP, SDG&E states: “To date, SDG&E has not suggested any adjustments to the HFTD. Recent modeling initiatives evaluated the wildfire risk of coastal canyons and the WUI for mitigation. Both efforts resulted in the exclusion of each proposed addition.” a. SDG&E also states that “The analysis found that wildfire risk associated with coastal canyons was lower than that associated with current HFTD segments.” Provide a detailed description of the analysis performed, and associated documentation and conclusions demonstrating the lower wildfire risk, including any associated risk scores in comparison to those within the HFTD. b. For analysis of the WUI, SDG&E also states that “While this layer may serve to prioritize the adjacent developed areas for fire infrastructure and suppression planning, it does not yield a usable layer for identifying areas where an energized wire down could spark a wildfire, or areas at heightened risk for ignition due to interference from vegetation.” i. Describe how this layer is used to prioritize fire infrastructure. ii. Explain why this layer is not a “usable layer” for evaluating wildfire risk as described. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.5 | 5.5 Risk Analysis Results and Presentation . | 5.5.1.2 | 5.5.1.2 Proposed Updates to the HFTD
63 | OEIS | 6 | OEIS-6 | 8 | OEIS-6.8 | Regarding Third-Party Risk Model Recommendations to Models: Pages 62-66 of SDG&E's 2026-2028 Base WMP, “SDGE Table 5-8: WiNGS-Planning Third Party Recommendations,” and “SDGE Table 5-9: WiNGS-Ops Risk Modeling Updates,” show third-party recommendations for SDG&E’s models. a. Multiple recommendations state that SDG&E’s model documentation is lacking, with a 2026 target deadline to provide documentation. Explain what efforts have been made to start creating each documentation recommended. b. One recommendation states that a report that tracks compliance with OIR requirements would help prevent potential violations. i. Provide a copy of this report, if it has been created. ii. If such a report has not been created, discuss SDG&E’s progress on creating this report. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | 5.6 | 5.6 Quality Assurance and Quality Control | 5.6.1 | 5.6.1 Independent Review
64 | OEIS | 6 | OEIS-6 | 9 | OEIS-6.9 | Regarding Climate Change: a. Provide a detailed description and relevant supporting documentation on how climate change is currently accounted for in SDG&E’s risk models. |  | Zhenying Shao | 2025-05-20 | 2025-05-23 |  |  |  |  | N/A | Climate Change in Risk Models |  | #N/A
65 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
66 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
67 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
68 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
69 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
70 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
71 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
72 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
73 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
74 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
75 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
76 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
77 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
78 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
79 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
80 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
81 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
82 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
83 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
84 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
85 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
86 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
87 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
88 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
89 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
90 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
91 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
92 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
93 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
94 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
95 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
96 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
97 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
98 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
99 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
100 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
101 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
102 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
103 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
104 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
105 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
106 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
107 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
108 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
109 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
110 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
111 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
112 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
113 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
114 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
115 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
116 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
117 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
118 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
119 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
120 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
121 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
122 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
123 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
124 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
125 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
126 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
127 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
128 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
129 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
130 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
131 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
132 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
133 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
134 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
135 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
136 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
137 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
138 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
139 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
140 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
141 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
142 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
143 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
144 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
145 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
146 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
147 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
148 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
149 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
150 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
151 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
152 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
153 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
154 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
155 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
156 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
157 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
158 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
159 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
160 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
161 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
162 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
163 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
164 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
165 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
166 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
167 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
168 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
169 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
170 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A

## WMP Sections (hidden)
| Section # | Section | Page #
1 Executive Summary ....................................................................................................................1 | 1 | 1 Executive Summary | 1
1.1 Primary Goal.................................................................................................................................. 2 | 1.1 | 1.1 Primary Goal. | 2
1.2 Objectives ...................................................................................................................................... 3 | 1.2 | 1.2 Objectives | 3
1.3 Framework for Development of the WMP ................................................................................... 4 | 1.3 | 1.3 Framework for Development of the WMP | 4
2 Responsible Persons ...................................................................................................................7 | 2 | 2 Responsible Persons . | 7
3 Overview of Base WMP ..............................................................................................................9 | 3 | 3 Overview of Base WMP | 9
3.1 Primary Goal.................................................................................................................................. 9 | 3.1 | 3.1 Primary Goal. | 9
3.2 Plan Objectives .............................................................................................................................. 9 | 3.2 | 3.2 Plan Objectives | 9
3.2.1 Public Safety Power Shutoff .................................................................................................. 9 | 3.2.1 | 3.2.1 Public Safety Power Shutoff | 9
3.2.2 Grid Design, Operations, and Maintenance ........................................................................ 10 | 3.2.2 | 3.2.2 Grid Design, Operations, and Maintenance | 10
3.2.3 Vegetation Management and Inspections .......................................................................... 10 | 3.2.3 | 3.2.3 Vegetation Management and Inspections | 10
3.3 Utility Mitigation Activity Tracking IDs ........................................................................................ 10 | 3.3 | 3.3 Utility Mitigation Activity Tracking IDs | 10
3.4 Prioritized List of Wildfire Risks and Risk Drivers ........................................................................ 11 | 3.4 | 3.4 Prioritized List of Wildfire Risks and Risk Drivers . | 11
3.5 Performance Metrics .................................................................................................................. 14 | 3.5 | 3.5 Performance Metrics . | 14
3.6 Projected Expenditures ............................................................................................................... 16 | 3.6 | 3.6 Projected Expenditures . | 16
3.7 Climate Change ........................................................................................................................... 16 | 3.7 | 3.7 Climate Change . | 16
4 Overview of the Service Territory .............................................................................................. 19 | 4 | 4 Overview of the Service Territory | 19
4.1 Service Territory .......................................................................................................................... 19 | 4.1 | 4.1 Service Territory . | 19
4.2 Catastrophic Wildfire History ...................................................................................................... 21 | 4.2 | 4.2 Catastrophic Wildfire History | 21
4.3 Frequently De-Energized Circuits ................................................................................................ 22 | 4.3 | 4.3 Frequently De-Energized Circuits | 22
5 Risk Methodology and Assessment ........................................................................................... 24 | 5 | 5 Risk Methodology and Assessment | 24
5.1 Methodology ............................................................................................................................... 24 | 5.1 | 5.1 Methodology . | 24
5.1.1 Overview ............................................................................................................................. 24 | 5.1.1 | 5.1.1 Overview | 24
5.2 Risk Analysis Framework ............................................................................................................. 29 | 5.2 | 5.2 Risk Analysis Framework | 29
5.2.1 Risk and Risk Component Identification ............................................................................. 30 | 5.2.1 | 5.2.1 Risk and Risk Component Identification | 30
5.2.1.1 WiNGS-Planning and WiNGS-Ops Models .................................................................. 33 | 5.2.1.1 | 5.2.1.1 WiNGS-Planning and WiNGS-Ops Models | 33
5.2.2 Risk and Risk Components Calculation ............................................................................... 34 | 5.2.2 | 5.2.2 Risk and Risk Components Calculation . | 34
5.2.2.1 Likelihood of Risk Event .............................................................................................. 37 | 5.2.2.1 | 5.2.2.1 Likelihood of Risk Event | 37
5.2.2.2 Consequence of Risk Event ......................................................................................... 37 | 5.2.2.2 | 5.2.2.2 Consequence of Risk Event | 37
5.2.2.3 Risk .............................................................................................................................. 40 | 5.2.2.3 | 5.2.2.3 Risk | 40
5.2.3 Key Assumptions and Limitations ....................................................................................... 43 | 5.2.3 | 5.2.3 Key Assumptions and Limitations . | 43
5.3 Risk Scenarios .............................................................................................................................. 46 | 5.3 | 5.3 Risk Scenarios . | 46
5.3.1 Design Basis Scenarios ........................................................................................................ 49 | 5.3.1 | 5.3.1 Design Basis Scenarios | 49
5.3.2 Extreme-Event/High Uncertainty Scenarios ....................................................................... 51 | 5.3.2 | 5.3.2 Extreme-Event/High Uncertainty Scenarios | 51
5.4 Summary of Risk Models ............................................................................................................. 53 | 5.4 | 5.4 Summary of Risk Models . | 53
5.5 Risk Analysis Results and Presentation ....................................................................................... 57 | 5.5 | 5.5 Risk Analysis Results and Presentation . | 57
5.5.1 Top Risk Areas within the HFRA .......................................................................................... 57 | 5.5.1 | 5.5.1 Top Risk Areas within the HFRA | 57
5.5.1.1 Geospatial Maps of Top-Risk Areas within the HFRA ................................................. 58 | 5.5.1.1 | 5.5.1.1 Geospatial Maps of Top-Risk Areas within the HFRA | 58
5.5.1.2 Proposed Updates to the HFTD .................................................................................. 59 | 5.5.1.2 | 5.5.1.2 Proposed Updates to the HFTD | 59
5.5.2 Top Risk-Contributing Circuits/Segments/Spans ................................................................ 60 | 5.5.2 | 5.5.2 Top Risk-Contributing Circuits/Segments/Spans | 60
5.6 Quality Assurance and Quality Control ....................................................................................... 60 | 5.6 | 5.6 Quality Assurance and Quality Control | 60
5.6.1 Independent Review ........................................................................................................... 60 | 5.6.1 | 5.6.1 Independent Review | 60
5.6.2 Model Controls, Design, and Review .................................................................................. 75 | 5.6.2 | 5.6.2 Model Controls, Design, and Review | 75
5.6.2.1 Modularization ............................................................................................................ 75 | 5.6.2.1 | 5.6.2.1 Modularization | 75
5.6.2.2 Reanalysis .................................................................................................................... 75 | 5.6.2.2 | 5.6.2.2 Reanalysis . | 75
5.6.2.3 Version Control ........................................................................................................... 75 | 5.6.2.3 | 5.6.2.3 Version Control . | 75
5.7 Risk Assessment Improvement Plan ........................................................................................... 76 | 5.7 | 5.7 Risk Assessment Improvement Plan | 76
5.7.1 Risk Assessment Methodology ........................................................................................... 76 | 5.7.1 | 5.7.1 Risk Assessment Methodology | 76
5.7.2 Design basis ......................................................................................................................... 76 | 5.7.2 | 5.7.2 Design basis . | 76
5.7.3 Risk Presentation ................................................................................................................ 77 | 5.7.3 | 5.7.3 Risk Presentation . | 77
5.7.4 Risk Event Tracking ............................................................................................................. 77 | 5.7.4 | 5.7.4 Risk Event Tracking | 77
5.7.5 Data Egineering Optimization ............................................................................................. 77 | 5.7.5 | 5.7.5 Data Egineering Optimization . | 77
6 Wildfire Mitigation Strategy ...................................................................................................... 81 | 6 | 6 Wildfire Mitigation Strategy | 81
6.1 Risk Evaluation ............................................................................................................................ 81 | 6.1 | 6.1 Risk Evaluation | 81
6.1.1 Approach ............................................................................................................................. 81 | 6.1.1 | 6.1.1 Approach | 81
6.1.2 Risk-Informed Prioritization ................................................................................................ 82 | 6.1.2 | 6.1.2 Risk-Informed Prioritization . | 82
6.1.2.1 Prioritized List of Risks ................................................................................................ 83 | 6.1.2.1 | 6.1.2.1 Prioritized List of Risks | 83
6.1.3 Activity Selection Process.................................................................................................... 85 | 6.1.3 | 6.1.3 Activity Selection Process. | 85
6.1.3.1 Identifying and Evaluating Mitigation Initiatives ........................................................ 86 | 6.1.3.1 | 6.1.3.1 Identifying and Evaluating Mitigation Initiatives | 86
6.1.3.2 Activity Prioritization ................................................................................................... 95 | 6.1.3.2 | 6.1.3.2 Activity Prioritization . | 95
6.1.3.3 Activity Scheduling .................................................................................................... 103 | 6.1.3.3 | 6.1.3.3 Activity Scheduling | 103
6.1.3.4 Key Stakeholders for Decision Making ...................................................................... 105 | 6.1.3.4 | 6.1.3.4 Key Stakeholders for Decision Making | 105
6.2 Wildfire Mitigation Strategy ...................................................................................................... 109 | 6.2 | 6.2 Wildfire Mitigation Strategy | 109
6.2.1 Anticipated Risk Reduction ............................................................................................... 109 | 6.2.1 | 6.2.1 Anticipated Risk Reduction | 109
6.2.1.1 Projected Overall Risk Reduction .............................................................................. 109 | 6.2.1.1 | 6.2.1.1 Projected Overall Risk Reduction | 109
6.2.1.2 Risk Impact of Activities ........................................................................................... 110 | 6.2.1.2 | 6.2.1.2 Risk Impact of Activities | 110
6.2.1.3 Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle | 6.2.1.3 | 6.2.1.3 Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle | cle
6.2.2 Interim Activities ............................................................................................................... 117 | 6.2.2 | 6.2.2 Interim Activities | 117
7 Public Safety Power Shutoff .................................................................................................... 119 | 7 | 7 Public Safety Power Shutoff . | 119
7.1 Overview ................................................................................................................................... 119 | 7.1 | 7.1 Overview | 119
7.2 Process for Initiating a PSPS De-Energization ........................................................................... 119 | 7.2 | 7.2 Process for Initiating a PSPS De-Energization | 119
7.3 PSPS Impact Redution on Frequently De-Energized Circuits .................................................... 122 | 7.3 | 7.3 PSPS Impact Redution on Frequently De-Energized Circuits | 122
7.4 Lessons Learned ........................................................................................................................ 123 | 7.4 | 7.4 Lessons Learned | 123
8 Grid Design, Operations, and Maintenance ............................................................................. 124 | 8 | 8 Grid Design, Operations, and Maintenance | 124
8.1 Targets....................................................................................................................................... 124 | 8.1 | 8.1 Targets. | 124
8.1.1 Qualitative Targets ............................................................................................................ 124 | 8.1.1 | 8.1.1 Qualitative Targets | 124
8.1.2 Quantitative Targets ......................................................................................................... 124 | 8.1.2 | 8.1.2 Quantitative Targets . | 124
8.2 Grid Design and System Hardening........................................................................................... 131 | 8.2 | 8.2 Grid Design and System Hardening | 131
8.2.1 Combined Covered Conductor Installation (WMP.455) ................................................... 131 | 8.2.1 | 8.2.1 Combined Covered Conductor Installation (WMP.455) | 131
8.2.1.1 Tracking ID ................................................................................................................. 131 | 8.2.1.1 | 8.2.1.1 Tracking ID | 131
8.2.1.2 | 8.2.1.2 | 8.2.1.2 | 1.2
8.2.1.3 Impact of the Activity on Wildfire Risk ...................................................................... 131 | 8.2.1.3 | 8.2.1.3 Impact of the Activity on Wildfire Risk . | 131
8.2.1.4 Impact of the Activity on Outage Program Risk ........................................................ 132 | 8.2.1.4 | 8.2.1.4 Impact of the Activity on Outage Program Risk . | 132
8.2.1.5 Updates to Activity .................................................................................................... 132 | 8.2.1.5 | 8.2.1.5 Updates to Activity | 132
8.2.1.6 Compatible Activities ................................................................................................ 132 | 8.2.1.6 | 8.2.1.6 Compatible Activities . | 132
8.2.2 Undergrounding of Electric Lines and/or Equipment (WMP.473) .................................... 132 | 8.2.2 | 8.2.2 Undergrounding of Electric Lines and/or Equipment (WMP.473) | 132
8.2.2.1 Tracking ID ................................................................................................................. 132 | 8.2.2.1 | 8.2.2.1 Tracking ID | 132
8.2.2.2 Overview of the Activity ............................................................................................ 133 | 8.2.2.2 | 8.2.2.2 Overview of the Activity | 133
8.2.2.3 Impact of the Activity on Wildfire Risk ...................................................................... 133 | 8.2.2.3 | 8.2.2.3 Impact of the Activity on Wildfire Risk | 133
8.2.2.4 Impact of the Activity on Outage Program Risk ........................................................ 133 | 8.2.2.4 | 8.2.2.4 Impact of the Activity on Outage Program Risk | 133
8.2.2.5 Updates to Activity .................................................................................................... 133 | 8.2.2.5 | 8.2.2.5 Updates to Activity | 133
8.2.2.6 Compatible Activities ................................................................................................ 134 | 8.2.2.6 | 8.2.2.6 Compatible Activities . | 134
8.2.3 Distribution Pole Replacements and Reinforcements ...................................................... 134 | 8.2.3 | 8.2.3 Distribution Pole Replacements and Reinforcements . | 134
8.2.3.1 Distribution Pole Replacement and Reinforcement Program .................................. 134 | 8.2.3.1 | 8.2.3.1 Distribution Pole Replacement and Reinforcement Program | 134
8.2.3.2 Strategic Pole Replacement Program (WMP.1189) .................................................. 135 | 8.2.3.2 | 8.2.3.2 Strategic Pole Replacement Program (WMP.1189) | 135
8.2.4 Transmission Pole/Tower Replacements and Reinforcements (WMP.472) ..................... 137 | 8.2.4 | 8.2.4 Transmission Pole/Tower Replacements and Reinforcements (WMP.472) | 137
8.2.4.1 Tracking ID ................................................................................................................. 137 | 8.2.4.1 | 8.2.4.1 Tracking ID | 137
8.2.4.2 Overview of the Activity ............................................................................................ 137 | 8.2.4.2 | 8.2.4.2 Overview of the Activity | 137
8.2.4.3 Impact of the Activity on Wildfire Risk ...................................................................... 137 | 8.2.4.3 | 8.2.4.3 Impact of the Activity on Wildfire Risk . | 137
8.2.4.4 Impact of the Activity on Outage Program Risk ........................................................ 137 | 8.2.4.4 | 8.2.4.4 Impact of the Activity on Outage Program Risk . | 137
8.2.4.5 Updates to Activity .................................................................................................... 137 | 8.2.4.5 | 8.2.4.5 Updates to Activity | 137
8.2.4.6 Compatible Activities ................................................................................................ 137 | 8.2.4.6 | 8.2.4.6 Compatible Activities . | 137
8.2.5 Traditional Overhead Hardening....................................................................................... 137 | 8.2.5 | 8.2.5 Traditional Overhead Hardening | 137
8.2.5.1 Distribution Overhead System Hardening (Traditional) (WMP.475) ........................ 137 | 8.2.5.1 | 8.2.5.1 Distribution Overhead System Hardening (Traditional) (WMP.475) | 137
8.2.5.2 Transmission System Hardening Program (WMP.543, WMP.545) ........................... 139 | 8.2.5.2 | 8.2.5.2 Transmission System Hardening Program (WMP.543, WMP.545) | 139
8.2.6 Emerging Grid Hardening Technology Installations and Pilots ......................................... 140 | 8.2.6 | 8.2.6 Emerging Grid Hardening Technology Installations and Pilots | 140
8.2.7 Microgrids (WMP.462) ...................................................................................................... 140 | 8.2.7 | 8.2.7 Microgrids (WMP.462) | 140
8.2.7.1 Tracking ID ................................................................................................................. 140 | 8.2.7.1 | 8.2.7.1 Tracking ID | 140
8.2.7.2 Overview of the Activity ............................................................................................ 140 | 8.2.7.2 | 8.2.7.2 Overview of the Activity | 140
8.2.7.3 Impact of the Activity on Wildfire Risk ...................................................................... 141 | 8.2.7.3 | 8.2.7.3 Impact of the Activity on Wildfire Risk | 141
8.2.7.4 Impact of the Activity on Outage Program Risk ........................................................ 141 | 8.2.7.4 | 8.2.7.4 Impact of the Activity on Outage Program Risk | 141
8.2.7.5 Updates to Activity .................................................................................................... 141 | 8.2.7.5 | 8.2.7.5 Updates to Activity | 141
8.2.7.6 Compatible Activities ................................................................................................ 141 | 8.2.7.6 | 8.2.7.6 Compatible Activities | 141
8.2.8 Installation of System Automation Equipment ................................................................. 141 | 8.2.8 | 8.2.8 Installation of System Automation Equipment | 141
8.2.8.1 Advanced Protection (WMP.463) ............................................................................. 141 | 8.2.8.1 | 8.2.8.1 Advanced Protection (WMP.463) | 141
8.2.9 Line Removal (in the HFTD) ............................................................................................... 144 | 8.2.9 | 8.2.9 Line Removal (in the HFTD) | 144
8.2.9.1 Tracking ID ................................................................................................................. 144 | 8.2.9.1 | 8.2.9.1 Tracking ID | 144
8.2.9.2 Overview of the Activity ............................................................................................ 144 | 8.2.9.2 | 8.2.9.2 Overview of the Activity | 144
8.2.9.3 Impact of the Activity on Wildfire Risk ...................................................................... 144 | 8.2.9.3 | 8.2.9.3 Impact of the Activity on Wildfire Risk | 144
8.2.9.4 Impact of the Activity on Outage Program Risk ........................................................ 144 | 8.2.9.4 | 8.2.9.4 Impact of the Activity on Outage Program Risk | 144
8.2.9.5 Updates to Activity .................................................................................................... 144 | 8.2.9.5 | 8.2.9.5 Updates to Activity | 144
8.2.9.6 Compatible Activities ................................................................................................ 144 | 8.2.9.6 | 8.2.9.6 Compatible Activities | 144
8.2.10 Other Grid Topology Improvements to Minimize Risk of Ignitions .................................. 144 | 8.2.10 | 8.2.10 Other Grid Topology Improvements to Minimize Risk of Ignitions | 144
8.2.11 Other Grid Topology Improvements to Mitigate or Reduce PSPS Events ........................ 145 | 8.2.11 | 8.2.11 Other Grid Topology Improvements to Mitigate or Reduce PSPS Events | 145
8.2.11.1 PSPS Sectionalizing Enhancement Program (WMP.461) .......................................... 145 | 8.2.11.1 | 8.2.11.1 PSPS Sectionalizing Enhancement Program (WMP.461) | 145
8.2.11.2 Standby Power Program (WMP.468) ........................................................................ 146 | 8.2.11.2 | 8.2.11.2 Standby Power Program (WMP.468) | 146
8.2.11.3 Customized Resiliency Assessments (WMP.1432) .................................................... 147 | 8.2.11.3 | 8.2.11.3 Customized Resiliency Assessments (WMP.1432) | 147
8.2.11.4 Generator Assistance Program (WMP.467) .............................................................. 148 | 8.2.11.4 | 8.2.11.4 Generator Assistance Program (WMP.467) | 148
8.2.12 Other Technologies and Systems not Listed Above .......................................................... 149 | 8.2.12 | 8.2.12 Other Technologies and Systems not Listed Above | 149
8.2.12.1 Ignition Management Program (WMP.558) ............................................................. 149 | 8.2.12.1 | 8.2.12.1 Ignition Management Program (WMP.558) | 149
8.2.13 Status Updates on Additional Technologies being Piloted ............................................... 149 | 8.2.13 | 8.2.13 Status Updates on Additional Technologies being Piloted | 149
8.3 Asset Inspections ...................................................................................................................... 150 | 8.3 | 8.3 Asset Inspections | 150
8.3.1 Distribution Overhead Detailed Inspections (WMP.478) ................................................. 153 | 8.3.1 | 8.3.1 Distribution Overhead Detailed Inspections (WMP.478) | 153
8.3.1.1 Overview ................................................................................................................... 153 | 8.3.1.1 | 8.3.1.1 Overview | 153
8.3.1.2 Frequency or Trigger ................................................................................................. 153 | 8.3.1.2 | 8.3.1.2 Frequency or Trigger | 153
8.3.1.3 Accomplishments, Roadblocks, and Updates ........................................................... 154 | 8.3.1.3 | 8.3.1.3 Accomplishments, Roadblocks, and Updates | 154
8.3.2 Transmission Overhead Detailed Inspections (WMP.479) ............................................... 155 | 8.3.2 | 8.3.2 Transmission Overhead Detailed Inspections (WMP.479) | 155
8.3.2.1 Overview ................................................................................................................... 155 | 8.3.2.1 | 8.3.2.1 Overview | 155
8.3.2.2 Frequency or Trigger ................................................................................................. 157 | 8.3.2.2 | 8.3.2.2 Frequency or Trigger | 157
8.3.2.3 Accomplishments, Roadblocks, and Updates ........................................................... 157 | 8.3.2.3 | 8.3.2.3 Accomplishments, Roadblocks, and Updates | 157
8.3.3 Transmission Infrared Inspections (WMP.482) ................................................................. 157 | 8.3.3 | 8.3.3 Transmission Infrared Inspections (WMP.482) | 157
8.3.3.1 Overview ................................................................................................................... 157 | 8.3.3.1 | 8.3.3.1 Overview | 157
8.3.3.2 Frequency or Trigger ................................................................................................. 158 | 8.3.3.2 | 8.3.3.2 Frequency or Trigger | 158
8.3.3.3 Accomplishments, Roadblocks, and Updates ........................................................... 159 | 8.3.3.3 | 8.3.3.3 Accomplishments, Roadblocks, and Updates | 159
8.3.4 Distribution Wood Pole Intrusive Inspections (WMP.483) ............................................... 159 | 8.3.4 | 8.3.4 Distribution Wood Pole Intrusive Inspections (WMP.483) | 159
8.3.4.1 Overview ................................................................................................................... 159 | 8.3.4.1 | 8.3.4.1 Overview | 159
8.3.4.2 Frequency or Trigger ................................................................................................. 160 | 8.3.4.2 | 8.3.4.2 Frequency or Trigger | 160
8.3.4.3 Accomplishments, Roadblocks, and Updates ........................................................... 161 | 8.3.4.3 | 8.3.4.3 Accomplishments, Roadblocks, and Updates | 161
8.3.5 Transmission Wood Pole Intrusive Inspections (WMP.1190) ........................................... 161 | 8.3.5 | 8.3.5 Transmission Wood Pole Intrusive Inspections (WMP.1190) | 161
8.3.5.1 Overview ................................................................................................................... 161 | 8.3.5.1 | 8.3.5.1 Overview | 161
8.3.5.2 Frequency or Trigger ................................................................................................. 161 | 8.3.5.2 | 8.3.5.2 Frequency or Trigger | 161
8.3.5.3 Accomplishments, Roadblocks, and Updates ........................................................... 161 | 8.3.5.3 | 8.3.5.3 Accomplishments, Roadblocks, and Updates | 161
8.3.6 Risk-Informed Drone Inspections (WMP.552) .................................................................. 162 | 8.3.6 | 8.3.6 Risk-Informed Drone Inspections (WMP.552) | 162
8.3.6.1 Overview ................................................................................................................... 162 | 8.3.6.1 | 8.3.6.1 Overview | 162
8.3.6.2 Frequency or Trigger ................................................................................................. 163 | 8.3.6.2 | 8.3.6.2 Frequency or Trigger | 163
8.3.6.3 Accomplishments, Roadblocks, and Updates ........................................................... 165 | 8.3.6.3 | 8.3.6.3 Accomplishments, Roadblocks, and Updates | 165
8.3.7 Distribution Overhead Patrol Inspections (WMP.488) ..................................................... 166 | 8.3.7 | 8.3.7 Distribution Overhead Patrol Inspections (WMP.488) | 166
8.3.7.1 Overview ................................................................................................................... 166 | 8.3.7.1 | 8.3.7.1 Overview | 166
8.3.7.2 Frequency or Trigger ................................................................................................. 166 | 8.3.7.2 | 8.3.7.2 Frequency or Trigger | 166
8.3.7.3 Accomplishments, Roadblocks, and Updates ........................................................... 167 | 8.3.7.3 | 8.3.7.3 Accomplishments, Roadblocks, and Update | 167
8.3.8 Transmission Overhead Patrol Inspections (WMP.489) ................................................... 167 | 8.3.8 | 8.3.8 Transmission Overhead Patrol Inspections (WMP.489) | 167
8.3.8.1 Overview ................................................................................................................... 167 | 8.3.8.1 | 8.3.8.1 Overview | 167
8.3.8.2 Frequency or Trigger ................................................................................................. 169 | 8.3.8.2 | 8.3.8.2 Frequency or Trigger | 169
8.3.8.3 Accomplishments, Roadblocks, and Updates ........................................................... 169 | 8.3.8.3 | 8.3.8.3 Accomplishments, Roadblocks, and Updates | 169
8.3.9 Substation Patrol Inspections (WMP.492) ........................................................................ 169 | 8.3.9 | 8.3.9 Substation Patrol Inspections (WMP.492) | 169
8.3.9.1 Overview ................................................................................................................... 169 | 8.3.9.1 | 8.3.9.1 Overview | 169
8.3.9.2 Frequency or Trigger ................................................................................................. 170 | 8.3.9.2 | 8.3.9.2 Frequency or Trigger | 170
8.3.9.3 Accomplishments, Roadblocks, and Updates ........................................................... 170 | 8.3.9.3 | 8.3.9.3 Accomplishments, Roadblocks, and Updates | 170
8.3.10 Discontinued Asset Inspection Programs ......................................................................... 171 | 8.3.10 | 8.3.10 Discontinued Asset Inspection Programs | 171
8.3.10.1 Distribution Infrared Inspections (WMP.481) ........................................................... 171 | 8.3.10.1 | 8.3.10.1 Distribution Infrared Inspections (WMP.481) | 171
8.3.10.2 Transmission 69 kV Tier 3 Visual Inspections (WMP.555) ........................................ 171 | 8.3.10.2 | 8.3.10.2 Transmission 69 kV Tier 3 Visual Inspections (WMP.555) | 171
8.3.11 Asset Inspection Pilot Programs ....................................................................................... 171 | 8.3.11 | 8.3.11 Asset Inspection Pilot Programs | 171
8.4 Equipment Maintenance and Repair (WMP.1130) ................................................................... 171 | 8.4 | 8.4 Equipment Maintenance and Repair (WMP.1130) | 171
8.4.1 Maintenance Strategies .................................................................................................... 171 | 8.4.1 | 8.4.1 Maintenance Strategies | 171
8.4.2 Timeframe for Remediation .............................................................................................. 174 | 8.4.2 | 8.4.2 Timeframe for Remediation | 174
8.4.3 Failure and Ignition Causes ............................................................................................... 176 | 8.4.3 | 8.4.3 Failure and Ignition Causes | 176
8.4.3.1 Failure Causes ........................................................................................................... 176 | 8.4.3.1 | 8.4.3.1 Failure Causes | 176
8.4.3.2 Ignition Causes .......................................................................................................... 176 | 8.4.3.2 | 8.4.3.2 Ignition Causes | 176
8.5 Quality Assurance and Quality Control ..................................................................................... 177 | 8.5 | 8.5 Quality Assurance and Quality Control | 177
8.5.1 Overview, Objectives, and Targets ................................................................................... 177 | 8.5.1 | 8.5.1 Overview, Objectives, and Targets | 177
8.5.2 QA and QC Procedures ...................................................................................................... 181 | 8.5.2 | 8.5.2 QA and QC Procedures | 181
8.5.2.1 Grid Design and System Hardening ........................................................................... 181 | 8.5.2.1 | 8.5.2.1 Grid Design and System Hardening | 181
8.5.2.2 Asset Inspections....................................................................................................... 181 | 8.5.2.2 | 8.5.2.2 Asset Inspections | 181
8.5.2.3 Equipment Maintenance and Repair ........................................................................ 182 | 8.5.2.3 | 8.5.2.3 Equipment Maintenance and Repair | 182
8.5.3 Sampling Plan .................................................................................................................... 182 | 8.5.3 | 8.5.3 Sampling Plan | 182
8.5.3.1 Grid Design and System Hardening ........................................................................... 182 | 8.5.3.1 | 8.5.3.1 Grid Design and System Hardening | 182
8.5.3.2 Asset Inspections....................................................................................................... 182 | 8.5.3.2 | 8.5.3.2 Asset Inspections | 182
8.5.3.3 Equipment Maintenance and Repair ........................................................................ 183 | 8.5.3.3 | 8.5.3.3 Equipment Maintenance and Repair | 183
8.5.4 Pass Rate Calculation ........................................................................................................ 183 | 8.5.4 | 8.5.4 Pass Rate Calculation | 183
8.5.4.1 Grid Design and System Hardening ........................................................................... 183 | 8.5.4.1 | 8.5.4.1 Grid Design and System Hardening | 183
8.5.4.2 Asset Inspections....................................................................................................... 184 | 8.5.4.2 | 8.5.4.2 Asset Inspections | 184
8.5.4.3 Equipment Maintenance and Repair ........................................................................ 185 | 8.5.4.3 | 8.5.4.3 Equipment Maintenance and Repair | 185
8.5.5 Other Metrics .................................................................................................................... 185 | 8.5.5 | 8.5.5 Other Metrics | 185
8.5.5.1 Grid Design and System Hardening ........................................................................... 185 | 8.5.5.1 | 8.5.5.1 Grid Design and System Hardening | 185
8.5.5.2 Asset Inspections....................................................................................................... 185 | 8.5.5.2 | 8.5.5.2 Asset Inspections | 185
8.5.5.3 Equipment Maintenance and Repair ........................................................................ 185 | 8.5.5.3 | 8.5.5.3 Equipment Maintenance and Repair | 185
8.5.6 Documentation of Findings ............................................................................................... 186 | 8.5.6 | 8.5.6 Documentation of Findings . | 186
8.5.6.1 Grid Design and System Hardening ........................................................................... 186 | 8.5.6.1 | 8.5.6.1 Grid Design and System Hardening | 186
8.5.6.2 Asset Inspections....................................................................................................... 186 | 8.5.6.2 | 8.5.6.2 Asset Inspections | 186
8.5.6.3 Equipment Maintenance and Repair ........................................................................ 187 | 8.5.6.3 | 8.5.6.3 Equipment Maintenance and Repair | 187
8.5.7 Changes to QA and QC Since Last WMP and Planned Improvements .............................. 187 | 8.5.7 | 8.5.7 Changes to QA and QC Since Last WMP and Planned Improvements | 187
8.5.7.1 Grid Design and System Hardening ........................................................................... 187 | 8.5.7.1 | 8.5.7.1 Grid Design and System Hardening | 187
8.5.7.2 Asset Inspections....................................................................................................... 188 | 8.5.7.2 | 8.5.7.2 Asset Inspections | 188
8.5.7.3 Equipment Maintenance and Repair ........................................................................ 188 | 8.5.7.3 | 8.5.7.3 Equipment Maintenance and Repair | 188
8.6 Work Orders .............................................................................................................................. 188 | 8.6 | 8.6 Work Orders . | 188
8.6.1 Procedures Documenting the Work Order Process .......................................................... 188 | 8.6.1 | 8.6.1 Procedures Documenting the Work Order Process | 188
8.6.2 Plan for Correcting Past Due Work Orders, if Applicable ................................................. 191 | 8.6.2 | 8.6.2 Plan for Correcting Past Due Work Orders, if Applicable | 191
8.6.3 Prioritization of Work Orders ............................................................................................ 191 | 8.6.3 | 8.6.3 Prioritization of Work Orders | 191
8.6.4 Procedure for Monitoring/Reinspecting Open Work Orders ........................................... 191 | 8.6.4 | 8.6.4 Procedure for Monitoring/Reinspecting Open Work Orders | 191
8.6.5 Open Work Order Trends .................................................................................................. 192 | 8.6.5 | 8.6.5 Open Work Order Trends | 192
8.7 Grid Operations and Procedures .............................................................................................. 194 | 8.7 | 8.7 Grid Operations and Procedures . | 194
8.7.1 Equipment Settings to Reduce Wildfire Risk ..................................................................... 194 | 8.7.1 | 8.7.1 Equipment Settings to Reduce Wildfire Risk | 194
8.7.1.1 Protective Equipment and Device Settings (WMP.991) ............................................ 194 | 8.7.1.1 | 8.7.1.1 Protective Equipment and Device Settings (WMP.991) | 194
8.7.1.2 Automatic Recloser Settings (WMP.1018) ................................................................ 195 | 8.7.1.2 | 8.7.1.2 Automatic Recloser Settings (WMP.1018) | 195
8.7.1.3 Settings of other Emerging Technologies ................................................................. 198 | 8.7.1.3 | 8.7.1.3 Settings of other Emerging Technologies | 198
8.7.2 Grid Response Procedures and Notifications ................................................................... 198 | 8.7.2 | 8.7.2 Grid Response Procedures and Notifications | 198
8.7.3 Personnel Work Procedures and Training in Conditions of Elevated Fire Risk ................. 199 | 8.7.3 | 8.7.3 Personnel Work Procedures and Training in Conditions of Elevated Fire Risk | 199
8.7.3.1 Work Procedures during Different Levels of Wildfire Risk ....................................... 199 | 8.7.3.1 | 8.7.3.1 Work Procedures during Different Levels of Wildfire Risk | 199
8.7.3.2 Procedures for Deployment of Fire Prevention and ignition Mitigation resources and Equipment…199 | 8.7.3.2 | 8.7.3.2 Procedures for Deployment of Fire Prevention and ignition Mitigation resources and Equipment | 199
8.8 Workforce Planning .................................................................................................................. 201 | 8.8 | 8.8 Workforce Planning | 201
9 Vegetation Management and Inspections ............................................................................... 206 | 9 | 9 Vegetation Management and Inspections | 206
9.1 Targets....................................................................................................................................... 207 | 9.1 | 9.1 Targets. | 207
9.1.1 Qualitative Targets ............................................................................................................ 207 | 9.1.1 | 9.1.1 Qualitative Targets | 207
9.1.2 Quantitative Targets ......................................................................................................... 207 | 9.1.2 | 9.1.2 Quantitative Targets . | 207
9.2 Vegetation Management Inspections ....................................................................................... 209 | 9.2 | 9.2 Vegetation Management Inspections . | 209
9.2.1 Detailed Inspections (WMP.494) ...................................................................................... 209 | 9.2.1 | 9.2.1 Detailed Inspections (WMP.494) | 209
9.2.1.1 Overview and Area Inspected ................................................................................... 209 | 9.2.1.1 | 9.2.1.1 Overview and Area Inspected | 209
9.2.1.2 Procedures ................................................................................................................ 209 | 9.2.1.2 | 9.2.1.2 Procedures . | 209
9.2.1.3 Clearance ................................................................................................................... 209 | 9.2.1.3 | 9.2.1.3 Clearance | 209
9.2.1.4 Fall-in Mitigation ....................................................................................................... 210 | 9.2.1.4 | 9.2.1.4 Fall-in Mitigation . | 210
9.2.1.5 Scheduling ................................................................................................................. 210 | 9.2.1.5 | 9.2.1.5 Scheduling . | 210
9.2.1.6 Updates ..................................................................................................................... 210 | 9.2.1.6 | 9.2.1.6 Updates . | 210
9.2.2 Off-Cycle Patrols (WMP.508) ............................................................................................ 210 | 9.2.2 | 9.2.2 Off-Cycle Patrols (WMP.508) | 210
9.2.2.1 Overview and Area Inspected ................................................................................... 210 | 9.2.2.1 | 9.2.2.1 Overview and Area Inspected | 210
9.2.2.2 Procedures ................................................................................................................ 210 | 9.2.2.2 | 9.2.2.2 Procedures . | 210
9.2.2.3 Clearance ................................................................................................................... 210 | 9.2.2.3 | 9.2.2.3 Clearance | 210
9.2.2.4 Fall-in Mitigation ....................................................................................................... 211 | 9.2.2.4 | 9.2.2.4 Fall-in Mitigation . | 211
9.2.2.5 Scheduling ................................................................................................................. 211 | 9.2.2.5 | 9.2.2.5 Scheduling . | 211
9.2.2.6 Updates ..................................................................................................................... 211 | 9.2.2.6 | 9.2.2.6 Updates . | 211
9.3 Pruning and Removal (WMP.501) ............................................................................................. 211 | 9.3 | 9.3 Pruning and Removal (WMP.501) | 211
9.3.1 Overview ........................................................................................................................... 211 | 9.3.1 | 9.3.1 Overview | 211
9.3.2 Procedures ........................................................................................................................ 211 | 9.3.2 | 9.3.2 Procedures | 211
9.3.3 Scheduling ......................................................................................................................... 211 | 9.3.3 | 9.3.3 Scheduling | 211
9.3.4 Updates ............................................................................................................................. 212 | 9.3.4 | 9.3.4 Updates . | 212
9.4 Pole Clearing (WMP.512) .......................................................................................................... 212 | 9.4 | 9.4 Pole Clearing (WMP.512) | 212
9.4.1 Overview ........................................................................................................................... 212 | 9.4.1 | 9.4.1 Overview | 212
9.4.2 Procedures ........................................................................................................................ 213 | 9.4.2 | 9.4.2 Procedures | 213
9.4.3 Scheduling ......................................................................................................................... 213 | 9.4.3 | 9.4.3 Scheduling | 213
9.4.4 Updates ............................................................................................................................. 213 | 9.4.4 | 9.4.4 Updates . | 213
9.5 Wood and Slash Management .................................................................................................. 214 | 9.5 | 9.5 Wood and Slash Management . | 214
9.5.1 Overview ........................................................................................................................... 214 | 9.5.1 | 9.5.1 Overview | 214
9.5.2 Procedures ........................................................................................................................ 214 | 9.5.2 | 9.5.2 Procedures | 214
9.5.3 Scheduling ......................................................................................................................... 214 | 9.5.3 | 9.5.3 Scheduling | 214
9.5.4 Updates ............................................................................................................................. 214 | 9.5.4 | 9.5.4 Updates . | 214
9.6 Defensible Space ....................................................................................................................... 214 | 9.6 | 9.6 Defensible Space | 214
9.6.1 Overview ........................................................................................................................... 214 | 9.6.1 | 9.6.1 Overview | 214
9.6.2 Procedures ........................................................................................................................ 215 | 9.6.2 | 9.6.2 Procedures | 215
9.6.3 Scheduling ......................................................................................................................... 215 | 9.6.3 | 9.6.3 Scheduling | 215
9.6.4 Updates ............................................................................................................................. 215 | 9.6.4 | 9.6.4 Updates . | 215
9.7 Integrated Vegetation Management: Fuels Management (WMP.497) .................................... 215 | 9.7 | 9.7 Integrated Vegetation Management: Fuels Management (WMP.497) | 215
9.7.1 Overview ........................................................................................................................... 215 | 9.7.1 | 9.7.1 Overview | 215
9.7.2 Procedures ........................................................................................................................ 215 | 9.7.2 | 9.7.2 Procedures | 215
9.7.3 Scheduling ......................................................................................................................... 215 | 9.7.3 | 9.7.3 Scheduling | 215
9.7.4 Updates ............................................................................................................................. 216 | 9.7.4 | 9.7.4 Updates . | 216
9.8 Partnerships .............................................................................................................................. 216 | 9.8 | 9.8 Partnerships | 216
9.8.1 Fire Safe Council of San Diego County .............................................................................. 217 | 9.8.1 | 9.8.1 Fire Safe Council of San Diego County | 217
9.8.1.1 Overview ................................................................................................................... 217 | 9.8.1.1 | 9.8.1.1 Overview | 217
9.8.1.2 Partnership History ................................................................................................... 217 | 9.8.1.2 | 9.8.1.2 Partnership History | 217
9.8.1.3 Future Projects .......................................................................................................... 217 | 9.8.1.3 | 9.8.1.3 Future Projects . | 217
9.8.2 Viejas Band of Kumeyaay Indians ..................................................................................... 218 | 9.8.2 | 9.8.2 Viejas Band of Kumeyaay Indians . | 218
9.8.2.1 Overview ................................................................................................................... 218 | 9.8.2.1 | 9.8.2.1 Overview | 218
9.8.2.2 Partnership History ................................................................................................... 218 | 9.8.2.2 | 9.8.2.2 Partnership History | 218
9.8.2.3 Future Projects .......................................................................................................... 218 | 9.8.2.3 | 9.8.2.3 Future Projects . | 218
9.8.3 Campo Band of Diegueno Mission Indians ....................................................................... 218 | 9.8.3 | 9.8.3 Campo Band of Diegueno Mission Indians | 218
9.8.3.1 Overview ................................................................................................................... 218 | 9.8.3.1 | 9.8.3.1 Overview | 218
9.8.3.2 Partnership History ................................................................................................... 219 | 9.8.3.2 | 9.8.3.2 Partnership History | 219
9.8.3.3 Future Projects .......................................................................................................... 219 | 9.8.3.3 | 9.8.3.3 Future Projects . | 219
9.8.4 San Diego Regional Fire & Emergency Services Foundation ............................................. 219 | 9.8.4 | 9.8.4 San Diego Regional Fire & Emergency Services Foundation . | 219
9.8.4.1 Overview ................................................................................................................... 219 | 9.8.4.1 | 9.8.4.1 Overview | 219
9.8.4.2 Partnership History ................................................................................................... 219 | 9.8.4.2 | 9.8.4.2 Partnership History | 219
9.8.4.3 Future Projects .......................................................................................................... 220 | 9.8.4.3 | 9.8.4.3 Future Projects . | 220
9.8.5 Inter-Tribal Long Term Recovery Foundation ................................................................... 220 | 9.8.5 | 9.8.5 Inter-Tribal Long Term Recovery Foundation | 220
9.8.5.1 Overview ................................................................................................................... 220 | 9.8.5.1 | 9.8.5.1 Overview | 220
9.8.5.2 Partnership History ................................................................................................... 220 | 9.8.5.2 | 9.8.5.2 Partnership History | 220
9.8.5.3 Future Projects .......................................................................................................... 220 | 9.8.5.3 | 9.8.5.3 Future Projects . | 220
9.8.6 San Diego County Fire ....................................................................................................... 220 | 9.8.6 | 9.8.6 San Diego County Fire | 220
9.8.6.1 Overview ................................................................................................................... 220 | 9.8.6.1 | 9.8.6.1 Overview | 220
9.8.6.2 Partnership History ................................................................................................... 221 | 9.8.6.2 | 9.8.6.2 Partnership History | 221
9.8.6.3 Future Projects .......................................................................................................... 221 | 9.8.6.3 | 9.8.6.3 Future Projects . | 221
9.9 Activities Based on Weather Conditions ................................................................................... 221 | 9.9 | 9.9 Activities Based on Weather Conditions . | 221
9.9.1 Overview ........................................................................................................................... 221 | 9.9.1 | 9.9.1 Overview | 221
9.9.2 Procedures ........................................................................................................................ 221 | 9.9.2 | 9.9.2 Procedures | 221
9.9.3 Scheduling ......................................................................................................................... 221 | 9.9.3 | 9.9.3 Scheduling | 221
9.9.4 Updates ............................................................................................................................. 222 | 9.9.4 | 9.9.4 Updates . | 222
9.10 Post-Fire Service Restoration .................................................................................................... 222 | 9.1 | 9.10 Post-Fire Service Restoration . | 222
9.10.1 Overview ........................................................................................................................... 222 | 9.10.1 | 9.10.1 Overview . | 222
9.10.2 Procedures ........................................................................................................................ 222 | 9.10.2 | 9.10.2 Procedures | 222
9.10.3 Scheduling ......................................................................................................................... 222 | 9.10.3 | 9.10.3 Scheduling | 222
9.10.4 Updates ............................................................................................................................. 222 | 9.10.4 | 9.10.4 Updates | 222
9.11 Quality Assurance and Quality Control of Vegetation Management (WMP.505) .................... 223 | 9.11 | 9.11 Quality Assurance and Quality Control of Vegetation Management (WMP.505) | 223
9.11.1 Overview, Objectives, and Targets ................................................................................... 223 | 9.11.1 | 9.11.1 Overview, Objectives, and Targets | 223
9.11.2 QA/QC Procedures ............................................................................................................ 225 | 9.11.2 | 9.11.2 QA/QC Procedures . | 225
9.11.3 Sample Sizes ...................................................................................................................... 225 | 9.11.3 | 9.11.3 Sample Sizes | 225
9.11.4 Pass Rate Calculation ........................................................................................................ 225 | 9.11.4 | 9.11.4 Pass Rate Calculation | 225
9.11.5 Other Metrics .................................................................................................................... 226 | 9.11.5 | 9.11.5 Other Metrics | 226
9.11.6 Documentation of Findings ............................................................................................... 226 | 9.11.6 | 9.11.6 Documentation of Findings | 226
9.11.7 Changes to QA/QC Since Last WMP and Planned Improvements .................................... 227 | 9.11.7 | 9.11.7 Changes to QA/QC Since Last WMP and Planned Improvements . | 227
9.12 Work Orders .............................................................................................................................. 227 | 9.12 | 9.12 Work Orders | 227
9.12.1 Priority Assignment ........................................................................................................... 227 | 9.12.1 | 9.12.1 Priority Assignment . | 227
9.12.2 Backlog Elimination ........................................................................................................... 227 | 9.12.2 | 9.12.2 Backlog Elimination . | 227
9.12.3 Trends ............................................................................................................................... 227 | 9.12.3 | 9.12.3 Trends . | 227
9.13 Workforce Planning (WMP.506) ............................................................................................... 229 | 9.13 | 9.13 Workforce Planning (WMP.506) | 229
9.13.1 Recruitment ...................................................................................................................... 232 | 9.13.1 | 9.13.1 Recruitment . | 232
9.13.2 Training and Retention...................................................................................................... 232 | 9.13.2 | 9.13.2 Training and Retention | 232
10 Situational Awareness and Forecasting ................................................................................... 234 | 10 | 10 Situational Awareness and Forecasting | 234
10.1 Targets....................................................................................................................................... 235 | 10.1 | 10.1 Targets | 235
10.1.1 Qualitative Targets ............................................................................................................ 235 | 10.1.1 | 10.1.1 Qualitative Targets . | 235
10.1.2 Quantitative Targets ......................................................................................................... 235 | 10.1.2 | 10.1.2 Quantitative Targets | 235
10.2 Environmental Monitoring Systems ......................................................................................... 237 | 10.2 | 10.2 Environmental Monitoring Systems . | 237
10.2.1 Existing Systems, Technologies, and Procedures .............................................................. 237 | 10.2.1 | 10.2.1 Existing Systems, Technologies, and Procedures . | 237
10.2.1.1 Weather Stations ...................................................................................................... 237 | 10.2.1.1 | 10.2.1.1 Weather Stations | 237
10.2.1.2 Air Quality Stations ................................................................................................... 237 | 10.2.1.2 | 10.2.1.2 Air Quality Stations . | 237
10.2.1.3 Fuel Moisture (WMP.1334) ....................................................................................... 238 | 10.2.1.3 | 10.2.1.3 Fuel Moisture (WMP.1334) | 238
10.2.2 Evaluation and Selection of New Systems ........................................................................ 238 | 10.2.2 | 10.2.2 Evaluation and Selection of New Systems | 238
10.2.3 Planned Improvements ..................................................................................................... 238 | 10.2.3 | 10.2.3 Planned Improvements | 238
10.2.4 Evaluating Activities .......................................................................................................... 239 | 10.2.4 | 10.2.4 Evaluating Activities | 239
10.3 Grid Monitoring Systems .......................................................................................................... 239 | 10.3 | 10.3 Grid Monitoring Systems | 239
10.3.1 Existing Systems, Technologies, and Procedures .............................................................. 239 | 10.3.1 | 10.3.1 Existing Systems, Technologies, and Procedures . | 239
10.3.2 Evaluation and Selection of New Systems ........................................................................ 242 | 10.3.2 | 10.3.2 Evaluation and Selection of New Systems | 242
10.3.3 Planned Improvements ..................................................................................................... 242 | 10.3.3 | 10.3.3 Planned Improvements | 242
10.3.4 Evaluating Activities .......................................................................................................... 242 | 10.3.4 | 10.3.4 Evaluating Activities | 242
10.4 Ignition Detection Systems ....................................................................................................... 243 | 10.4 | 10.4 Ignition Detection Systems . | 243
10.4.1 Existing Ignition Detection Sensors and Systems .............................................................. 243 | 10.4.1 | 10.4.1 Existing Ignition Detection Sensors and Systems | 243
10.4.1.1 Satellite Based Remote Sensing (WMP.971)............................................................. 243 | 10.4.1.1 | 10.4.1.1 Satellite Based Remote Sensing (WMP.971) | 243
10.4.1.2 Cameras (WMP.1343) ............................................................................................... 244 | 10.4.1.2 | 10.4.1.2 Cameras (WMP.1343) | 244
10.4.1.3 Fire Growth Potential Software ................................................................................ 245 | 10.4.1.3 | 10.4.1.3 Fire Growth Potential Software . | 245
10.4.2 Evaluation and Selection of New Detection Systems ....................................................... 246 | 10.4.2 | 10.4.2 Evaluation and Selection of New Detection Systems | 246
10.4.3 Planned Integration of New Ignition Detection Technologies .......................................... 246 | 10.4.3 | 10.4.3 Planned Integration of New Ignition Detection Technologies | 246
10.4.4 Evaluating Activities .......................................................................................................... 246 | 10.4.4 | 10.4.4 Evaluating Activities | 246
10.5 Weather Forecasting ................................................................................................................. 247 | 10.5 | 10.5 Weather Forecasting | 247
10.5.1 Existing Modeling Approach ............................................................................................. 247 | 10.5.1 | 10.5.1 Existing Modeling Approach | 247
10.5.1.1 Weather Research and Forecasting (WMP.541) ....................................................... 248 | 10.5.1.1 | 10.5.1.1 Weather Research and Forecasting (WMP.541) | 248
10.5.1.2 SAWTI (WMP.540)..................................................................................................... 248 | 10.5.1.2 | 10.5.1.2 SAWTI (WMP.540). | 248
10.5.2 Known Limitations of Existing Approach .......................................................................... 248 | 10.5.2 | 10.5.2 Known Limitations of Existing Approach . | 248
10.5.3 Planned Improvements ..................................................................................................... 248 | 10.5.3 | 10.5.3 Planned Improvements | 248
10.5.4 Evaluating Activities .......................................................................................................... 249 | 10.5.4 | 10.5.4 Evaluating Activities | 249
10.5.5 Weather Station Maintenance and Calibration ................................................................ 252 | 10.5.5 | 10.5.5 Weather Station Maintenance and Calibration . | 252
10.6 Fire Potential Index (WMP.450) ................................................................................................ 252 | 10.6 | 10.6 Fire Potential Index (WMP.450) | 252
10.6.1 Existing Calculation Approach and Use ............................................................................. 252 | 10.6.1 | 10.6.1 Existing Calculation Approach and Use | 252
10.6.2 Known Limitations of Existing Approach .......................................................................... 254 | 10.6.2 | 10.6.2 Known Limitations of Existing Approach . | 254
10.6.3 Planned Improvements ..................................................................................................... 254 | 10.6.3 | 10.6.3 Planned Improvements | 254
11 Emergency Preparedness, Collaboration, and Community Outreach ........................................ 255 | 11 | 11 Emergency Preparedness, Collaboration, and Community Outreach | 255
11.1 Targets....................................................................................................................................... 256 | 11.1 | 11.1 Targets | 256
11.1.1 Qualitative Targets ............................................................................................................ 256 | 11.1.1 | 11.1.1 Qualitative Targets . | 256
11.2 Emergency Preparedness and Recovery Plan ........................................................................... 258 | 11.2 | 11.2 Emergency Preparedness and Recovery Plan . | 258
11.2.1 Overview of Wildfire and PSPS Emergency Preparedness and Service Restoration ........ 258 | 11.2.1 | 11.2.1 Overview of Wildfire and PSPS Emergency Preparedness and Service Restoration | 258
11.2.1.1 Overview of Wildfire and PSPS Protocols, Policies, and Procedures ........................ 258 | 11.2.1.1 | 11.2.1.1 Overview of Wildfire and PSPS Protocols, Policies, and Procedures | 258
11.2.1.2 Key Personnel, Qualifications, and Training ............................................................. 261 | 11.2.1.2 | 11.2.1.2 Key Personnel, Qualifications, and Training | 261
11.2.1.3 Memorandum of Agreements .................................................................................. 262 | 11.2.1.3 | 11.2.1.3 Memorandum of Agreements | 262
11.2.2 Planning and Allocation of Resources ............................................................................... 263 | 11.2.2 | 11.2.2 Planning and Allocation of Resources | 263
11.3 External Collaboration and Coordination ................................................................................. 264 | 11.3 | 11.3 External Collaboration and Coordination | 264
11.3.1 Communication Strategy with Public Safety Partners ...................................................... 264 | 11.3.1 | 11.3.1 Communication Strategy with Public Safety Partners | 264
11.3.2 Collaboration on Local and Regional Wildfire Mitigation Planning .................................. 266 | 11.3.2 | 11.3.2 Collaboration on Local and Regional Wildfire Mitigation Planning . | 266
11.3.3 Collaboration with Tribal Governments ............................................................................ 268 | 11.3.3 | 11.3.3 Collaboration with Tribal Governments | 268
11.4 Public Communication, Outreach, and Education Awareness.................................................. 270 | 11.4 | 11.4 Public Communication, Outreach, and Education Awareness | 270
11.4.1 Protocols for Emergency Communications ....................................................................... 271 | 11.4.1 | 11.4.1 Protocols for Emergency Communications . | 271
11.4.2 Messaging ......................................................................................................................... 273 | 11.4.2 | 11.4.2 Messaging | 273
11.4.3 Outreach and Education Awareness Activities ................................................................. 274 | 11.4.3 | 11.4.3 Outreach and Education Awareness Activities . | 274
11.4.4 Engagement with Access and Functional Needs Populations .......................................... 276 | 11.4.4 | 11.4.4 Engagement with Access and Functional Needs Populations | 276
11.4.4.1 Summary of Key AFN Demographics ........................................................................ 276 | 11.4.4.1 | 11.4.4.1 Summary of Key AFN Demographics | 276
11.4.4.2 Evaluation of Challenges and Needs during a Wildfire or PSPS Event ...................... 277 | 11.4.4.2 | 11.4.4.2 Evaluation of Challenges and Needs during a Wildfire or PSPS Event | 277
11.4.4.3 Plans to Address Needs of the AFN Customer Base ................................................. 277 | 11.4.4.3 | 11.4.4.3 Plans to Address Needs of the AFN Customer Base | 277
11.4.5 Engagement with Tribal Nations ....................................................................................... 277 | 11.4.5 | 11.4.5 Engagement with Tribal Nations . | 277
11.4.6 Current Gaps and Limitations ........................................................................................... 278 | 11.4.6 | 11.4.6 Current Gaps and Limitations | 278
11.5 Customer Support in Wildfire and PSPS Emergencies .............................................................. 279 | 11.5 | 11.5 Customer Support in Wildfire and PSPS Emergencies | 279
11.5.1 Outage Reporting .............................................................................................................. 279 | 11.5.1 | 11.5.1 Outage Reporting . | 279
11.5.2 Support for Low-Income Customers ................................................................................. 279 | 11.5.2 | 11.5.2 Support for Low-Income Customers . | 279
11.5.3 Billing Adjustments ........................................................................................................... 280 | 11.5.3 | 11.5.3 Billing Adjustments . | 280
11.5.4 Deposit Waivers ................................................................................................................ 280 | 11.5.4 | 11.5.4 Deposit Waivers | 280
11.5.5 Extended Payment Plans ................................................................................................... 280 | 11.5.5 | 11.5.5 Extended Payment Plans . | 280
11.5.6 Suspension of Disconnection and Nonpayment Fees ....................................................... 280 | 11.5.6 | 11.5.6 Suspension of Disconnection and Nonpayment Fees | 280
11.5.7 Repair Processing and Timing ........................................................................................... 280 | 11.5.7 | 11.5.7 Repair Processing and Timing | 280
11.5.8 Community Assistance Locations and Services ................................................................. 280 | 11.5.8 | 11.5.8 Community Assistance Locations and Services . | 280
11.5.9 Medical Baseline Support Services ................................................................................... 282 | 11.5.9 | 11.5.9 Medical Baseline Support Services | 282
11.5.10 Access to Electrical Corporation Representatives ........................................................ 282 | 11.5.10 | 11.5.10 Access to Electrical Corporation Representatives | 282
12 Enterprise Systems ................................................................................................................. 284 | 12 | 12 Enterprise Systems . | 284
12.1 | 12.1 | 12.1 | 2.1
12.1.1 Qualitative Targets ............................................................................................................ 284 | 12.1.1 | 12.1.1 Qualitative Targets . | 284
12.2 Summary of Enterprise Systems ............................................................................................... 286 | 12.2 | 12.2 Summary of Enterprise Systems . | 286
13 Lessons Learned ..................................................................................................................... 289 | 13 | 13 Lessons Learned . | 289
13.1 Description and Summary of Lessons Learned ......................................................................... 295 | 13.1 | 13.1 Description and Summary of Lessons Learned . | 295
13.1.1 Feedback from Government Agencies and Stakeholders ................................................. 295 | 13.1.1 | 13.1.1 Feedback from Government Agencies and Stakeholders | 295
13.1.2 Collaboration with Other Electrical Corporations and Industry Experts .......................... 295 | 13.1.2 | 13.1.2 Collaboration with Other Electrical Corporations and Industry Experts | 295
13.1.3 PSPS or Outage Events ...................................................................................................... 295 | 13.1.3 | 13.1.3 PSPS or Outage Events | 295
13.1.4 Outcomes from Previous WMP Cycles ............................................................................. 296 | 13.1.4 | 13.1.4 Outcomes from Previous WMP Cycles | 296
13.1.5 Areas for Continued Improvement ................................................................................... 296 | 13.1.5 | 13.1.5 Areas for Continued Improvement | 296
13.2 Working Group Meetings .......................................................................................................... 296 | 13.2 | 13.2 Working Group Meetings | 296
13.2.1 PSPS Working Group ......................................................................................................... 296 | 13.2.1 | 13.2.1 PSPS Working Group | 296
13.2.2 Risk Modeling Working Group .......................................................................................... 296 | 13.2.2 | 13.2.2 Risk Modeling Working Group . | 296
13.2.3 Grid Hardening Working Groups ....................................................................................... 296 | 13.2.3 | 13.2.3 Grid Hardening Working Groups | 296
13.2.4 Enhanced Vegetation Management Working Group ........................................................ 297 | 13.2.4 | 13.2.4 Enhanced Vegetation Management Working Group | 297
13.3 Discontinued Activities .............................................................................................................. 298 | 13.3 | 13.3 Discontinued Activities | 298
OEIS Table 3-1: List of Risks and Risk Drivers to Prioritize .......................................................................... 11 | OEIS Table 3-1 | 3-1: List of Risks and Risk Drivers to Prioritize 11
OEIS Table 3-2: Self-Identified Performance Metrics Table ........................................................................ 14 | OEIS Table 3-2 | 3-2: Self-Identified Performance Metrics Table . 14
OEIS Table 3-3: Summary of Projected WMP Expenditures ....................................................................... 16 | OEIS Table 3-3 | 3-3: Summary of Projected WMP Expenditures 16
OEIS Table 4-1: High-Level Service Territory Components ......................................................................... 19 | OEIS Table 4-1 | 4-1: High-Level Service Territory Components .. 19
OEIS Table 4-2: Catastrophic Electrical Corporation Wildfires ................................................................... 21 | OEIS Table 4-2 | 4-2: Catastrophic Electrical Corporation Wildfires . 21
OEIS Table 4-3: Frequently De-energized Circuits ...................................................................................... 23 | OEIS Table 4-3 | 4-3: Frequently De-energized Circuits 23
OEIS Table 5-1: Risk Modeling Assumptions and Limitations ..................................................................... 43 | OEIS Table 5-1 | 5-1: Risk Modeling Assumptions and Limitations 43
OEIS Table 5-2: Summary of Design Scenarios ........................................................................................... 49 | OEIS Table 5-2 | 5-2: Summary of Design Scenarios .. 49
OEIS Table 5-3: Summary of Extreme-Event Scenarios .............................................................................. 52 | OEIS Table 5-3 | 5-3: Summary of Extreme-Event Scenarios 52
OEIS Table 5-4: Summary of Risk Models ................................................................................................... 53 | OEIS Table 5-4 | 5-4: Summary of Risk Models .. 53
OEIS Table 5-5: Summary of Top-Risk Circuits, Segments, or Spans .......................................................... 60 | OEIS Table 5-5 | 5-5: Summary of Top-Risk Circuits, Segments, or Spans 60
OEIS Table 5-6: Utility Risk Assessment Improvement Plan ....................................................................... 79 | OEIS Table 5-6 | 5-6: Utility Risk Assessment Improvement Plan 79
OEIS Table 6-1: List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk ................................................................................................................................................... 84 | OEIS Table 6-1 | 6-1: List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk 84
OEIS Table 6-2: Stakeholder Roles and Responsibilities in the Decision-Making Process ........................ 106 | OEIS Table 6-2 | 6-2: Stakeholder Roles and Responsibilities in the Decision-Making Process 106
OEIS Table 6-3: Risk Impact of Activities ................................................................................................... 111 | OEIS Table 6-3 | 6-3: Risk Impact of Activities .. 111
OEIS Table 6-4: Summary of Risk Reduction for Top-Risk Circuits ............................................................ 116 | OEIS Table 6-4 | 6-4: Summary of Risk Reduction for Top-Risk Circuits .. 116
OEIS Table 8-1: Grid Design, Operations, and Maintenance Targets by Year .......................................... 126 | OEIS Table 8-1 | 8-1: Grid Design, Operations, and Maintenance Targets by Year 126
OEIS Table 8-2: Asset Inspection Frequency, Method, and Criteria ......................................................... 151 | OEIS Table 8-2 | 8-2: Asset Inspection Frequency, Method, and Criteria .. 151
OEIS Table 8-3: Grid Design, Asset Inspections, and Maintenance QA and QC Program Objectives ....... 177 | OEIS Table 8-3 | 8-3: Grid Design, Asset Inspections, and Maintenance QA and QC Program Objectives . 177
OEIS Table 8-4: Grid Design, Asset Inspections, and Maintenance QA and QC Activity Targets .............. 179 | OEIS Table 8-4 | 8-4: Grid Design, Asset Inspections, and Maintenance QA and QC Activity Targets 179
OEIS Table 8-5: Number of Past Due Asset Work Orders Categorized by Age ......................................... 193 | OEIS Table 8-5 | 8-5: Number of Past Due Asset Work Orders Categorized by Age .. 193
OEIS Table 8-6: Number of Past Due Asset Work Orders Categorized by Age for Priority Levels ............ 194 | OEIS Table 8-6 | 8-6: Number of Past Due Asset Work Orders Categorized by Age for Priority Levels . 194
OEIS Table 8-7: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years ........................... 194 | OEIS Table 8-7 | 8-7: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years 194
OEIS Table 8-8: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years ........................... 196 | OEIS Table 8-8 | 8-8: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years 196
OEIS Table 9-1: Vegetation Management Targets by Year (Non-inspection Targets) .............................. 207 | OEIS Table 9-1 | 9-1: Vegetation Management Targets by Year (Non-inspection Targets) 207
OEIS Table 9-2: Vegetation Inspections and Pole Clearing Targets by Year ............................................. 208 | OEIS Table 9-2 | 9-2: Vegetation Inspections and Pole Clearing Targets by Year 208
OEIS Table 9-3: Vegetation Management Inspection Frequency, Method, and Criteria ......................... 209 | OEIS Table 9-3 | 9-3: Vegetation Management Inspection Frequency, Method, and Criteria . 209
OEIS Table 9-4: Partnerships in Vegetation Management ....................................................................... 216 | OEIS Table 9-4 | 9-4: Partnerships in Vegetation Management 216
OEIS Table 9-5: Vegetation Management QA and QC Program Objectives ............................................. 224 | OEIS Table 9-5 | 9-5: Vegetation Management QA and QC Program Objectives 224
OEIS Table 9-6: Vegetation Management QA and QC Activity Targets .................................................... 224 | OEIS Table 9-6 | 9-6: Vegetation Management QA and QC Activity Targets .. 224
OEIS Table 9-7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier ................................................................................................................................................... 228 | OEIS Table 9-7 | 9-7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier 228
OEIS Table 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels ............................................................................................................................................ 228 | OEIS Table 9-8 | 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels . 228
OEIS Table 9-9: Vegetation Management Qualifications and Training ..................................................... 229 | OEIS Table 9-9 | 9-9: Vegetation Management Qualifications and Training 229
OEIS Table 10-1: Situational Awareness Targets by Year ......................................................................... 235 | OEIS Table 10-1 | 10-1: Situational Awareness Targets by Year .. 235
OEIS Table 10-2: Environmental Monitoring Systems .............................................................................. 237 | OEIS Table 10-2 | 10-2: Environmental Monitoring Systems 237
OEIS Table 10-3: Grid Operation Monitoring Systems .............................................................................. 239 | OEIS Table 10-3 | 10-3: Grid Operation Monitoring Systems 239
OEIS Table 10-4: Ignition Detection Systems Currently Deployed ............................................................ 243 | OEIS Table 10-4 | 10-4: Ignition Detection Systems Currently Deployed .. 243
OEIS Table 10-5: Fire Potential Features .................................................................................................. 253 | OEIS Table 10-5 | 10-5: Fire Potential Features . 253
OEIS Table 11-1: Emergency Preparedness and Community Outreach Targets by Year .......................... 256 | OEIS Table 11-1 | 11-1: Emergency Preparedness and Community Outreach Targets by Year .. 256
OEIS Table 11-2: Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan ......................................................................................................................................... 263 | OEIS Table 11-2 | 11-2: Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan . 263
OEIS Table 11-3: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners ..................................................................................................................................................... 265 | OEIS Table 11-3 | 11-3: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners 265
OEIS Table 11-4: Gaps and Limitations in Communication Coordination with Public Safety Partners .... 266 | OEIS Table 11-4 | 11-4: Gaps and Limitations in Communication Coordination with Public Safety Partners . 266
OEIS Table 11-5: Collaboration in Local and Regional Wildfire Mitigation Planning ................................ 267 | OEIS Table 11-5 | 11-5: Collaboration in Local and Regional Wildfire Mitigation Planning 267
OEIS Table 11-6: Key Gaps and Limitations in Collaborating on Local and Regional Wildfire Mitigation Planning .................................................................................................................................................... 268 | OEIS Table 11-6 | 11-6: Key Gaps and Limitations in Collaborating on Local and Regional Wildfire Mitigation Planning . 268
OEIS Table 11-7: Collaboration with Tribal Agencies ................................................................................ 268 | OEIS Table 11-7 | 11-7: Collaboration with Tribal Agencies .. 268
OEIS Table 11-8: Key Gaps and Limitations in Collaborating with Tribal Agencies ................................... 270 | OEIS Table 11-8 | 11-8: Key Gaps and Limitations in Collaborating with Tribal Agencies 270
OEIS Table 11-9: Protocols for Emergency Communication to Stakeholder Groups ............................... 272 | OEIS Table 11-9 | 11-9: Protocols for Emergency Communication to Stakeholder Groups . 272
OEIS Table 11-10: List of Target Communities .......................................................................................... 274 | OEIS Table 11-1 | 11-10: List of Target Communities . 274
OEIS Table 11-11: Key Gaps and Limitations in Public Emergency Communication Strategy .................. 278 | OEIS Table 11-1 | 11-11: Key Gaps and Limitations in Public Emergency Communication Strategy .. 278
OEIS Table 12-1: Enterprise Systems Targets ........................................................................................... 284 | OEIS Table 12-1 | 12-1: Enterprise Systems Targets .. 284
OEIS Table 13-1: Lessons Learned ............................................................................................................. 290 | OEIS Table 13-1 | 13-1: Lessons Learned . 290
OEIS Table 13-2: Lessons Learned from Discontinued Activities .............................................................. 299 | OEIS Table 13-2 | 13-2: Lessons Learned from Discontinued Activities . 299
SDGE Table 5-1: CoRE Attributes and Dollar Equivalencies ........................................................................ 27 | SDGE Table 5-1 | 5-1: CoRE Attributes and Dollar Equivalencies . 27
SDGE Table 5-2: Safety Sub-Attributes, Values, and Dollar Equivalencies ................................................. 28 | SDGE Table 5-2 | 5-2: Safety Sub-Attributes, Values, and Dollar Equivalencies .. 28
SDGE Table 5-3: Risk Components for LoRE ............................................................................................... 37 | SDGE Table 5-3 | 5-3: Risk Components for LoRE . 37
SDGE Table 5-4: Attributes for Wildfire Consequence ............................................................................... 38 | SDGE Table 5-4 | 5-4: Attributes for Wildfire Consequence . 38
SDGE Table 5-5: Attributes for PSPS Consequence ..................................................................................... 39 | SDGE Table 5-5 | 5-5: Attributes for PSPS Consequence . 39
SDGE Table 5-6: Attributes for PEDS Consequence .................................................................................... 40 | SDGE Table 5-6 | 5-6: Attributes for PEDS Consequence 40
SDGE Table 5-7: Pre-Mitigation Wildfire, PSPS, PEDS, and Overall Utility Risk estimates for the Service Territory ...................................................................................................................................................... 42 | SDGE Table 5-7 | 5-7: Pre-Mitigation Wildfire, PSPS, PEDS, and Overall Utility Risk estimates for the Service Territory . 42
SDGE Table 5-8: WiNGS-Planning Third Party Recommendations ............................................................. 62 | SDGE Table 5-8 | 5-8: WiNGS-Planning Third Party Recommendations 62
SDGE Table 5-9: WiNGS-Ops Risk Modeling Updates ................................................................................. 66 | SDGE Table 5-9 | 5-9: WiNGS-Ops Risk Modeling Updates 66
SDGE Table 6-1: Potential Mitigation Activities for Risk Drivers included in List of Prioritized Circuit Segments ..................................................................................................................................................... 89 | SDGE Table 6-1 | 6-1: Potential Mitigation Activities for Risk Drivers included in List of Prioritized Circuit Segments 89
SDGE Table 6-2: Interim Mitigations Initiatives ........................................................................................ 117 | SDGE Table 6-2 | 6-2: Interim Mitigations Initiatives .. 117
SDGE Table 8-1: Risk Event Rate with Pending Infractions ....................................................................... 154 | SDGE Table 8-1 | 8-1: Risk Event Rate with Pending Infractions 154
SDGE Table 8-2: Maintenance and Replacement Strategies .................................................................... 172 | SDGE Table 8-2 | 8-2: Maintenance and Replacement Strategies .. 172
SDGE Table 8-3: Timeframe for Remediation of Distribution Findings .................................................... 174 | SDGE Table 8-3 | 8-3: Timeframe for Remediation of Distribution Findings .. 174
SDGE Table 8-4: Timeframe for Remediation of Transmission Findings .................................................. 175 | SDGE Table 8-4 | 8-4: Timeframe for Remediation of Transmission Findings 175
SDGE Table 8-5: Ignition Rate and Failure Rate ........................................................................................ 177 | SDGE Table 8-5 | 8-5: Ignition Rate and Failure Rate .. 177
SDGE Table 8-6: Faults by HFTD Tier and Weather Condition .................................................................. 197 | SDGE Table 8-6 | 8-6: Faults by HFTD Tier and Weather Condition 197
SDGE Table 8-7: 5-Year Average Ignition Rate .......................................................................................... 197 | SDGE Table 8-7 | 8-7: 5-Year Average Ignition Rate . 197
SDGE Table 8-8: Estimated Faults and Ignitions Avoided ......................................................................... 197 | SDGE Table 8-8 | 8-8: Estimated Faults and Ignitions Avoided .. 197
SDGE Table 8-9: Workforce Planning, Asset Inspections .......................................................................... 201 | SDGE Table 8-9 | 8-9: Workforce Planning, Asset Inspections 201
SDGE Table 8-10: Workforce Planning, Grid Hardening ........................................................................... 203 | SDGE Table 8-10 | 8-10: Workforce Planning, Grid Hardening . 203
SDGE Table 8-11: Workforce Planning, Risk Event Inspection .................................................................. 205 | SDGE Table 8-11 | 8-11: Workforce Planning, Risk Event Inspection 205
SDGE Table 9-1: Fire Safe Council of San Diego County Project History .................................................. 217 | SDGE Table 9-1 | 9-1: Fire Safe Council of San Diego County Project History 217
SDGE Table 9-2: Viejas Band of Kumeyaay Indians Project History .......................................................... 218 | SDGE Table 9-2 | 9-2: Viejas Band of Kumeyaay Indians Project History 218
SDGE Table 9-3: Campo Band of Diegueno Mission Indians ..................................................................... 219 | SDGE Table 9-3 | 9-3: Campo Band of Diegueno Mission Indians 219
SDGE Table 9-4: San Diego County Fire Project History ........................................................................... 221 | SDGE Table 9-4 | 9-4: San Diego County Fire Project History . 221
SDGE Table 10-1: Five-Year Average Ignition Rate (2019-2023) .............................................................. 254 | SDGE Table 10-1 | 10-1: Five-Year Average Ignition Rate (2019-2023) . 254
SDGE Table 11-1: CRC Locations and Services .......................................................................................... 281 | SDGE Table 11-1 | 11-1: CRC Locations and Services . 281
Figure 1-1: 2026-2028 Expected Risk Reduction .......................................................................................... 3 | Figure 1-1 | 1-1: 2026-2028 Expected Risk Reduction . 3
Figure 1-2: Long-Term Risk Reduction Approach ......................................................................................... 4 | Figure 1-2 | 1-2: Long-Term Risk Reduction Approach 4
Figure 1-3: Enterprise Risk Management Framework for Development of the WMP ................................. 5 | Figure 1-3 | 1-3: Enterprise Risk Management Framework for Development of the WMP . 5
Figure 3-1: Summary of Projected WMP Expenditures .............................................................................. 16 | Figure 3-1 | 3-1: Summary of Projected WMP Expenditures 16
Figure 4-1: Utility Service Territory of the Enterprise Risk Management Framework ............................... 19 | Figure 4-1 | 4-1: Utility Service Territory of the Enterprise Risk Management Framework . 19
Figure 4-2: Service Territory (polygons) and Distribution of Customers Served ........................................ 20 | Figure 4-2 | 4-2: Service Territory (polygons) and Distribution of Customers Served . 20
Figure 4-3: Frequently De-energized Circuits ............................................................................................. 22 | Figure 4-3 | 4-3: Frequently De-energized Circuits . 22
Figure 5-1: Enterprise Risk Management Framework ................................................................................ 26 | Figure 5-1 | 5-1: Enterprise Risk Management Framework .. 26
Figure 5-2: Enterprise CoRE Attributes and Sub-Attributes ........................................................................ 27 | Figure 5-2 | 5-2: Enterprise CoRE Attributes and Sub-Attributes . 27
Figure 5-3: Risk Identification Step of the Enterprise Risk Management Framework ................................ 31 | Figure 5-3 | 5-3: Risk Identification Step of the Enterprise Risk Management Framework 31
Figure 5-4: Enterprise Utility Risk Overview ............................................................................................... 32 | Figure 5-4 | 5-4: Enterprise Utility Risk Overview . 32
Figure 5-5: Risk Analysis Step of the Enterprise Risk Management Framework ........................................ 34 | Figure 5-5 | 5-5: Risk Analysis Step of the Enterprise Risk Management Framework . 34
Figure 5-6: WiNGS-Planning and Ops Calculation Schematic ..................................................................... 36 | Figure 5-6 | 5-6: WiNGS-Planning and Ops Calculation Schematic 36
Figure 5-7: SDG&E Convex Risk Aversion Function ..................................................................................... 42 | Figure 5-7 | 5-7: SDG&E Convex Risk Aversion Function . 42
Figure 5-8: HFTD Risk Including Risk Aversion Attitude .............................................................................. 43 | Figure 5-8 | 5-8: HFTD Risk Including Risk Aversion Attitude 43
Figure 5-9: WiNGS-Ops Fire Visualization Platform Screenshot ................................................................. 48 | Figure 5-9 | 5-9: WiNGS-Ops Fire Visualization Platform Screenshot .. 48
Figure 5-10: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ......... 57 | Figure 5-10 | 5-10: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework . 57
Figure 5-11: Higher-Risk Urban Areas in Relation to HFTD ......................................................................... 58 | Figure 5-11 | 5-11: Higher-Risk Urban Areas in Relation to HFTD .. 58
Figure 5-12: Map of Service Territory with HFTD Circuit-Segments Categorized by Mean Overall Risk (as of 2025) ....................................................................................................................................................... 59 | Figure 5-12 | 5-12: Map of Service Territory with HFTD Circuit-Segments Categorized by Mean Overall Risk (as of 2025) .. 59
Figure 5-13: Independent Review Process ................................................................................................. 61 | Figure 5-13 | 5-13: Independent Review Process 61
Figure 6-1: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ........... 82 | Figure 6-1 | 6-1: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework 82
Figure 6-2: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk .................................. 100 | Figure 6-2 | 6-2: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk .. 100
Figure 6-3: Risk Mitigation Plan Development & Documentation Step of the Enterprise Risk Management Framework ................................................................................................................................................ 109 | Figure 6-3 | 6-3: Risk Mitigation Plan Development & Documentation Step of the Enterprise Risk Management Framework 109
Figure 6-4: Wildfire Hardening Targets ..................................................................................................... 110 | Figure 6-4 | 6-4: Wildfire Hardening Targets . 110
Figure 6-5: Estimated Wildfire Risk Reduction 2007-2037 ....................................................................... 110 | Figure 6-5 | 6-5: Estimated Wildfire Risk Reduction 2007-2037 110
Figure 7-1: PSPS Decision-Making Framework ......................................................................................... 121 | Figure 7-1 | 7-1: PSPS Decision-Making Framework 121
Figure 8-1: Risk-Informed Investment decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework .................................................................................................................. 124 | Figure 8-1 | 8-1: Risk-Informed Investment decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework . 124
Figure 8-2: Distribution Detailed Overhead Inspections Process Flow ..................................................... 153 | Figure 8-2 | 8-2: Distribution Detailed Overhead Inspections Process Flow 153
Figure 8-3: Transmission Detailed Overhead Inspections Process Flow ................................................... 156 | Figure 8-3 | 8-3: Transmission Detailed Overhead Inspections Process Flow . 156
Figure 8-4: Transmission Infrared Inspections Process Flow .................................................................... 158 | Figure 8-4 | 8-4: Transmission Infrared Inspections Process Flow .. 158
Figure 8-5: Wood Pole Intrusive Inspections Process Flow (Transmission and Distribution) ................... 160 | Figure 8-5 | 8-5: Wood Pole Intrusive Inspections Process Flow (Transmission and Distribution) 160
Figure 8-6: Risk-Informed Drone Inspections Process Flow ..................................................................... 163 | Figure 8-6 | 8-6: Risk-Informed Drone Inspections Process Flow 163
Figure 8-7: RIDI Inspection Prioritization Model ....................................................................................... 165 | Figure 8-7 | 8-7: RIDI Inspection Prioritization Model . 165
Figure 8-8: Distribution Patrol Inspections Process Flow ......................................................................... 166 | Figure 8-8 | 8-8: Distribution Patrol Inspections Process Flow .. 166
Figure 8-9: Transmission Overhead Patrol Inspections Process Flow ...................................................... 168 | Figure 8-9 | 8-9: Transmission Overhead Patrol Inspections Process Flow . 168
Figure 8-10: Substation Patrol Inspection Workflow ................................................................................ 170 | Figure 8-10 | 8-10: Substation Patrol Inspection Workflow .. 170
Figure 8-11: Asset Criticality and Maintenance/Replacement Strategies ................................................ 172 | Figure 8-11 | 8-11: Asset Criticality and Maintenance/Replacement Strategies . 172
Figure 8-12: Open Work Orders: Corrective Maintenance ....................................................................... 190 | Figure 8-12 | 8-12: Open Work Orders: Corrective Maintenance 190
Figure 8-13: Annual Percentage of Deferred Work Orders ...................................................................... 193 | Figure 8-13 | 8-13: Annual Percentage of Deferred Work Orders . 193
Figure 8-14: Work Orders by Number of Days Past Due .......................................................................... 193 | Figure 8-14 | 8-14: Work Orders by Number of Days Past Due 193
Figure 8-15: Results of Reclosure Protocols in Fault Avoidance ............................................................... 198 | Figure 8-15 | 8-15: Results of Reclosure Protocols in Fault Avoidance 198
Figure 10-1: Smoke Detection Image Identified by AI Smoke Detection Algorithm ................................. 245 | Figure 10-1 | 10-1: Smoke Detection Image Identified by AI Smoke Detection Algorithm . 245
Figure 10-2: Historical Major Wildfire Correlation to FPI ......................................................................... 249 | Figure 10-2 | 10-2: Historical Major Wildfire Correlation to FPI .. 249
Figure 10-3: SAWTI Across Time and Incidences of Major Wildfires ........................................................ 250 | Figure 10-3 | 10-3: SAWTI Across Time and Incidences of Major Wildfires . 250
Figure 10-4: Wind Gust Machine Learning Validation for West Alpine .................................................... 251 | Figure 10-4 | 10-4: Wind Gust Machine Learning Validation for West Alpine .. 251
Figure 10-5: Example of Machine Learning Gust Forecast Model Output ............................................... 251 | Figure 10-5 | 10-5: Example of Machine Learning Gust Forecast Model Output 251
Figure 11-1: EOC Activation Levels ........................................................................................................... 259 | Figure 11-1 | 11-1: EOC Activation Levels .. 259
Figure 11-2: Wildfire and PSPS Emergency Response Phases .................................................................. 260 | Figure 11-2 | 11-2: Wildfire and PSPS Emergency Response Phases 260
Figure 13-1: Monitoring & Review Step of the Enterprise Risk Management Framework ...................... 289 | Figure 13-1 | 13-1: Monitoring & Review Step of the Enterprise Risk Management Framework 289
Appendix A: Definitions | Appendix A | Definitions
Appendix B: Supporting Documentation for Risk Methodology and Assessment | Appendix B | Supporting Documentation for Risk Methodology and Assessment
Appendix C: Additional Maps | Appendix C | Additional Maps
Appendix D: Areas for Continued Improvement | Appendix D | Areas for Continued Improvement
Appendix E: Referenced Regulations, Codes, and Standards | Appendix E | Referenced Regulations, Codes, and Standards
Appendix F: Tables | Appendix F | Tables
Appendix G: Cost Benefit and Risk Reduction Supporting Data | Appendix G | Cost Benefit and Risk Reduction Supporting Data
Appendix H: 2025 Plan to Support Populations with Access and Functional Needs During Public Safety Power Shutoffs | Appendix H | 2025 Plan to Support Populations with Access and Functional Needs During Public Safety Power Shutoffs

## DR Count (hidden)
Data Requests
#REF! | #REF! | #REF! | Count = | #REF! | *Check Range When Updating*
#REF! | #REF! | #REF!
#REF! | #REF! | #REF! | Jan | 0
#REF! | #REF! | #REF! | Feb | 0
#REF! | #REF! | #REF! | Mar | #REF!
#REF! | #REF! | #REF! | Apr | #REF!
#REF! | #REF! | #REF! | May | 3
#REF! | #REF! | #REF! | Jun | 1
#REF! | #REF! | #REF! | Jul
#REF! | #REF! | #REF! | Aug
#REF! | #REF! | #REF! | Sep
#REF! | #REF! | #REF!
#REF! | #REF! | #REF! |  | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
- | - | 0
0 | 0 | 0

## Analytics (hidden)
|  | 2024 WMP Data Requests (Case Related) |  | 2024 WMP Data Requests (Non-Case Related) |  | Party | Non-Case DR Name | Question #
# of Questions
Row Labels | Count of Data Requests | # of DRs | 1 | # of DRs | 52
0 | 171 | # of DR Questions | #REF! | # of DR Questions | 176
Grand Total | 171
|  | # of Requests per Party | 0 | # of Requests per Party | 52
|  | CalPA | 0 | CalPA | 3
|  | MGRA | 0 | MGRA | 1
|  | OEIS | 0 | SPD | 0
|  | GPI | 0 | OEIS | 8
|  | SPD | 0 | IE | 40
|  |  |  | 4LEAF | Ask Shaun G
|  | # of Questions per Party | 342
|  | CalPA | 342 | # of Questions per Party | 176
|  | MGRA | 0 | CalPA | 20
|  | OEIS | 0 | MGRA | 7
|  | GPI | 0 | SPD | 0
|  | SPD | 0 | OEIS | 106
|  |  |  | IE | 43
|  | 2024-06-24 |  | 4LEAF | Ask Shaun G
|  | Count Check |  | 2024-06-24
|  | # of DRs | #REF! | Manually Input
|  | # of DR Questions | 170