## 5Yr SAIFI and SAIDI
FY | Sum of CI | Sum of CMI | Sum of SAIFI | 5-Year Ave. SAIFI | Sum of SAIDI | 5-Year Ave. SAIDI | NO LONGER USED
2000 | 53328 | 3683689 | 1.42 | 0 | 98.02 | 0
2001 | 92647 | 6629840 | 2.44 | 0 | 174.29 | 0
2002 | 69139 | 5947725 | 1.8 | 0 | 154.75 | 0
2003 | 60739 | 5686958 | 1.57 | 0 | 145.73 | 0
2004 | 59169 | 4867092 | 1.49 | 1.744 | 122.78 | 139.114
2005 | 72356 | 8667063 | 1.8 | 1.82 | 215.56 | 162.622
2006 | 94190 | 12251231 | 2.37 | 1.806 | 308.42 | 189.448
2007 | 97553 | 9538500 | 2.49 | 1.944 | 243.05 | 207.108
2008 | 83027 | 9542625 | 2.04 | 2.038 | 234.79 | 224.92
2009 | 78037 | 7613909 | 1.92 | 2.124 | 186.91 | 237.746
2010 | 55636 | 6536445 | 1.34 | 2.032 | 157.76 | 226.186
2011 | 61728 | 6803781 | 1.49 | 1.856 | 163.76 | 197.254
2012 | 48358 | 4464691 | 1.16 | 1.59 | 106.73 | 169.99
2013 | 68817 | 6834349 | 1.6212 | 1.5062 | 162.2762 | 155.4872
2014 | 63877.6667 | 7145798.3333 | 1.5364 | 1.4295 | 172.1151 | 152.5283
2015 | 19963 | 3045226.2 | 0.58 | 1.2775 | 61.05 | 133.1863
CY | Sum of CI | Sum of CMI | Sum of SAIFI (right) | 5-Year Avg. SAIFI (right) | Sum of SAIDI (left) | 5-Year Avg. SAIDI (left)
2000
2001
2002
2003
2004
2005
2006
2007
2008
2009
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020 | 38628 | 4736058 | 1.5764 | 1.5764 | 181.64 | 181.64
2021 | 31534 | 5208246 | 2.202 | 1.8892 | 455.6588 | 318.6494
2022 | 27258 | 3758826 | 2.308 | 2.0288 | 378.5484 | 338.6157
2023 | 32435 | 4331882.66 | 1.4532 | 1.8849 | 219.5669 | 308.8535
2024 | 33884 | 3642292.23 | 1.4651 | 1.8009 | 207.5786 | 288.5985
2025 Projection | 19963 | 3045226.2 | 1.4933 | 1.7843 | 244.7211 | 301.2148

## Live Indices
SAIFI
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 0.0035769 | 0.21448 | 0.032625 | 0.076498 | 0.05691 | 0.021967 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40606 | 1.4933
2024 Results | 0.1144 | 0.2034 | 0.42211 | 0.097446 | 0.005763 | 0.053459 | 0.088792 | 0.050707 | 0.12568 | 0.074555 | 0.18809 | 0.040737 | 1.4651
5 Year Average | 0.28932 | 0.078006 | 0.13287 | 0.053432 | 0.050292 | 0.10993 | 0.28343 | 0.13409 | 0.14853 | 0.15232 | 0.10515 | 0.26367 | 1.801
Projection | 0.0035769 | 0.21448 | 0.032625 | 0.076498 | 0.05691 | 0.021967 | 0.28343 | 0.13409 | 0.14853 | 0.15232 | 0.10515 | 0.26367
SAIDI
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 0.50043 | 33.0237 | 2.817 | 7.9904 | 14.4639 | 3.146 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9413 | 244.7211
2024 Results | 6.1991 | 11.591 | 96.8843 | 13.195 | 1.2513 | 5.4391 | 14.506 | 9.1153 | 13.8214 | 3.6265 | 25.4649 | 6.4847 | 207.5786
5 Year Average | 39.2428 | 10.2757 | 26.0437 | 7.0843 | 8.5368 | 14.6359 | 25.6993 | 12.663 | 15.1244 | 26.4007 | 25.0874 | 77.8051 | 288.5989
Projection | 0.50043 | 33.0237 | 2.817 | 7.9904 | 14.4639 | 3.146 | 25.6993 | 12.663 | 15.1244 | 26.4007 | 25.0874 | 77.8051
CAIDI
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 139.9063 | 153.9696 | 86.3439 | 104.453 | 254.1515 | 143.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 152.543 | 163.8843
2024 Results | 54.1879 | 56.9862 | 229.5266 | 135.4083 | 217.1286 | 101.7441 | 163.3705 | 179.7638 | 109.973 | 48.642 | 135.3853 | 159.1837 | 141.6787
5 Year Average | 109.9905 | 243.3826 | 244.0778 | 157.0629 | 158.8299 | 122.4831 | 115.0513 | 135.8128 | 106.9241 | 140.4047 | 228.2878 | 206.9116 | 160.2394
Events
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 10 | 45 | 12 | 7 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 403.8
2024 Results | 38 | 33 | 32 | 25 | 26 | 86 | 62 | 67 | 35 | 41 | 82 | 34 | 561
5 Year Average | 42.2 | 30 | 38.8 | 35.2 | 35.2 | 60.2 | 73.8 | 53.2 | 49.8 | 34 | 47.2 | 31.8 | 531.4
Projection | 10 | 45 | 12 | 7 | 24 | 16 | 73.8 | 53.2 | 49.8 | 34 | 47.2 | 31.8
CI
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 175 | 10545 | 1604 | 3761 | 2798 | 1080 | 0 | 0 | 0 | 0 | 0 | 0 | 19963 | 19963
2024 Results | [12 empty] | 0
5 Year Average | [12 empty] | 0
Projection | 175 | 10545 | 1604 | 3761 | 2798 | 1080 | 0 | 0 | 0 | 0 | 0 | 0
CMI
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 24483.6 | 1623609.6 | 138495.6 | 392847.6 | 711115.8 | 154674 | 0 | 0 | 0 | 0 | 0 | 0 | 3045226.2 | 3045226.2
2024 Results | [12 empty] | 0
5 Year Average | [12 empty] | 0
Projection | 24483.6 | 1623609.6 | 138495.6 | 392847.6 | 711115.8 | 154674 | 0 | 0 | 0 | 0 | 0 | 0
CS
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 48925 | 49165 | 49165 | 49165 | 49165 | 49165 | 46427 | 46573 | 47485 | 47545 | 47942 | 47953 | 48222.9167 | 48222.9167
2024 Results | 45718 | 45718 | 45631 | 45836 | 45977 | 45977 | 46427 | 46573 | 47485 | 47545 | 47942 | 47953 | 46565.1667
5 Year Average | 45494.6 | 45444.4 | 45474.2 | 45459.8 | 45475 | 45543.8 | 45629.4 | 45806.6 | 45988.4 | 46006.6 | 46106 | 46113.2 | 45711.8333
CIII
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 17.5 | 234.3333 | 133.6667 | 537.2857 | 116.5833 | 67.5 | 0 | 0 | 0 | 0 | 0 | 0 | 175.114 | 49.4378
2024 Results | 46.3684 | 27.3636 | 131.25 | 92.36 | 27.7692 | 64.2674 | 30.9032 | 88.5522 | 9.0857 | 54.4878 | 67.8537 | 73.4118 | 0
5 Year Average | 43.0891 | 43.2901 | 91.4809 | 78.5009 | 39.9388 | 50.7861 | 65.4748 | 78.1639 | 54.8027 | 57.6482 | 57.6203 | 65.7959 | 0
`

## Jan
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
120036038 | POR3100 | 2025-01-01 | Q1 | 18:11 | 20:52 | 2:41 |  |  | 160.57 | 1 | 155.4 |  | REPLACED BAD CONNECTION AT WEATHERHEAD AND METER SUPPLIED FROM POLE 70502 RIO GRANDE ST DUE TO DETERIORATION. | Equipment | Corrosion/Decay | Review Complete | None | NORTH LAKE TAHOE
120036127 | MEY3300 | 2025-01-02 | Q1 | 22:29 | 0:30 | 2:02 |  |  | 121.1 | 8 | 968.4 |  | REPLACED 10K FUSE P123149 BLITZEN RD - CAUSE UNKNOWN | Other | Unknown | Review Complete | None | SOUTH LAKE TAHOE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120036063 | MEY3500 | 2025-01-02 | Q1 | 11:45 | 18:25 | 6:40 |  |  | 399.78 | 47 | 18789 |  | MANUALLY OPENED 15 AMP LINE FUSE P135179 JACARILLO TRL TO INSTALL NEW POLE BETWEEN P135184 &amp; P135185. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 32 | 1219 | 265479 | 48925 | 5.4262 | 0.024916 | 217.7842 | 38.0938
120036148 | TAH7300 | 2025-01-03 | Q1 | 11:27 | 13:36 | 2:09 |  |  | 129.37 | 34 | 4398.6 |  | BLOWN 40AMP LINE FUSE P73307 BELLEVIEW AVE. DUE TO FALLEN TREE AT P36634. REPLACED 2 SPANS OF WIRE FROM P236633 AND REPAIRED BROKEN CROSSARM AT P36634. | Vegetation | Fall In Tree | Review Complete | None | NORTH LAKE TAHOE
231058561 | STL3501 | 2025-01-06 | Q1 | 12:55 | 16:30 | 3:35 |  |  | 215 | 40 | 8599.8 |  | MANUALLY OPENED 11AMP LINE FUSE TO REPLACE POLE AND INSTALL NEW TRANSFORMER P79158 JANET DR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | E2_Exclusion | PLANNED OUTAGE
120036438 | STL3501 | 2025-01-07 | Q1 | 20:45 | 23:50 | 3:05 |  |  | 185 | 3 | 555 |  | MANUALLY OPENED TRANSFORMER FUSE P292456 PENTAGON DR TO REPAIR BAD CONNECTION AT TRANSFORMER | Equipment | Vibration/Loose Connection | Review Complete | None | SOUTH LAKE TAHOE
231058702 | NST8400 | 2025-01-07 | Q1 | 16:00 | 17:55 | 1:55 |  |  | 115 | 357 | 41055 |  | MANUALLY OPENED VFI-202 NORTHSTAR DR TO REBUILD T-PAD &amp; RETAINING WALL | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231058647 | MEY3400 | 2025-01-07 | Q1 | 12:00 | 15:30 | 3:30 |  |  | 210 | 3 | 630 |  | MANUALLY OPENED TRANSFORMER FUSE P251648 MOUNTAIN MEADOW DR TO REPLACE TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 20 | 1010 | 240273 | 48925 | 4.911 | 0.020644 | 237.8941 | 50.5
231058631 | MEY3400 | 2025-01-07 | Q1 | 11:30 | 14:35 | 3:05 |  |  | 185 | 27 | 4995 |  | MANUALLY OPENED TRANSFORMER FUSE P72466 CLEMENT ST FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE
120036474 | TAH5201 | 2025-01-08 | Q1 | 14:35 | 16:30 | 1:55 |  |  | 114.75 | 1 | 114.6 |  | TIGHTENED LOOSE CONNECTORS AT WEATHERHEAD P100456 CARNELIAN CIRCLE. | Equipment | Vibration/Loose Connection | Review Complete | None | NORTH LAKE TAHOE | E2_Exclusion | THIRD PARTY
231058882 | MEY3400 | 2025-01-09 | Q1 | 11:35 | 17:25 | 5:50 |  |  | 350 | 102 | 35700 |  | MANUALLY OPENED 30AMP LINE FUSE P244957 FORREST MOUNTAIN DR FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE
232004963 | MEY3200 | 2025-01-15 | Q1 | 12:14 | 15:53 | 3:39 |  |  | 219 | 8 | 1752 |  | MANUALLY OPENED P68846 PATRICIA LN TO REPLACE POLE &amp; TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
232004964 | MEY3200 | 2025-01-15 | Q1 | 12:14 | 15:53 | 3:39 |  |  | 219 | 14 | 3066 |  | MANUALLY OPENED P68845 PATRICIA LN TO REPLACE POLE &amp; TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 2 | 34 | 722.4 | 48925 | 0.014765 | 0.00069494 | 21.2471 | 17
232004957 | MEY3200 | 2025-01-15 | Q1 | 12:00 | 15:00 | 3:00 |  |  | 180 | 1 | 180 |  | MANUALLY OPENED ELBOW 3887 TAHOE KEYS BLVD FOR MAINTENANCE WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE
232004954 | MEY3400 | 2025-01-15 | Q1 | 11:49 | 17:35 | 5:46 |  |  | 346 | 27 | 9342 |  | MANUALLY OPENED LINE FUSE P294935 FOREST MOUNTAIN DR-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | E2_Exclusion | (blank)
231059359 | MEY3200 | 2025-01-16 | Q1 | 19:50 | 20:05 | 0:15 |  |  | 14.58 | 29 | 422.4 |  | REPAIRED BROKEN CONDUIT BETWEEN VFI D &amp; FIRST BOX VENICE DR E | Act Of Man | Dig in | Review Complete | THIRD PARTY | SOUTH LAKE TAHOE
120036939 | STL3501 | 2025-01-16 | Q1 | 14:19 | 16:17 | 1:58 |  |  | 117.85 | 1 | 117.6 |  | DAMAGED SECONDARY UG FROM POLE 66563 WARR RD. RAN TEMP SERVICE AND REFERRED TO SUPERVISOR TO HAVE U/G REPLACED AT A LATER DATE | Equipment | Corrosion/Decay | Review Complete | None | SOUTH LAKE TAHOE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120036952 | POR3100 | 2025-01-17 | Q1 | 2:00 | 5:00 | 3:00 |  |  | 180 | 1 | 180 |  | DE-ENERGIZED TRANSFORMER TO REPLACE BURNT CROSSARM AT P145010 COUNTY HWY A15 | Equipment | Fire | Review Complete | None | NORTH LAKE TAHOE |  |  | 0 | 48925 | 0 | 0 | #DIV/0! | #DIV/0!
231059622 | MEY3300 | 2025-01-20 | Q1 | 11:33 | 16:05 | 4:32 |  |  | 272 | 6 | 1632 |  | MANUALLY OPENED P293704 CHILICOTHE ST FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE
231059562 | MEY3100 | 2025-01-20 | Q1 | 5:30 | 7:00 | 1:30 |  |  | 90 | 9 | 810 |  | MANUALLY OPENED TRANSFORMER FUSE P297102 COLD CREEK TRL - SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | E2_Exclusion | (blank)
120037222 | POR3100 | 2025-01-21 | Q1 | 13:32 | 15:42 | 2:10 |  |  | 130 | 50 | 6499.8 |  | BLOWN 10 AMP LINE FUSE P70502 4TH AVE, DEAD SQUIRREL REMOVED FROM P138023 OFF RIO GRANDE ST. | Animal | Squirrel | Review Complete | None | NORTH LAKE TAHOE
231059796 | STL3101 | 2025-01-22 | Q1 | 12:45 | 3:45 | 3:00 |  |  | 900 | 34 | 30600 |  | MANUALLY OPENED PRIMARY RISER FUSE 31SU32 P78872 KELLER RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231059788 | MULLER1296 | 2025-01-22 | Q1 | 10:55 | 17:54 | 6:59 |  |  | 419 | 64 | 26815.8 |  | MANUALLY OPENED FUSED TAP P278665 STATE ROUTE 88 FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE |  |  | 0 | 48925 | 0 | 0 | #DIV/0! | #DIV/0!
231059892 | STL2300 | 2025-01-23 | Q1 | 16:50 | 17:50 | 1:00 |  |  | 60 | 5 | 300 |  | MANUALLY OPENED TRANSFORMER FUSE P131279 AZURE AVE SO REPAIRS COULD BE MADE TO U/G WIRES - DIG IN BY EXCAVATOR | Act Of Man | Dig in | None | THIRD PARTY | SOUTH LAKE TAHOE
120037297 | POR3200 | 2025-01-24 | Q1 | 14:12 | 17:42 | 3:30 |  |  | 210 | 54 | 11340 |  | BLOWN (2)-20 AMP FUSES DUE TO BROKEN CUTOUT P130502 MEADOW WAY | Equipment | Other | None | None | NORTH LAKE TAHOE | E2_Exclusion | (blank)
120037497 | SRB51 | 2025-01-29 | Q1 | 12:02 | 15:06 | 3:04 |  |  | 184 | 232 | 42688.2 |  | MANUALLY OPENED HIGH SIDE SWITCH TO REPLACE RECLOSER AT SB SUB | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE
231060227 | MULLER1296 | 2025-01-29 | Q1 | 11:50 | 14:51 | 3:01 |  |  | 181 | 3 | 543 |  | MANUALLY OPENED TRANSFORMER FUSE P267082 FOOTHILL RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231060384 | KBH4203 | 2025-01-30 | Q1 | 17:48 | 17:55 | 0:07 |  |  | 7 | 22 | 154.2 |  | MANUALLY OPENED P100180 TO CORRECT VOLTAGE ISSUES TO HOUSE 8157 RAINBOW AVE - CHANGED TAP SIZE | Equipment | Other | Review Complete | None | NORTH LAKE TAHOE |  |  | 0 | 48925 | 0 | 0 | #DIV/0! | #DIV/0!
231060345 | MEY3500 | 2025-01-30 | Q1 | 14:30 | 18:00 | 3:30 |  |  | 210 | 10 | 2100 |  | MANUALLY OPENED TRANSFORMER FUSE P153606 ONNONTIOGA ST-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE
231060332 | MULLER1296 | 2025-01-30 | Q1 | 11:00 | 17:00 | 6:00 |  |  | 360 | 2 | 720 |  | MANUALLY OPENED LINE FUSE P143841 BARBER WAY-POLE &amp; TRANSFORMER REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | E2_Exclusion | (blank)
231060349 | MULLER1296 | 2025-01-30 | Q1 | 9:00 | 16:20 | 7:20 |  |  | 440 | 23 | 10120.2 |  | MANUALLY OPENED LINE FUSE P214654 CARSON VIEW-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE
231060455 | MULLER1296 | 2025-01-31 | Q1 | 11:10 | 13:25 | 2:15 |  |  | 135 | 1 | 135 |  | MANUALLY OPENED LINE FUSE P143840 BARBER WAY-POLE REPLACEMENT &amp; RECONDUCTOR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
|  |  | Q1 |  |  | 0:00 |  |  | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 48925 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | Q1 |  |  | 0:00 |  |  | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 |  |  | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | None | [6 empty] | This box shows the monthly results per the local reporting criteria
|  |  | Q1 |  |  | 0:00 |  |  | #DIV/0! | [8 empty] | #N/A | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
|  |  | Q1 |  |  | 0:00 |  |  | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyse - Change Data Source
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A | 10 | 175 | 24483.6 | 48925 | 0.50043 | 0.0035769 | 139.9063 | 17.5
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A | [10 empty] | Off | On | HR/MIN | Cust |  | Off | On | HR/MIN | Cust | TOTAL
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A | [9 empty] | P37 B PHASE | 14:54 | 15:08 | 0:14 | 224 | 16L1 | 15:08 | 16:16 | 1:08 | 291
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A | [10 empty] | 0 | 14 | 14 | 3136 |  | 1 | 8 | 68 | 19788 | 22924
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Feb
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | Under 5 Minutes? | Is CMI = to CI*Duration? | E2_Exclusion | (All)
120037803 | TPZ1202 | 2025-02-02 | Q1 | 2:44 | 4:40 | 1:56 | 1 | 56 | 116 | 680 | 78813 | COLEVILLE | TPZ1202-R1 LOCK OUT, ALL CUSTOMERS RESTORED 4:40 AM CAUSE UNKNOWN POSSIBLY HIGH WINDS | Weather | Wind | Review Complete | NONE | South Lake | FALSE | FALSE
120037825 | POR3200 | 2025-02-02 | Q1 | 21:20 | 21:35 | 0:15 | 0 | 15 | 15 | 3 | 45 | PORTOLA | BLOWN 15 AMP TRANSFORMER FUSE P250174 INDUSTRIAL WAY-BIRD | Animal | Bird | Review Complete | NONE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231060690 | MULLER1296 | 2025-02-03 | Q1 | 10:00 | 13:00 | 3:00 | 3 | 0 | 180 | 2 | 360 |  | MANUALLY OPENED 10 AMP LINE FUSE P143841 BARBER RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | 73 | 15292 | 1827162 | 49165 | 37.1639 | 0.31103 | 119.4848 | 209.4795
120037844 | MEY3500 | 2025-02-03 | Q1 | 11:45 | 16:00 | 4:15 | 4 | 15 | 255 | 132 | 33660 | SOUTH LAKE TAHOE | MANUALLY OPENED 35MU37 LINE FUSE P297012 MACINAW RD TO REPLACE LJE-65 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120037932 | MULLER1296 | 2025-02-04 | Q1 | 13:16 | 17:36 | 4:19 | 4 | 19 | 259.82 | 1 | 259.8 | MARKLEEVILLE | CUT SECONDARY WIRES AT POLE 214652 EMIGRANT TRL TO REPLACE POLE. | Weather | Wind | Review Complete | NONE | South Lake | FALSE | TRUE | E2_Exclusion | PLANNED OUTAGE
120037904 | TPZ1202 | 2025-02-04 | Q1 | 17:32 | 18:58 | 1:26 | 1 | 26 | 86.43 | 81 | 6932.4 | COLEVILLE | PTR 1202-R3 LOCKED OUT - IN EXTREME FIRE SEASON - NO CAUSE FOUND, HIGH WINDS IN AREA.&#x0D; | Weather | Wind | Review Complete | NONE | South Lake | FALSE | FALSE
231060902 | TPZ1202 | 2025-02-04 | Q1 | 19:22 | 0:04 | 4:42 | 4 | 42 | 282 | 697 | 168404.4 | COLEVILLE | PTR 1202-R1 &amp; 1202-R3 LOCKED OPEN - IN EXTREME FIRE SEASON - 1202-R1 CLOSED @ 19:56 - L/O AGAIN @ 20:36 | Weather | Wind | Review Complete | NONE | South Lake | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231060936 | MULLER1296 | 2025-02-05 | Q1 | 11:10 | 15:05 | 3:55 | 3 | 55 | 235 | 31 | 7285.2 |  | MANUALLY OPENED LINE FUSE P278659 FOOTHILL RD-RECONDUCTOR OVER HWY X-ING &amp; POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | 23 | 2712 | 149681.4 | 49165 | 3.0445 | 0.055161 | 55.1923 | 117.913
231061069 | MULLER1296 | 2025-02-06 | Q1 | 11:00 | 12:33 | 1:33 | 1 | 33 | 93 | 4 | 372 |  | MANUALLY OPENED FUSE AT P290716 DIAMOND VALLEY RD - SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120038031 | SQV7201 | 2025-02-07 | Q1 | 2:23 | 19:50 | 17:26 | 17 | 26 | 1046.9 | 598 | 310943.4 | ALPINE MEADOWS | 7201-R1 L/O DUE TO FALLEN TREE BETWEEN P96634 &amp; P292063 | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | FALSE | E2_Exclusion | LOSS OF SUPPLY
120038034 | MEY3200 | 2025-02-07 | Q1 | 3:21 | 8:16 | 4:54 | 4 | 54 | 294.58 | 316 | 70531.2 | SOUTH LAKE TAHOE | BLOWN 2-40K FUSE P294786 JAMES AVE. REPLACED BROKEN PRIMARY BETWEEN P68846 &amp;70250 DUE TO FALLEN TREE LIMB | Vegetation | Fall In Limb | Review Complete | NONE | South Lake | FALSE | FALSE
120038045 | TPZ1202 | 2025-02-07 | Q1 | 12:07 | 14:54 | 2:47 | 2 | 47 | 167.2 | 697 | 30848.4 | COLEVILLE | 1202-R1 L/O WITH NRA ISSUED - BLOWN SINGLE PHASE PRIMARY P293554 US HWY 395 | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120038047 | STL3501 | 2025-02-07 | Q1 | 12:23 | 12:47 | 0:24 | 0 | 24 | 24 | 9 | 216 | SOUTH LAKE TAHOE | REPLACED PRIMARY NEUTRAL P292459 LAKE TAHOE BLVD-NO CAUSE FOUND | Other | Unknown | Review Complete | NONE | South Lake | FALSE | TRUE | 2 | 1999 | 49402.2 | 49165 | 1.0048 | 0.040659 | 24.7135 | 999.5
120038050 | TAH7300 | 2025-02-07 | Q1 | 12:27 | 22:45 | 10:17 | 10 | 17 | 617.55 | 1 | 543 | TAHOE CITY | REATTACHED SERVICE P151432 GLEN ALPINE AVE-TREE | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | FALSE
120038053 | TAH7300 | 2025-02-07 | Q1 | 13:39 | 22:43 | 9:04 | 9 | 4 | 544 | 1 | 544.2 | TAHOE CITY | REATTACHED SERVICE P92495 W LAKE BLVD-TREE | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | TRUE | E2_Exclusion | THIRD PARTY
231061235 | SQV8200 | 2025-02-07 | Q1 | 17:36 | 19:00 | 1:24 | 1 | 24 | 84.12 | 16 | 1345.8 | OLYMPIC VALLEY | BLOWN 30 AMP LINE FUSE P291105 LANNY LN-WIRE MOVEMENT CAUSED CROSSING OF LINES | Equipment | Wire Movement | Review Complete | NONE | North Lake | FALSE | TRUE
231061379 | MULLER1296 | 2025-02-10 | Q1 | 11:35 | 16:30 | 4:55 | 4 | 55 | 295 | 4 | 1180.2 |  | MANUALLY OPENED 40 AMP LINE FUSE P290716 DIAMOND VALLEY RD-SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231061383 | TPZ1202 | 2025-02-10 | Q1 | 11:52 | 17:00 | 5:08 | 5 | 8 | 308 | 8 | 2464.2 |  | MANUALLY OPENED 15 AMP LINE FUSE P266630 US HWY 395-SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | 3 | 36 | 4468.8 | 49165 | 0.090894 | 0.00073223 | 124.1333 | 12
120038113 | MEY3400 | 2025-02-10 | Q1 | 12:41 | 17:30 | 4:48 | 4 | 48 | 288.68 | 38 | 10969.8 |  | MANUALLY OPENED NEW CUTOUTS P146101 DUNDEE CIR TO REPLACE POLES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120038121 | MEY3300 | 2025-02-10 | Q1 | 14:37 | 4:31 | 13:53 | 13 | 53 | 833.7 | 59 | 49189.2 | SOUTH LAKE TAHOE | BLOWN CENTER PHASE P153257 COUNTRY CLUB DR - FAILED UG CABLE FEEDING XFMR 15097 | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | FALSE | TRUE | E2_Exclusion | (blank)
231061487 | MEY3300 | 2025-02-11 | Q1 | 12:21 | 15:33 | 3:12 | 3 | 12 | 192 | 28 | 5376 |  | MANUALLY OPENED 15 AMP LINE FUSE P116682 W SAN BERNARDINO AVE TO REFRAME P293704 &amp; P116688 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231061490 | MULLER1296 | 2025-02-11 | Q1 | 12:40 | 15:45 | 3:05 | 3 | 5 | 185 | 4 | 739.8 |  | MANUALLY OPENED 40 AMP LINE FUSE P290716 DIAMOND VALLEY RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120038182 | MEY3400 | 2025-02-12 | Q1 | 12:23 | 16:00 | 3:37 | 3 | 37 | 217.38 | 17 | 3695.4 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P80764 JAMES AVE TO REPLACE POLES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231061566 | MULLER1296 | 2025-02-12 | Q1 | 13:03 | 17:00 | 3:57 | 3 | 57 | 237 | 6 | 1422 |  | MANUALLY OPENED FUSE AT P143843 STATE ROUTE 89 FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120038214 | TAH7100 | 2025-02-13 | Q1 | 14:35 | 15:50 | 1:15 | 1 | 15 | 75 | 155 | 11625 | TAHOE CITY | BLOWN 2 50 AMP FUSES P108878 SLIVERTIP DR -SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE | E2_Exclusion | (blank)
120038225 | GLS7400 | 2025-02-13 | Q1 | 15:52 | 17:15 | 1:23 | 1 | 23 | 83 | 48 | 3984 | TRUCKEE | BLOWN 2 25 AMP FUSE P167874 - SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE
120038232 | KBH4202 | 2025-02-13 | Q1 | 17:05 | 19:15 | 2:10 | 2 | 10 | 130.07 | 1 | 130.2 | KINGS BEACH | SERVICE REPAIRED TO MAIN HOUSE AND RECONNECTED. SMALLER BLDG NEEDS ELECTRICIAN-TREE | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120038245 | TAH7100; TAH7200 | 2025-02-13 | Q1 | 19:46 | 8:54 | 13:07 | 13 | 7 | 787.72 | 1616 | 209904.6 | TAHOE CITY | 7100 CB L/O DUE TO FALLEN TREE BETWEEN P161198 &amp; P161199 | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | FALSE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
120038262 | MEY3400 | 2025-02-13 | Q1 | 23:34 | 1:45 | 2:11 | 2 | 11 | 131 | 46 | 5787 | SOUTH LAKE TAHOE | BLOWN FUSE P192824 N UPPER TRUCKEE RD AND BLOWN FUSE P146127 LAKE TAHOE BLVD | Vegetation | Fall In Limb | Review Complete | NONE | South Lake | FALSE | FALSE
120038284 | TAH7300 | 2025-02-14 | Q1 | 0:08 | 1:29 | 25:20 | 25 | 20 | 1520.58 | 15 | 22680.6 | TAHOE CITY | BLOWN 65 AMP LINE FUSE P208511 - MANUALLY OPENED 2ND LINE FUSE-DOWN PRIMARY BETWEEN P137676 &amp; 9137677 W LAKE BLVD | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | FALSE | E2_Exclusion | (blank)
120038272 | GLS7400 | 2025-02-14 | Q1 | 1:35 | 4:45 | 3:10 | 3 | 10 | 190 | 49 | 6328.2 | TRUCKEE | BLOWN 20A FUSES P167874 ROLANDS WAY - SNOW OFFLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | FALSE
120038296 | TAH7300 | 2025-02-14 | Q1 | 1:56 | 2:45 | 24:49 | 24 | 49 | 1489 | 10 | 14890.2 |  | BLOWN FUSE P8713 INTERLAKEN RD - REPAIRED BROKEN CROSSARM P8713 GRIMSEL PASS | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120038303 | TAH7300 | 2025-02-14 | Q1 | 1:56 | 8:40 | 30:44 | 30 | 44 | 1844.28 | 2 | 2903.4 | TAHOE CITY | BROKEN DEAD END ARM P79978 ELIZABETH DR | Other | Unknown | Review Complete | NONE | North Lake | FALSE | FALSE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
121000092 | TAH7300 | 2025-02-14 | Q1 | 1:56 | 2:07 | 24:11 | 24 | 11 | 1451.37 | 3681 | 41825.4 | TAHOE CITY | EMERGENCY OPENED 7300-R1 TO SAFELY OPEN DAMAGED CUTOUTS @ P8713 - ALSO SEE INC 120038296 | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | FALSE
120038243 | TRK7202 | 2025-02-14 | Q1 | 2:06 | 20:08 | 42:02 | 42 | 2 | 2522.57 | 150 | 91202.4 |  | MANUALLY OPENED PTR 7202D2 &amp; LB 72-55 DUE TO SUSPECTED DOWNED PHASE - ADDITIONAL SWITCHING EXECUTED TO REPAIR DOWNED LINES AT MULTIPLE LOCATIONS: P281393-281394, P39591-271891, P294607-137680 | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | FALSE | E2_Exclusion | NONE | [6 empty] | This box shows the monthly results per the local reporting criteria
120038276 | SQV7201 | 2025-02-14 | Q1 | 6:25 | 19:44 | 13:19 | 13 | 19 | 799.3 | 598 | 354031.8 | ALPINE MEADOWS | PTR 7201-R1 LOCKED OUT - P96628 (TREE ON WIRE) P100408 &amp; 100409 (WIRE DOWN) - BROKEN PHASE AND 2 PHASES ALSO DOWN BETWEEN P115884 AND 292985 | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | FALSE | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
231061924 | STL3501 | 2025-02-14 | Q1 | 7:30 | 10:00 | 2:30 | 2 | 30 | 150 | 11 | 1650 |  | MANUALLY OPENED FUSE P295733 HERBERT AVE DUE TO WIRE SLAPPING LIGHT POST BETWEEN POLES 511360 &amp; 616881 HEAVY SNOW LOAD CAUSED A LONG SPAN OF LINE TO SAG | Weather | Ice/Snow | Review Complete | NONE | South Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyse - Change Data Source
120038282 | GLS7400 | 2025-02-14 | Q1 | 9:22 | 11:41 | 2:18 | 2 | 18 | 138.48 | 1 | 138.6 | TRUCKEE | WIRE POPPED OUT FROM P189416 - REHUNG AND RE-ENERGIZED | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE | 45 | 10545 | 1623609.6 | 49165 | 33.0237 | 0.21448 | 153.9696 | 234.3333
120038283 | MEY3300 | 2025-02-14 | Q1 | 9:47 | 10:40 | 0:53 | 0 | 53 | 53 | 32 | 1696.2 | SOUTH LAKE TAHOE | BLOWN 25K LINE FUSE P293154 E SAN BERNARDINO AVE - POTENTIAL WIRE SLAP | Weather | Wind | Review Complete | NONE | South Lake | FALSE | TRUE
120038313 | MEY3300 | 2025-02-14 | Q1 | 11:35 | 12:30 | 0:55 | 0 | 55 | 55 | 139 | 7622.4 | SOUTH LAKE TAHOE | BLOWN 25 AMP FUSES P293154 E SAN BERNARDINO AVE, TRIPPED VFI 3300 21 C -WIRES SLAPPING TOGETHER | Weather | Wind | Review Complete | NONE | South Lake | FALSE | FALSE
120038314 | MEY3300 | 2025-02-14 | Q1 | 12:45 | 13:45 | 1:00 | 1 | 0 | 60 | 14 | 840 | SOUTH LAKE TAHOE | (2) BLOWN 10 AMP FUSES P123015 MANDAN ST - SUSPECTS WIRE SLAP | Weather | Ice/Snow | Review Complete | NONE | South Lake | FALSE | TRUE
120038319 | MEY3300 | 2025-02-14 | Q1 | 13:42 | 16:30 | 2:48 | 2 | 48 | 168.03 | 139 | 6399 | SOUTH LAKE TAHOE | BLOWN VFI 3300-21 'C' POS - FAILED XFMR @ P93352 | Equipment | Other | Review Complete | NONE | South Lake | FALSE | FALSE
120038328 | MEY3500 | 2025-02-14 | Q1 | 13:48 | 15:06 | 1:18 | 1 | 18 | 78.32 | 273 | 21169.2 |  | BLOWN 65 AMP LINE FUSE P135349 LODI AVE-WIRES SLAPPED TOGETHER | Weather | Ice/Snow | Review Complete | NONE | South Lake | FALSE | FALSE
120038335 | TRK7204 | 2025-02-14 | Q1 | 14:16 | 20:08 | 5:52 | 5 | 52 | 352.47 | 42 | 14059.2 | TRUCKEE | MANUALLY OPENED 30 AMP LINE FUSES P189376 THE STRAND TO REPAIR BROKEN JUMPER P189392 | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | FALSE
120038336 | MEY3400 | 2025-02-14 | Q1 | 14:24 | 16:59 | 2:34 | 2 | 34 | 154.75 | 1 | 154.8 | SOUTH LAKE TAHOE | SECONDARY SPLICE CAME LOOSE AT TREE ATTACHMENT - ADDED ON BAD SECONDARY WHERE JACKETED | Equipment | Vibration/Loose Connection | Review Complete | NONE | South Lake | FALSE | TRUE
121000083 | TAH7300 | 2025-02-14 | Q1 | 16:31 | 21:05 | 4:34 | 4 | 34 | 274.17 | 19 | 5208.6 | TAHOE CITY | BLOWN 20A FUSES P68683 - SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE
121000063 | SQV8200 | 2025-02-14 | Q1 | 17:10 | 21:46 | 4:36 | 4 | 36 | 276.43 | 158 | 43678.8 | OLYMPIC VALLEY | VFI-139 TRIPPED ALL 3 PHASES OF 'D' POS - SUSPECTED SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | FALSE
121000081 | MEY3300 | 2025-02-14 | Q1 | 18:25 | 19:55 | 1:29 | 1 | 29 | 89.42 | 1 | 89.4 | SOUTH LAKE TAHOE | REPLACED CONNECTORS AND WIRE | Equipment | Wire Movement | Review Complete | NONE | South Lake | FALSE | TRUE
121000173 | MEY3400 | 2025-02-15 | Q1 | 12:50 | 0:50 | 12:00 | 12 | 0 | 720 | 1 | 720 | SOUTH LAKE TAHOE | REPLACED BROKEN NEUTRAL P63623 TATA LN | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | FALSE | TRUE
231062282 | MEY3300 | 2025-02-15 | Q1 | 14:38 | 15:00 | 0:22 | 0 | 22 | 22 | 21 | 462 |  | MANUALLY OPENED XFMR FUSE P107275 TO REPAIR BROKEN NEUTRAL | Weather | Ice/Snow | Review Complete | NONE | South Lake | FALSE | TRUE
121000123 | SQV7201 | 2025-02-15 | Q1 | 17:18 | 23:30 | 6:12 | 6 | 12 | 372 | 43 | 14610 | ALPINE MEADOWS | MANUALLY OPEN DISCONNECT AT P115859 BEAR CREEK RD TO REPLACE TRANSFORMER AT P115859. SNOW LOADING CAUSED PRIMARY AND SECONDARY TO COME IN CONTACT. | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | FALSE
121000174 | TRK7202 | 2025-02-15 | Q1 | 23:44 | 4:00 | 4:16 | 4 | 16 | 256 | 19 | 4864.2 |  | BLOWN 25 AMP LINE FUSE P68741 RIVER RD, DUE TO HEAVY WINDS. | Weather | Wind | Review Complete | NONE | North Lake | FALSE | TRUE
121000193 | TAH7100 | 2025-02-16 | Q1 | 16:34 | 19:15 | 2:41 | 2 | 41 | 161 | 93 | 14973 | TAHOE CITY | 2 BLOWN 65 AMP LINE FUSES P124662 EDELWEISS LN SNOWLOAD DROPPED CAUSING PRIMARY &amp; SECONDARY TO SLAP | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE
120038359 | GLS7600 | 2025-02-17 | Q1 | 12:15 | 16:00 | 3:45 | 3 | 45 | 225 | 5 | 1125 | TRUCKEE | 2 BLOWN 15 AMP TRANSFORMER FUSES P252959 HINTON DR-SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE
120038373 | POR3200 | 2025-02-17 | Q1 | 13:35 | 14:00 | 0:25 | 0 | 25 | 25.3 | 1941 | 47778 | PORTOLA | MANUALLY OPENED POR3100 &amp; POR3200 CB FOR NVE SWITCHING ON 619 LINE | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120038379 | MEY3400 | 2025-02-17 | Q1 | 14:15 | 15:00 | 0:45 | 0 | 45 | 45 | 2 | 90 |  | MANUALLY OPENED 11 AMP LINE FUSE P264063 JAMESON BEACH RD / TREE CREW INADVERTENTLY DROPPED TREE LIMB ON WIRE / OPENED FUSE TO MAKE SAFE | Act Of Man | Vegetation clearing | Review Complete | THIRD PARTY | South Lake | FALSE | TRUE
120038405 | GLS7400 | 2025-02-17 | Q1 | 19:53 | 21:00 | 1:06 | 1 | 6 | 66.68 | 2 | 133.2 | TRUCKEE | BLOWN 15 AMP LINE FUSE P212383 MARTIS PEAK RD-SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | FALSE | TRUE
231062612 | MEY3400 | 2025-02-18 | Q1 | 11:30 | 17:05 | 29:35 | 29 | 35 | 1775 | 2 | 3550.2 |  | MANUALLY OPENED FUSE AT P264063 FOR SYSTEM UPGRADES. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120038438 | CEM41 | 2025-02-18 | Q1 | 14:03 | 18:53 | 4:50 | 4 | 50 | 290.07 | 211 | 17790.6 | LOYALTON | LUCA25-1023 - MANUALLY CLOSED 41-42 LB &amp; MANUALLY OPENED CUTOUTS @ P135038. INSTALLED TEMP DISCS @ P206915 FOR CUSTOMER OUTAGES UNDER NRA 3732. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | FALSE
231062721 | MEY3400 | 2025-02-19 | Q1 | 16:41 | 17:51 | 1:10 | 1 | 10 | 70 | 55 | 3850.2 | SOUTH LAKE TAHOE | MANUALLY OPENED LINE FUSE P296215 12TH ST TO REPLACE CROSS ARM | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231062785 | MEY3400 | 2025-02-20 | Q1 | 12:15 | 17:25 | 5:10 | 5 | 10 | 310 | 2 | 619.8 |  | MANUALLY OPENED LINE FUSE P264063 JAMESON BEACH BLVD - SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120038849 | POR3100; POR3200 | 2025-02-20 | Q1 | 18:01 | 18:16 | 0:14 | 0 | 14 | 14.53 | 1941 | 22799.4 | PORTOLA | MANUALLY OPENED 3100 &amp; 3200 CBS FOR 619 LINE RESTORATION FROM NVE WORK BETWEEN 619N &amp; 619J | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | FALSE
231062837 | MEY3400 | 2025-02-21 | Q1 | 10:15 | 11:45 | 1:30 | 1 | 30 | 90 | 2 | 180 |  | MANUALLY OPENED FUSE AT P264063 JAMESON BEACH RD FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120039111 | CEM41 | 2025-02-24 | Q1 | 12:00 | 12:33 | 0:33 | 0 | 33 | 33 | 57 | 1881 |  | MANUALLY OPENED LINE FUSE P206915 HILL ST TO REPLACE DAMAGED HARDWARE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120039114 | MULLER1296 | 2025-02-24 | Q1 | 12:46 | 14:25 | 1:39 | 1 | 39 | 99 | 19 | 1881 |  | MANUALLY OPENED LINE FUSE P62632 EMIGRANT TRL-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120039130 | WSH201 | 2025-02-25 | Q1 | 3:14 | 3:42 | 0:28 | 0 | 28 | 28 | 58 | 1624.2 | FLORISTON | NVE LOSS OF SOURCE - WSH 204 CB LOCKED OPEN - WIND SUSPECTED | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE
120039167 | CEM42 | 2025-02-25 | Q1 | 18:37 | 23:18 | 4:41 | 4 | 41 | 281 | 12 | 3372 | LOYALTON | BLOWN TRANSFORMER FUSE, REATTACHED SECONDARY P209788 1ST ST, CUSTOMER TRIMMING TREES | Act Of Man | Vegetation clearing | Review Complete | THIRD PARTY | North Lake | FALSE | TRUE
120039203 | MEY3400 | 2025-02-27 | Q1 | 12:23 | 14:32 | 2:09 | 2 | 9 | 129.38 | 67 | 8650.8 |  | MANUALLY OPENED AT P168243 FOR RECONDUCTOR WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | FALSE
231063209 | TAH5201 | 2025-02-27 | Q1 | 17:42 | 18:30 | 0:47 | 0 | 47 | 47.93 | 22 | 1006.8 | CARNELIAN BAY | BLOWN FUSE P151300 - SERVICE RIPPED OFF 275 OLD COUNTY RD BY TRUCK - SERVICE WILL NEED TO BE REPAIRED BEFORE RECONNECT - REFUSED TRANSFORMERS | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | North Lake | FALSE | FALSE
120039219 | KBH5200 | 2025-02-27 | Q1 | 23:34 | 1:22 | 1:47 | 1 | 47 | 107.42 | 1 | 107.4 | TAHOE VISTA | LIMB ON LINE P167929 - CUT EXPOSED SPARE WIRE | Vegetation | Fall In Limb | Review Complete | NONE | North Lake | FALSE | TRUE
231063259 | MULLER1296 | 2025-02-28 | Q1 | 11:00 | 15:30 | 4:30 | 4 | 30 | 270 | 66 | 17820 |  | MANUALLY OPENED LINE FUSE P278665 STATE HWY 88 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231063266 | MEY3300 | 2025-02-28 | Q1 | 12:12 | 14:46 | 2:33 | 2 | 33 | 153.75 | 9 | 1377 | SOUTH LAKE TAHOE | MANUALLY OPENED XFMR FUSES AT P81780 &amp; P81778 ARAPAHOE ST - RECONDUCTOR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | FALSE
231063275 | TAH7100 | 2025-02-28 | Q1 | 13:50 | 18:01 | 4:11 | 4 | 11 | 251 | 7 | 1756.8 |  | MANUALLY OPENED XFMR FUSES P161199 HOLLY RD - CHANGE POLE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Mar
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | Under 5 Minutes? | Is CMI = to CI*Duration? | E2_Exclusion | (All)
231063462 | MEY3500 | 2025-03-04 | Q1 | 2:00 | 3:12 | 1:12 | 1 | 12 | 72 | 3 | 216 |  | MANUALLY OPENED TRANSFORMER 43166 LAKE TAHOE BLVD TO WIRE PANEL FOR CT'S | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231063497 | MULLER1296 | 2025-03-04 | Q1 | 11:03 | 13:52 | 2:49 | 2 | 49 | 169 | 31 | 5239.2 |  | MANUALLY OPENED LINE FUSE P278659 FOOTHILL RD TO REPLACE POLE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231063526 | MEY3300 | 2025-03-04 | Q1 | 13:34 | 16:30 | 2:56 | 2 | 56 | 176 | 9 | 1584 |  | MANUALLY OPENED TRANSFORMER FUSE P131323 ZAPOTEC DR FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE | 70 | 27020 | 9242065.2 | 49165 | 187.9806 | 0.54958 | 342.0453 | 386
231063551 | MULLER1296 | 2025-03-04 | Q1 | 14:26 | 18:00 | 3:34 | 3 | 34 | 214 | 4 | 856.2 |  | MANUALLY OPENED 40 AMP LINE FUSE P217286 DIAMOND VALLEY RD FOR RESILIENCY PROJECT. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120039794 | STL3501 | 2025-03-05 | Q1 | 10:19 | 17:05 | 6:46 | 6 | 46 | 406 | 2518 | 1018774.8 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE | E2_Exclusion | CUSTOMER OWNED
120039894 | MEY3200 | 2025-03-05 | Q1 | 10:19 | 16:38 | 6:19 | 6 | 19 | 379 | 3809 | 1441326.6 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE
120039898 | MEY3200; MEY3400 | 2025-03-05 | Q1 | 10:19 | 17:15 | 6:56 | 6 | 56 | 416.28 | 4039 | 1446412.2 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120039902 | MEY3500 | 2025-03-05 | Q1 | 10:19 | 16:52 | 6:33 | 6 | 33 | 393 | 3828 | 1501348.8 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE | 2 | 2 | 367.8 | 49165 | 0.0074809 | 4.0679e-05 | 183.9 | 1
120039897 | MEY3300 | 2025-03-05 | Q1 | 10:19 | 16:38 | 6:18 | 6 | 18 | 378.55 | 3611 | 1366818.6 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE
120039864 | STL3101 | 2025-03-05 | Q1 | 10:20 | 16:04 | 5:44 | 5 | 44 | 344 | 2307 | 793071.6 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE | E2_Exclusion | PLANNED OUTAGE
120039888 | MEY3100 | 2025-03-05 | Q1 | 10:20 | 16:31 | 6:11 | 6 | 11 | 371 | 2398 | 889059 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE
120039912 | MULLER1296 | 2025-03-05 | Q1 | 10:20 | 13:57 | 3:36 | 3 | 36 | 216.85 | 633 | 137266.2 | MARKLEEVILLE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120039904 | STL2200 | 2025-03-05 | Q1 | 10:34 | 17:24 | 6:49 | 6 | 49 | 409.67 | 97 | 39652.8 |  | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE | 39 | 1481 | 271152.6 | 49165 | 5.5152 | 0.030123 | 183.0875 | 37.9744
120039905 | STL2300 | 2025-03-05 | Q1 | 10:35 | 16:56 | 6:20 | 6 | 20 | 380.53 | 475 | 180745.2 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | FALSE | FALSE
231063868 | TPZ1202 | 2025-03-05 | Q1 | 12:45 | 13:05 | 0:20 | 0 | 20 | 20 | 8 | 160.2 |  | MANUALLY OPENED LINE FUSE P266630 HWY 395-GO INFRACTIONS | Planned | Maintenance | Review Complete | PLANNED OUTAGE / IEEE MED | SOUTH LAKE TAHOE | FALSE | TRUE | E2_Exclusion | LOSS OF SUPPLY
120039995 | MEY3300 | 2025-03-05 | Q1 | 17:44 | 19:10 | 1:26 | 1 | 26 | 86 | 14 | 1204.2 | SOUTH LAKE TAHOE | BLOWN 10 AMP LINE FUSE P123015 MANDAN ST-UNKNOWN CAUSE | Other | Unknown | Review Complete | IEEE MED | SOUTH LAKE TAHOE | FALSE | TRUE
120040021 | MEY3100 | 2025-03-06 | Q1 | 10:08 | 13:57 | 3:49 | 3 | 49 | 229.58 | 1 | 229.8 | SOUTH LAKE TAHOE | PARTIAL POWER AT P83313 COPPER WAY AFTER CONNECTORS PULLED LOOSE. REPLACED CONNECTORS AND MADE REPAIRS. | Equipment | Vibration/Loose Connection | Review Complete | CUSTOMER OWNED | SOUTH LAKE TAHOE | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231064018 | MULLER1296 | 2025-03-06 | Q1 | 11:20 | 16:35 | 5:15 | 5 | 15 | 315 | 7 | 2205 |  | MANUALLY OPENED LINE FUSE P143848 STATE HWY 89 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE | 3 | 154 | 9996 | 49165 | 0.20332 | 0.0031323 | 64.9091 | 51.3333
231064014 | MULLER1296 | 2025-03-06 | Q1 | 11:45 | 14:50 | 3:05 | 3 | 5 | 185 | 31 | 5734.8 | MARKLEEVILLE | MANUALLY OPENED LINE FUSE P272120 STATE ROUTE 89 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120040058 | MEY3300 | 2025-03-06 | Q1 | 17:38 | 20:06 | 2:27 | 2 | 27 | 147.9 | 1 | 147.6 | SOUTH LAKE TAHOE | REPLACED LOOSE CONNECTIONS AT P146357 SKYLINE DR | Equipment | Vibration/Loose Connection | Review Complete | NONE | SOUTH LAKE TAHOE | FALSE | TRUE | E2_Exclusion | THIRD PARTY
120040065 | STL3101 | 2025-03-06 | Q1 | 21:59 | 0:15 | 2:15 | 2 | 15 | 135.03 | 1 | 135 | SOUTH LAKE TAHOE | REPLACED LOOSE CONNECTIONS AT P63948 WILLOW AVE | Equipment | Vibration/Loose Connection | Review Complete | NONE | SOUTH LAKE TAHOE | FALSE | TRUE
120040068 | MULLER1296 | 2025-03-07 | Q1 | 2:09 | 7:08 | 4:58 | 4 | 58 | 298.23 | 243 | 71317.2 | MARKLEEVILLE | PLANNED POLE REPLACEMENTS ON HAWKINS RANCH RD - ALL CUSTOMERS DOWN STREAM OF P143849 DE-ENERGIZED FOR DURATION OF WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120040108 | MULLER1296 | 2025-03-07 | Q1 | 11:24 | 14:30 | 3:06 | 3 | 6 | 186.27 | 73 | 13596 | MARKLEEVILLE | MANUALLY OPENED CUTOUTS P106434 TIMBER LN FOR POLE REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | FALSE | 2 | 42 | 6213 | 49165 | 0.12637 | 0.00085427 | 147.9286 | 21
120040298 | STL2300 | 2025-03-10 | Q1 | 11:00 | 12:30 | 1:30 | 1 | 30 | 90 | 68 | 6120 | SOUTH LAKE TAHOE | MANUALLY OPENED LINE FUSE P76600 LAKE TAHOE BLVD TO RECONNECT WIRES BETWEEN P211090 AND P211163 AZURE AVE. | Other | Unknown | Review Complete | NONE | SOUTH LAKE TAHOE | FALSE | TRUE
231064574 | STL3501 | 2025-03-11 | Q1 | 1:30 | 2:00 | 0:30 | 0 | 30 | 30 | 35 | 1050 |  | MANUALLY OPENED LINE FUSE P79154 GLENWOOD WAY - POLE REPAIR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE | E2_Exclusion | (Multiple Items)
120040327 | STL3501 | 2025-03-11 | Q1 | 2:30 | 4:01 | 1:30 | 1 | 30 | 90.78 | 493 | 44725.2 | SOUTH LAKE TAHOE | MANUALLY OPENED 65A &amp; 40A LINE FUSES P90993 GLENWOOD WAY TO REPLACE CROSSARM AT P90992 SPRUCE AVE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | FALSE
231064592 | MULLER1296 | 2025-03-11 | Q1 | 11:06 | 16:51 | 5:45 | 5 | 45 | 345 | 11 | 3795 |  | MANUALLY OPENED LINE FUSE P143846 UPPER MANZANITA DR-MAINTENANCE WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120040339 | MEY3200 | 2025-03-11 | Q1 | 13:35 | 15:24 | 1:49 | 1 | 49 | 109 | 13 | 1417.2 | SOUTH LAKE TAHOE | 2 BLOWN 20 AMP LINE FUSES P97039 ELKS CLUB DR, SQUIRREL REMOVED P97045 BEL AIRE CIR | Animal | Squirrel | Review Complete | NONE | SOUTH LAKE TAHOE | FALSE | TRUE | 12 | 23737 | 8815840.2 | 49165 | 179.3113 | 0.4828 | 371.3966 | 1978.0833
120040352 | MEY3100 | 2025-03-11 | Q1 | 18:42 | 20:59 | 2:17 | 2 | 17 | 137.72 | 1 | 138 | SOUTH LAKE TAHOE | PARTIAL POWER DUE TO LOOSE CONNECTIONS P294713 MERCED AVE | Equipment | Vibration/Loose Connection | Review Complete | CUSTOMER OWNED | SOUTH LAKE TAHOE | FALSE | TRUE
120040358 | STL3101 | 2025-03-11 | Q1 | 21:07 | 21:30 | 0:23 | 0 | 23 | 23 | 31 | 712.8 | SOUTH LAKE TAHOE | MANUALLY OPENED RISER FUSE P251640 SPRUCE AVE-REPAIR PADMOUNT TRANSFORMER TS62 | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | SOUTH LAKE TAHOE | FALSE | TRUE | E2_Exclusion | (blank)
232005021 | MULLER1296 | 2025-03-12 | Q1 | 9:15 | 11:00 | 1:45 | 1 | 45 | 105 | 1 | 105 |  | MANUALLY OPENED TRANSFORMER FUSE P290461 UPPER MANZANITA DR-RESILIENCY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
121000218 | TRK7202 | 2025-03-12 | Q1 | 17:46 | 20:16 | 2:29 | 2 | 29 | 149.52 | 4 | 542.4 | TRUCKEE | BLOWN 2-50AMP LINE FUSES P269574 &amp; 2-30AMP LINE FUSES P269575 CABIN CREEK RD-BROKEN INSULATOR P252814 | Equipment | Corrosion/Decay | Review Complete | NONE | NORTH LAKE TAHOE | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231064778 | MULLER1296 | 2025-03-13 | Q1 | 12:00 | 13:26 | 1:26 | 1 | 26 | 86 | 1 | 85.8 |  | MANUALLY OPENED TRANSFORMER FUSE P129021 UPPER MANZANITA DR-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
120041272 | MEY3400 | 2025-03-14 | Q1 | 23:13 | 0:30 | 1:17 | 1 | 17 | 77 | 55 | 4234.8 | SOUTH LAKE TAHOE | BLOWN (3) 12 AMP FUSES P296215 12TH ST - CAUSE UNKNOWN POSSIBLY OVERLOAD | Other | Unknown | Review Complete | NONE | SOUTH LAKE TAHOE | FALSE | TRUE
120041437 | SLK257 | 2025-03-17 | Q1 | 4:08 | 4:45 | 0:36 | 0 | 36 | 36.53 | 3 | 109.8 |  | LOSS OF SOURCE - SLK 257 CB LOCKOUT (NVE) - MVA POLE HIT ON NVE SIDE | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | NORTH LAKE TAHOE | FALSE | TRUE | E2_Exclusion | NONE | [6 empty] | This box shows the monthly results per the local reporting criteria
120041802 | MULLER1296 | 2025-03-18 | Q1 | 11:10 |  | 0:00 |  |  | 1443.68 | 11 | 0 |  | MANUALLY OPENED 15 AMP LINE FUSE P143846 UPPER MANZANITA DR-RESILIENCY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | FALSE | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
231066278 | MEY3100 | 2025-03-18 | Q1 | 12:00 | 12:30 | 0:30 | 0 | 30 | 30 | 23 | 690 |  | MANUALLY OPENED TRANSFORMER FUSE P290458 SAN FRANCISCO AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyse - Change Data Source
231066330 | MEY3100 | 2025-03-18 | Q1 | 12:15 |  | 0:00 |  |  | 177.88 | 0 | 0 |  | MANUALLY OPENED TRANSFORMER FUSE P63847 OAKLAND AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE | 12 | 1604 | 138495.6 | 49165 | 2.817 | 0.032625 | 86.3439 | 133.6667
120041562 | MEY3100 | 2025-03-18 | Q1 | 12:31 | 12:41 | 0:10 | 0 | 10 | 10 | 12 | 120 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P192985 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231066385 | MEY3100 | 2025-03-18 | Q1 | 12:51 | 13:02 | 0:11 | 0 | 11 | 11 | 13 | 142.8 |  | MANUALLY OPENED TRANSFORMER FUSE P293179 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231066335 | MEY3100 | 2025-03-18 | Q1 | 13:20 | 13:31 | 0:11 | 0 | 11 | 11 | 14 | 154.2 |  | MANUALLY OPENED TRANSFORMER FUSE P192841 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231066380 | MEY3100 | 2025-03-18 | Q1 | 13:31 | 13:41 | 0:10 | 0 | 10 | 10 | 12 | 120 |  | MANUALLY OPENED TRANSFORMER FUSE P293178 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231066343 | MEY3100 | 2025-03-18 | Q1 | 14:10 | 14:22 | 0:12 | 0 | 12 | 12 | 23 | 276 |  | MANUALLY OPENED TRANSFORMER FUSE P192985 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231066375 | MEY3100 | 2025-03-18 | Q1 | 14:35 | 14:44 | 0:09 | 0 | 9 | 9 | 9 | 81 |  | MANUALLY OPENED TRANSFORMER FUSE P205163 BELLEVUE AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231066354 | MEY3100 | 2025-03-18 | Q1 | 14:51 | 14:59 | 0:08 | 0 | 8 | 8 | 17 | 136.2 |  | MANUALLY OPENED TRANSFORMER FUSE P90833 BELLEVUE AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120041592 | TPZ1202 | 2025-03-18 | Q1 | 20:30 | 4:50 | 8:20 | 8 | 20 | 500 | 11 | 5500.2 | COLEVILLE | MANUALLY OPENED LINE FUSE P163558 WESTERN DR, DOWN GUYS WERE DUG UP CAUSING POLE TO LEAN HEAVILY INTO THE TREES-RESET POLE | Act Of Man | Other | Review Complete | THIRD PARTY | SOUTH LAKE TAHOE | FALSE | TRUE
231066429 | STL2300 | 2025-03-19 | Q1 | 1:00 | 3:29 | 2:29 | 2 | 29 | 149 | 11 | 1639.2 |  | MANUALLY OPENED TS-178-111582 AT LAKE TAHOE BLVD FOR REPLACEMENT OF MAIN BREAKER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120041806 | MULLER1296 | 2025-03-19 | Q1 | 11:02 | 15:50 | 4:48 | 4 | 48 | 288 | 11 | 3168 |  | MANUALLY OPENED 15 AMP LINE FUSE P143846 UPPER MANZANITA DR-RESILIENCY PROJECT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231067049 | MEY3100 | 2025-03-19 | Q1 | 12:54 | 19:00 | 6:06 | 6 | 6 | 366 | 45 | 16470 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P66312 MERCED AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
231067778 | MULLER1296 | 2025-03-20 | Q1 | 1:00 | 6:13 | 5:13 | 5 | 13 | 313 | 172 | 53836.2 | MARKLEEVILLE | MANUALLY OPENED 40 AMP LINE FUSE P277686 MONTGOMERY ST TO REPLACE P39343 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120042132 | TPZ1202 | 2025-03-20 | Q1 | 9:51 | 15:00 | 5:09 | 5 | 9 | 309.22 | 5 | 1546.2 | COLEVILLE | BLOWN 15T LINE FUSE P181148 EASTSIDE RD-UNKNOWN CAUSE | Other | Unknown | Review Complete | NONE | SOUTH LAKE TAHOE | FALSE | TRUE
120042163 | MULLER1296 | 2025-03-20 | Q1 | 15:40 | 15:47 | 0:06 | 0 | 6 | 6.95 | 2 | 13.8 |  | MANUALLY OPENED TRANSFORMER FUSE P297169 DIAMOND VALLEY RD-RESILIENCY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120042439 | MEY3200 | 2025-03-24 | Q1 | 10:55 | 17:31 | 6:35 | 6 | 35 | 395.88 | 84 | 33255.6 |  | MANUALLY OPENED 32MU41 P135340 WINNEMUCCA AVE TO REMOVE TREES NEAR P66424 &amp; P87937 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | FALSE
231068199 | KBH5200 | 2025-03-24 | Q1 | 12:57 | 13:18 | 0:21 | 0 | 21 | 21 | 4 | 84 |  | BLOWN TRANSFORMER FUSE P124929 LINCOLN GREEN DR-FUSE BLEW WHILE DOING MAINTENANCE WORK | Other | Construction by Co. Contractor | Review Complete | NONE | NORTH LAKE TAHOE | FALSE | TRUE
120042555 | TAH7300 | 2025-03-26 | Q1 | 11:38 | 15:38 | 4:00 | 4 | 0 | 240.08 | 12 | 2641.2 |  | MANUALLY LIFTED TAPS AT P73314 IDLEWILD WAY - DE-ENERGIZING PRIMARY FOR TREE CREW/CONTRACTOR TO REMOVE TREE BETWEEN P236632 &amp; P236634 IDLEWILD WAY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | FALSE
120042557 | MEY3400 | 2025-03-26 | Q1 | 12:47 | 13:46 | 0:58 | 0 | 58 | 58.78 | 5 | 294 |  | PLANNED OUTAGE TO PULL WIRES BETWEEN P131421 - P122948 TATA LN AND BUILDING SECONDARY RISER. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120042580 | MEY3400 | 2025-03-26 | Q1 | 20:00 | 21:05 | 1:05 | 1 | 5 | 65.6 | 3 | 196.8 | TAHOMA | BLOWN 15K LINE FUSE P291674 EMERALD BAY RD-WIND | Weather | Wind | Review Complete | NONE | SOUTH LAKE TAHOE | FALSE | TRUE
231068561 | TAH7300 | 2025-03-27 | Q1 | 11:00 | 13:00 | 2:00 | 2 | 0 | 120 | 7 | 840 |  | MANUALLY OPENED TRANSFORMER FUSE P92257 SCENIC DR-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | TRUE
231068564 | TAH7300 | 2025-03-27 | Q1 | 11:00 | 13:00 | 2:00 | 2 | 0 | 120 | 4 | 480 |  | MANUALLY OPENED TRANSFORMER FUSE P92259 SCENIC DR-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | TRUE
231068567 | TAH7300 | 2025-03-27 | Q1 | 11:00 | 13:05 | 2:05 | 2 | 5 | 125 | 14 | 1750.2 |  | MANUALLY OPENED TRANSFORMER FUSE P73328 INTERLAKEN RD-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | TRUE
231068595 | TAH7300 | 2025-03-27 | Q1 | 13:45 | 16:00 | 2:15 | 2 | 15 | 135 | 11 | 1485 |  | MANUALLY OPENED 25 AMP TRANSFORMER FUSE P8714 INTERLAKEN RD-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | TRUE
231068628 | MULLER1296 | 2025-03-27 | Q1 | 14:30 | 15:05 | 0:35 | 0 | 35 | 35 | 2 | 70.2 | MARKLEEVILLE | MANUALLY OPENED 10K TRANSFORMER FUSE P156947 CALIFORNIA RD TO MAKE REPAIRS ON METER PANEL | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | FALSE | TRUE
120042621 | TAH7100 | 2025-03-27 | Q1 | 15:33 | 17:55 | 2:21 | 2 | 21 | 141.45 | 237 | 29868.6 | TAHOE CITY | VFI-119 'B' POSITION TRIPPED OPEN-SQUIRREL CONTACT TRANSFORMER 8927 CEDAR CT | Animal | Squirrel | Review Complete | NONE | NORTH LAKE TAHOE | FALSE | FALSE
231068714 | TAH7300 | 2025-03-28 | Q1 | 11:07 | 14:50 | 3:43 | 3 | 43 | 223 | 6 | 1338 |  | MANUALLY OPENED TRANSFORMER FUSE P105216 LAGOON RD-REPLACED GREY WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | TRUE
231068719 | TAH7300 | 2025-03-28 | Q1 | 11:07 | 12:50 | 1:43 | 1 | 43 | 103 | 14 | 1441.8 |  | MANUALLY OPENED TRANSFORMER FUSE P105212 LAGOON RD REPLACED GREY WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | TRUE
231068768 | TAH7300 | 2025-03-28 | Q1 | 15:15 | 15:55 | 0:40 | 0 | 40 | 40 | 5 | 199.8 |  | MANUALLY OPENED TRANSFORMER FUSE TAKE DOWN OLD SERVICE AND REATTACH NEW SERVICE P242122 MEADOW RD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | FALSE | TRUE
120042676 | TAH7300 | 2025-03-28 | Q1 | 18:00 | 18:49 | 0:49 | 0 | 49 | 49.43 | 13 | 642.6 | TIMBERLAND | BLOWN LINE FUSE P59748 SUGAR PINE RD DUE TO BURNT UP CUT OUT | Equipment | Corrosion/Decay | Review Complete | NONE | NORTH LAKE TAHOE | FALSE | TRUE
120043219 | CAL2501 | 2025-03-30 | Q1 | 22:42 | 23:48 | 1:05 | 1 | 5 | 65.93 | 96 | 6309.6 | VERDI | LOSS OF SOURCE (NVE) CAL 2501 CB LOCKED OPEN - NVE TO PATROL | Loss of Supply | Other | Review Complete | LOSS OF SUPPLY | NORTH LAKE TAHOE | FALSE | FALSE
120043224 | WSH201 | 2025-03-30 | Q1 | 22:42 | 23:47 | 1:05 | 1 | 5 | 65.03 | 55 | 3576.6 | FLORISTON | LOSS OF SOURCE (NVE) CAL 2501 CB LOCKED OPEN - NVE TO PATROL | Loss of Supply | Other |  | LOSS OF SUPPLY | NORTH LAKE TAHOE | FALSE | TRUE
120043265 | POR3200 | 2025-03-31 | Q1 | 8:47 | 12:05 | 3:18 | 3 | 18 | 198 | 1200 | 93560.4 | PORTOLA | POR3200 CB LOCKED OUT - BLOWN 11A FUSE P37900 OFF DELLEKER RD-WIND SLAPPED WIRES TOGETHER | Weather | Wind |  | NONE | NORTH LAKE TAHOE | FALSE | FALSE
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! | [8 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Apr
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
120044719 | MEY3300; MEY3400 | 2025-04-17 | Q2 | 16:13 | 17:02 | 24:49 | 24 | 49 | 1489.43 | 77 | 2610 | SOUTH LAKE TAHOE | MANUALLY OPENED 33MU94 &amp; 33MU132 DISCS &amp; LIFTED TAPS AT P123205 &amp; P292968 SKYLINE DR. CREWS REPLACING POLES 111280 AND P123202 IN MEYERS ROW | Planned | Maintenance | Mismatch - Number of customers | PLANNED OUTAGE | South Lake
231070566 | TPZ1202 | 2025-04-09 | Q2 | 10:40 | 16:25 | 5:45 | 5 | 45 | 345 | 2 | 690 |  | MANUALLY OPENED P295428 PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | South Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231072461 | TAH7300 | 2025-04-24 | Q2 | 14:12 | 17:41 | 3:29 | 3 | 29 | 209 | 12 | 2508 |  | MANUALLY OPENED P105244 REPLACE OPEN WIRE - PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | 53 | 8875 | 642906 | 49165 | 13.0765 | 0.18051 | 72.4401 | 167.4528
120043417 | TAH7300 | 2025-04-01 | Q2 | 19:38 | 4:42 | 9:03 | 9 | 3 | 543.65 | 3679 | 387713.4 | TAHOMA | PTR 7300-R1 LOCKOUT - BURNED THROUGH PRIMARY WIRE &amp; CONNECTOR P269477 GRAND AVE | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake
120043423 | STL3101 | 2025-04-01 | Q2 | 21:11 | 5:00 | 7:48 | 7 | 48 | 468.57 | 12 | 5622.6 | SOUTH LAKE TAHOE | BLOWN 15 AMP T-FUSE P292481 WILDWOOD AVE-MVA P90796 | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | South Lake | E2_Exclusion | PLANNED OUTAGE
120043634 | MEY3100; STL3501 | 2025-04-03 | Q2 | 0:21 | 5:45 | 5:24 | 5 | 24 | 324.4 | 4297 | 115529.4 | SOUTH LAKE TAHOE | MANUALLY OPENED P131294 35SU10 TO FLYING TAPS P83404 HERBERT AVE FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
120043656 | POR3200 | 2025-04-03 | Q2 | 13:40 | 4:00 | 14:20 | 14 | 20 | 860 | 11 | 9460.2 | PORTOLA | MANUALLY OPENED TRANSFORMER FUSE P70757 TO REPLACE DAMAGED CROSSARMS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120044244 | MEY3200 | 2025-04-07 | Q2 | 11:47 | 12:55 | 1:08 | 1 | 8 | 68 | 22 | 1495.8 |  | MANUALLY OPENED TRANSFORMER FUSE T31846 ALA WAI BLVD TO REPLACE TRANSFORMER PAD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 45 | 5102 | 244435.8 | 49165 | 4.9717 | 0.10377 | 47.9098 | 113.3778
120044245 | MEY3200 | 2025-04-07 | Q2 | 11:47 | 12:55 | 1:08 | 1 | 8 | 68 | 32 | 2176.2 |  | MANUALLY OPENED TRANSFORMER FUSE T31890 ALA WAI BLVD TO REPLACE TRANSFORMER PAD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
120044246 | MEY3200 | 2025-04-07 | Q2 | 11:47 | 12:55 | 1:08 | 1 | 8 | 68 | 30 | 2040 |  | MANUALLY OPENED TRANSFORMER FUSE T10003 ALA WAI BLVD TO REPLACE TRANSFORMER PAD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | E2_Exclusion | (Multiple Items)
120044307 | POR3100 | 2025-04-08 | Q2 | 12:23 | 18:15 | 5:51 | 5 | 51 | 351.73 | 1 | 351.6 |  | MANUALLY LIFTED TAPS P225777 IN ROW OFF DELLEKER RD - MAINTENANCE REPLACEMENT OF P66213 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
120044380 | MEY3400 | 2025-04-10 | Q2 | 11:20 | 12:20 | 1:00 | 1 | 0 | 60 | 34 | 2040 | SOUTH LAKE TAHOE | BLOWN 2 15K FUSES P131426 TUCKER AVE - CAUSE UNKNOWN. | Other | Unknown | Review Complete | NONE | South Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120044382 | HOB7700 | 2025-04-10 | Q2 | 11:44 | 17:15 | 5:31 | 5 | 31 | 331.05 | 1 | 436.2 |  | MANUALLY OPENED LINE FUSE P232498 TO REPAIR BROKEN POLE 96842 AND PIN. | Equipment | Other | Review Complete | NONE | North Lake | 1 | 12 | 5622.6 | 49165 | 0.11436 | 0.00024408 | 468.55 | 12
120044641 | MULLER1296 | 2025-04-16 | Q2 | 1:02 | 3:56 | 2:54 | 2 | 54 | 174 | 208 | 36192 | MARKLEEVILLE | MANUALLY OPENED PTR 1296-R4 P290784 HWY 89-POLE REPLACEMENTS P39832, P34330, P39933, &amp; P39834 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
120044650 | TPZ1202 | 2025-04-16 | Q2 | 10:30 | 18:01 | 7:31 | 7 | 31 | 451 | 6 | 2706 |  | MANUALLY OPENED 15 AMP LINE FUSE P286985 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | E2_Exclusion | (blank)
120044660 | POR3200 | 2025-04-16 | Q2 | 11:38 | 12:38 | 1:00 | 1 | 0 | 60 | 45 | 2700 |  | MANUALLY OPENED 11 AMP LINE FUSE P225976 W MOHAWK AVE-REPLACING BUCKARM | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
120044663 | TPZ1202 | 2025-04-16 | Q2 | 12:26 | 15:45 | 3:19 | 3 | 19 | 199 | 2 | 397.8 |  | MANUALLY OPENED 25 AMP LINE FUSE P293569 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120044668 | POR3200 | 2025-04-16 | Q2 | 13:15 | 14:29 | 1:14 | 1 | 14 | 74 | 2 | 148.2 |  | MANUALLY OPENED TRANSFORMER FUSE P240998 IDLE HOUR DR TO REPLACE LEAKING TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
120045544 | TAH7300 | 2025-04-21 | Q2 | 11:46 | 12:48 | 1:01 | 1 | 1 | 61.97 | 3 | 186 |  | FAILED SPLICE INSIDE PADMOUNT TRANSFORMER 16657 W LAKE BLVD | Equipment | Other | Review Complete | NONE | North Lake
120045755 | TAH7200 | 2025-04-24 | Q2 | 5:27 | 5:59 | 0:32 | 0 | 32 | 32.03 | 4 | 127.8 |  | MANUALLY OPENED TS-9 'B' POS ELBOWS @ HWY 89 / CREWS TO RE-SET OS-60 BACK ON PAD AFTER BEING HIT BY A SNOW PLOW | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | E2_Exclusion | (blank)
120045766 | TAH7300 | 2025-04-24 | Q2 | 11:00 | 13:52 | 2:52 | 2 | 52 | 172 | 10 | 1720.2 |  | MANUALLY OPENED TRANSFORMER FUSE P292489 WILLIAMS LN-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
120045836 | TAH7300 | 2025-04-25 | Q2 | 15:50 | 17:05 | 1:15 | 1 | 15 | 75 | 7 | 525 |  | MANUALLY OPENED TRANSFORMER FUSE P105234 BAY VIEW DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120045837 | MEY3400 | 2025-04-25 | Q2 | 16:12 | 16:59 | 0:46 | 0 | 46 | 46.35 | 1 | 46.2 | SOUTH LAKE TAHOE | BLOWN 6 AMP FUSES (2) P131251 TATA LN-NO CAUSE FOUND | Unknown |  | Review Complete | NONE | South Lake |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
120048520 | POR3200 | 2025-04-30 | Q2 | 6:56 |  | 0:00 |  |  | 145.23 | 0 | 0 |  | LUCA25-1057 - MANUALLY CLOSED FUSES P240960 OPENED FUSES P291147 &amp; LIFTED TAPS P160264 FOR REPLACEMENT OF DAMAGED CROSS ARM P160264 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
120048681 | TAH7300 | 2025-04-30 | Q2 | 12:22 | 14:12 | 1:50 | 1 | 50 | 110 | 13 | 1429.8 |  | MANUALLY OPENED TRANSFORMER FUSE P216263 HARRIS AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | E2_Exclusion | (blank)
120048749 | TAH7300 | 2025-04-30 | Q2 | 14:46 | 16:54 | 2:08 | 2 | 8 | 128 | 6 | 768 |  | MANUALLY OPENED TRANSFORMER FUSE P115688 CHINKAPIN RD-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
121000267 | HOB7700 | 2025-04-11 | Q2 | 4:47 | 5:30 | 0:43 | 0 | 43 | 43.47 | 32 | 1375.8 | TRUCKEE | MANUALLY OPENED HOB7700 BREAKER TO REPAIR PHASE OFF INSULATOR AT P59720 STATE HWY 89 SEE RB876. | Equipment | Wire Movement | Review Complete | NONE | North Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231069733 | MEY3400 | 2025-04-03 | Q2 | 2:55 | 6:45 | 3:50 | 3 | 50 | 230 | 5 | 1150.2 |  | MANUALLY OPENED TRANSFORMER FUSE P131421 TATA LN TO REPLACE CUTOUTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231070139 | STL3101 | 2025-04-05 | Q2 | 13:00 | 14:00 | 1:00 | 1 | 0 | 60 | 20 | 1200 |  | MANUALLY OPENED 6 AMP TRANSFORMER FUSES P83255 TAMARACK AVE TO REPLACE POLE/LINE EXTENSION | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
231070396 | TPZ1202 | 2025-04-07 | Q2 | 14:09 | 17:45 | 3:36 | 3 | 36 | 216 | 2 | 432 |  | MANUALLY OPENED 15AMP LINE FUSE P295423 TOPAZ LN-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | E2_Exclusion | (blank)
231070467 | TPZ1202 | 2025-04-08 | Q2 | 10:53 | 17:50 | 6:57 | 6 | 57 | 417 | 2 | 834 |  | MANUALLY OPENED 15 AMP LINE FUSE P295428 TOPAZ LN-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
231070480 | MEY3100 | 2025-04-08 | Q2 | 11:52 | 14:15 | 2:23 | 2 | 23 | 143 | 15 | 2145 | SOUTH LAKE TAHOE | MANUALLY OPENED 11 AMP LINE FUSE P239180 TROUT CREEK AVE-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231070652 | TPZ1202 | 2025-04-10 | Q2 | 7:33 | 15:45 | 8:12 | 8 | 12 | 492 | 2 | 984 |  | MANUALLY OPENED LINE FUSE P295428 TOPAZ LN TO REPLACE CONDUCTOR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231070689 | MEY3100 | 2025-04-10 | Q2 | 8:50 | 14:45 | 5:55 | 5 | 55 | 355 | 13 | 4615.2 |  | MANAULLY OPENED TRANSFORMER FUSE AT P98942 FOR POLE REPLACEMENT. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
231070976 | TPZ1202 | 2025-04-14 | Q2 | 14:10 | 18:25 | 4:15 | 4 | 15 | 255 | 6 | 1530 |  | MANUALLY OPENED 15 AMP FUSE P286985 US HWY 395 TO REBUILD TAP | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | E2_Exclusion | NONE | [6 empty] | This box shows the monthly results per the local reporting criteria
231071036 | TPZ1202 | 2025-04-15 | Q2 | 11:00 | 17:45 | 6:45 | 6 | 45 | 405 | 6 | 2430 |  | MANUALLY OPENED 15 AMP LINE FUSE P286985 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
231071202 | TPZ1202 | 2025-04-17 | Q2 | 11:00 | 15:26 | 4:26 | 4 | 26 | 266 | 2 | 532.2 |  | MANUALLY OPENED LINE FUSE P293569 US HIGHWAY 395, REBUILD TAP | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
231071207 | TPZ1202 | 2025-04-17 | Q2 | 11:00 | 15:45 | 4:45 | 4 | 45 | 285 | 6 | 1710 |  | MANUALLY OPENED 15 AMP LINE FUSE P286985 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 7 | 3761 | 392847.6 | 49165 | 7.9904 | 0.076498 | 104.453 | 537.2857
231071336 | TPZ1202 | 2025-04-18 | Q2 | 11:00 | 15:30 | 4:30 | 4 | 30 | 270 | 2 | 540 |  | MANUALLY OPENED LINE FUSE P293569 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
231071910 | TAH5201 | 2025-04-21 | Q2 | 12:00 | 14:50 | 2:50 | 2 | 50 | 170 | 18 | 3060 |  | MANUALLY OPENED TRANSFORMER FUSE P232484 LASSEN DR-REPLACE P131246 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072183 | MEY3200 | 2025-04-22 | Q2 | 12:20 | 15:30 | 3:10 | 3 | 10 | 190 | 84 | 15960 | SOUTH LAKE TAHOE | MANUALLY OPENED 65 AMP LINE FUSES P135340 WINNEMUCCA AVE-REPLACE P66424 &amp; P87937 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
231072292 | TAH7300 | 2025-04-23 | Q2 | 11:00 | 13:42 | 2:42 | 2 | 42 | 162 | 10 | 1620 |  | MANUALLY OPENED TRANSFORMER FUSE P100189 WOODLAND DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072297 | TAH7300 | 2025-04-23 | Q2 | 11:02 | 13:13 | 2:11 | 2 | 11 | 131 | 19 | 2488.8 |  | MANUALLY OPENED TRANSFORMER FUSE P85700 CEDAR LN-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072325 | TAH7300 | 2025-04-23 | Q2 | 13:30 | 17:00 | 3:30 | 3 | 30 | 210 | 14 | 2940 |  | MANUALLY OPENED TRANSFORMER FUSE P115505 SNOWBIRD LOOP-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072333 | TAH7300 | 2025-04-23 | Q2 | 14:37 | 17:33 | 2:56 | 2 | 56 | 176 | 4 | 703.8 |  | MANUALLY OPENED TRANSFORMER FUSE P100251 CREST DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072379 | TAH7300 | 2025-04-23 | Q2 | 17:24 | 18:35 | 1:11 | 1 | 11 | 71 | 13 | 922.8 |  | MANUALLY OPENED TRANSFORMER FUSE P81718 LARK DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072396 | TAH7300 | 2025-04-23 | Q2 | 23:20 | 4:30 | 5:10 | 5 | 10 | 310.2 | 5 | 1551 |  | MANUALLY OPENED 20 AMP LINE FUSE P8531 STATE HWY 89-REPLACED P92494 &amp; INSTALLED NEW POLE BETWEEN P92494 &amp; P92495 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072423 | TAH7300 | 2025-04-24 | Q2 | 11:42 | 15:40 | 3:58 | 3 | 58 | 238 | 30 | 7140 |  | MANUALLY OPENED LINE FUSE P296726 FLICKER AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231072507 | MEY3300 | 2025-04-25 | Q2 | 3:15 | 4:50 | 1:35 | 1 | 35 | 95.47 | 11 | 1050 |  | REPLACED LEAKING TRANSFORMER P120347 TOPPEWETAH ST | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake
231072540 | TAH7300 | 2025-04-25 | Q2 | 11:06 | 16:12 | 5:06 | 5 | 6 | 306 | 4 | 1224 |  | MANUALLY OPENED TRANSFORMER FUSES P105231 LAKEVIEW DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231073303 | MULLER1296 | 2025-04-29 | Q2 | 13:08 | 17:25 | 4:17 | 4 | 17 | 257 | 16 | 4111.8 | MARKLEEVILLE | MANUALLY OPENED LINE FUSE P117493 PINION RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
231074773 | TAH7300 | 2025-04-30 | Q2 | 11:05 | 11:48 | 0:43 | 0 | 43 | 43 | 1 | 43.2 |  | MANUALLY OPENED TRANSFORMER FUSE P275814 FOREST VIEW DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake
231075048 | MEY3200 | 2025-04-30 | Q2 | 16:20 | 17:22 | 1:02 | 1 | 2 | 62 | 16 | 991.8 |  | MANUALLY OPENED TRANSFORMER FUSE P77123 RAINBOW DR-REPLACE LEAKING TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 | [5 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## May
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | Under 5 Minutes? | Is CMI = to CI*Duration? | E2_Exclusion | (All)
120049496 | TAH7300 | 2025-05-01 | Q2 | 11:00 | 12:54 | 1:54 | 1 | 54 | 114 | 13 | 1482 |  | MANUALLY OPENED TRANSFORMER FUSE P115683 ANTELOPE WAY-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231076383 | TAH7300 | 2025-05-01 | Q2 | 13:09 | 15:39 | 2:30 | 2 | 30 | 150 | 3 | 450 |  | MANUALLY OPENED TRANSFORMER FUSES P99233 PLACER ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231076388 | TAH7300 | 2025-05-01 | Q2 | 13:19 | 15:25 | 2:06 | 2 | 6 | 126 | 9 | 1134 |  | MANUALLY OPENED TRANSFORMER FUSES P99236 PLACER ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | 99 | 7741 | 1972950 | 49165 | 40.1292 | 0.15745 | 254.8702 | 78.1919
120049672 | MEY3300 | 2025-05-02 | Q2 | 1:15 | 7:02 | 5:47 | 5 | 47 | 347.28 | 921 | 68073 | SOUTH LAKE TAHOE | MANUALLY OPENED PTR 3300-R3 FOR PLANNED WORK P111401 REPLACEMENT. MANUALLY OPENED 33M58 DISC. SWITCHING TO RESTORE FROM 33-34-T1 DURING WORK. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | FALSE
120049712 | TAH7300 | 2025-05-02 | Q2 | 11:06 | 12:50 | 1:44 | 1 | 44 | 104 | 8 | 832.2 |  | MANUALLY OPENED TRANSFORMER FUSE P73389 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | E2_Exclusion | PLANNED OUTAGE
120049734 | TAH7300 | 2025-05-02 | Q2 | 12:56 | 15:25 | 2:29 | 2 | 29 | 149 | 9 | 1341 |  | MANUALLY OPENED TRANSFORMER FUSE P77266 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120049735 | TAH7300 | 2025-05-02 | Q2 | 13:00 | 15:37 | 2:37 | 2 | 37 | 157 | 12 | 1884 |  | MANUALLY OPENED TRANSFORMER FUSE P77269 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231077961 | TAH7300 | 2025-05-02 | Q2 | 15:48 | 18:24 | 2:36 | 2 | 36 | 156 | 17 | 2652 |  | MANUALLY OPENED TRANSFORMER FUSE P269681 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | 71 | 4251 | 1227707.4 | 49165 | 24.9712 | 0.086464 | 288.8044 | 59.8732
120049911 | TAH7300 | 2025-05-03 | Q2 | 16:01 | 20:45 | 4:44 | 4 | 44 | 284 | 42 | 11928 | TAHOMA | BLOWN 15 AMP LINE FUSES P216281 2ND AVE-TREE FELL ONTO PRIMARY P216285 DURING VEGETATION CLEARING | Act Of Man | Vegetation clearing | Review Complete | THIRD PARTY | North Lake | FALSE | TRUE
231078791 | TRK7202 | 2025-05-03 | Q2 | 22:21 | 2:05 | 3:44 | 3 | 44 | 224 | 3 | 672 | TRUCKEE | BLOWN 15 AMP LINE FUSE P224058 RIVER RD-SQUIRREL CONTACT, DURING PATROL, A BROKEN CROSSARM P29394 RIVER RD WAS FOUND | Animal | Squirrel | Review Complete | NONE | North Lake | FALSE | TRUE | E2_Exclusion | LOSS OF SUPPLY
120050015 | KBH5200 | 2025-05-05 | Q2 | 11:00 | 12:52 | 1:52 | 1 | 52 | 112 | 9 | 1008 |  | MANUALLY OPENED TRANSFORMER FUSE P236658 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120050016 | KBH5200 | 2025-05-05 | Q2 | 11:00 | 12:50 | 1:50 | 1 | 50 | 110 | 6 | 660 |  | MANUALLY OPENED TRANSFORMER FUSE P96794 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120050033 | SQV7201 | 2025-05-05 | Q2 | 11:57 | 13:33 | 1:36 | 1 | 36 | 96 | 14 | 1344 |  | MANUALLY OPENED TRANSFORMER FUSE P115872 BEAR CREEK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | 1 | 632 | 20856 | 49165 | 0.4242 | 0.012855 | 33 | 632
231079063 | KBH5200 | 2025-05-05 | Q2 | 13:08 | 14:38 | 1:30 | 1 | 30 | 90 | 8 | 720 |  | MANUALLY OPENED TRANSFORMER FUSE P292097 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120050065 | SQV7201 | 2025-05-05 | Q2 | 14:19 | 16:29 | 2:10 | 2 | 10 | 130 | 10 | 1300.2 |  | MANUALLY OPENED TRANSFORMER FUSE P206081 BEAR CREEK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | E2_Exclusion | THIRD PARTY
120050064 | KBH5200 | 2025-05-05 | Q2 | 14:48 | 17:00 | 2:12 | 2 | 12 | 132 | 11 | 1452 |  | MANUALLY OPENED TRANSFORMER FUSE P292095 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231079223 | KBH5200 | 2025-05-06 | Q2 | 11:00 | 13:08 | 2:08 | 2 | 8 | 128 | 8 | 1024.2 |  | MANUALLY OPENED TRANSFORMER FUSES P281583 WILDCHERRY LN-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231079227 | KBH5200 | 2025-05-06 | Q2 | 11:00 | 13:08 | 2:08 | 2 | 8 | 128 | 8 | 1024.2 |  | MANUALLY OPENED TRANSFORMER FUSES P292094 WILDCHERRY LN-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | 3 | 60 | 13270.8 | 49165 | 0.26992 | 0.0012204 | 221.18 | 20
231079236 | KBH5200 | 2025-05-06 | Q2 | 11:06 | 13:32 | 2:26 | 2 | 26 | 146 | 12 | 1752 |  | MANUALLY OPENED TRANSFORMER FUSES P81466 WOODCHUCK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231079242 | KBH5200 | 2025-05-06 | Q2 | 11:06 | 13:32 | 2:26 | 2 | 26 | 146 | 17 | 2482.2 |  | MANUALLY OPENED TRANSFORMER FUSES P81468 WOODCHUCK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | E2_Exclusion | (blank)
120050240 | KBH5200 | 2025-05-07 | Q2 | 11:03 | 14:24 | 3:21 | 3 | 21 | 201 | 8 | 1608 |  | MANUALLY OPENED TRANSFORMER FUSE P61481 TERRACE AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120050238 | POR3200 | 2025-05-07 | Q2 | 11:04 | 18:00 | 6:56 | 6 | 56 | 416 | 56 | 23296.2 | PORTOLA | MANUALLY OPENED 140A FUSES P193853 TO LIFT TAPS AT P193849 FOR RT CLEARANCE# 1061 - MAINTENANCE POLE AND CROSS ARM REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120050239 | KBH5200 | 2025-05-07 | Q2 | 11:10 | 14:20 | 3:10 | 3 | 10 | 190 | 7 | 1330.2 |  | MANUALLY OPENED TRANSFORMER FUSE P45306 TERRACE AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231079471 | KBH5200 | 2025-05-07 | Q2 | 14:54 | 16:11 | 1:17 | 1 | 17 | 77 | 9 | 693 |  | MANUALLY OPENED TRANSFORMER FUSE P68501 NEVADA ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231079492 | KBH5200 | 2025-05-07 | Q2 | 16:23 | 17:09 | 0:46 | 0 | 46 | 46 | 6 | 276 |  | MANUALLY OPENED TRANSFORMER FUSE P68504 NEVADA ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | E2_Exclusion | (blank)
120050291 | TAH5201 | 2025-05-07 | Q2 | 19:36 | 6:36 | 10:59 | 10 | 59 | 659.95 | 263 | 89980.8 | TAHOE CITY | BLOWN 40A RISER FUSE (1 OF 3) P140177 LAKE FOREST RD - MANUALLY OPENED OTHER TWO FUSES - MADE OPEN AT GLEN BAIRD - FAILED CABLE ON GLEN BAIRD AT VAULT 1791 | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | FALSE
120050293 | MEY3200 | 2025-05-07 | Q2 | 23:16 | 5:26 | 6:09 | 6 | 9 | 369.8 | 544 | 201180 | SOUTH LAKE TAHOE | MANUALLY OPENED VFI-903-75 'B' POS L/B AT VENICE DR FOR REPLACEMENT OF OS-900 WITH LJE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231079599 | KBH5200 | 2025-05-08 | Q2 | 11:56 | 14:05 | 2:09 | 2 | 9 | 129 | 7 | 903 |  | MANUALLY OPENED P291799 REPLACE OPEN WIRE - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231079602 | KBH5200 | 2025-05-08 | Q2 | 12:00 | 14:05 | 2:05 | 2 | 5 | 125 | 7 | 874.8 |  | MANUALLY OPENED P232345 REPLACE OPEN WIRE - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120050416 | KBH5200 | 2025-05-09 | Q2 | 11:18 | 13:15 | 1:57 | 1 | 57 | 117 | 2 | 234 |  | MANUALLY OPENED TRANSFORMER FUSE P183396 MOUNTAIN CIR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | E2_Exclusion | (blank)
120050417 | KBH5200 | 2025-05-09 | Q2 | 11:26 | 13:25 | 1:59 | 1 | 59 | 119 | 3 | 357 |  | MANUALLY OPENED TRANSFORMER FUSE P183397 MOUNTAIN CIR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231079745 | MEY3100 | 2025-05-09 | Q2 | 11:50 | 12:00 | 0:10 | 0 | 10 | 10 | 14 | 139.8 |  | MANUALLY OPENED TRANSFORMER FUSES P192841 LAKEVIEW AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231079754 | MEY3100 | 2025-05-09 | Q2 | 12:05 | 12:11 | 0:06 | 0 | 6 | 6 | 23 | 138 |  | MANUALLY OPENED TRANSFORMER FUSES P192985 LAKEVIEW AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231079763 | MEY3100 | 2025-05-09 | Q2 | 12:15 | 12:31 | 0:16 | 0 | 16 | 16 | 12 | 192 |  | MANUALLY OPENED TRANSFORMER FUSES P293178 LAKEVIEW AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231079769 | MEY3100 | 2025-05-09 | Q2 | 12:38 | 12:56 | 0:18 | 0 | 18 | 18 | 23 | 414 |  | MANUALLY OPENED TRANSFORMER FUSES P2904458 SAN FRANSICO AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | E2_Exclusion | NONE | [6 empty] | This box shows the monthly results per the local reporting criteria
120050482 | POR3100 | 2025-05-10 | Q2 | 18:38 | 0:02 | 5:24 | 5 | 24 | 324.3 | 1 | 324.6 | PORTOLA | BLOWN FUSE P281378 PARK ST-FAILED CUTOUTS | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | TRUE | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
120050557 | MEY3400 | 2025-05-11 | Q2 | 17:10 | 17:22 | 0:11 | 0 | 11 | 11.7 | 264 | 3074.4 | SOUTH LAKE TAHOE | MANUALLY OPENED 3400-R2 DUE TO 'A' PHASE OFF OF LOW SIDE OF RECLOSER - MANUALLY OPENED 3400-R1 TO SAFELY BYPASS 3400-R1 | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
120050564 | TPZ1202 | 2025-05-11 | Q2 | 19:53 | 23:10 | 3:17 | 3 | 17 | 197 | 1 | 196.8 | WALKER | BROKEN NEUTRAL AT THE TOP OF TRANSFORMER P264126 EASTSIDE LN | Equipment | Vibration/Loose Connection | Review Complete | NONE | South Lake | FALSE | TRUE | 24 | 2798 | 711115.8 | 49165 | 14.4639 | 0.05691 | 254.1515 | 116.5833
120050572 | GLS7400 | 2025-05-11 | Q2 | 23:37 | 7:45 | 8:08 | 8 | 8 | 488.5 | 11 | 3708.6 | TRUCKEE | BLOWN 20 AMP LINE FUSE P224119 LA MIRADA RD, TREE TOOK PRIMARY DOWN P239508 LA MIRADA RD | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | FALSE
231080014 | MEY3400 | 2025-05-12 | Q2 | 1:00 | 1:35 | 0:35 | 0 | 35 | 35 | 6 | 210 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P135280 UPLANDS WAY-REPAIRED LOOSE CLAMPS | Equipment | Other | Review Complete | NONE | South Lake | FALSE | TRUE
231080031 | MEY3400 | 2025-05-12 | Q2 | 3:40 | 16:20 | 12:40 | 12 | 40 | 760.15 | 249 | 189277.2 | SOUTH LAKE TAHOE | 3400-R3 PTR L/O - TREE DOWN AT P286894 NEAR BALDWIN DR | Vegetation | Fall In Tree | Review Complete | NONE | South Lake | FALSE | TRUE
120050576 | STL3501 | 2025-05-12 | Q2 | 5:47 | 11:25 | 5:38 | 5 | 38 | 338 | 198 | 66924 | SOUTH LAKE TAHOE | BLOWN 40K LINE FUSE P97024 RUFUS ALLEN BLVD-TREE DOWN, WIRE DOWN BETWEEN P62581 &amp; P68528 PICKETT AVE | Vegetation | Fall In Tree | Review Complete | NONE | South Lake | FALSE | TRUE
120050638 | TAH5201 | 2025-05-12 | Q2 | 10:06 | 11:52 | 1:46 | 1 | 46 | 106.48 | 31 | 3300.6 | CARNELIAN BAY | BLOWN 20 AMP LINE FUSE P124671 RUMAR WAY-WIRES SLAPPED TOGETHER AT P295808 (FORMERLY P151349) | Weather | Wind | Review Complete | NONE | North Lake | FALSE | TRUE
120050655 | MULLER1296 | 2025-05-12 | Q2 | 11:58 | 16:00 | 4:02 | 4 | 2 | 242 | 1 | 241.8 | MARKLEEVILLE | BLOWN 15 AMP LINE FUSE P214638 CARSON RIVER RD-WIND | Weather | Wind | Review Complete | NONE | South Lake | FALSE | TRUE
120050665 | TPZ1202 | 2025-05-12 | Q2 | 12:14 | 19:15 | 7:01 | 7 | 1 | 421.13 | 5 | 2105.4 |  | BLOWN 20 AMP LINE FUSE P286952 US HWY 395-TREE LIMB ON WIRES | Vegetation | Fall In Limb | Review Complete | NONE | South Lake | FALSE | TRUE
120050648 | TPZ1202 | 2025-05-12 | Q2 | 12:21 | 19:15 | 6:54 | 6 | 54 | 414 | 702 | 290338.8 | COLEVILLE | PTR 1202-R1 L/O (DID HAVE FIRE SEASON ON)-BROKEN TAP BEYOND FUSES AT P286952, WIRE DOWN P92757 | Weather | Wind | Review Complete | NONE | South Lake | FALSE | FALSE
120050701 | TPZ1202 | 2025-05-12 | Q2 | 23:05 | 1:15 | 2:09 | 2 | 9 | 129.85 | 1 | 129.6 | COLEVILLE | BAD SECONDARY &amp; CONNECTIONS P199419 US HWY 395 | Weather | Wind | Review Complete | NONE | South Lake | FALSE | TRUE
231080310 | MEY3400 | 2025-05-13 | Q2 | 11:40 | 17:00 | 5:20 | 5 | 20 | 320 | 4 | 1279.8 |  | MANUALLY OPENED 11 AMP LINE FUSE P234199 FALLEN LEAF RD-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231080314 | KBH5200 | 2025-05-13 | Q2 | 11:48 | 14:40 | 2:52 | 2 | 52 | 172 | 6 | 1032 |  | MANUALLY OPENED TRANSFORMER FUSE P81589 WILDWOOD RD-REPLACE SECONDARY WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231080317 | KBH5200 | 2025-05-13 | Q2 | 11:48 | 14:40 | 2:52 | 2 | 52 | 172 | 4 | 688.2 |  | MANUALLY OPENED TRANSFORMER FUSE P81590 WILDWOOD RD-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231080320 | KBH5200 | 2025-05-13 | Q2 | 11:48 | 14:57 | 3:09 | 3 | 9 | 189 | 5 | 945 |  | MANUALLY OPENED TRANSFORMER FUSE P81592 CATALPA DR-REPLACE OPEN WIRE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | FALSE | TRUE
120050729 | TPZ1202 | 2025-05-13 | Q2 | 15:52 | 17:40 | 1:47 | 1 | 47 | 108 | 2 | 216 | TOPAZ | BLOWN 15K FUSE P 266619 - LIKELY DUE TO WIND | Weather | Wind | Review Complete | NONE | South Lake | FALSE | TRUE
231080459 | MEY3400 | 2025-05-14 | Q2 | 11:00 | 15:45 | 4:45 | 4 | 45 | 285 | 4 | 1140 |  | MANUALLY OPENED 11 AMP LINE FUSE P234199 FALLEN LEAF RD-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120050982 | TAH5201 | 2025-05-14 | Q2 | 17:55 | 18:15 | 0:20 | 0 | 20 | 20 | 1 | 19.8 | TAHOE CITY | REPLACED LOOSE CONNECTOR ON P242217 SERVICE WIRES - GROVE ST. | Equipment | Vibration/Loose Connection | Review Complete | NONE | North Lake | FALSE | TRUE
120050989 | POR3100 | 2025-05-15 | Q2 | 1:23 | 8:21 | 6:57 | 6 | 57 | 417.88 | 734 | 306554.4 | PORTOLA | MANUALLY OPENED POR3100 CB FOR PLANNED OUTAGE - POLE REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | FALSE
120050999 | POR3200 | 2025-05-15 | Q2 | 2:10 | 8:21 | 6:10 | 6 | 10 | 370.8 | 1199 | 444231 | PORTOLA | MANUALLY OPENED 3200-7 L/B FOR PLANNED WORK - POLE REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | FALSE
120051335 | MEY3500 | 2025-05-18 | Q2 | 12:36 | 2:35 | 13:59 | 13 | 59 | 839.33 | 5 | 3926.4 | SOUTH LAKE TAHOE | BLOWN RISER FUSES P259771 MEADOW CREST DR-FAILED TRANSFORMER #55202 | Equipment | Other | Review Complete | NONE | South Lake | FALSE | FALSE
120051407 | MULLER1296 | 2025-05-18 | Q2 | 23:00 | 1:00 | 2:00 | 2 | 0 | 120 | 2 | 240 | MARKLEEVILLE | MANUALLY OPENED TRANSFORMER FUSE P277655 CRYSTAL SPRINGS RD-TREE TOOK DOWN SECONDARY ACROSS RIVER | Vegetation | Fall In Tree | Review Complete | NONE | South Lake | FALSE | TRUE
120051469 | SQV8100; SQV8200 | 2025-05-19 | Q2 | 10:30 | 11:20 | 0:50 | 0 | 50 | 50.22 | 956 | 47133.6 | OLYMPIC VALLEY | SQUAW VALLEY 1001 CS LOCKED OUT - 8100 &amp; 8200 CIRCUITS DE-ENERGIZED - FAILED REG 1 CAUSED BUS LOCKOUT | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | FALSE
231081457 | MEY3400 | 2025-05-19 | Q2 | 11:27 | 18:05 | 6:38 | 6 | 38 | 398 | 4 | 1591.8 |  | MANUALLY OPENED FUSE P234199 FALLEN LEAF RD - TAP REBUILD | Planned | Maintenance |  | PLANNED OUTAGE | South Lake | FALSE | TRUE
231082739 | MEY3400 | 2025-05-20 | Q2 | 11:30 | 20:00 | 8:30 | 8 | 30 | 510 | 4 | 2040 |  | MANUALLY OPENED 11 AMP LINE FUSE P234199 FALLEN LEAF RD-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231082885 | TAH7100 | 2025-05-21 | Q2 | 11:00 | 14:05 | 3:05 | 3 | 5 | 185 | 3 | 555 |  | MANUALLY OPENED TRANSFORMER FUSE P90663 GRANLIBAKKEN RD-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231082882 | TAH7100 | 2025-05-21 | Q2 | 11:10 | 14:15 | 3:05 | 3 | 5 | 185.43 | 9 | 1668.6 |  | MANUALLY OPENED TRANSFORMER FUSE P90665 GRANLIBAKKEN RD-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120052203 | POR3200 | 2025-05-21 | Q2 | 12:25 | 19:40 | 7:15 | 7 | 15 | 435 | 15 | 6525 | PORTOLA | MANUALLY OPENED 11 AMP LINE FUSE P70989 N GULLING ST-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231082932 | TAH7100 | 2025-05-21 | Q2 | 14:15 | 16:57 | 2:42 | 2 | 42 | 162 | 12 | 1944 |  | MANUALLY OPENED TRANSFORMER FUSE P90668 RAWHIDE DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231082939 | TAH7100 | 2025-05-21 | Q2 | 14:46 | 17:57 | 3:10 | 3 | 10 | 190.82 | 11 | 2098.8 |  | MANULLY OPENED TRANSFORMER FUSE P90670 RAWHIDE DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231082998 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 37 | 16834.8 |  | MANUALLY OPENED P68780 TREE REMOVAL - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231083001 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:38 | 7:38 | 7 | 38 | 458 | 20 | 9160.2 |  | MANUALLY OPENED P68783 ELOSIE TREE REMOVAL - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231083004 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 11 | 5005.2 | SOUTH LAKE TAHOE | MANUALLY OPENED P68784 ELOSIE TREE REMOVAL - PLANNED OUTAGE &#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231083007 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 28 | 12739.8 | SOUTH LAKE TAHOE | MANUALLY OPENED P68787 ELOSIE TREE REMOVAL - PLANNED OUTAGE &#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231083014 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 13 | 5914.8 |  | MANUALLY OPENED P290425 ELOSIE TREE REMOVAL - PLANNED OUTAGE&#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231083017 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 4 | 1819.8 |  | MANUALLY OPENED P69852 12th ST TREE REMOVAL - PLANNED OUTAGE &#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120052436 | TAH5201 | 2025-05-22 | Q2 | 11:01 | 15:30 | 4:29 | 4 | 29 | 269.08 | 25 | 2490.6 | TAHOE CITY | BLOWN 10 AMP LINE FUSE P232266 &amp; P249279 BLOWN 11 AMP FUSE REPLACED U/G PADMOUNT TRANSFORMER 142 | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | FALSE
120052438 | KBH4202 | 2025-05-22 | Q2 | 11:09 | 13:17 | 2:07 | 2 | 7 | 127.55 | 36 | 4591.2 |  | MANUALLY OPENED TRANSFORMER FUSE P92263 GOLDEN AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083042 | MEY3400 | 2025-05-22 | Q2 | 11:17 | 19:23 | 8:06 | 8 | 6 | 486.32 | 4 | 1945.2 |  | MANUALLY OPENED 11K FUSE P234199 FOR PLANNED WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231083069 | KBH4202 | 2025-05-22 | Q2 | 13:37 | 15:50 | 2:13 | 2 | 13 | 133 | 17 | 2260.8 |  | MANUALLY OPENED P242138 REPLACE OPEN WIRE SALMON AVE - PLANNED OUTAGE | Planned | Other | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083070 | KBH4202 | 2025-05-22 | Q2 | 13:37 | 15:50 | 2:13 | 2 | 13 | 133 | 15 | 1995 |  | MANUALLY OPENED P81491 REPLACE OPEN WIRE SALMON AVE - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083108 | KBH4202 | 2025-05-22 | Q2 | 16:05 | 16:55 | 0:50 | 0 | 50 | 50 | 10 | 499.8 |  | MANUALLY OPENED P81487 CHIPMUNK REPLACE OPEN WIRE PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083111 | KBH4202 | 2025-05-22 | Q2 | 16:05 | 16:55 | 0:50 | 0 | 50 | 50 | 6 | 300 |  | MANUALLY OPENED P81488 CHIPMUNK REPLACE OPEN WIRE PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120052595 | KBH4202 | 2025-05-23 | Q2 | 11:00 | 12:24 | 1:24 | 1 | 24 | 84 | 9 | 756 |  | MANUALLY OPENED TRANSFORMER FUSE P60543 SPEEDBOAT AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083240 | TAH7300 | 2025-05-23 | Q2 | 11:19 | 12:58 | 1:39 | 1 | 39 | 99 | 7 | 693 |  | MANUALLY OPENED XFMR FUSES P124755 GROUSE DR - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083249 | TAH7300 | 2025-05-23 | Q2 | 12:37 | 14:15 | 1:38 | 1 | 38 | 98 | 10 | 979.8 |  | MANUALLY OPENED XFMRS P134312 GROUSE DR - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120052601 | KBH4203 | 2025-05-23 | Q2 | 12:45 | 14:26 | 1:41 | 1 | 41 | 101 | 14 | 1414.2 |  | MANUALLY OPENED TRANSFORMER FUSE P60529 BEAR ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083254 | KBH4203 | 2025-05-23 | Q2 | 13:03 | 14:37 | 1:34 | 1 | 34 | 94 | 5 | 469.8 |  | MANUALLY OPENED XFMR FUSES P60526 BEAR ST - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083284 | TAH7300 | 2025-05-23 | Q2 | 14:30 | 16:20 | 1:50 | 1 | 50 | 110 | 9 | 990 |  | MANUALLY OPENED XFMR FUSES P134316 CHUKAR CIR - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120052610 | KBH4203 | 2025-05-23 | Q2 | 15:00 | 15:34 | 0:34 | 0 | 34 | 34 | 12 | 408 |  | MANUALLY OPENED TRANSFORMER FUSE P35583 BEAR ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120052723 | MULLER1296 | 2025-05-24 | Q2 | 11:13 | 11:46 | 0:33 | 0 | 33 | 33 | 632 | 20856 |  | NVE 112 LINE LOCKOUT ROUND HILL TO BUCKEYE - TRANSMISISON FAULT BETWEEN ROUND HILL AND MULLER | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | FALSE | TRUE
231083680 | TAH7100 | 2025-05-27 | Q2 | 11:10 | 14:14 | 3:04 | 3 | 4 | 184 | 22 | 4048.2 | TAHOE CITY | MANUALLY OPENED TRANSFORMER FUSE P90692 VIRGINIA DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231083855 | TAH7300 | 2025-05-28 | Q2 | 10:43 | 11:11 | 0:28 | 0 | 28 | 28 | 6 | 168 |  | MANUALLY OPENED TRANSFORMER FUSE P155487 STATE HWY 89-REPLACED CUTOUT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120053128 | MEY3500 | 2025-05-28 | Q2 | 11:53 | 15:41 | 3:47 | 3 | 47 | 227.77 | 4 | 910.8 |  | MANUALLY DISCONNECTED PRIMARY P81961 &amp; P81962 RUBICON TRL-REPLACED PRIMARY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120053171 | MEY3200 | 2025-05-28 | Q2 | 18:00 | 4:20 | 10:20 | 10 | 20 | 620.5 | 95 | 58947.6 | SOUTH LAKE TAHOE | MANUALLY OPENED VFI-3200-2 'E' POS-PRIMARY U/G REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231084021 | TAH5201 | 2025-05-29 | Q2 | 13:01 | 13:14 | 0:13 | 0 | 13 | 13 | 17 | 220.8 |  | MANUALLY OPNED P281490 PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | FALSE | TRUE
231084027 | TAH5201 | 2025-05-29 | Q2 | 13:23 | 13:32 | 0:09 | 0 | 9 | 9 | 10 | 90 |  | MANUALLY OPENED P61458 REPLACE CUTOUT -PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | FALSE | TRUE
120053218 | STL3501 | 2025-05-29 | Q2 | 14:04 | 17:27 | 3:23 | 3 | 23 | 203 | 16 | 3247.8 | SOUTH LAKE TAHOE | BLOWN TRANSFORMER FUSE P71162 DEER PARK AVE - NO CAUSE FOUND. | Other | Unknown | Review Complete | NONE | South Lake | FALSE | TRUE
120053206 | MEY3300 | 2025-05-29 | Q2 | 14:06 | 15:26 | 1:19 | 1 | 19 | 79.63 | 14 | 1114.8 | SOUTH LAKE TAHOE | BLOWN TRANSFORMER FUSE P84216 NAVAHOE DR-SERVICE RIPPED DOWN BY TRUCK. CSP UNSAFE TO OPERATE | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | South Lake | FALSE | TRUE
120053223 | MEY3200 | 2025-05-29 | Q2 | 15:16 | 16:13 | 0:57 | 0 | 57 | 57 | 4 | 228 | SOUTH LAKE TAHOE | BLOWN TRANSFORMER FUSE P84634 ELOISE AVE-SERVICE RIPPED DOWN BY TRUCK | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | South Lake | FALSE | TRUE
231084161 | KBH5200 | 2025-05-30 | Q2 | 13:23 | 13:35 | 0:12 | 0 | 12 | 12 | 6 | 72 |  | MANUALLY OPENED CUT OUTS AND REPLACED THEM AT P239496 CARNELIAN DR | Equipment | Other | Review Complete | NONE | North Lake | FALSE | TRUE
120053420 | MEY3200 | 2025-05-31 | Q2 | 9:29 | 10:38 | 1:09 | 1 | 9 | 69 | 1 | 69 | SOUTH LAKE TAHOE | PARTIAL POWER P290767 TATA LN DUE TO BAD CONNECTIONS | Equipment | Other | Review Complete | NONE | South Lake | FALSE | TRUE
120053437 | TAH5201 | 2025-05-31 | Q2 | 13:03 | 14:10 | 1:07 | 1 | 7 | 67 | 48 | 3216 | TAHOE CITY | BLOWN 20 AMP FUSE P137671 GROVE ST - NO CAUSE FOUND; SUN SAID HE DIDNT FIND AN OBVIOUS CAUSE - SUSPECTS IT MIGHT HAVE BEEN A TREE LIMB TOUCH | Unknown |  | Review Complete | NONE | North Lake | FALSE | TRUE
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## June
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | Under 5 Minutes? | Is CMI = to CI*Duration? | E2_Exclusion | (All)
120053508 | MULLER1296 | 2025-06-01 | Q2 | 12:38 | 14:04 | 1:26 | 1 | 26 | 86 | 632 | 54352.2 | MARKLEEVILLE | NVE 112 LINE LOCKOUT ROUND HILL TO BUCKEYE - TRANSMISISON FAULT BETWEEN BUCKEYE (NVE) &amp; ROUNDHILL (NVE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | FALSE | TRUE
231084420 | STL3501 | 2025-06-02 | Q2 | 0:00 | 19:30 | 19:30 | 19 | 30 | 1170 | 39 | 45630 |  | MANUALLY OPENED 25AMP LINE FUSE P291287 BLACKWOOD RD PULLED NEW UG | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
231084424 | STL3501 | 2025-06-02 | Q2 | 11:00 | 19:30 | 8:30 | 8 | 30 | 510 | 19 | 9690 | SOUTH LAKE TAHOE | MANUALLY OPENED 25 AMP LINE FUSE P291288 PULLED NEW UG | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | 67 | 29034 | 4140615 | 49165 | 84.2188 | 0.59054 | 142.6126 | 433.3433
231084433 | KBH5200 | 2025-06-02 | Q2 | 12:01 | 12:10 | 0:09 | 0 | 9 | 9 | 5 | 45 |  | MANUALLY OPENED TRANSFORMER FUSE, REPLACED DAMAGED CUTOUT P206174 CARNELIAN BAY RD | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | TRUE
120053556 | KBH4202 | 2025-06-02 | Q2 | 12:07 | 17:03 | 4:55 | 4 | 55 | 295.93 | 1 | 91.2 | KINGS BEACH | RAN MID SPAN TAP AND ELIMINATE APPROXIMATELY 35FT OF CABLE PARK LN | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | FALSE | E2_Exclusion | PLANNED OUTAGE
120053608 | MEY3400 | 2025-06-03 | Q2 | 11:44 | 15:59 | 4:15 | 4 | 15 | 255 | 15 | 3825 |  | MANUALLY OPENED LB 34-59 FOR PLANNED MAINTENANCE REPLACING SPAN GUY WITH DOWN GUY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120053645 | TAH7300 | 2025-06-03 | Q2 | 18:39 | 8:56 | 14:17 | 14 | 17 | 857.47 | 784 | 113171.4 | MEEKS BAY | PTR 7300-R2 P291747 HWY 89 LOCKED OPEN / SWITCHING TO ISOLATE OUTAGE - BLOWN FUSES P134488 HWY 89 - FAILED CABLE BETWEEN HH @ XFMR 13523 TO NEXT HH TO NORTH | Equipment | Corrosion/Decay | Mismatch - Number of customers | NONE | North Lake | FALSE | FALSE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120053662 | MEY3200 | 2025-06-03 | Q2 | 21:14 | 3:39 | 6:25 | 6 | 25 | 385.37 | 12 | 4263.6 |  | MANUALLY OPENED OS-902-23 'A' POS @ CAPRI DR AND PADMOUNT XFMR 3938 TAHOE KEYS BLVD ELBOWS TOWARD VFI-3200-2 'E' POS FOR CREW WORKING ON TAHOE KEYS UG REBUILD / RETURNED MEY 3400 AND 3200 TO NORMAL CONFIG - FS-903-65 'A' POS IS NORMAL OPEN TIE SWITCH - PHASING ISSUE RESOLVED | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | FALSE | 28 | 1679 | 383646.6 | 49165 | 7.8032 | 0.03415 | 228.4971 | 59.9643
120053823 | POR3200 | 2025-06-04 | Q2 | 12:41 | 15:33 | 2:52 | 2 | 52 | 172.55 | 32 | 5521.8 | PORTOLA | MANUALLY HUNG TEMPORARY CUTOUTS P155557 LADERA LN-REPLACE P130544 HUERTA WAY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120053934 | TAH7100 | 2025-06-05 | Q2 | 15:11 | 16:30 | 1:18 | 1 | 18 | 78.87 | 25 | 1971 | TAHOE CITY | BLOWN 25K LINE FUSES P108875 BIG PINE DR-GARBAGE TRUCK CLIPPED PHONE LINE CAUSING PHASES TO BUMP | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | North Lake | FALSE | TRUE | E2_Exclusion | LOSS OF SUPPLY
120053944 | MULLER1296 | 2025-06-05 | Q2 | 18:29 | 19:30 | 1:01 | 1 | 1 | 61 | 632 | 38551.8 | MARKLEEVILLE | 1296 CB @ MULLER (NVE) LOCKED OPEN - DUE TO DOWN WIRE AT NVE SIDE | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | FALSE | TRUE
120053966 | CAL2501 | 2025-06-05 | Q2 | 21:57 | 22:53 | 0:56 | 0 | 56 | 56 | 96 | 5376 | VERDI | CALIFORNIA 2501 CB (NVE) LOCKED OPEN / FIRE MODE &amp; WEATHER | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120053969 | WSH201 | 2025-06-05 | Q2 | 21:57 | 22:53 | 0:56 | 0 | 56 | 56 | 55 | 3079.8 | TRUCKEE | CALIFORNIA 2501 CB (NVE) LOCKED OPEN / FIRE MODE &amp; WEATHER | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE | 22 | 26250 | 3600323.4 | 49165 | 73.2294 | 0.53392 | 137.1552 | 1193.1818
120053976 | TPZ1202 | 2025-06-06 | Q2 | 1:01 | 3:44 | 2:43 | 2 | 43 | 163 | 595 | 96985.2 | COLEVILLE | MANUALLY OPENED LB# 1261-F @ P266658 HWY 395, REPLACED P# 128913 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | [9 empty] | 0.012102 | 55.09% | 1.9726 | 62.7%
120054056 | STL3501 | 2025-06-06 | Q2 | 11:39 | 11:52 | 0:13 | 0 | 13 | 13.43 | 38 | 510.6 |  | MANUALLY OPENED 25 AMP RISER FUSE P291287 BLACKWOOD RD-U/G SECONDARY MOLDINGS WERE MELTING | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | FALSE | TRUE | E2_Exclusion | THIRD PARTY
231085189 | SQV8200 | 2025-06-06 | Q2 | 11:40 | 13:10 | 1:30 | 1 | 30 | 90 | 96 | 8640 |  | MANUALLY OPENED 65 AMP LINE FUSE P278419 WINDING CREEK RD-REPLACED CROSSARMS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120054165 | TAH7300 | 2025-06-07 | Q2 | 11:07 | 18:34 | 7:27 | 7 | 27 | 447 | 6 | 2682 | TAHOE CITY | BLOWN TRANSFORMER FUSE P248973 QUAIL LN-REPLACED CUTOUT AND LEAKING TRANSFORMER | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120054499 | POR3200 | 2025-06-09 | Q2 | 11:00 | 13:20 | 2:20 | 2 | 20 | 140 | 11 | 1540.2 |  | MANUALLY OPENED LINE FUSE P193848 IDLE HOUR DR-REPLACE P155736 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | 1 | 25 | 1971 | 49165 | 0.040089 | 0.00050849 | 78.84 | 25
231085484 | MEY3400 | 2025-06-09 | Q2 | 11:44 | 13:15 | 1:31 | 1 | 31 | 91 | 3 | 273 |  | MANUALLY OPENED CUTOUT AT P291674 FOR PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120054579 | MULLER1296 | 2025-06-09 | Q2 | 22:52 | 0:59 | 2:07 | 2 | 7 | 127 | 633 | 80391 | MARKLEEVILLE | LOSS OF SOURCE FROM NVE - FAILED LIGHTNING ARRESTORS ON 1296-R1 (NVE) - BYPASSED&#x0D; | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | FALSE | TRUE | E2_Exclusion | (blank)
231085731 | GLS7400 | 2025-06-10 | Q2 | 13:41 | 14:45 | 1:04 | 1 | 4 | 64 | 10 | 640.2 |  | MANUALLY OPENED TRANSFORMER FUSE P161168 EDINBURGH DR-TRANSFORMER REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231085795 | GLS7600 | 2025-06-10 | Q2 | 16:25 | 16:35 | 0:10 | 0 | 10 | 10 | 1 | 10.2 |  | MANUALLY OPENED TRANSFORMER FUSE P252953 HINTON DR-PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120054673 | SLK257 | 2025-06-10 | Q2 | 21:35 | 21:52 | 0:17 | 0 | 17 | 17.35 | 3 | 52.2 | BORDERTOWN | LOSS OF SOURCE FROM NVE. CAUSE UNKNOWN | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231085854 | TAH5201 | 2025-06-11 | Q2 | 11:00 | 15:19 | 4:19 | 4 | 19 | 259 | 225 | 58275 | TAHOE CITY | MANUALLY OPENED 40 AMP LINE FUSE P92062 MAMMOTH DR-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231085950 | MEY3200 | 2025-06-12 | Q2 | 1:38 | 3:00 | 1:22 | 1 | 22 | 82 | 2 | 163.8 |  | MANUALLY OPENED LINE FUSES P84847 EMERALD BAY RD-REPLACE BROKEN CROSSARMS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | E2_Exclusion | (blank)
120054941 | SQV7201 | 2025-06-13 | Q2 | 11:45 | 14:45 | 3:00 | 3 | 0 | 180.2 | 96 | 17299.2 |  | MANUALLY LIFTED TAPS P292066 ALPINE MEADOWS RD-REPLACE CROSSARM P201221 (CLIMB JOB) | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120055062 | SQV8200 | 2025-06-15 | Q2 | 11:33 | 14:32 | 2:59 | 2 | 59 | 179 | 158 | 28282.2 | OLYMPIC VALLEY | BLOWN VFI 139- D POSTION VICTOR DR ANIMAL CONTACT P224075 VICTOR PLC | Animal | Squirrel | Review Complete | NONE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120055088 | MEY3400 | 2025-06-15 | Q2 | 21:25 | 22:07 | 0:42 | 0 | 42 | 42.42 | 23 | 975.6 | SOUTH LAKE TAHOE | BLOWN 30A LINE FUSES (2) P90945 LAKE TAHOE BLVD-RAVEN MADE CONTACT WITH WIRE AT P98772 COYOTE RIDGE CIR | Animal | Bird | Review Complete | NONE | South Lake | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
231086422 | TRK7202 | 2025-06-16 | Q2 | 15:35 | 15:51 | 0:16 | 0 | 16 | 16 | 4 | 64.2 |  | MANUALLY OPENED TRANSFORMER FUSE P68748 RIVER RD-REPAIRS TO LIGHTNING ARRESTOR | Equipment | Vibration/Loose Connection | Review Complete | NONE | North Lake | FALSE | TRUE
120055186 | STL3101 | 2025-06-17 | Q2 | 11:12 | 17:01 | 5:49 | 5 | 49 | 349.27 | 1 | 349.2 |  | MANUALLY OPENED 3101-R1 - MAINTENANCE ON CROSS ARMS AND JUMPERS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | E2_Exclusion | (blank)
120055392 | POR3100 | 2025-06-18 | Q2 | 11:35 | 17:28 | 5:52 | 5 | 52 | 352.78 | 201 | 70842 | PORTOLA | MANUALLY OPENED L./B# 31-4 AND FUSES P209782-MAINTENANCE REPLACING P215897 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | FALSE
231086902 | TPZ1202 | 2025-06-19 | Q2 | 1:11 | 4:00 | 2:48 | 2 | 48 | 168.82 | 8 | 1350.6 | COLEVILLE | MANUALLY OPENED 15 AMP LINE FUSE P266630 US HWY 395-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
120055466 | POR3200 | 2025-06-19 | Q2 | 11:24 | 17:14 | 5:50 | 5 | 50 | 350.85 | 24 | 8420.4 |  | MANUALLY OPENED JUMPERS P215801 MANZANITA ST-REPLACE P150554 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE |  |  | 0 | 49165 | 0 | 0 | #DIV/0! | #DIV/0!
120055467 | STL3501 | 2025-06-19 | Q2 | 11:52 | 16:26 | 4:34 | 4 | 34 | 274.53 | 82 | 22512 |  | MANUALLY LIFTED TAPS AT P286998 JUNIPER AVE - MAINTENANCE POLE &amp; CROSS ARM REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120055576 | MEY3500 | 2025-06-20 | Q2 | 13:22 | 14:00 | 0:38 | 0 | 38 | 38 | 5 | 190.2 | SOUTH LAKE TAHOE | BLOWN 25A LINE FUSE P297961 LODI AVE-BIRD | Animal | Bird | Review Complete | NONE | South Lake | FALSE | TRUE | E2_Exclusion | NONE | [6 empty] | This box shows the monthly results per the local reporting criteria
120055622 | TAH7300 | 2025-06-20 | Q2 | 21:38 | 5:47 | 8:09 | 8 | 9 | 489.25 | 1 | 489 | HOMEWOOD | REPLACED LOOSE HARDWARE AT THE CUTOUT 9291421 MOANA CIR | Equipment | Vibration/Loose Connection | Review Complete | NONE | North Lake | FALSE | TRUE | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
120055709 | KBH4202 | 2025-06-22 | Q2 | 19:16 | 0:09 | 4:53 | 4 | 53 | 293.43 | 1 | 293.4 | KINGS BEACH | BURNT SERVICE LINE AND CONNECTIONS P278531 BEAVER ST | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | TRUE | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
120055719 | MEY3200 | 2025-06-23 | Q2 | 11:21 | 13:20 | 1:58 | 1 | 58 | 118.58 | 41 | 4861.8 | SOUTH LAKE TAHOE | BLOWN RISER FUSE P87807 (1 OF 3). MANUALLY OPENED REMAINING 2 AT 10:31AM - REPLACED BAD UG CABLE | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | FALSE | TRUE | 16 | 1080 | 154674 | 49165 | 3.146 | 0.021967 | 143.2167 | 67.5
231087482 | TRK7203 | 2025-06-23 | Q2 | 14:11 | 18:59 | 4:47 | 4 | 47 | 287.7 | 8 | 2301.6 |  | MANUALLY OPENED VFI -170 C POSTION -INSTALL TRANFORMER P10551 FILOLI | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120055831 | POR3200 | 2025-06-24 | Q2 | 1:00 | 6:33 | 29:33 | 29 | 33 | 1773 | 3 | 1332 | PORTOLA | REPLACED FAILED TRANSFORMER P130541 LADERA LN | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | FALSE | FALSE
120055839 | MEY3300 | 2025-06-25 | Q2 | 0:19 | 2:18 | 1:59 | 1 | 59 | 119.37 | 139 | 16591.8 | SOUTH LAKE TAHOE | MANUALLY OPENED VFI-3300-21 'C' POS FUSES; REPLACING VAULT TOP SECTION SIDEWALK PROJECT NEAR P205200 APACHE AVE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120055834 | TPZ1202 | 2025-06-25 | Q2 | 0:20 | 2:05 | 1:44 | 1 | 44 | 104.97 | 2 | 210 | COLEVILLE | BLOWN 3A TRANSFORMER FUSE P294852 LARSON LN-NO PROBABLE CAUSE FOUND | UNKNOWN |  | Review Complete | NONE | South Lake | FALSE | TRUE
231087895 | TAH7100 | 2025-06-26 | Q2 | 11:08 | 14:00 | 2:52 | 2 | 52 | 172 | 6 | 1032 |  | MANUALLY OPENED TRANSFORMER FUSE P124649 ALPINE WAY-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120055997 | MEY3100 | 2025-06-26 | Q2 | 14:48 | 15:03 | 0:14 | 0 | 14 | 14.82 | 5 | 73.8 | SOUTH LAKE TAHOE | MANUALLY SWITCHED TO CREATE CLEARANCE ON 640 LINE AND 3100 FEEDER FOR MAINTENANCE ON POLE (G.O VIOLATIONS) | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
120056194 | POR3200 | 2025-06-27 | Q2 | 12:00 | 18:17 | 6:17 | 6 | 17 | 377 | 13 | 4900.8 | PORTOLA | MANUALLY OPENED TRANSFORMER FUSE P66233 MAGNOLIA AVE- POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
231088061 | MEY3300 | 2025-06-27 | Q2 | 12:08 | 14:00 | 1:52 | 1 | 52 | 112 | 9 | 1008 |  | MANUALLY OPENED TRANSFORMER FUSE P97014 ELF LN-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
231088214 | MEY3400 | 2025-06-28 | Q2 | 11:00 | 12:05 | 1:05 | 1 | 5 | 65 | 21 | 886.2 |  | MANUALLY OPENED TRANSFORMER FUSE P293729 12TH ST MANUALLY OPENED TRANSFORMER FUSE P69516 TAHOE ISLAND DR- TRANSFORMER UPGRADE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | FALSE
120057355 | NST8400; NST8500; NST8600 | 2025-06-29 | Q2 | 0:18 | 0:44 | 24:26 | 24 | 26 | 1466 | 1564 | 45010.2 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057142 | TAH7300 | 2025-06-29 | Q2 | 20:58 | 23:30 | 2:32 | 2 | 32 | 152.47 | 1 | 152.4 | TAHOE CITY | REMOVED TREE AND REHUNG SERVICE, W LAKE BLVD | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | FALSE | TRUE
120057225 | SQV8300 | 2025-06-29 | Q2 | 22:06 | 6:33 | 8:27 | 8 | 27 | 507.9 | 1 | 508.2 |  | MANUALLY OPENED OS-77 'B' POS, REPLACED 500' OF CABLE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | FALSE | TRUE
120057282 | CEM41; CEM42 | 2025-06-30 | Q2 | 0:18 | 3:43 | 3:25 | 3 | 25 | 205.25 | 482 | 98929.2 | LOYALTON | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057288 | KBH4201; KBH4202 | 2025-06-30 | Q2 | 0:18 | 3:20 | 3:02 | 3 | 2 | 182.3 | 1868 | 339022.2 | KINGS BEACH | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057293 | POR3100 | 2025-06-30 | Q2 | 0:18 | 3:11 | 2:52 | 2 | 52 | 172.57 | 732 | 126318.6 | PORTOLA | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057296 | POR3200 | 2025-06-30 | Q2 | 0:18 | 3:11 | 2:52 | 2 | 52 | 172.75 | 1198 | 206973.6 | PORTOLA | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057380 | GLS7400 | 2025-06-30 | Q2 | 0:18 | 3:47 | 3:29 | 3 | 29 | 209.23 | 1232 | 257795.4 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057405 | SQV7201; SQV8100; SQV8200; SQV8300 | 2025-06-30 | Q2 | 0:18 | 4:14 | 3:55 | 3 | 55 | 235.7 | 1952 | 421427.4 | OLYMPIC VALLEY | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057657 | KBH4203; KBH5100; KBH5200 | 2025-06-30 | Q2 | 0:18 | 3:22 | 3:03 | 3 | 3 | 183.77 | 3478 | 626472 | KINGS BEACH | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057661 | TAH7300 | 2025-06-30 | Q2 | 0:18 | 0:45 | 0:26 | 0 | 26 | 26.88 | 4447 | 119545.2 | TAHOMA | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057663 | TAH5201; TAH7100; TAH7200 | 2025-06-30 | Q2 | 0:18 | 4:39 | 4:20 | 4 | 20 | 260.63 | 4858 | 1104498.6 | TAHOE CITY | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057670 | GLS7600 | 2025-06-30 | Q2 | 0:18 | 3:50 | 3:31 | 3 | 31 | 211.8 | 55 | 11649 |  | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE
120057671 | TRK7203 | 2025-06-30 | Q2 | 0:18 | 0:44 | 0:26 | 0 | 26 | 26 | 1836 | 47736 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE
120057672 | TRK7202 | 2025-06-30 | Q2 | 0:18 | 0:45 | 0:26 | 0 | 26 | 26.52 | 151 | 4006.8 | TAHOE CITY | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057673 | TRK7204 | 2025-06-30 | Q2 | 0:18 | 0:44 | 0:26 | 0 | 26 | 26.02 | 48 | 1248.6 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE
120057674 | SRB51 | 2025-06-30 | Q2 | 0:18 | 0:44 | 0:26 | 0 | 26 | 26.4 | 243 | 6415.2 | LOYALTON | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | TRUE
120057675 | RUS7900 | 2025-06-30 | Q2 | 0:18 | 0:45 | 0:26 | 0 | 26 | 26.75 | 55 | 1472.4 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | FALSE | FALSE
120057735 | TAH7100 | 2025-06-30 | Q2 | 9:35 | 12:44 | 3:09 | 3 | 9 | 189 | 7 | 1323 | TAHOE CITY | BLOWN 6AMP TRANSFORMER FUSE P120577 CHAPEL LN-CAUSE UNKNOWN | UNKNOWN |  | Review Complete | NONE | North Lake | FALSE | TRUE
120057792 | MEY3100 | 2025-06-30 | Q2 | 13:04 | 13:26 | 0:22 | 0 | 22 | 22.57 | 5 | 112.8 |  | RESTORE SWITCHING FOR LUCA25-1110 - MULTIPLE REPAIRS ON 3100 FEEDER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | FALSE | TRUE
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q2 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## July
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46427 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 46427 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46427 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46427 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46427 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46427 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46427 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items) | [6 empty] | This box shows the monthly results per the PUC criteria
[9 empty] | #DIV/0! | [8 empty] | #N/A | [8 empty] | To refresh data select cell Y39 and go to Pivot Table Tools - Analyze, and select Refresh
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 46427 | 0 | 0 | 0 | 0
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 |  |  | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Aug
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46573 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 46573 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 46573 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 46573 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46573 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 46573 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 46573 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items) | [6 empty] | This box shows the monthly results per the PUC criteria
[9 empty] | #DIV/0! | [8 empty] | #N/A | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 46573 | 0 | 0 | 0 | 0
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Sept
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47485 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47485 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47485 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47485 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47485 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47485 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47485 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A |  |  |  | 47485 | 0 | 0 | 0 | 0
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q3 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Oct
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47545 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47545 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47545 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47545 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47545 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47545 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47545 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items) | [6 empty] | This box shows the monthly results per the PUC criteria
[9 empty] | #DIV/0! | [8 empty] | #N/A | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47545 | 0 | 0 | 0 | 0
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 | [14 empty] | #N/A
|  |  | Q4 | [14 empty] | #N/A
Q4
Q4
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Nov
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
#N/A
[18 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[18 empty] | #N/A |  |  | 0 | 47942 | 0 | 0 | #DIV/0! | #DIV/0!
#N/A
[18 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47942 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47942 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47942 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47942 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47942 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (blank)
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  | 0 | 47942 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A | E2_Exclusion | (Multiple Items) | [6 empty] | This box shows the monthly results per the PUC criteria
[9 empty] | #DIV/0! | [8 empty] | #N/A | [8 empty] | To refresh data select cell X39 and go to Pivot Table Tools - Analyze, and select Refresh
[9 empty] | #DIV/0! | [8 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
[9 empty] | #DIV/0! | [8 empty] | #N/A |  |  |  | 47942 | 0 | 0 | 0 | 0
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
[9 empty] | #DIV/0! | [8 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  |  | 0 | 0 | [9 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## Dec
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | Subcause | Construction Type | E2_Exclusion | District | E2_Exclusion | (All)
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [11 empty] | 0 | 47953 | 0 | 0 | #DIV/0! | #DIV/0!
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | E2_Exclusion | (Multiple Items)
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [12 empty] | 47953 | 0 | 0 | #DIV/0! | #DIV/0!
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | E2_Exclusion | (blank)
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [11 empty] | 0 | 47953 | 0 | 0 | #DIV/0! | #DIV/0!
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | E2_Exclusion | (blank)
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [11 empty] | 0 | 47953 | 0 | 0 | #DIV/0! | #DIV/0!
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | E2_Exclusion | (blank)
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [11 empty] | 0 | 47953 | 0 | 0 | #DIV/0! | #DIV/0!
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | E2_Exclusion | (blank)
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [11 empty] | 0 | 47953 | 0 | 0 | #DIV/0! | #DIV/0!
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | E2_Exclusion | (blank)
#DIV/0!
[9 empty] | #DIV/0! | [9 empty] | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII
[9 empty] | #DIV/0! | [11 empty] | 0 | 47953 | 0 | 0 | #DIV/0! | #DIV/0!
#DIV/0!
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | E2_Exclusion | (Multiple Items) | [6 empty] | This box shows the monthly results per the PUC criteria
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | [8 empty] | To refresh data select cell y39 and go to Pivot Table Tools - Analyze, and select Refresh
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | Count of ID | Sum of CI | Sum of CMI | CS | SAIDI | SAIFI | CAIDI | CIII | Remember to change data source to match this tab - Analyze - Change Data Source
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A |  |  |  | 47953 | 0 | 0 | 0 | 0
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
|  |  | Q4 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A
Note on Q1: Joel Rivera: Former follow-up required? Field
Note on Z4: Joel Rivera: To be provided by Anthea every month. Update this cell only with the actual customer count.

## ALL
ID | Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | SubCause | Follow Up Required? | E2_Exclusion | District | Month | Year | Weekday | Cust Serv | Cust Serv Feeder | FEEDER SAIFI | FEEDER SAIDI | SAIFI | SAIDI
231060455 | MULLER1296 | 2025-01-31 | Q1 | 11:10 | 13:25 | 2:15 |  |  | 135 | 1 | 135 |  | MANUALLY OPENED LINE FUSE P143840 BARBER WAY-POLE REPLACEMENT &amp; RECONDUCTOR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 6 | 48925 | 635 | 0.0015748 | 0.2126 | 2.0439e-05 | 0.0027593
231060384 | KBH4203 | 2025-01-30 | Q1 | 17:48 | 17:55 | 0:07 |  |  | 7 | 22 | 154.2 |  | MANUALLY OPENED P100180 TO CORRECT VOLTAGE ISSUES TO HOUSE 8157 RAINBOW AVE - CHANGED TAP SIZE | Equipment | Other | Review Complete | None | NORTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 509 | 0.043222 | 0.30295 | 0.00044967 | 0.0031518
231060345 | MEY3500 | 2025-01-30 | Q1 | 14:30 | 18:00 | 3:30 |  |  | 210 | 10 | 2100 |  | MANUALLY OPENED TRANSFORMER FUSE P153606 ONNONTIOGA ST-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 3820 | 0.0026178 | 0.54974 | 0.00020439 | 0.042923
231060332 | MULLER1296 | 2025-01-30 | Q1 | 11:00 | 17:00 | 6:00 |  |  | 360 | 2 | 720 |  | MANUALLY OPENED LINE FUSE P143841 BARBER WAY-POLE &amp; TRANSFORMER REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 635 | 0.0031496 | 1.1339 | 4.0879e-05 | 0.014716
231060349 | MULLER1296 | 2025-01-30 | Q1 | 9:00 | 16:20 | 7:20 |  |  | 440 | 23 | 10120.2 |  | MANUALLY OPENED LINE FUSE P214654 CARSON VIEW-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 635 | 0.03622 | 15.9373 | 0.00047011 | 0.20685
120037497 | SRB51 | 2025-01-29 | Q1 | 12:02 | 15:06 | 3:04 |  |  | 184 | 232 | 42688.2 |  | MANUALLY OPENED HIGH SIDE SWITCH TO REPLACE RECLOSER AT SB SUB | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 242 | 0.95868 | 176.3975 | 0.004742 | 0.87252
231060227 | MULLER1296 | 2025-01-29 | Q1 | 11:50 | 14:51 | 3:01 |  |  | 181 | 3 | 543 |  | MANUALLY OPENED TRANSFORMER FUSE P267082 FOOTHILL RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 635 | 0.0047244 | 0.85512 | 6.1318e-05 | 0.011099
120037297 | POR3200 | 2025-01-24 | Q1 | 14:12 | 17:42 | 3:30 |  |  | 210 | 54 | 11340 |  | BLOWN (2)-20 AMP FUSES DUE TO BROKEN CUTOUT P130502 MEADOW WAY | Equipment | Other | None | None | NORTH LAKE TAHOE | 1 | 2025 | 6 | 48925 | 1211 | 0.044591 | 9.3642 | 0.0011037 | 0.23178
231059892 | STL2300 | 2025-01-23 | Q1 | 16:50 | 17:50 | 1:00 |  |  | 60 | 5 | 300 |  | MANUALLY OPENED TRANSFORMER FUSE P131279 AZURE AVE SO REPAIRS COULD BE MADE TO U/G WIRES - DIG IN BY EXCAVATOR | Act Of Man | Dig in | None | THIRD PARTY | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 473 | 0.010571 | 0.63425 | 0.0001022 | 0.0061318
231059796 | STL3101 | 2025-01-22 | Q1 | 12:45 | 3:45 | 3:00 |  |  | 900 | 34 | 30600 |  | MANUALLY OPENED PRIMARY RISER FUSE 31SU32 P78872 KELLER RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 2312 | 0.014706 | 13.2353 | 0.00069494 | 0.62545
231059788 | MULLER1296 | 2025-01-22 | Q1 | 10:55 | 17:54 | 6:59 |  |  | 419 | 64 | 26815.8 |  | MANUALLY OPENED FUSED TAP P278665 STATE ROUTE 88 FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 635 | 0.10079 | 42.2296 | 0.0013081 | 0.5481
120037222 | POR3100 | 2025-01-21 | Q1 | 13:32 | 15:42 | 2:10 |  |  | 130 | 50 | 6499.8 |  | BLOWN 10 AMP LINE FUSE P70502 4TH AVE, DEAD SQUIRREL REMOVED FROM P138023 OFF RIO GRANDE ST. | Animal | Squirrel | Review Complete | None | NORTH LAKE TAHOE | 1 | 2025 | 3 | 48925 | 745 | 0.067114 | 8.7246 | 0.001022 | 0.13285
231059622 | MEY3300 | 2025-01-20 | Q1 | 11:33 | 16:05 | 4:32 |  |  | 272 | 6 | 1632 |  | MANUALLY OPENED P293704 CHILICOTHE ST FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 2 | 48925 | 3580 | 0.001676 | 0.45587 | 0.00012264 | 0.033357
231059562 | MEY3100 | 2025-01-20 | Q1 | 5:30 | 7:00 | 1:30 |  |  | 90 | 9 | 810 |  | MANUALLY OPENED TRANSFORMER FUSE P297102 COLD CREEK TRL - SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 2 | 48925 | 2391 | 0.0037641 | 0.33877 | 0.00018396 | 0.016556
120036952 | POR3100 | 2025-01-17 | Q1 | 2:00 | 5:00 | 3:00 |  |  | 180 | 1 | 180 |  | DE-ENERGIZED TRANSFORMER TO REPLACE BURNT CROSSARM AT P145010 COUNTY HWY A15 | Equipment | Fire | Review Complete | None | NORTH LAKE TAHOE | 1 | 2025 | 6 | 48925 | 745 | 0.0013423 | 0.24161 | 2.0439e-05 | 0.0036791
231059359 | MEY3200 | 2025-01-16 | Q1 | 19:50 | 20:05 | 0:15 |  |  | 14.58 | 29 | 422.4 |  | REPAIRED BROKEN CONDUIT BETWEEN VFI D &amp; FIRST BOX VENICE DR E | Act Of Man | Dig in | Review Complete | THIRD PARTY | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 3837 | 0.007558 | 0.11009 | 0.00059274 | 0.0086336
120036939 | STL3501 | 2025-01-16 | Q1 | 14:19 | 16:17 | 1:58 |  |  | 117.85 | 1 | 117.6 |  | DAMAGED SECONDARY UG FROM POLE 66563 WARR RD. RAN TEMP SERVICE AND REFERRED TO SUPERVISOR TO HAVE U/G REPLACED AT A LATER DATE | Equipment | Corrosion/Decay | Review Complete | None | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 2521 | 0.00039667 | 0.046648 | 2.0439e-05 | 0.0024037
232004963 | MEY3200 | 2025-01-15 | Q1 | 12:14 | 15:53 | 3:39 |  |  | 219 | 8 | 1752 |  | MANUALLY OPENED P68846 PATRICIA LN TO REPLACE POLE &amp; TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 3837 | 0.002085 | 0.45661 | 0.00016352 | 0.03581
232004964 | MEY3200 | 2025-01-15 | Q1 | 12:14 | 15:53 | 3:39 |  |  | 219 | 14 | 3066 |  | MANUALLY OPENED P68845 PATRICIA LN TO REPLACE POLE &amp; TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 3837 | 0.0036487 | 0.79906 | 0.00028615 | 0.062667
232004957 | MEY3200 | 2025-01-15 | Q1 | 12:00 | 15:00 | 3:00 |  |  | 180 | 1 | 180 |  | MANUALLY OPENED ELBOW 3887 TAHOE KEYS BLVD FOR MAINTENANCE WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 3837 | 0.00026062 | 0.046912 | 2.0439e-05 | 0.0036791
232004954 | MEY3400 | 2025-01-15 | Q1 | 11:49 | 17:35 | 5:46 |  |  | 346 | 27 | 9342 |  | MANUALLY OPENED LINE FUSE P294935 FOREST MOUNTAIN DR-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 4051 | 0.006665 | 2.3061 | 0.00055187 | 0.19095
231058882 | MEY3400 | 2025-01-09 | Q1 | 11:35 | 17:25 | 5:50 |  |  | 350 | 102 | 35700 |  | MANUALLY OPENED 30AMP LINE FUSE P244957 FORREST MOUNTAIN DR FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 4051 | 0.025179 | 8.8126 | 0.0020848 | 0.72969
120036474 | TAH5201 | 2025-01-08 | Q1 | 14:35 | 16:30 | 1:55 |  |  | 114.75 | 1 | 114.6 |  | TIGHTENED LOOSE CONNECTORS AT WEATHERHEAD P100456 CARNELIAN CIRCLE. | Equipment | Vibration/Loose Connection | Review Complete | None | NORTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 3185 | 0.00031397 | 0.035981 | 2.0439e-05 | 0.0023424
120036438 | STL3501 | 2025-01-07 | Q1 | 20:45 | 23:50 | 3:05 |  |  | 185 | 3 | 555 |  | MANUALLY OPENED TRANSFORMER FUSE P292456 PENTAGON DR TO REPAIR BAD CONNECTION AT TRANSFORMER | Equipment | Vibration/Loose Connection | Review Complete | None | SOUTH LAKE TAHOE | 1 | 2025 | 3 | 48925 | 2521 | 0.00119 | 0.22015 | 6.1318e-05 | 0.011344
231058702 | NST8400 | 2025-01-07 | Q1 | 16:00 | 17:55 | 1:55 |  |  | 115 | 357 | 41055 |  | MANUALLY OPENED VFI-202 NORTHSTAR DR TO REBUILD T-PAD &amp; RETAINING WALL | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 1 | 2025 | 3 | 48925 | 587 | 0.60818 | 69.9404 | 0.0072969 | 0.83914
231058647 | MEY3400 | 2025-01-07 | Q1 | 12:00 | 15:30 | 3:30 |  |  | 210 | 3 | 630 |  | MANUALLY OPENED TRANSFORMER FUSE P251648 MOUNTAIN MEADOW DR TO REPLACE TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 3 | 48925 | 4051 | 0.00074056 | 0.15552 | 6.1318e-05 | 0.012877
231058631 | MEY3400 | 2025-01-07 | Q1 | 11:30 | 14:35 | 3:05 |  |  | 185 | 27 | 4995 |  | MANUALLY OPENED TRANSFORMER FUSE P72466 CLEMENT ST FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 3 | 48925 | 4051 | 0.006665 | 1.233 | 0.00055187 | 0.1021
231058561 | STL3501 | 2025-01-06 | Q1 | 12:55 | 16:30 | 3:35 |  |  | 215 | 40 | 8599.8 |  | MANUALLY OPENED 11AMP LINE FUSE TO REPLACE POLE AND INSTALL NEW TRANSFORMER P79158 JANET DR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 2 | 48925 | 2521 | 0.015867 | 3.4113 | 0.00081758 | 0.17578
120036148 | TAH7300 | 2025-01-03 | Q1 | 11:27 | 13:36 | 2:09 |  |  | 129.37 | 34 | 4398.6 |  | BLOWN 40AMP LINE FUSE P73307 BELLEVIEW AVE. DUE TO FALLEN TREE AT P36634. REPLACED 2 SPANS OF WIRE FROM P236633 AND REPAIRED BROKEN CROSSARM AT P36634. | Vegetation | Fall In Tree | Review Complete | None | NORTH LAKE TAHOE | 1 | 2025 | 6 | 48925 | 4455 | 0.0076319 | 0.98734 | 0.00069494 | 0.089905
120036127 | MEY3300 | 2025-01-02 | Q1 | 22:29 | 0:30 | 2:02 |  |  | 121.1 | 8 | 968.4 |  | REPLACED 10K FUSE P123149 BLITZEN RD - CAUSE UNKNOWN | Other | Unknown | Review Complete | None | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 3580 | 0.0022346 | 0.2705 | 0.00016352 | 0.019794
120036063 | MEY3500 | 2025-01-02 | Q1 | 11:45 | 18:25 | 6:40 |  |  | 399.78 | 47 | 18789 |  | MANUALLY OPENED 15 AMP LINE FUSE P135179 JACARILLO TRL TO INSTALL NEW POLE BETWEEN P135184 &amp; P135185. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 1 | 2025 | 5 | 48925 | 3820 | 0.012304 | 4.9186 | 0.00096065 | 0.38404
120036038 | POR3100 | 2025-01-01 | Q1 | 18:11 | 20:52 | 2:41 |  |  | 160.57 | 1 | 155.4 |  | REPLACED BAD CONNECTION AT WEATHERHEAD AND METER SUPPLIED FROM POLE 70502 RIO GRANDE ST DUE TO DETERIORATION. | Equipment | Corrosion/Decay | Review Complete | None | NORTH LAKE TAHOE | 1 | 2025 | 4 | 48925 | 745 | 0.0013423 | 0.20859 | 2.0439e-05 | 0.0031763
120037803 | TPZ1202 | 2025-02-02 | Q1 | 2:44 | 4:40 | 1:56 | 1 | 56 | 116 | 680 | 78813 | COLEVILLE | TPZ1202-R1 LOCK OUT, ALL CUSTOMERS RESTORED 4:40 AM CAUSE UNKNOWN POSSIBLY HIGH WINDS | Weather | Wind | Review Complete | NONE | South Lake | 2 | 2025 | 1 | 49165 | 727 | 0.93535 | 108.4085 | 0.013831 | 1.603
120037825 | POR3200 | 2025-02-02 | Q1 | 21:20 | 21:35 | 0:15 | 0 | 15 | 15 | 3 | 45 | PORTOLA | BLOWN 15 AMP TRANSFORMER FUSE P250174 INDUSTRIAL WAY-BIRD | Animal | Bird | Review Complete | NONE | North Lake | 2 | 2025 | 1 | 49165 | 1214 | 0.0024712 | 0.037068 | 6.1019e-05 | 0.00091529
231060690 | MULLER1296 | 2025-02-03 | Q1 | 10:00 | 13:00 | 3:00 | 3 | 0 | 180 | 2 | 360 |  | MANUALLY OPENED 10 AMP LINE FUSE P143841 BARBER RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 2 | 49165 | 641 | 0.0031201 | 0.56162 | 4.0679e-05 | 0.0073223
120037844 | MEY3500 | 2025-02-03 | Q1 | 11:45 | 16:00 | 4:15 | 4 | 15 | 255 | 132 | 33660 | SOUTH LAKE TAHOE | MANUALLY OPENED 35MU37 LINE FUSE P297012 MACINAW RD TO REPLACE LJE-65 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 2 | 49165 | 3852 | 0.034268 | 8.7383 | 0.0026848 | 0.68463
120037932 | MULLER1296 | 2025-02-04 | Q1 | 13:16 | 17:36 | 4:19 | 4 | 19 | 259.82 | 1 | 259.8 | MARKLEEVILLE | CUT SECONDARY WIRES AT POLE 214652 EMIGRANT TRL TO REPLACE POLE. | Weather | Wind | Review Complete | NONE | South Lake | 2 | 2025 | 3 | 49165 | 641 | 0.0015601 | 0.4053 | 2.034e-05 | 0.0052842
120037904 | TPZ1202 | 2025-02-04 | Q1 | 17:32 | 18:58 | 1:26 | 1 | 26 | 86.43 | 81 | 6932.4 | COLEVILLE | PTR 1202-R3 LOCKED OUT - IN EXTREME FIRE SEASON - NO CAUSE FOUND, HIGH WINDS IN AREA.&#x0D; | Weather | Wind | Review Complete | NONE | South Lake | 2 | 2025 | 3 | 49165 | 727 | 0.11142 | 9.5356 | 0.0016475 | 0.141
231060902 | TPZ1202 | 2025-02-04 | Q1 | 19:22 | 0:04 | 4:42 | 4 | 42 | 282 | 697 | 168404.4 | COLEVILLE | PTR 1202-R1 &amp; 1202-R3 LOCKED OPEN - IN EXTREME FIRE SEASON - 1202-R1 CLOSED @ 19:56 - L/O AGAIN @ 20:36 | Weather | Wind | Review Complete | NONE | South Lake | 2 | 2025 | 3 | 49165 | 727 | 0.95873 | 231.6429 | 0.014177 | 3.4253
231060936 | MULLER1296 | 2025-02-05 | Q1 | 11:10 | 15:05 | 3:55 | 3 | 55 | 235 | 31 | 7285.2 |  | MANUALLY OPENED LINE FUSE P278659 FOOTHILL RD-RECONDUCTOR OVER HWY X-ING &amp; POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 4 | 49165 | 641 | 0.048362 | 11.3654 | 0.00063053 | 0.14818
231061069 | MULLER1296 | 2025-02-06 | Q1 | 11:00 | 12:33 | 1:33 | 1 | 33 | 93 | 4 | 372 |  | MANUALLY OPENED FUSE AT P290716 DIAMOND VALLEY RD - SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 5 | 49165 | 641 | 0.0062402 | 0.58034 | 8.1359e-05 | 0.0075664
120038031 | SQV7201 | 2025-02-07 | Q1 | 2:23 | 19:50 | 17:26 | 17 | 26 | 1046.9 | 598 | 310943.4 | ALPINE MEADOWS | 7201-R1 L/O DUE TO FALLEN TREE BETWEEN P96634 &amp; P292063 | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 743 | 0.80485 | 418.4972 | 0.012163 | 6.3245
120038034 | MEY3200 | 2025-02-07 | Q1 | 3:21 | 8:16 | 4:54 | 4 | 54 | 294.58 | 316 | 70531.2 | SOUTH LAKE TAHOE | BLOWN 2-40K FUSE P294786 JAMES AVE. REPLACED BROKEN PRIMARY BETWEEN P68846 &amp;70250 DUE TO FALLEN TREE LIMB | Vegetation | Fall In Limb | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 3851 | 0.082057 | 18.315 | 0.0064273 | 1.4346
120038045 | TPZ1202 | 2025-02-07 | Q1 | 12:07 | 14:54 | 2:47 | 2 | 47 | 167.2 | 697 | 30848.4 | COLEVILLE | 1202-R1 L/O WITH NRA ISSUED - BLOWN SINGLE PHASE PRIMARY P293554 US HWY 395 | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 727 | 0.95873 | 42.4325 | 0.014177 | 0.62745
120038047 | STL3501 | 2025-02-07 | Q1 | 12:23 | 12:47 | 0:24 | 0 | 24 | 24 | 9 | 216 | SOUTH LAKE TAHOE | REPLACED PRIMARY NEUTRAL P292459 LAKE TAHOE BLVD-NO CAUSE FOUND | Other | Unknown | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 2530 | 0.0035573 | 0.085375 | 0.00018306 | 0.0043934
120038050 | TAH7300 | 2025-02-07 | Q1 | 12:27 | 22:45 | 10:17 | 10 | 17 | 617.55 | 1 | 543 | TAHOE CITY | REATTACHED SERVICE P151432 GLEN ALPINE AVE-TREE | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 4479 | 0.00022326 | 0.12123 | 2.034e-05 | 0.011044
120038053 | TAH7300 | 2025-02-07 | Q1 | 13:39 | 22:43 | 9:04 | 9 | 4 | 544 | 1 | 544.2 | TAHOE CITY | REATTACHED SERVICE P92495 W LAKE BLVD-TREE | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 4479 | 0.00022326 | 0.1215 | 2.034e-05 | 0.011069
231061235 | SQV8200 | 2025-02-07 | Q1 | 17:36 | 19:00 | 1:24 | 1 | 24 | 84.12 | 16 | 1345.8 | OLYMPIC VALLEY | BLOWN 30 AMP LINE FUSE P291105 LANNY LN-WIRE MOVEMENT CAUSED CROSSING OF LINES | Equipment | Wire Movement | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 888 | 0.018018 | 1.5155 | 0.00032543 | 0.027373
231061379 | MULLER1296 | 2025-02-10 | Q1 | 11:35 | 16:30 | 4:55 | 4 | 55 | 295 | 4 | 1180.2 |  | MANUALLY OPENED 40 AMP LINE FUSE P290716 DIAMOND VALLEY RD-SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 2 | 49165 | 641 | 0.0062402 | 1.8412 | 8.1359e-05 | 0.024005
231061383 | TPZ1202 | 2025-02-10 | Q1 | 11:52 | 17:00 | 5:08 | 5 | 8 | 308 | 8 | 2464.2 |  | MANUALLY OPENED 15 AMP LINE FUSE P266630 US HWY 395-SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 2 | 49165 | 727 | 0.011004 | 3.3895 | 0.00016272 | 0.050121
120038113 | MEY3400 | 2025-02-10 | Q1 | 12:41 | 17:30 | 4:48 | 4 | 48 | 288.68 | 38 | 10969.8 |  | MANUALLY OPENED NEW CUTOUTS P146101 DUNDEE CIR TO REPLACE POLES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 2 | 49165 | 4066 | 0.0093458 | 2.6979 | 0.00077291 | 0.22312
120038121 | MEY3300 | 2025-02-10 | Q1 | 14:37 | 4:31 | 13:53 | 13 | 53 | 833.7 | 59 | 49189.2 | SOUTH LAKE TAHOE | BLOWN CENTER PHASE P153257 COUNTRY CLUB DR - FAILED UG CABLE FEEDING XFMR 15097 | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | 2 | 2025 | 2 | 49165 | 3628 | 0.016262 | 13.5582 | 0.0012 | 1.0005
231061487 | MEY3300 | 2025-02-11 | Q1 | 12:21 | 15:33 | 3:12 | 3 | 12 | 192 | 28 | 5376 |  | MANUALLY OPENED 15 AMP LINE FUSE P116682 W SAN BERNARDINO AVE TO REFRAME P293704 &amp; P116688 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 3 | 49165 | 3628 | 0.0077178 | 1.4818 | 0.00056951 | 0.10935
231061490 | MULLER1296 | 2025-02-11 | Q1 | 12:40 | 15:45 | 3:05 | 3 | 5 | 185 | 4 | 739.8 |  | MANUALLY OPENED 40 AMP LINE FUSE P290716 DIAMOND VALLEY RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 3 | 49165 | 641 | 0.0062402 | 1.1541 | 8.1359e-05 | 0.015047
120038182 | MEY3400 | 2025-02-12 | Q1 | 12:23 | 16:00 | 3:37 | 3 | 37 | 217.38 | 17 | 3695.4 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P80764 JAMES AVE TO REPLACE POLES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 4 | 49165 | 4066 | 0.004181 | 0.90885 | 0.00034577 | 0.075163
231061566 | MULLER1296 | 2025-02-12 | Q1 | 13:03 | 17:00 | 3:57 | 3 | 57 | 237 | 6 | 1422 |  | MANUALLY OPENED FUSE AT P143843 STATE ROUTE 89 FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 4 | 49165 | 641 | 0.0093604 | 2.2184 | 0.00012204 | 0.028923
120038214 | TAH7100 | 2025-02-13 | Q1 | 14:35 | 15:50 | 1:15 | 1 | 15 | 75 | 155 | 11625 | TAHOE CITY | BLOWN 2 50 AMP FUSES P108878 SLIVERTIP DR -SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 5 | 49165 | 1621 | 0.09562 | 7.1715 | 0.0031526 | 0.23645
120038225 | GLS7400 | 2025-02-13 | Q1 | 15:52 | 17:15 | 1:23 | 1 | 23 | 83 | 48 | 3984 | TRUCKEE | BLOWN 2 25 AMP FUSE P167874 - SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 5 | 49165 | 1234 | 0.038898 | 3.2285 | 0.0009763 | 0.081033
120038232 | KBH4202 | 2025-02-13 | Q1 | 17:05 | 19:15 | 2:10 | 2 | 10 | 130.07 | 1 | 130.2 | KINGS BEACH | SERVICE REPAIRED TO MAIN HOUSE AND RECONNECTED. SMALLER BLDG NEEDS ELECTRICIAN-TREE | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 2 | 2025 | 5 | 49165 | 1348 | 0.00074184 | 0.096588 | 2.034e-05 | 0.0026482
120038245 | TAH7100; TAH7200 | 2025-02-13 | Q1 | 19:46 | 8:54 | 13:07 | 13 | 7 | 787.72 | 1616 | 209904.6 | TAHOE CITY | 7100 CB L/O DUE TO FALLEN TREE BETWEEN P161198 &amp; P161199 | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 2 | 2025 | 5 | 49165 | #N/A | #N/A | #N/A | 0.032869 | 4.2694
120038262 | MEY3400 | 2025-02-13 | Q1 | 23:34 | 1:45 | 2:11 | 2 | 11 | 131 | 46 | 5787 | SOUTH LAKE TAHOE | BLOWN FUSE P192824 N UPPER TRUCKEE RD AND BLOWN FUSE P146127 LAKE TAHOE BLVD | Vegetation | Fall In Limb | Review Complete | NONE | South Lake | 2 | 2025 | 5 | 49165 | 4066 | 0.011313 | 1.4233 | 0.00093562 | 0.11771
120038284 | TAH7300 | 2025-02-14 | Q1 | 0:08 | 1:29 | 25:20 | 25 | 20 | 1520.58 | 15 | 22680.6 | TAHOE CITY | BLOWN 65 AMP LINE FUSE P208511 - MANUALLY OPENED 2ND LINE FUSE-DOWN PRIMARY BETWEEN P137676 &amp; 9137677 W LAKE BLVD | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 4479 | 0.003349 | 5.0638 | 0.0003051 | 0.46132
120038272 | GLS7400 | 2025-02-14 | Q1 | 1:35 | 4:45 | 3:10 | 3 | 10 | 190 | 49 | 6328.2 | TRUCKEE | BLOWN 20A FUSES P167874 ROLANDS WAY - SNOW OFFLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 1234 | 0.039708 | 5.1282 | 0.00099664 | 0.12871
120038296 | TAH7300 | 2025-02-14 | Q1 | 1:56 | 2:45 | 24:49 | 24 | 49 | 1489 | 10 | 14890.2 |  | BLOWN FUSE P8713 INTERLAKEN RD - REPAIRED BROKEN CROSSARM P8713 GRIMSEL PASS | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 4479 | 0.0022326 | 3.3244 | 0.0002034 | 0.30286
120038303 | TAH7300 | 2025-02-14 | Q1 | 1:56 | 8:40 | 30:44 | 30 | 44 | 1844.28 | 2 | 2903.4 | TAHOE CITY | BROKEN DEAD END ARM P79978 ELIZABETH DR | Other | Unknown | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 4479 | 0.00044653 | 0.64823 | 4.0679e-05 | 0.059054
121000092 | TAH7300 | 2025-02-14 | Q1 | 1:56 | 2:07 | 24:11 | 24 | 11 | 1451.37 | 3681 | 41825.4 | TAHOE CITY | EMERGENCY OPENED 7300-R1 TO SAFELY OPEN DAMAGED CUTOUTS @ P8713 - ALSO SEE INC 120038296 | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 4479 | 0.82184 | 9.3381 | 0.07487 | 0.85071
120038243 | TRK7202 | 2025-02-14 | Q1 | 2:06 | 20:08 | 42:02 | 42 | 2 | 2522.57 | 150 | 91202.4 |  | MANUALLY OPENED PTR 7202D2 &amp; LB 72-55 DUE TO SUSPECTED DOWNED PHASE - ADDITIONAL SWITCHING EXECUTED TO REPAIR DOWNED LINES AT MULTIPLE LOCATIONS: P281393-281394, P39591-271891, P294607-137680 | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 151 | 0.99338 | 603.9894 | 0.003051 | 1.855
120038276 | SQV7201 | 2025-02-14 | Q1 | 6:25 | 19:44 | 13:19 | 13 | 19 | 799.3 | 598 | 354031.8 | ALPINE MEADOWS | PTR 7201-R1 LOCKED OUT - P96628 (TREE ON WIRE) P100408 &amp; 100409 (WIRE DOWN) - BROKEN PHASE AND 2 PHASES ALSO DOWN BETWEEN P115884 AND 292985 | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 743 | 0.80485 | 476.4896 | 0.012163 | 7.2009
231061924 | STL3501 | 2025-02-14 | Q1 | 7:30 | 10:00 | 2:30 | 2 | 30 | 150 | 11 | 1650 |  | MANUALLY OPENED FUSE P295733 HERBERT AVE DUE TO WIRE SLAPPING LIGHT POST BETWEEN POLES 511360 &amp; 616881 HEAVY SNOW LOAD CAUSED A LONG SPAN OF LINE TO SAG | Weather | Ice/Snow | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 2530 | 0.0043478 | 0.65217 | 0.00022374 | 0.03356
120038282 | GLS7400 | 2025-02-14 | Q1 | 9:22 | 11:41 | 2:18 | 2 | 18 | 138.48 | 1 | 138.6 | TRUCKEE | WIRE POPPED OUT FROM P189416 - REHUNG AND RE-ENERGIZED | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 1234 | 0.00081037 | 0.11232 | 2.034e-05 | 0.0028191
120038283 | MEY3300 | 2025-02-14 | Q1 | 9:47 | 10:40 | 0:53 | 0 | 53 | 53 | 32 | 1696.2 | SOUTH LAKE TAHOE | BLOWN 25K LINE FUSE P293154 E SAN BERNARDINO AVE - POTENTIAL WIRE SLAP | Weather | Wind | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 3628 | 0.0088203 | 0.46753 | 0.00065087 | 0.0345
120038313 | MEY3300 | 2025-02-14 | Q1 | 11:35 | 12:30 | 0:55 | 0 | 55 | 55 | 139 | 7622.4 | SOUTH LAKE TAHOE | BLOWN 25 AMP FUSES P293154 E SAN BERNARDINO AVE, TRIPPED VFI 3300 21 C -WIRES SLAPPING TOGETHER | Weather | Wind | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 3628 | 0.038313 | 2.101 | 0.0028272 | 0.15504
120038314 | MEY3300 | 2025-02-14 | Q1 | 12:45 | 13:45 | 1:00 | 1 | 0 | 60 | 14 | 840 | SOUTH LAKE TAHOE | (2) BLOWN 10 AMP FUSES P123015 MANDAN ST - SUSPECTS WIRE SLAP | Weather | Ice/Snow | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 3628 | 0.0038589 | 0.23153 | 0.00028476 | 0.017085
120038319 | MEY3300 | 2025-02-14 | Q1 | 13:42 | 16:30 | 2:48 | 2 | 48 | 168.03 | 139 | 6399 | SOUTH LAKE TAHOE | BLOWN VFI 3300-21 'C' POS - FAILED XFMR @ P93352 | Equipment | Other | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 3628 | 0.038313 | 1.7638 | 0.0028272 | 0.13015
120038328 | MEY3500 | 2025-02-14 | Q1 | 13:48 | 15:06 | 1:18 | 1 | 18 | 78.32 | 273 | 21169.2 |  | BLOWN 65 AMP LINE FUSE P135349 LODI AVE-WIRES SLAPPED TOGETHER | Weather | Ice/Snow | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 3852 | 0.070872 | 5.4956 | 0.0055527 | 0.43057
120038335 | TRK7204 | 2025-02-14 | Q1 | 14:16 | 20:08 | 5:52 | 5 | 52 | 352.47 | 42 | 14059.2 | TRUCKEE | MANUALLY OPENED 30 AMP LINE FUSES P189376 THE STRAND TO REPAIR BROKEN JUMPER P189392 | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 48 | 0.875 | 292.9 | 0.00085427 | 0.28596
120038336 | MEY3400 | 2025-02-14 | Q1 | 14:24 | 16:59 | 2:34 | 2 | 34 | 154.75 | 1 | 154.8 | SOUTH LAKE TAHOE | SECONDARY SPLICE CAME LOOSE AT TREE ATTACHMENT - ADDED ON BAD SECONDARY WHERE JACKETED | Equipment | Vibration/Loose Connection | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 4066 | 0.00024594 | 0.038072 | 2.034e-05 | 0.0031486
121000083 | TAH7300 | 2025-02-14 | Q1 | 16:31 | 21:05 | 4:34 | 4 | 34 | 274.17 | 19 | 5208.6 | TAHOE CITY | BLOWN 20A FUSES P68683 - SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 4479 | 0.004242 | 1.1629 | 0.00038645 | 0.10594
121000063 | SQV8200 | 2025-02-14 | Q1 | 17:10 | 21:46 | 4:36 | 4 | 36 | 276.43 | 158 | 43678.8 | OLYMPIC VALLEY | VFI-139 TRIPPED ALL 3 PHASES OF 'D' POS - SUSPECTED SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 6 | 49165 | 888 | 0.17793 | 49.1878 | 0.0032137 | 0.88841
121000081 | MEY3300 | 2025-02-14 | Q1 | 18:25 | 19:55 | 1:29 | 1 | 29 | 89.42 | 1 | 89.4 | SOUTH LAKE TAHOE | REPLACED CONNECTORS AND WIRE | Equipment | Wire Movement | Review Complete | NONE | South Lake | 2 | 2025 | 6 | 49165 | 3628 | 0.00027563 | 0.024642 | 2.034e-05 | 0.0018184
121000173 | MEY3400 | 2025-02-15 | Q1 | 12:50 | 0:50 | 12:00 | 12 | 0 | 720 | 1 | 720 | SOUTH LAKE TAHOE | REPLACED BROKEN NEUTRAL P63623 TATA LN | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | 2 | 2025 | 7 | 49165 | 4066 | 0.00024594 | 0.17708 | 2.034e-05 | 0.014645
231062282 | MEY3300 | 2025-02-15 | Q1 | 14:38 | 15:00 | 0:22 | 0 | 22 | 22 | 21 | 462 |  | MANUALLY OPENED XFMR FUSE P107275 TO REPAIR BROKEN NEUTRAL | Weather | Ice/Snow | Review Complete | NONE | South Lake | 2 | 2025 | 7 | 49165 | 3628 | 0.0057883 | 0.12734 | 0.00042713 | 0.0093969
121000123 | SQV7201 | 2025-02-15 | Q1 | 17:18 | 23:30 | 6:12 | 6 | 12 | 372 | 43 | 14610 | ALPINE MEADOWS | MANUALLY OPEN DISCONNECT AT P115859 BEAR CREEK RD TO REPLACE TRANSFORMER AT P115859. SNOW LOADING CAUSED PRIMARY AND SECONDARY TO COME IN CONTACT. | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 7 | 49165 | 743 | 0.057873 | 19.6635 | 0.00087461 | 0.29716
121000174 | TRK7202 | 2025-02-15 | Q1 | 23:44 | 4:00 | 4:16 | 4 | 16 | 256 | 19 | 4864.2 |  | BLOWN 25 AMP LINE FUSE P68741 RIVER RD, DUE TO HEAVY WINDS. | Weather | Wind | Review Complete | NONE | North Lake | 2 | 2025 | 7 | 49165 | 151 | 0.12583 | 32.2132 | 0.00038645 | 0.098936
121000193 | TAH7100 | 2025-02-16 | Q1 | 16:34 | 19:15 | 2:41 | 2 | 41 | 161 | 93 | 14973 | TAHOE CITY | 2 BLOWN 65 AMP LINE FUSES P124662 EDELWEISS LN SNOWLOAD DROPPED CAUSING PRIMARY &amp; SECONDARY TO SLAP | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 1 | 49165 | 1621 | 0.057372 | 9.2369 | 0.0018916 | 0.30455
120038359 | GLS7600 | 2025-02-17 | Q1 | 12:15 | 16:00 | 3:45 | 3 | 45 | 225 | 5 | 1125 | TRUCKEE | 2 BLOWN 15 AMP TRANSFORMER FUSES P252959 HINTON DR-SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 2 | 49165 | 56 | 0.089286 | 20.0893 | 0.0001017 | 0.022882
120038373 | POR3200 | 2025-02-17 | Q1 | 13:35 | 14:00 | 0:25 | 0 | 25 | 25.3 | 1941 | 47778 | PORTOLA | MANUALLY OPENED POR3100 &amp; POR3200 CB FOR NVE SWITCHING ON 619 LINE | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 2 | 2025 | 2 | 49165 | 1214 | 1.5988 | 39.3558 | 0.039479 | 0.97179
120038379 | MEY3400 | 2025-02-17 | Q1 | 14:15 | 15:00 | 0:45 | 0 | 45 | 45 | 2 | 90 |  | MANUALLY OPENED 11 AMP LINE FUSE P264063 JAMESON BEACH RD / TREE CREW INADVERTENTLY DROPPED TREE LIMB ON WIRE / OPENED FUSE TO MAKE SAFE | Act Of Man | Vegetation clearing | Review Complete | THIRD PARTY | South Lake | 2 | 2025 | 2 | 49165 | 4066 | 0.00049188 | 0.022135 | 4.0679e-05 | 0.0018306
120038405 | GLS7400 | 2025-02-17 | Q1 | 19:53 | 21:00 | 1:06 | 1 | 6 | 66.68 | 2 | 133.2 | TRUCKEE | BLOWN 15 AMP LINE FUSE P212383 MARTIS PEAK RD-SNOW UNLOADING | Weather | Ice/Snow | Review Complete | NONE | North Lake | 2 | 2025 | 2 | 49165 | 1234 | 0.0016207 | 0.10794 | 4.0679e-05 | 0.0027092
231062612 | MEY3400 | 2025-02-18 | Q1 | 11:30 | 17:05 | 29:35 | 29 | 35 | 1775 | 2 | 3550.2 |  | MANUALLY OPENED FUSE AT P264063 FOR SYSTEM UPGRADES. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 3 | 49165 | 4066 | 0.00049188 | 0.87314 | 4.0679e-05 | 0.07221
120038438 | CEM41 | 2025-02-18 | Q1 | 14:03 | 18:53 | 4:50 | 4 | 50 | 290.07 | 211 | 17790.6 | LOYALTON | LUCA25-1023 - MANUALLY CLOSED 41-42 LB &amp; MANUALLY OPENED CUTOUTS @ P135038. INSTALLED TEMP DISCS @ P206915 FOR CUSTOMER OUTAGES UNDER NRA 3732. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 2 | 2025 | 3 | 49165 | 272 | 0.77574 | 65.4066 | 0.0042917 | 0.36185
231062721 | MEY3400 | 2025-02-19 | Q1 | 16:41 | 17:51 | 1:10 | 1 | 10 | 70 | 55 | 3850.2 | SOUTH LAKE TAHOE | MANUALLY OPENED LINE FUSE P296215 12TH ST TO REPLACE CROSS ARM | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 4 | 49165 | 4066 | 0.013527 | 0.94693 | 0.0011187 | 0.078312
231062785 | MEY3400 | 2025-02-20 | Q1 | 12:15 | 17:25 | 5:10 | 5 | 10 | 310 | 2 | 619.8 |  | MANUALLY OPENED LINE FUSE P264063 JAMESON BEACH BLVD - SYSTEM UPGRADES | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 5 | 49165 | 4066 | 0.00049188 | 0.15243 | 4.0679e-05 | 0.012607
120038849 | POR3100; POR3200 | 2025-02-20 | Q1 | 18:01 | 18:16 | 0:14 | 0 | 14 | 14.53 | 1941 | 22799.4 | PORTOLA | MANUALLY OPENED 3100 &amp; 3200 CBS FOR 619 LINE RESTORATION FROM NVE WORK BETWEEN 619N &amp; 619J | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 2 | 2025 | 5 | 49165 | #N/A | #N/A | #N/A | 0.039479 | 0.46373
231062837 | MEY3400 | 2025-02-21 | Q1 | 10:15 | 11:45 | 1:30 | 1 | 30 | 90 | 2 | 180 |  | MANUALLY OPENED FUSE AT P264063 JAMESON BEACH RD FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 6 | 49165 | 4066 | 0.00049188 | 0.04427 | 4.0679e-05 | 0.0036611
120039111 | CEM41 | 2025-02-24 | Q1 | 12:00 | 12:33 | 0:33 | 0 | 33 | 33 | 57 | 1881 |  | MANUALLY OPENED LINE FUSE P206915 HILL ST TO REPLACE DAMAGED HARDWARE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 2 | 2025 | 2 | 49165 | 272 | 0.20956 | 6.9154 | 0.0011594 | 0.038259
120039114 | MULLER1296 | 2025-02-24 | Q1 | 12:46 | 14:25 | 1:39 | 1 | 39 | 99 | 19 | 1881 |  | MANUALLY OPENED LINE FUSE P62632 EMIGRANT TRL-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 2 | 49165 | 641 | 0.029641 | 2.9345 | 0.00038645 | 0.038259
120039130 | WSH201 | 2025-02-25 | Q1 | 3:14 | 3:42 | 0:28 | 0 | 28 | 28 | 58 | 1624.2 | FLORISTON | NVE LOSS OF SOURCE - WSH 204 CB LOCKED OPEN - WIND SUSPECTED | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 2 | 2025 | 3 | 49165 | 58 | 1 | 28.0034 | 0.0011797 | 0.033036
120039167 | CEM42 | 2025-02-25 | Q1 | 18:37 | 23:18 | 4:41 | 4 | 41 | 281 | 12 | 3372 | LOYALTON | BLOWN TRANSFORMER FUSE, REATTACHED SECONDARY P209788 1ST ST, CUSTOMER TRIMMING TREES | Act Of Man | Vegetation clearing | Review Complete | THIRD PARTY | North Lake | 2 | 2025 | 3 | 49165 | 214 | 0.056075 | 15.757 | 0.00024408 | 0.068585
120039203 | MEY3400 | 2025-02-27 | Q1 | 12:23 | 14:32 | 2:09 | 2 | 9 | 129.38 | 67 | 8650.8 |  | MANUALLY OPENED AT P168243 FOR RECONDUCTOR WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 5 | 49165 | 4066 | 0.016478 | 2.1276 | 0.0013628 | 0.17595
231063209 | TAH5201 | 2025-02-27 | Q1 | 17:42 | 18:30 | 0:47 | 0 | 47 | 47.93 | 22 | 1006.8 | CARNELIAN BAY | BLOWN FUSE P151300 - SERVICE RIPPED OFF 275 OLD COUNTY RD BY TRUCK - SERVICE WILL NEED TO BE REPAIRED BEFORE RECONNECT - REFUSED TRANSFORMERS | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | North Lake | 2 | 2025 | 5 | 49165 | 3188 | 0.0069009 | 0.31581 | 0.00044747 | 0.020478
120039219 | KBH5200 | 2025-02-27 | Q1 | 23:34 | 1:22 | 1:47 | 1 | 47 | 107.42 | 1 | 107.4 | TAHOE VISTA | LIMB ON LINE P167929 - CUT EXPOSED SPARE WIRE | Vegetation | Fall In Limb | Review Complete | NONE | North Lake | 2 | 2025 | 5 | 49165 | 2902 | 0.00034459 | 0.037009 | 2.034e-05 | 0.0021845
231063259 | MULLER1296 | 2025-02-28 | Q1 | 11:00 | 15:30 | 4:30 | 4 | 30 | 270 | 66 | 17820 |  | MANUALLY OPENED LINE FUSE P278665 STATE HWY 88 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 6 | 49165 | 641 | 0.10296 | 27.8003 | 0.0013424 | 0.36245
231063266 | MEY3300 | 2025-02-28 | Q1 | 12:12 | 14:46 | 2:33 | 2 | 33 | 153.75 | 9 | 1377 | SOUTH LAKE TAHOE | MANUALLY OPENED XFMR FUSES AT P81780 &amp; P81778 ARAPAHOE ST - RECONDUCTOR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 2 | 2025 | 6 | 49165 | 3628 | 0.0024807 | 0.37955 | 0.00018306 | 0.028008
231063275 | TAH7100 | 2025-02-28 | Q1 | 13:50 | 18:01 | 4:11 | 4 | 11 | 251 | 7 | 1756.8 |  | MANUALLY OPENED XFMR FUSES P161199 HOLLY RD - CHANGE POLE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 2 | 2025 | 6 | 49165 | 1621 | 0.0043183 | 1.0838 | 0.00014238 | 0.035733
231063462 | MEY3500 | 2025-03-04 | Q1 | 2:00 | 3:12 | 1:12 | 1 | 12 | 72 | 3 | 216 |  | MANUALLY OPENED TRANSFORMER 43166 LAKE TAHOE BLVD TO WIRE PANEL FOR CT'S | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 3852 | 0.00077882 | 0.056075 | 6.1019e-05 | 0.0043934
231063497 | MULLER1296 | 2025-03-04 | Q1 | 11:03 | 13:52 | 2:49 | 2 | 49 | 169 | 31 | 5239.2 |  | MANUALLY OPENED LINE FUSE P278659 FOOTHILL RD TO REPLACE POLE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 641 | 0.048362 | 8.1735 | 0.00063053 | 0.10656
231063526 | MEY3300 | 2025-03-04 | Q1 | 13:34 | 16:30 | 2:56 | 2 | 56 | 176 | 9 | 1584 |  | MANUALLY OPENED TRANSFORMER FUSE P131323 ZAPOTEC DR FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 3628 | 0.0024807 | 0.4366 | 0.00018306 | 0.032218
231063551 | MULLER1296 | 2025-03-04 | Q1 | 14:26 | 18:00 | 3:34 | 3 | 34 | 214 | 4 | 856.2 |  | MANUALLY OPENED 40 AMP LINE FUSE P217286 DIAMOND VALLEY RD FOR RESILIENCY PROJECT. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 641 | 0.0062402 | 1.3357 | 8.1359e-05 | 0.017415
120039794 | STL3501 | 2025-03-05 | Q1 | 10:19 | 17:05 | 6:46 | 6 | 46 | 406 | 2518 | 1018774.8 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 2530 | 0.99526 | 402.6778 | 0.051215 | 20.7215
120039894 | MEY3200 | 2025-03-05 | Q1 | 10:19 | 16:38 | 6:19 | 6 | 19 | 379 | 3809 | 1441326.6 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 3851 | 0.98909 | 374.2733 | 0.077474 | 29.3161
120039898 | MEY3200; MEY3400 | 2025-03-05 | Q1 | 10:19 | 17:15 | 6:56 | 6 | 56 | 416.28 | 4039 | 1446412.2 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | #N/A | #N/A | #N/A | 0.082152 | 29.4196
120039902 | MEY3500 | 2025-03-05 | Q1 | 10:19 | 16:52 | 6:33 | 6 | 33 | 393 | 3828 | 1501348.8 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 3852 | 0.99377 | 389.7583 | 0.07786 | 30.5369
120039897 | MEY3300 | 2025-03-05 | Q1 | 10:19 | 16:38 | 6:18 | 6 | 18 | 378.55 | 3611 | 1366818.6 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 3628 | 0.99531 | 376.7416 | 0.073447 | 27.8006
120039864 | STL3101 | 2025-03-05 | Q1 | 10:20 | 16:04 | 5:44 | 5 | 44 | 344 | 2307 | 793071.6 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 2316 | 0.99611 | 342.4316 | 0.046924 | 16.1308
120039888 | MEY3100 | 2025-03-05 | Q1 | 10:20 | 16:31 | 6:11 | 6 | 11 | 371 | 2398 | 889059 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 2411 | 0.99461 | 368.7511 | 0.048775 | 18.0832
120039912 | MULLER1296 | 2025-03-05 | Q1 | 10:20 | 13:57 | 3:36 | 3 | 36 | 216.85 | 633 | 137266.2 | MARKLEEVILLE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 641 | 0.98752 | 214.1438 | 0.012875 | 2.7919
120039904 | STL2200 | 2025-03-05 | Q1 | 10:34 | 17:24 | 6:49 | 6 | 49 | 409.67 | 97 | 39652.8 |  | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 98 | 0.9898 | 404.6204 | 0.0019729 | 0.80652
120039905 | STL2300 | 2025-03-05 | Q1 | 10:35 | 16:56 | 6:20 | 6 | 20 | 380.53 | 475 | 180745.2 | SOUTH LAKE TAHOE | LOSS OF SUPPLY-BOTH TRANSMISSION LINES-120 KV BREAKER &amp; CAPACITOR BANK FAILURE BUCKEYE SUB | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 480 | 0.98958 | 376.5525 | 0.0096613 | 3.6763
231063868 | TPZ1202 | 2025-03-05 | Q1 | 12:45 | 13:05 | 0:20 | 0 | 20 | 20 | 8 | 160.2 |  | MANUALLY OPENED LINE FUSE P266630 HWY 395-GO INFRACTIONS | Planned | Maintenance | Review Complete | PLANNED OUTAGE / IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 727 | 0.011004 | 0.22036 | 0.00016272 | 0.0032584
120039995 | MEY3300 | 2025-03-05 | Q1 | 17:44 | 19:10 | 1:26 | 1 | 26 | 86 | 14 | 1204.2 | SOUTH LAKE TAHOE | BLOWN 10 AMP LINE FUSE P123015 MANDAN ST-UNKNOWN CAUSE | Other | Unknown | Review Complete | IEEE MED | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 3628 | 0.0038589 | 0.33192 | 0.00028476 | 0.024493
120040021 | MEY3100 | 2025-03-06 | Q1 | 10:08 | 13:57 | 3:49 | 3 | 49 | 229.58 | 1 | 229.8 | SOUTH LAKE TAHOE | PARTIAL POWER AT P83313 COPPER WAY AFTER CONNECTORS PULLED LOOSE. REPLACED CONNECTORS AND MADE REPAIRS. | Equipment | Vibration/Loose Connection | Review Complete | CUSTOMER OWNED | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 2411 | 0.00041477 | 0.095313 | 2.034e-05 | 0.0046741
231064018 | MULLER1296 | 2025-03-06 | Q1 | 11:20 | 16:35 | 5:15 | 5 | 15 | 315 | 7 | 2205 |  | MANUALLY OPENED LINE FUSE P143848 STATE HWY 89 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 641 | 0.01092 | 3.4399 | 0.00014238 | 0.044849
231064014 | MULLER1296 | 2025-03-06 | Q1 | 11:45 | 14:50 | 3:05 | 3 | 5 | 185 | 31 | 5734.8 | MARKLEEVILLE | MANUALLY OPENED LINE FUSE P272120 STATE ROUTE 89 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 641 | 0.048362 | 8.9466 | 0.00063053 | 0.11664
120040058 | MEY3300 | 2025-03-06 | Q1 | 17:38 | 20:06 | 2:27 | 2 | 27 | 147.9 | 1 | 147.6 | SOUTH LAKE TAHOE | REPLACED LOOSE CONNECTIONS AT P146357 SKYLINE DR | Equipment | Vibration/Loose Connection | Review Complete | NONE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 3628 | 0.00027563 | 0.040684 | 2.034e-05 | 0.0030021
120040065 | STL3101 | 2025-03-06 | Q1 | 21:59 | 0:15 | 2:15 | 2 | 15 | 135.03 | 1 | 135 | SOUTH LAKE TAHOE | REPLACED LOOSE CONNECTIONS AT P63948 WILLOW AVE | Equipment | Vibration/Loose Connection | Review Complete | NONE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 2316 | 0.00043178 | 0.05829 | 2.034e-05 | 0.0027459
120040068 | MULLER1296 | 2025-03-07 | Q1 | 2:09 | 7:08 | 4:58 | 4 | 58 | 298.23 | 243 | 71317.2 | MARKLEEVILLE | PLANNED POLE REPLACEMENTS ON HAWKINS RANCH RD - ALL CUSTOMERS DOWN STREAM OF P143849 DE-ENERGIZED FOR DURATION OF WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 6 | 49165 | 641 | 0.3791 | 111.2593 | 0.0049425 | 1.4506
120040108 | MULLER1296 | 2025-03-07 | Q1 | 11:24 | 14:30 | 3:06 | 3 | 6 | 186.27 | 73 | 13596 | MARKLEEVILLE | MANUALLY OPENED CUTOUTS P106434 TIMBER LN FOR POLE REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 6 | 49165 | 641 | 0.11388 | 21.2106 | 0.0014848 | 0.27654
120040298 | STL2300 | 2025-03-10 | Q1 | 11:00 | 12:30 | 1:30 | 1 | 30 | 90 | 68 | 6120 | SOUTH LAKE TAHOE | MANUALLY OPENED LINE FUSE P76600 LAKE TAHOE BLVD TO RECONNECT WIRES BETWEEN P211090 AND P211163 AZURE AVE. | Other | Unknown | Review Complete | NONE | SOUTH LAKE TAHOE | 3 | 2025 | 2 | 49165 | 480 | 0.14167 | 12.75 | 0.0013831 | 0.12448
231064574 | STL3501 | 2025-03-11 | Q1 | 1:30 | 2:00 | 0:30 | 0 | 30 | 30 | 35 | 1050 |  | MANUALLY OPENED LINE FUSE P79154 GLENWOOD WAY - POLE REPAIR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2530 | 0.013834 | 0.41502 | 0.00071189 | 0.021357
120040327 | STL3501 | 2025-03-11 | Q1 | 2:30 | 4:01 | 1:30 | 1 | 30 | 90.78 | 493 | 44725.2 | SOUTH LAKE TAHOE | MANUALLY OPENED 65A &amp; 40A LINE FUSES P90993 GLENWOOD WAY TO REPLACE CROSSARM AT P90992 SPRUCE AVE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2530 | 0.19486 | 17.6779 | 0.010027 | 0.9097
231064592 | MULLER1296 | 2025-03-11 | Q1 | 11:06 | 16:51 | 5:45 | 5 | 45 | 345 | 11 | 3795 |  | MANUALLY OPENED LINE FUSE P143846 UPPER MANZANITA DR-MAINTENANCE WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 641 | 0.017161 | 5.9204 | 0.00022374 | 0.077189
120040339 | MEY3200 | 2025-03-11 | Q1 | 13:35 | 15:24 | 1:49 | 1 | 49 | 109 | 13 | 1417.2 | SOUTH LAKE TAHOE | 2 BLOWN 20 AMP LINE FUSES P97039 ELKS CLUB DR, SQUIRREL REMOVED P97045 BEL AIRE CIR | Animal | Squirrel | Review Complete | NONE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 3851 | 0.0033757 | 0.36801 | 0.00026442 | 0.028825
120040352 | MEY3100 | 2025-03-11 | Q1 | 18:42 | 20:59 | 2:17 | 2 | 17 | 137.72 | 1 | 138 | SOUTH LAKE TAHOE | PARTIAL POWER DUE TO LOOSE CONNECTIONS P294713 MERCED AVE | Equipment | Vibration/Loose Connection | Review Complete | CUSTOMER OWNED | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.00041477 | 0.057238 | 2.034e-05 | 0.0028069
120040358 | STL3101 | 2025-03-11 | Q1 | 21:07 | 21:30 | 0:23 | 0 | 23 | 23 | 31 | 712.8 | SOUTH LAKE TAHOE | MANUALLY OPENED RISER FUSE P251640 SPRUCE AVE-REPAIR PADMOUNT TRANSFORMER TS62 | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2316 | 0.013385 | 0.30777 | 0.00063053 | 0.014498
232005021 | MULLER1296 | 2025-03-12 | Q1 | 9:15 | 11:00 | 1:45 | 1 | 45 | 105 | 1 | 105 |  | MANUALLY OPENED TRANSFORMER FUSE P290461 UPPER MANZANITA DR-RESILIENCY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 641 | 0.0015601 | 0.16381 | 2.034e-05 | 0.0021357
121000218 | TRK7202 | 2025-03-12 | Q1 | 17:46 | 20:16 | 2:29 | 2 | 29 | 149.52 | 4 | 542.4 | TRUCKEE | BLOWN 2-50AMP LINE FUSES P269574 &amp; 2-30AMP LINE FUSES P269575 CABIN CREEK RD-BROKEN INSULATOR P252814 | Equipment | Corrosion/Decay | Review Complete | NONE | NORTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 151 | 0.02649 | 3.5921 | 8.1359e-05 | 0.011032
231064778 | MULLER1296 | 2025-03-13 | Q1 | 12:00 | 13:26 | 1:26 | 1 | 26 | 86 | 1 | 85.8 |  | MANUALLY OPENED TRANSFORMER FUSE P129021 UPPER MANZANITA DR-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 641 | 0.0015601 | 0.13385 | 2.034e-05 | 0.0017451
120041272 | MEY3400 | 2025-03-14 | Q1 | 23:13 | 0:30 | 1:17 | 1 | 17 | 77 | 55 | 4234.8 | SOUTH LAKE TAHOE | BLOWN (3) 12 AMP FUSES P296215 12TH ST - CAUSE UNKNOWN POSSIBLY OVERLOAD | Other | Unknown | Review Complete | NONE | SOUTH LAKE TAHOE | 3 | 2025 | 6 | 49165 | 4066 | 0.013527 | 1.0415 | 0.0011187 | 0.086134
120041437 | SLK257 | 2025-03-17 | Q1 | 4:08 | 4:45 | 0:36 | 0 | 36 | 36.53 | 3 | 109.8 |  | LOSS OF SOURCE - SLK 257 CB LOCKOUT (NVE) - MVA POLE HIT ON NVE SIDE | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | NORTH LAKE TAHOE | 3 | 2025 | 2 | 49165 | 3 | 1 | 36.6 | 6.1019e-05 | 0.0022333
120041802 | MULLER1296 | 2025-03-18 | Q1 | 11:10 |  | 0:00 |  |  | 1443.68 | 11 | 0 |  | MANUALLY OPENED 15 AMP LINE FUSE P143846 UPPER MANZANITA DR-RESILIENCY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 641 | 0.017161 | 0 | 0.00022374 | 0
231066278 | MEY3100 | 2025-03-18 | Q1 | 12:00 | 12:30 | 0:30 | 0 | 30 | 30 | 23 | 690 |  | MANUALLY OPENED TRANSFORMER FUSE P290458 SAN FRANCISCO AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.0095396 | 0.28619 | 0.00046781 | 0.014034
231066330 | MEY3100 | 2025-03-18 | Q1 | 12:15 |  | 0:00 |  |  | 177.88 | 0 | 0 |  | MANUALLY OPENED TRANSFORMER FUSE P63847 OAKLAND AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0 | 0 | 0 | 0
120041562 | MEY3100 | 2025-03-18 | Q1 | 12:31 | 12:41 | 0:10 | 0 | 10 | 10 | 12 | 120 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P192985 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.0049772 | 0.049772 | 0.00024408 | 0.0024408
231066385 | MEY3100 | 2025-03-18 | Q1 | 12:51 | 13:02 | 0:11 | 0 | 11 | 11 | 13 | 142.8 |  | MANUALLY OPENED TRANSFORMER FUSE P293179 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.005392 | 0.059229 | 0.00026442 | 0.0029045
231066335 | MEY3100 | 2025-03-18 | Q1 | 13:20 | 13:31 | 0:11 | 0 | 11 | 11 | 14 | 154.2 |  | MANUALLY OPENED TRANSFORMER FUSE P192841 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.0058067 | 0.063957 | 0.00028476 | 0.0031364
231066380 | MEY3100 | 2025-03-18 | Q1 | 13:31 | 13:41 | 0:10 | 0 | 10 | 10 | 12 | 120 |  | MANUALLY OPENED TRANSFORMER FUSE P293178 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.0049772 | 0.049772 | 0.00024408 | 0.0024408
231066343 | MEY3100 | 2025-03-18 | Q1 | 14:10 | 14:22 | 0:12 | 0 | 12 | 12 | 23 | 276 |  | MANUALLY OPENED TRANSFORMER FUSE P192985 LAKEVIEW AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.0095396 | 0.11448 | 0.00046781 | 0.0056137
231066375 | MEY3100 | 2025-03-18 | Q1 | 14:35 | 14:44 | 0:09 | 0 | 9 | 9 | 9 | 81 |  | MANUALLY OPENED TRANSFORMER FUSE P205163 BELLEVUE AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.0037329 | 0.033596 | 0.00018306 | 0.0016475
231066354 | MEY3100 | 2025-03-18 | Q1 | 14:51 | 14:59 | 0:08 | 0 | 8 | 8 | 17 | 136.2 |  | MANUALLY OPENED TRANSFORMER FUSE P90833 BELLEVUE AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 2411 | 0.007051 | 0.056491 | 0.00034577 | 0.0027703
120041592 | TPZ1202 | 2025-03-18 | Q1 | 20:30 | 4:50 | 8:20 | 8 | 20 | 500 | 11 | 5500.2 | COLEVILLE | MANUALLY OPENED LINE FUSE P163558 WESTERN DR, DOWN GUYS WERE DUG UP CAUSING POLE TO LEAN HEAVILY INTO THE TREES-RESET POLE | Act Of Man | Other | Review Complete | THIRD PARTY | SOUTH LAKE TAHOE | 3 | 2025 | 3 | 49165 | 727 | 0.015131 | 7.5656 | 0.00022374 | 0.11187
231066429 | STL2300 | 2025-03-19 | Q1 | 1:00 | 3:29 | 2:29 | 2 | 29 | 149 | 11 | 1639.2 |  | MANUALLY OPENED TS-178-111582 AT LAKE TAHOE BLVD FOR REPLACEMENT OF MAIN BREAKER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 480 | 0.022917 | 3.415 | 0.00022374 | 0.033341
120041806 | MULLER1296 | 2025-03-19 | Q1 | 11:02 | 15:50 | 4:48 | 4 | 48 | 288 | 11 | 3168 |  | MANUALLY OPENED 15 AMP LINE FUSE P143846 UPPER MANZANITA DR-RESILIENCY PROJECT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 641 | 0.017161 | 4.9423 | 0.00022374 | 0.064436
231067049 | MEY3100 | 2025-03-19 | Q1 | 12:54 | 19:00 | 6:06 | 6 | 6 | 366 | 45 | 16470 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P66312 MERCED AVE FOR CIRCUIT LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 2411 | 0.018664 | 6.8312 | 0.00091529 | 0.33499
231067778 | MULLER1296 | 2025-03-20 | Q1 | 1:00 | 6:13 | 5:13 | 5 | 13 | 313 | 172 | 53836.2 | MARKLEEVILLE | MANUALLY OPENED 40 AMP LINE FUSE P277686 MONTGOMERY ST TO REPLACE P39343 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 641 | 0.26833 | 83.9878 | 0.0034984 | 1.095
120042132 | TPZ1202 | 2025-03-20 | Q1 | 9:51 | 15:00 | 5:09 | 5 | 9 | 309.22 | 5 | 1546.2 | COLEVILLE | BLOWN 15T LINE FUSE P181148 EASTSIDE RD-UNKNOWN CAUSE | Other | Unknown | Review Complete | NONE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 727 | 0.0068776 | 2.1268 | 0.0001017 | 0.031449
120042163 | MULLER1296 | 2025-03-20 | Q1 | 15:40 | 15:47 | 0:06 | 0 | 6 | 6.95 | 2 | 13.8 |  | MANUALLY OPENED TRANSFORMER FUSE P297169 DIAMOND VALLEY RD-RESILIENCY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 641 | 0.0031201 | 0.021529 | 4.0679e-05 | 0.00028069
120042439 | MEY3200 | 2025-03-24 | Q1 | 10:55 | 17:31 | 6:35 | 6 | 35 | 395.88 | 84 | 33255.6 |  | MANUALLY OPENED 32MU41 P135340 WINNEMUCCA AVE TO REMOVE TREES NEAR P66424 &amp; P87937 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 2 | 49165 | 3851 | 0.021813 | 8.6356 | 0.0017085 | 0.67641
231068199 | KBH5200 | 2025-03-24 | Q1 | 12:57 | 13:18 | 0:21 | 0 | 21 | 21 | 4 | 84 |  | BLOWN TRANSFORMER FUSE P124929 LINCOLN GREEN DR-FUSE BLEW WHILE DOING MAINTENANCE WORK | Other | Construction by Co. Contractor | Review Complete | NONE | NORTH LAKE TAHOE | 3 | 2025 | 2 | 49165 | 2902 | 0.0013784 | 0.028946 | 8.1359e-05 | 0.0017085
120042555 | TAH7300 | 2025-03-26 | Q1 | 11:38 | 15:38 | 4:00 | 4 | 0 | 240.08 | 12 | 2641.2 |  | MANUALLY LIFTED TAPS AT P73314 IDLEWILD WAY - DE-ENERGIZING PRIMARY FOR TREE CREW/CONTRACTOR TO REMOVE TREE BETWEEN P236632 &amp; P236634 IDLEWILD WAY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 4479 | 0.0026792 | 0.58969 | 0.00024408 | 0.053721
120042557 | MEY3400 | 2025-03-26 | Q1 | 12:47 | 13:46 | 0:58 | 0 | 58 | 58.78 | 5 | 294 |  | PLANNED OUTAGE TO PULL WIRES BETWEEN P131421 - P122948 TATA LN AND BUILDING SECONDARY RISER. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 4066 | 0.0012297 | 0.072307 | 0.0001017 | 0.0059799
120042580 | MEY3400 | 2025-03-26 | Q1 | 20:00 | 21:05 | 1:05 | 1 | 5 | 65.6 | 3 | 196.8 | TAHOMA | BLOWN 15K LINE FUSE P291674 EMERALD BAY RD-WIND | Weather | Wind | Review Complete | NONE | SOUTH LAKE TAHOE | 3 | 2025 | 4 | 49165 | 4066 | 0.00073783 | 0.048401 | 6.1019e-05 | 0.0040028
231068561 | TAH7300 | 2025-03-27 | Q1 | 11:00 | 13:00 | 2:00 | 2 | 0 | 120 | 7 | 840 |  | MANUALLY OPENED TRANSFORMER FUSE P92257 SCENIC DR-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 4479 | 0.0015628 | 0.18754 | 0.00014238 | 0.017085
231068564 | TAH7300 | 2025-03-27 | Q1 | 11:00 | 13:00 | 2:00 | 2 | 0 | 120 | 4 | 480 |  | MANUALLY OPENED TRANSFORMER FUSE P92259 SCENIC DR-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 4479 | 0.00089306 | 0.10717 | 8.1359e-05 | 0.009763
231068567 | TAH7300 | 2025-03-27 | Q1 | 11:00 | 13:05 | 2:05 | 2 | 5 | 125 | 14 | 1750.2 |  | MANUALLY OPENED TRANSFORMER FUSE P73328 INTERLAKEN RD-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 4479 | 0.0031257 | 0.39076 | 0.00028476 | 0.035598
231068595 | TAH7300 | 2025-03-27 | Q1 | 13:45 | 16:00 | 2:15 | 2 | 15 | 135 | 11 | 1485 |  | MANUALLY OPENED 25 AMP TRANSFORMER FUSE P8714 INTERLAKEN RD-GREY WIRE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 4479 | 0.0024559 | 0.33155 | 0.00022374 | 0.030204
231068628 | MULLER1296 | 2025-03-27 | Q1 | 14:30 | 15:05 | 0:35 | 0 | 35 | 35 | 2 | 70.2 | MARKLEEVILLE | MANUALLY OPENED 10K TRANSFORMER FUSE P156947 CALIFORNIA RD TO MAKE REPAIRS ON METER PANEL | Planned | Maintenance | Review Complete | PLANNED OUTAGE | SOUTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 641 | 0.0031201 | 0.10952 | 4.0679e-05 | 0.0014278
120042621 | TAH7100 | 2025-03-27 | Q1 | 15:33 | 17:55 | 2:21 | 2 | 21 | 141.45 | 237 | 29868.6 | TAHOE CITY | VFI-119 'B' POSITION TRIPPED OPEN-SQUIRREL CONTACT TRANSFORMER 8927 CEDAR CT | Animal | Squirrel | Review Complete | NONE | NORTH LAKE TAHOE | 3 | 2025 | 5 | 49165 | 1621 | 0.14621 | 18.426 | 0.0048205 | 0.60752
231068714 | TAH7300 | 2025-03-28 | Q1 | 11:07 | 14:50 | 3:43 | 3 | 43 | 223 | 6 | 1338 |  | MANUALLY OPENED TRANSFORMER FUSE P105216 LAGOON RD-REPLACED GREY WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 6 | 49165 | 4479 | 0.0013396 | 0.29873 | 0.00012204 | 0.027214
231068719 | TAH7300 | 2025-03-28 | Q1 | 11:07 | 12:50 | 1:43 | 1 | 43 | 103 | 14 | 1441.8 |  | MANUALLY OPENED TRANSFORMER FUSE P105212 LAGOON RD REPLACED GREY WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 6 | 49165 | 4479 | 0.0031257 | 0.3219 | 0.00028476 | 0.029326
231068768 | TAH7300 | 2025-03-28 | Q1 | 15:15 | 15:55 | 0:40 | 0 | 40 | 40 | 5 | 199.8 |  | MANUALLY OPENED TRANSFORMER FUSE TAKE DOWN OLD SERVICE AND REATTACH NEW SERVICE P242122 MEADOW RD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | NORTH LAKE TAHOE | 3 | 2025 | 6 | 49165 | 4479 | 0.0011163 | 0.044608 | 0.0001017 | 0.0040639
120042676 | TAH7300 | 2025-03-28 | Q1 | 18:00 | 18:49 | 0:49 | 0 | 49 | 49.43 | 13 | 642.6 | TIMBERLAND | BLOWN LINE FUSE P59748 SUGAR PINE RD DUE TO BURNT UP CUT OUT | Equipment | Corrosion/Decay | Review Complete | NONE | NORTH LAKE TAHOE | 3 | 2025 | 6 | 49165 | 4479 | 0.0029024 | 0.14347 | 0.00026442 | 0.01307
120043219 | CAL2501 | 2025-03-30 | Q1 | 22:42 | 23:48 | 1:05 | 1 | 5 | 65.93 | 96 | 6309.6 | VERDI | LOSS OF SOURCE (NVE) CAL 2501 CB LOCKED OPEN - NVE TO PATROL | Loss of Supply | Other | Review Complete | LOSS OF SUPPLY | NORTH LAKE TAHOE | 3 | 2025 | 1 | 49165 | 97 | 0.98969 | 65.0474 | 0.0019526 | 0.12834
120043224 | WSH201 | 2025-03-30 | Q1 | 22:42 | 23:47 | 1:05 | 1 | 5 | 65.03 | 55 | 3576.6 | FLORISTON | LOSS OF SOURCE (NVE) CAL 2501 CB LOCKED OPEN - NVE TO PATROL | Loss of Supply | Other |  | LOSS OF SUPPLY | NORTH LAKE TAHOE | 3 | 2025 | 1 | 49165 | 58 | 0.94828 | 61.6655 | 0.0011187 | 0.072747
120043265 | POR3200 | 2025-03-31 | Q1 | 8:47 | 12:05 | 3:18 | 3 | 18 | 198 | 1200 | 93560.4 | PORTOLA | POR3200 CB LOCKED OUT - BLOWN 11A FUSE P37900 OFF DELLEKER RD-WIND SLAPPED WIRES TOGETHER | Weather | Wind |  | NONE | NORTH LAKE TAHOE | 3 | 2025 | 2 | 49165 | 1214 | 0.98847 | 77.0679 | 0.024408 | 1.903
120044719 | MEY3300; MEY3400 | 2025-04-17 | Q2 | 16:13 | 17:02 | 24:49 | 24 | 49 | 1489.43 | 77 | 2610 | SOUTH LAKE TAHOE | MANUALLY OPENED 33MU94 &amp; 33MU132 DISCS &amp; LIFTED TAPS AT P123205 &amp; P292968 SKYLINE DR. CREWS REPLACING POLES 111280 AND P123202 IN MEYERS ROW | Planned | Maintenance | Mismatch - Number of customers | PLANNED OUTAGE | South Lake | 4 | 2025 | 5 | 49165 | #N/A | #N/A | #N/A | 0.0015662 | 0.053087
231070566 | TPZ1202 | 2025-04-09 | Q2 | 10:40 | 16:25 | 5:45 | 5 | 45 | 345 | 2 | 690 |  | MANUALLY OPENED P295428 PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | South Lake | 4 | 2025 | 4 | 49165 | 727 | 0.002751 | 0.94911 | 4.0679e-05 | 0.014034
231072461 | TAH7300 | 2025-04-24 | Q2 | 14:12 | 17:41 | 3:29 | 3 | 29 | 209 | 12 | 2508 |  | MANUALLY OPENED P105244 REPLACE OPEN WIRE - PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | 4 | 2025 | 5 | 49165 | 4479 | 0.0026792 | 0.55995 | 0.00024408 | 0.051012
120043417 | TAH7300 | 2025-04-01 | Q2 | 19:38 | 4:42 | 9:03 | 9 | 3 | 543.65 | 3679 | 387713.4 | TAHOMA | PTR 7300-R1 LOCKOUT - BURNED THROUGH PRIMARY WIRE &amp; CONNECTOR P269477 GRAND AVE | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 4 | 2025 | 3 | 49165 | 4479 | 0.82139 | 86.5625 | 0.07483 | 7.886
120043423 | STL3101 | 2025-04-01 | Q2 | 21:11 | 5:00 | 7:48 | 7 | 48 | 468.57 | 12 | 5622.6 | SOUTH LAKE TAHOE | BLOWN 15 AMP T-FUSE P292481 WILDWOOD AVE-MVA P90796 | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | South Lake | 4 | 2025 | 3 | 49165 | 2316 | 0.0051813 | 2.4277 | 0.00024408 | 0.11436
120043634 | MEY3100; STL3501 | 2025-04-03 | Q2 | 0:21 | 5:45 | 5:24 | 5 | 24 | 324.4 | 4297 | 115529.4 | SOUTH LAKE TAHOE | MANUALLY OPENED P131294 35SU10 TO FLYING TAPS P83404 HERBERT AVE FOR POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 5 | 49165 | #N/A | #N/A | #N/A | 0.0874 | 2.3498
120043656 | POR3200 | 2025-04-03 | Q2 | 13:40 | 4:00 | 14:20 | 14 | 20 | 860 | 11 | 9460.2 | PORTOLA | MANUALLY OPENED TRANSFORMER FUSE P70757 TO REPLACE DAMAGED CROSSARMS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 5 | 49165 | 1214 | 0.009061 | 7.7926 | 0.00022374 | 0.19242
120044244 | MEY3200 | 2025-04-07 | Q2 | 11:47 | 12:55 | 1:08 | 1 | 8 | 68 | 22 | 1495.8 |  | MANUALLY OPENED TRANSFORMER FUSE T31846 ALA WAI BLVD TO REPLACE TRANSFORMER PAD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 2 | 49165 | 3851 | 0.0057128 | 0.38842 | 0.00044747 | 0.030424
120044245 | MEY3200 | 2025-04-07 | Q2 | 11:47 | 12:55 | 1:08 | 1 | 8 | 68 | 32 | 2176.2 |  | MANUALLY OPENED TRANSFORMER FUSE T31890 ALA WAI BLVD TO REPLACE TRANSFORMER PAD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 2 | 49165 | 3851 | 0.0083095 | 0.5651 | 0.00065087 | 0.044263
120044246 | MEY3200 | 2025-04-07 | Q2 | 11:47 | 12:55 | 1:08 | 1 | 8 | 68 | 30 | 2040 |  | MANUALLY OPENED TRANSFORMER FUSE T10003 ALA WAI BLVD TO REPLACE TRANSFORMER PAD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 2 | 49165 | 3851 | 0.0077902 | 0.52973 | 0.00061019 | 0.041493
120044307 | POR3100 | 2025-04-08 | Q2 | 12:23 | 18:15 | 5:51 | 5 | 51 | 351.73 | 1 | 351.6 |  | MANUALLY LIFTED TAPS P225777 IN ROW OFF DELLEKER RD - MAINTENANCE REPLACEMENT OF P66213 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 3 | 49165 | 748 | 0.0013369 | 0.47005 | 2.034e-05 | 0.0071514
120044380 | MEY3400 | 2025-04-10 | Q2 | 11:20 | 12:20 | 1:00 | 1 | 0 | 60 | 34 | 2040 | SOUTH LAKE TAHOE | BLOWN 2 15K FUSES P131426 TUCKER AVE - CAUSE UNKNOWN. | Other | Unknown | Review Complete | NONE | South Lake | 4 | 2025 | 5 | 49165 | 4066 | 0.008362 | 0.50172 | 0.00069155 | 0.041493
120044382 | HOB7700 | 2025-04-10 | Q2 | 11:44 | 17:15 | 5:31 | 5 | 31 | 331.05 | 1 | 436.2 |  | MANUALLY OPENED LINE FUSE P232498 TO REPAIR BROKEN POLE 96842 AND PIN. | Equipment | Other | Review Complete | NONE | North Lake | 4 | 2025 | 5 | 49165 | 32 | 0.03125 | 13.6312 | 2.034e-05 | 0.0088722
120044641 | MULLER1296 | 2025-04-16 | Q2 | 1:02 | 3:56 | 2:54 | 2 | 54 | 174 | 208 | 36192 | MARKLEEVILLE | MANUALLY OPENED PTR 1296-R4 P290784 HWY 89-POLE REPLACEMENTS P39832, P34330, P39933, &amp; P39834 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 4 | 49165 | 641 | 0.32449 | 56.4618 | 0.0042307 | 0.73613
120044650 | TPZ1202 | 2025-04-16 | Q2 | 10:30 | 18:01 | 7:31 | 7 | 31 | 451 | 6 | 2706 |  | MANUALLY OPENED 15 AMP LINE FUSE P286985 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 4 | 49165 | 727 | 0.0082531 | 3.7221 | 0.00012204 | 0.055039
120044660 | POR3200 | 2025-04-16 | Q2 | 11:38 | 12:38 | 1:00 | 1 | 0 | 60 | 45 | 2700 |  | MANUALLY OPENED 11 AMP LINE FUSE P225976 W MOHAWK AVE-REPLACING BUCKARM | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 1214 | 0.037068 | 2.2241 | 0.00091529 | 0.054917
120044663 | TPZ1202 | 2025-04-16 | Q2 | 12:26 | 15:45 | 3:19 | 3 | 19 | 199 | 2 | 397.8 |  | MANUALLY OPENED 25 AMP LINE FUSE P293569 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 4 | 49165 | 727 | 0.002751 | 0.54718 | 4.0679e-05 | 0.0080911
120044668 | POR3200 | 2025-04-16 | Q2 | 13:15 | 14:29 | 1:14 | 1 | 14 | 74 | 2 | 148.2 |  | MANUALLY OPENED TRANSFORMER FUSE P240998 IDLE HOUR DR TO REPLACE LEAKING TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 1214 | 0.0016474 | 0.12208 | 4.0679e-05 | 0.0030143
120045544 | TAH7300 | 2025-04-21 | Q2 | 11:46 | 12:48 | 1:01 | 1 | 1 | 61.97 | 3 | 186 |  | FAILED SPLICE INSIDE PADMOUNT TRANSFORMER 16657 W LAKE BLVD | Equipment | Other | Review Complete | NONE | North Lake | 4 | 2025 | 2 | 49165 | 4479 | 0.00066979 | 0.041527 | 6.1019e-05 | 0.0037832
120045755 | TAH7200 | 2025-04-24 | Q2 | 5:27 | 5:59 | 0:32 | 0 | 32 | 32.03 | 4 | 127.8 |  | MANUALLY OPENED TS-9 'B' POS ELBOWS @ HWY 89 / CREWS TO RE-SET OS-60 BACK ON PAD AFTER BEING HIT BY A SNOW PLOW | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 5 | 49165 | 80 | 0.05 | 1.5975 | 8.1359e-05 | 0.0025994
120045766 | TAH7300 | 2025-04-24 | Q2 | 11:00 | 13:52 | 2:52 | 2 | 52 | 172 | 10 | 1720.2 |  | MANUALLY OPENED TRANSFORMER FUSE P292489 WILLIAMS LN-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 5 | 49165 | 4479 | 0.0022326 | 0.38406 | 0.0002034 | 0.034988
120045836 | TAH7300 | 2025-04-25 | Q2 | 15:50 | 17:05 | 1:15 | 1 | 15 | 75 | 7 | 525 |  | MANUALLY OPENED TRANSFORMER FUSE P105234 BAY VIEW DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 6 | 49165 | 4479 | 0.0015628 | 0.11721 | 0.00014238 | 0.010678
120045837 | MEY3400 | 2025-04-25 | Q2 | 16:12 | 16:59 | 0:46 | 0 | 46 | 46.35 | 1 | 46.2 | SOUTH LAKE TAHOE | BLOWN 6 AMP FUSES (2) P131251 TATA LN-NO CAUSE FOUND | Unknown |  | Review Complete | NONE | South Lake | 4 | 2025 | 6 | 49165 | 4066 | 0.00024594 | 0.011363 | 2.034e-05 | 0.00093969
120048520 | POR3200 | 2025-04-30 | Q2 | 6:56 |  | 0:00 |  |  | 145.23 | 0 | 0 |  | LUCA25-1057 - MANUALLY CLOSED FUSES P240960 OPENED FUSES P291147 &amp; LIFTED TAPS P160264 FOR REPLACEMENT OF DAMAGED CROSS ARM P160264 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 1214 | 0 | 0 | 0 | 0
120048681 | TAH7300 | 2025-04-30 | Q2 | 12:22 | 14:12 | 1:50 | 1 | 50 | 110 | 13 | 1429.8 |  | MANUALLY OPENED TRANSFORMER FUSE P216263 HARRIS AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.0029024 | 0.31922 | 0.00026442 | 0.029082
120048749 | TAH7300 | 2025-04-30 | Q2 | 14:46 | 16:54 | 2:08 | 2 | 8 | 128 | 6 | 768 |  | MANUALLY OPENED TRANSFORMER FUSE P115688 CHINKAPIN RD-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.0013396 | 0.17147 | 0.00012204 | 0.015621
121000267 | HOB7700 | 2025-04-11 | Q2 | 4:47 | 5:30 | 0:43 | 0 | 43 | 43.47 | 32 | 1375.8 | TRUCKEE | MANUALLY OPENED HOB7700 BREAKER TO REPAIR PHASE OFF INSULATOR AT P59720 STATE HWY 89 SEE RB876. | Equipment | Wire Movement | Review Complete | NONE | North Lake | 4 | 2025 | 6 | 49165 | 32 | 1 | 42.9937 | 0.00065087 | 0.027983
231069733 | MEY3400 | 2025-04-03 | Q2 | 2:55 | 6:45 | 3:50 | 3 | 50 | 230 | 5 | 1150.2 |  | MANUALLY OPENED TRANSFORMER FUSE P131421 TATA LN TO REPLACE CUTOUTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 5 | 49165 | 4066 | 0.0012297 | 0.28288 | 0.0001017 | 0.023395
231070139 | STL3101 | 2025-04-05 | Q2 | 13:00 | 14:00 | 1:00 | 1 | 0 | 60 | 20 | 1200 |  | MANUALLY OPENED 6 AMP TRANSFORMER FUSES P83255 TAMARACK AVE TO REPLACE POLE/LINE EXTENSION | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 7 | 49165 | 2316 | 0.0086356 | 0.51813 | 0.00040679 | 0.024408
231070396 | TPZ1202 | 2025-04-07 | Q2 | 14:09 | 17:45 | 3:36 | 3 | 36 | 216 | 2 | 432 |  | MANUALLY OPENED 15AMP LINE FUSE P295423 TOPAZ LN-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 2 | 49165 | 727 | 0.002751 | 0.59422 | 4.0679e-05 | 0.0087867
231070467 | TPZ1202 | 2025-04-08 | Q2 | 10:53 | 17:50 | 6:57 | 6 | 57 | 417 | 2 | 834 |  | MANUALLY OPENED 15 AMP LINE FUSE P295428 TOPAZ LN-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 3 | 49165 | 727 | 0.002751 | 1.1472 | 4.0679e-05 | 0.016963
231070480 | MEY3100 | 2025-04-08 | Q2 | 11:52 | 14:15 | 2:23 | 2 | 23 | 143 | 15 | 2145 | SOUTH LAKE TAHOE | MANUALLY OPENED 11 AMP LINE FUSE P239180 TROUT CREEK AVE-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 3 | 49165 | 2411 | 0.0062215 | 0.88967 | 0.0003051 | 0.043629
231070652 | TPZ1202 | 2025-04-10 | Q2 | 7:33 | 15:45 | 8:12 | 8 | 12 | 492 | 2 | 984 |  | MANUALLY OPENED LINE FUSE P295428 TOPAZ LN TO REPLACE CONDUCTOR | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 5 | 49165 | 727 | 0.002751 | 1.3535 | 4.0679e-05 | 0.020014
231070689 | MEY3100 | 2025-04-10 | Q2 | 8:50 | 14:45 | 5:55 | 5 | 55 | 355 | 13 | 4615.2 |  | MANAULLY OPENED TRANSFORMER FUSE AT P98942 FOR POLE REPLACEMENT. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 5 | 49165 | 2411 | 0.005392 | 1.9142 | 0.00026442 | 0.093872
231070976 | TPZ1202 | 2025-04-14 | Q2 | 14:10 | 18:25 | 4:15 | 4 | 15 | 255 | 6 | 1530 |  | MANUALLY OPENED 15 AMP FUSE P286985 US HWY 395 TO REBUILD TAP | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 2 | 49165 | 727 | 0.0082531 | 2.1045 | 0.00012204 | 0.03112
231071036 | TPZ1202 | 2025-04-15 | Q2 | 11:00 | 17:45 | 6:45 | 6 | 45 | 405 | 6 | 2430 |  | MANUALLY OPENED 15 AMP LINE FUSE P286985 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 3 | 49165 | 727 | 0.0082531 | 3.3425 | 0.00012204 | 0.049425
231071202 | TPZ1202 | 2025-04-17 | Q2 | 11:00 | 15:26 | 4:26 | 4 | 26 | 266 | 2 | 532.2 |  | MANUALLY OPENED LINE FUSE P293569 US HIGHWAY 395, REBUILD TAP | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 5 | 49165 | 727 | 0.002751 | 0.73205 | 4.0679e-05 | 0.010825
231071207 | TPZ1202 | 2025-04-17 | Q2 | 11:00 | 15:45 | 4:45 | 4 | 45 | 285 | 6 | 1710 |  | MANUALLY OPENED 15 AMP LINE FUSE P286985 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 5 | 49165 | 727 | 0.0082531 | 2.3521 | 0.00012204 | 0.034781
231071336 | TPZ1202 | 2025-04-18 | Q2 | 11:00 | 15:30 | 4:30 | 4 | 30 | 270 | 2 | 540 |  | MANUALLY OPENED LINE FUSE P293569 US HWY 395-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 6 | 49165 | 727 | 0.002751 | 0.74278 | 4.0679e-05 | 0.010983
231071910 | TAH5201 | 2025-04-21 | Q2 | 12:00 | 14:50 | 2:50 | 2 | 50 | 170 | 18 | 3060 |  | MANUALLY OPENED TRANSFORMER FUSE P232484 LASSEN DR-REPLACE P131246 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 2 | 49165 | 3188 | 0.0056462 | 0.95985 | 0.00036611 | 0.062239
231072183 | MEY3200 | 2025-04-22 | Q2 | 12:20 | 15:30 | 3:10 | 3 | 10 | 190 | 84 | 15960 | SOUTH LAKE TAHOE | MANUALLY OPENED 65 AMP LINE FUSES P135340 WINNEMUCCA AVE-REPLACE P66424 &amp; P87937 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 3 | 49165 | 3851 | 0.021813 | 4.1444 | 0.0017085 | 0.32462
231072292 | TAH7300 | 2025-04-23 | Q2 | 11:00 | 13:42 | 2:42 | 2 | 42 | 162 | 10 | 1620 |  | MANUALLY OPENED TRANSFORMER FUSE P100189 WOODLAND DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.0022326 | 0.36169 | 0.0002034 | 0.03295
231072297 | TAH7300 | 2025-04-23 | Q2 | 11:02 | 13:13 | 2:11 | 2 | 11 | 131 | 19 | 2488.8 |  | MANUALLY OPENED TRANSFORMER FUSE P85700 CEDAR LN-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.004242 | 0.55566 | 0.00038645 | 0.050621
231072325 | TAH7300 | 2025-04-23 | Q2 | 13:30 | 17:00 | 3:30 | 3 | 30 | 210 | 14 | 2940 |  | MANUALLY OPENED TRANSFORMER FUSE P115505 SNOWBIRD LOOP-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.0031257 | 0.6564 | 0.00028476 | 0.059799
231072333 | TAH7300 | 2025-04-23 | Q2 | 14:37 | 17:33 | 2:56 | 2 | 56 | 176 | 4 | 703.8 |  | MANUALLY OPENED TRANSFORMER FUSE P100251 CREST DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.00089306 | 0.15713 | 8.1359e-05 | 0.014315
231072379 | TAH7300 | 2025-04-23 | Q2 | 17:24 | 18:35 | 1:11 | 1 | 11 | 71 | 13 | 922.8 |  | MANUALLY OPENED TRANSFORMER FUSE P81718 LARK DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.0029024 | 0.20603 | 0.00026442 | 0.018769
231072396 | TAH7300 | 2025-04-23 | Q2 | 23:20 | 4:30 | 5:10 | 5 | 10 | 310.2 | 5 | 1551 |  | MANUALLY OPENED 20 AMP LINE FUSE P8531 STATE HWY 89-REPLACED P92494 &amp; INSTALLED NEW POLE BETWEEN P92494 &amp; P92495 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.0011163 | 0.34628 | 0.0001017 | 0.031547
231072423 | TAH7300 | 2025-04-24 | Q2 | 11:42 | 15:40 | 3:58 | 3 | 58 | 238 | 30 | 7140 |  | MANUALLY OPENED LINE FUSE P296726 FLICKER AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 5 | 49165 | 4479 | 0.0066979 | 1.5941 | 0.00061019 | 0.14523
231072507 | MEY3300 | 2025-04-25 | Q2 | 3:15 | 4:50 | 1:35 | 1 | 35 | 95.47 | 11 | 1050 |  | REPLACED LEAKING TRANSFORMER P120347 TOPPEWETAH ST | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | 4 | 2025 | 6 | 49165 | 3628 | 0.003032 | 0.28942 | 0.00022374 | 0.021357
231072540 | TAH7300 | 2025-04-25 | Q2 | 11:06 | 16:12 | 5:06 | 5 | 6 | 306 | 4 | 1224 |  | MANUALLY OPENED TRANSFORMER FUSES P105231 LAKEVIEW DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 6 | 49165 | 4479 | 0.00089306 | 0.27328 | 8.1359e-05 | 0.024896
231073303 | MULLER1296 | 2025-04-29 | Q2 | 13:08 | 17:25 | 4:17 | 4 | 17 | 257 | 16 | 4111.8 | MARKLEEVILLE | MANUALLY OPENED LINE FUSE P117493 PINION RD-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 3 | 49165 | 641 | 0.024961 | 6.4147 | 0.00032543 | 0.083633
231074773 | TAH7300 | 2025-04-30 | Q2 | 11:05 | 11:48 | 0:43 | 0 | 43 | 43 | 1 | 43.2 |  | MANUALLY OPENED TRANSFORMER FUSE P275814 FOREST VIEW DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 4 | 2025 | 4 | 49165 | 4479 | 0.00022326 | 0.009645 | 2.034e-05 | 0.00087867
231075048 | MEY3200 | 2025-04-30 | Q2 | 16:20 | 17:22 | 1:02 | 1 | 2 | 62 | 16 | 991.8 |  | MANUALLY OPENED TRANSFORMER FUSE P77123 RAINBOW DR-REPLACE LEAKING TRANSFORMER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 4 | 2025 | 4 | 49165 | 3851 | 0.0041548 | 0.25754 | 0.00032543 | 0.020173
120049496 | TAH7300 | 2025-05-01 | Q2 | 11:00 | 12:54 | 1:54 | 1 | 54 | 114 | 13 | 1482 |  | MANUALLY OPENED TRANSFORMER FUSE P115683 ANTELOPE WAY-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 4479 | 0.0029024 | 0.33088 | 0.00026442 | 0.030143
231076383 | TAH7300 | 2025-05-01 | Q2 | 13:09 | 15:39 | 2:30 | 2 | 30 | 150 | 3 | 450 |  | MANUALLY OPENED TRANSFORMER FUSES P99233 PLACER ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 4479 | 0.00066979 | 0.10047 | 6.1019e-05 | 0.0091529
231076388 | TAH7300 | 2025-05-01 | Q2 | 13:19 | 15:25 | 2:06 | 2 | 6 | 126 | 9 | 1134 |  | MANUALLY OPENED TRANSFORMER FUSES P99236 PLACER ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 4479 | 0.0020094 | 0.25318 | 0.00018306 | 0.023065
120049672 | MEY3300 | 2025-05-02 | Q2 | 1:15 | 7:02 | 5:47 | 5 | 47 | 347.28 | 921 | 68073 | SOUTH LAKE TAHOE | MANUALLY OPENED PTR 3300-R3 FOR PLANNED WORK P111401 REPLACEMENT. MANUALLY OPENED 33M58 DISC. SWITCHING TO RESTORE FROM 33-34-T1 DURING WORK. | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 6 | 49165 | 3628 | 0.25386 | 18.7632 | 0.018733 | 1.3846
120049712 | TAH7300 | 2025-05-02 | Q2 | 11:06 | 12:50 | 1:44 | 1 | 44 | 104 | 8 | 832.2 |  | MANUALLY OPENED TRANSFORMER FUSE P73389 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 4479 | 0.0017861 | 0.1858 | 0.00016272 | 0.016927
120049734 | TAH7300 | 2025-05-02 | Q2 | 12:56 | 15:25 | 2:29 | 2 | 29 | 149 | 9 | 1341 |  | MANUALLY OPENED TRANSFORMER FUSE P77266 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 4479 | 0.0020094 | 0.2994 | 0.00018306 | 0.027276
120049735 | TAH7300 | 2025-05-02 | Q2 | 13:00 | 15:37 | 2:37 | 2 | 37 | 157 | 12 | 1884 |  | MANUALLY OPENED TRANSFORMER FUSE P77269 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 4479 | 0.0026792 | 0.42063 | 0.00024408 | 0.03832
231077961 | TAH7300 | 2025-05-02 | Q2 | 15:48 | 18:24 | 2:36 | 2 | 36 | 156 | 17 | 2652 |  | MANUALLY OPENED TRANSFORMER FUSE P269681 OLYMPIC DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 4479 | 0.0037955 | 0.5921 | 0.00034577 | 0.053941
120049911 | TAH7300 | 2025-05-03 | Q2 | 16:01 | 20:45 | 4:44 | 4 | 44 | 284 | 42 | 11928 | TAHOMA | BLOWN 15 AMP LINE FUSES P216281 2ND AVE-TREE FELL ONTO PRIMARY P216285 DURING VEGETATION CLEARING | Act Of Man | Vegetation clearing | Review Complete | THIRD PARTY | North Lake | 5 | 2025 | 7 | 49165 | 4479 | 0.0093771 | 2.6631 | 0.00085427 | 0.24261
231078791 | TRK7202 | 2025-05-03 | Q2 | 22:21 | 2:05 | 3:44 | 3 | 44 | 224 | 3 | 672 | TRUCKEE | BLOWN 15 AMP LINE FUSE P224058 RIVER RD-SQUIRREL CONTACT, DURING PATROL, A BROKEN CROSSARM P29394 RIVER RD WAS FOUND | Animal | Squirrel | Review Complete | NONE | North Lake | 5 | 2025 | 7 | 49165 | 151 | 0.019868 | 4.4503 | 6.1019e-05 | 0.013668
120050015 | KBH5200 | 2025-05-05 | Q2 | 11:00 | 12:52 | 1:52 | 1 | 52 | 112 | 9 | 1008 |  | MANUALLY OPENED TRANSFORMER FUSE P236658 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 2 | 49165 | 2902 | 0.0031013 | 0.34735 | 0.00018306 | 0.020502
120050016 | KBH5200 | 2025-05-05 | Q2 | 11:00 | 12:50 | 1:50 | 1 | 50 | 110 | 6 | 660 |  | MANUALLY OPENED TRANSFORMER FUSE P96794 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 2 | 49165 | 2902 | 0.0020675 | 0.22743 | 0.00012204 | 0.013424
120050033 | SQV7201 | 2025-05-05 | Q2 | 11:57 | 13:33 | 1:36 | 1 | 36 | 96 | 14 | 1344 |  | MANUALLY OPENED TRANSFORMER FUSE P115872 BEAR CREEK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 2 | 49165 | 743 | 0.018843 | 1.8089 | 0.00028476 | 0.027337
231079063 | KBH5200 | 2025-05-05 | Q2 | 13:08 | 14:38 | 1:30 | 1 | 30 | 90 | 8 | 720 |  | MANUALLY OPENED TRANSFORMER FUSE P292097 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 2 | 49165 | 2902 | 0.0027567 | 0.2481 | 0.00016272 | 0.014645
120050065 | SQV7201 | 2025-05-05 | Q2 | 14:19 | 16:29 | 2:10 | 2 | 10 | 130 | 10 | 1300.2 |  | MANUALLY OPENED TRANSFORMER FUSE P206081 BEAR CREEK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 2 | 49165 | 743 | 0.013459 | 1.7499 | 0.0002034 | 0.026446
120050064 | KBH5200 | 2025-05-05 | Q2 | 14:48 | 17:00 | 2:12 | 2 | 12 | 132 | 11 | 1452 |  | MANUALLY OPENED TRANSFORMER FUSE P292095 N RIDGE DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 2 | 49165 | 2902 | 0.0037905 | 0.50034 | 0.00022374 | 0.029533
231079223 | KBH5200 | 2025-05-06 | Q2 | 11:00 | 13:08 | 2:08 | 2 | 8 | 128 | 8 | 1024.2 |  | MANUALLY OPENED TRANSFORMER FUSES P281583 WILDCHERRY LN-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 2902 | 0.0027567 | 0.35293 | 0.00016272 | 0.020832
231079227 | KBH5200 | 2025-05-06 | Q2 | 11:00 | 13:08 | 2:08 | 2 | 8 | 128 | 8 | 1024.2 |  | MANUALLY OPENED TRANSFORMER FUSES P292094 WILDCHERRY LN-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 2902 | 0.0027567 | 0.35293 | 0.00016272 | 0.020832
231079236 | KBH5200 | 2025-05-06 | Q2 | 11:06 | 13:32 | 2:26 | 2 | 26 | 146 | 12 | 1752 |  | MANUALLY OPENED TRANSFORMER FUSES P81466 WOODCHUCK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 2902 | 0.0041351 | 0.60372 | 0.00024408 | 0.035635
231079242 | KBH5200 | 2025-05-06 | Q2 | 11:06 | 13:32 | 2:26 | 2 | 26 | 146 | 17 | 2482.2 |  | MANUALLY OPENED TRANSFORMER FUSES P81468 WOODCHUCK DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 2902 | 0.005858 | 0.85534 | 0.00034577 | 0.050487
120050240 | KBH5200 | 2025-05-07 | Q2 | 11:03 | 14:24 | 3:21 | 3 | 21 | 201 | 8 | 1608 |  | MANUALLY OPENED TRANSFORMER FUSE P61481 TERRACE AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 2902 | 0.0027567 | 0.5541 | 0.00016272 | 0.032706
120050238 | POR3200 | 2025-05-07 | Q2 | 11:04 | 18:00 | 6:56 | 6 | 56 | 416 | 56 | 23296.2 | PORTOLA | MANUALLY OPENED 140A FUSES P193853 TO LIFT TAPS AT P193849 FOR RT CLEARANCE# 1061 - MAINTENANCE POLE AND CROSS ARM REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 1214 | 0.046129 | 19.1896 | 0.001139 | 0.47384
120050239 | KBH5200 | 2025-05-07 | Q2 | 11:10 | 14:20 | 3:10 | 3 | 10 | 190 | 7 | 1330.2 |  | MANUALLY OPENED TRANSFORMER FUSE P45306 TERRACE AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 2902 | 0.0024121 | 0.45837 | 0.00014238 | 0.027056
231079471 | KBH5200 | 2025-05-07 | Q2 | 14:54 | 16:11 | 1:17 | 1 | 17 | 77 | 9 | 693 |  | MANUALLY OPENED TRANSFORMER FUSE P68501 NEVADA ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 2902 | 0.0031013 | 0.2388 | 0.00018306 | 0.014095
231079492 | KBH5200 | 2025-05-07 | Q2 | 16:23 | 17:09 | 0:46 | 0 | 46 | 46 | 6 | 276 |  | MANUALLY OPENED TRANSFORMER FUSE P68504 NEVADA ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 2902 | 0.0020675 | 0.095107 | 0.00012204 | 0.0056137
120050291 | TAH5201 | 2025-05-07 | Q2 | 19:36 | 6:36 | 10:59 | 10 | 59 | 659.95 | 263 | 89980.8 | TAHOE CITY | BLOWN 40A RISER FUSE (1 OF 3) P140177 LAKE FOREST RD - MANUALLY OPENED OTHER TWO FUSES - MADE OPEN AT GLEN BAIRD - FAILED CABLE ON GLEN BAIRD AT VAULT 1791 | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 5 | 2025 | 4 | 49165 | 3188 | 0.082497 | 28.2248 | 0.0053493 | 1.8302
120050293 | MEY3200 | 2025-05-07 | Q2 | 23:16 | 5:26 | 6:09 | 6 | 9 | 369.8 | 544 | 201180 | SOUTH LAKE TAHOE | MANUALLY OPENED VFI-903-75 'B' POS L/B AT VENICE DR FOR REPLACEMENT OF OS-900 WITH LJE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 4 | 49165 | 3851 | 0.14126 | 52.241 | 0.011065 | 4.0919
231079599 | KBH5200 | 2025-05-08 | Q2 | 11:56 | 14:05 | 2:09 | 2 | 9 | 129 | 7 | 903 |  | MANUALLY OPENED P291799 REPLACE OPEN WIRE - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 2902 | 0.0024121 | 0.31116 | 0.00014238 | 0.018367
231079602 | KBH5200 | 2025-05-08 | Q2 | 12:00 | 14:05 | 2:05 | 2 | 5 | 125 | 7 | 874.8 |  | MANUALLY OPENED P232345 REPLACE OPEN WIRE - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 2902 | 0.0024121 | 0.30145 | 0.00014238 | 0.017793
120050416 | KBH5200 | 2025-05-09 | Q2 | 11:18 | 13:15 | 1:57 | 1 | 57 | 117 | 2 | 234 |  | MANUALLY OPENED TRANSFORMER FUSE P183396 MOUNTAIN CIR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 2902 | 0.00068918 | 0.080634 | 4.0679e-05 | 0.0047595
120050417 | KBH5200 | 2025-05-09 | Q2 | 11:26 | 13:25 | 1:59 | 1 | 59 | 119 | 3 | 357 |  | MANUALLY OPENED TRANSFORMER FUSE P183397 MOUNTAIN CIR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 2902 | 0.0010338 | 0.12302 | 6.1019e-05 | 0.0072613
231079745 | MEY3100 | 2025-05-09 | Q2 | 11:50 | 12:00 | 0:10 | 0 | 10 | 10 | 14 | 139.8 |  | MANUALLY OPENED TRANSFORMER FUSES P192841 LAKEVIEW AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 6 | 49165 | 2411 | 0.0058067 | 0.057984 | 0.00028476 | 0.0028435
231079754 | MEY3100 | 2025-05-09 | Q2 | 12:05 | 12:11 | 0:06 | 0 | 6 | 6 | 23 | 138 |  | MANUALLY OPENED TRANSFORMER FUSES P192985 LAKEVIEW AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 6 | 49165 | 2411 | 0.0095396 | 0.057238 | 0.00046781 | 0.0028069
231079763 | MEY3100 | 2025-05-09 | Q2 | 12:15 | 12:31 | 0:16 | 0 | 16 | 16 | 12 | 192 |  | MANUALLY OPENED TRANSFORMER FUSES P293178 LAKEVIEW AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 6 | 49165 | 2411 | 0.0049772 | 0.079635 | 0.00024408 | 0.0039052
231079769 | MEY3100 | 2025-05-09 | Q2 | 12:38 | 12:56 | 0:18 | 0 | 18 | 18 | 23 | 414 |  | MANUALLY OPENED TRANSFORMER FUSES P2904458 SAN FRANSICO AVE-LOAD BALANCING | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 6 | 49165 | 2411 | 0.0095396 | 0.17171 | 0.00046781 | 0.0084206
120050482 | POR3100 | 2025-05-10 | Q2 | 18:38 | 0:02 | 5:24 | 5 | 24 | 324.3 | 1 | 324.6 | PORTOLA | BLOWN FUSE P281378 PARK ST-FAILED CUTOUTS | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 5 | 2025 | 7 | 49165 | 748 | 0.0013369 | 0.43396 | 2.034e-05 | 0.0066023
120050557 | MEY3400 | 2025-05-11 | Q2 | 17:10 | 17:22 | 0:11 | 0 | 11 | 11.7 | 264 | 3074.4 | SOUTH LAKE TAHOE | MANUALLY OPENED 3400-R2 DUE TO 'A' PHASE OFF OF LOW SIDE OF RECLOSER - MANUALLY OPENED 3400-R1 TO SAFELY BYPASS 3400-R1 | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | 5 | 2025 | 1 | 49165 | 4066 | 0.064929 | 0.75612 | 0.0053697 | 0.062532
120050564 | TPZ1202 | 2025-05-11 | Q2 | 19:53 | 23:10 | 3:17 | 3 | 17 | 197 | 1 | 196.8 | WALKER | BROKEN NEUTRAL AT THE TOP OF TRANSFORMER P264126 EASTSIDE LN | Equipment | Vibration/Loose Connection | Review Complete | NONE | South Lake | 5 | 2025 | 1 | 49165 | 727 | 0.0013755 | 0.2707 | 2.034e-05 | 0.0040028
120050572 | GLS7400 | 2025-05-11 | Q2 | 23:37 | 7:45 | 8:08 | 8 | 8 | 488.5 | 11 | 3708.6 | TRUCKEE | BLOWN 20 AMP LINE FUSE P224119 LA MIRADA RD, TREE TOOK PRIMARY DOWN P239508 LA MIRADA RD | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 5 | 2025 | 1 | 49165 | 1234 | 0.0089141 | 3.0053 | 0.00022374 | 0.075432
231080014 | MEY3400 | 2025-05-12 | Q2 | 1:00 | 1:35 | 0:35 | 0 | 35 | 35 | 6 | 210 | SOUTH LAKE TAHOE | MANUALLY OPENED TRANSFORMER FUSE P135280 UPLANDS WAY-REPAIRED LOOSE CLAMPS | Equipment | Other | Review Complete | NONE | South Lake | 5 | 2025 | 2 | 49165 | 4066 | 0.0014757 | 0.051648 | 0.00012204 | 0.0042713
231080031 | MEY3400 | 2025-05-12 | Q2 | 3:40 | 16:20 | 12:40 | 12 | 40 | 760.15 | 249 | 189277.2 | SOUTH LAKE TAHOE | 3400-R3 PTR L/O - TREE DOWN AT P286894 NEAR BALDWIN DR | Vegetation | Fall In Tree | Review Complete | NONE | South Lake | 5 | 2025 | 2 | 49165 | 4066 | 0.06124 | 46.5512 | 0.0050646 | 3.8498
120050576 | STL3501 | 2025-05-12 | Q2 | 5:47 | 11:25 | 5:38 | 5 | 38 | 338 | 198 | 66924 | SOUTH LAKE TAHOE | BLOWN 40K LINE FUSE P97024 RUFUS ALLEN BLVD-TREE DOWN, WIRE DOWN BETWEEN P62581 &amp; P68528 PICKETT AVE | Vegetation | Fall In Tree | Review Complete | NONE | South Lake | 5 | 2025 | 2 | 49165 | 2530 | 0.078261 | 26.4522 | 0.0040273 | 1.3612
120050638 | TAH5201 | 2025-05-12 | Q2 | 10:06 | 11:52 | 1:46 | 1 | 46 | 106.48 | 31 | 3300.6 | CARNELIAN BAY | BLOWN 20 AMP LINE FUSE P124671 RUMAR WAY-WIRES SLAPPED TOGETHER AT P295808 (FORMERLY P151349) | Weather | Wind | Review Complete | NONE | North Lake | 5 | 2025 | 2 | 49165 | 3188 | 0.009724 | 1.0353 | 0.00063053 | 0.067133
120050655 | MULLER1296 | 2025-05-12 | Q2 | 11:58 | 16:00 | 4:02 | 4 | 2 | 242 | 1 | 241.8 | MARKLEEVILLE | BLOWN 15 AMP LINE FUSE P214638 CARSON RIVER RD-WIND | Weather | Wind | Review Complete | NONE | South Lake | 5 | 2025 | 2 | 49165 | 641 | 0.0015601 | 0.37722 | 2.034e-05 | 0.0049181
120050665 | TPZ1202 | 2025-05-12 | Q2 | 12:14 | 19:15 | 7:01 | 7 | 1 | 421.13 | 5 | 2105.4 |  | BLOWN 20 AMP LINE FUSE P286952 US HWY 395-TREE LIMB ON WIRES | Vegetation | Fall In Limb | Review Complete | NONE | South Lake | 5 | 2025 | 2 | 49165 | 727 | 0.0068776 | 2.896 | 0.0001017 | 0.042823
120050648 | TPZ1202 | 2025-05-12 | Q2 | 12:21 | 19:15 | 6:54 | 6 | 54 | 414 | 702 | 290338.8 | COLEVILLE | PTR 1202-R1 L/O (DID HAVE FIRE SEASON ON)-BROKEN TAP BEYOND FUSES AT P286952, WIRE DOWN P92757 | Weather | Wind | Review Complete | NONE | South Lake | 5 | 2025 | 2 | 49165 | 727 | 0.96561 | 399.3656 | 0.014278 | 5.9054
120050701 | TPZ1202 | 2025-05-12 | Q2 | 23:05 | 1:15 | 2:09 | 2 | 9 | 129.85 | 1 | 129.6 | COLEVILLE | BAD SECONDARY &amp; CONNECTIONS P199419 US HWY 395 | Weather | Wind | Review Complete | NONE | South Lake | 5 | 2025 | 2 | 49165 | 727 | 0.0013755 | 0.17827 | 2.034e-05 | 0.002636
231080310 | MEY3400 | 2025-05-13 | Q2 | 11:40 | 17:00 | 5:20 | 5 | 20 | 320 | 4 | 1279.8 |  | MANUALLY OPENED 11 AMP LINE FUSE P234199 FALLEN LEAF RD-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 3 | 49165 | 4066 | 0.00098377 | 0.31476 | 8.1359e-05 | 0.026031
231080314 | KBH5200 | 2025-05-13 | Q2 | 11:48 | 14:40 | 2:52 | 2 | 52 | 172 | 6 | 1032 |  | MANUALLY OPENED TRANSFORMER FUSE P81589 WILDWOOD RD-REPLACE SECONDARY WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 2902 | 0.0020675 | 0.35562 | 0.00012204 | 0.020991
231080317 | KBH5200 | 2025-05-13 | Q2 | 11:48 | 14:40 | 2:52 | 2 | 52 | 172 | 4 | 688.2 |  | MANUALLY OPENED TRANSFORMER FUSE P81590 WILDWOOD RD-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 2902 | 0.0013784 | 0.23715 | 8.1359e-05 | 0.013998
231080320 | KBH5200 | 2025-05-13 | Q2 | 11:48 | 14:57 | 3:09 | 3 | 9 | 189 | 5 | 945 |  | MANUALLY OPENED TRANSFORMER FUSE P81592 CATALPA DR-REPLACE OPEN WIRE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 2902 | 0.0017229 | 0.32564 | 0.0001017 | 0.019221
120050729 | TPZ1202 | 2025-05-13 | Q2 | 15:52 | 17:40 | 1:47 | 1 | 47 | 108 | 2 | 216 | TOPAZ | BLOWN 15K FUSE P 266619 - LIKELY DUE TO WIND | Weather | Wind | Review Complete | NONE | South Lake | 5 | 2025 | 3 | 49165 | 727 | 0.002751 | 0.29711 | 4.0679e-05 | 0.0043934
231080459 | MEY3400 | 2025-05-14 | Q2 | 11:00 | 15:45 | 4:45 | 4 | 45 | 285 | 4 | 1140 |  | MANUALLY OPENED 11 AMP LINE FUSE P234199 FALLEN LEAF RD-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 4 | 49165 | 4066 | 0.00098377 | 0.28037 | 8.1359e-05 | 0.023187
120050982 | TAH5201 | 2025-05-14 | Q2 | 17:55 | 18:15 | 0:20 | 0 | 20 | 20 | 1 | 19.8 | TAHOE CITY | REPLACED LOOSE CONNECTOR ON P242217 SERVICE WIRES - GROVE ST. | Equipment | Vibration/Loose Connection | Review Complete | NONE | North Lake | 5 | 2025 | 4 | 49165 | 3188 | 0.00031368 | 0.0062108 | 2.034e-05 | 0.00040273
120050989 | POR3100 | 2025-05-15 | Q2 | 1:23 | 8:21 | 6:57 | 6 | 57 | 417.88 | 734 | 306554.4 | PORTOLA | MANUALLY OPENED POR3100 CB FOR PLANNED OUTAGE - POLE REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 748 | 0.98128 | 409.8321 | 0.014929 | 6.2352
120050999 | POR3200 | 2025-05-15 | Q2 | 2:10 | 8:21 | 6:10 | 6 | 10 | 370.8 | 1199 | 444231 | PORTOLA | MANUALLY OPENED 3200-7 L/B FOR PLANNED WORK - POLE REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 1214 | 0.98764 | 365.9234 | 0.024387 | 9.0355
120051335 | MEY3500 | 2025-05-18 | Q2 | 12:36 | 2:35 | 13:59 | 13 | 59 | 839.33 | 5 | 3926.4 | SOUTH LAKE TAHOE | BLOWN RISER FUSES P259771 MEADOW CREST DR-FAILED TRANSFORMER #55202 | Equipment | Other | Review Complete | NONE | South Lake | 5 | 2025 | 1 | 49165 | 3852 | 0.001298 | 1.0193 | 0.0001017 | 0.079862
120051407 | MULLER1296 | 2025-05-18 | Q2 | 23:00 | 1:00 | 2:00 | 2 | 0 | 120 | 2 | 240 | MARKLEEVILLE | MANUALLY OPENED TRANSFORMER FUSE P277655 CRYSTAL SPRINGS RD-TREE TOOK DOWN SECONDARY ACROSS RIVER | Vegetation | Fall In Tree | Review Complete | NONE | South Lake | 5 | 2025 | 1 | 49165 | 641 | 0.0031201 | 0.37441 | 4.0679e-05 | 0.0048815
120051469 | SQV8100; SQV8200 | 2025-05-19 | Q2 | 10:30 | 11:20 | 0:50 | 0 | 50 | 50.22 | 956 | 47133.6 | OLYMPIC VALLEY | SQUAW VALLEY 1001 CS LOCKED OUT - 8100 &amp; 8200 CIRCUITS DE-ENERGIZED - FAILED REG 1 CAUSED BUS LOCKOUT | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 5 | 2025 | 2 | 49165 | #N/A | #N/A | #N/A | 0.019445 | 0.95868
231081457 | MEY3400 | 2025-05-19 | Q2 | 11:27 | 18:05 | 6:38 | 6 | 38 | 398 | 4 | 1591.8 |  | MANUALLY OPENED FUSE P234199 FALLEN LEAF RD - TAP REBUILD | Planned | Maintenance |  | PLANNED OUTAGE | South Lake | 5 | 2025 | 2 | 49165 | 4066 | 0.00098377 | 0.39149 | 8.1359e-05 | 0.032377
231082739 | MEY3400 | 2025-05-20 | Q2 | 11:30 | 20:00 | 8:30 | 8 | 30 | 510 | 4 | 2040 |  | MANUALLY OPENED 11 AMP LINE FUSE P234199 FALLEN LEAF RD-TAP REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 3 | 49165 | 4066 | 0.00098377 | 0.50172 | 8.1359e-05 | 0.041493
231082885 | TAH7100 | 2025-05-21 | Q2 | 11:00 | 14:05 | 3:05 | 3 | 5 | 185 | 3 | 555 |  | MANUALLY OPENED TRANSFORMER FUSE P90663 GRANLIBAKKEN RD-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 1621 | 0.0018507 | 0.34238 | 6.1019e-05 | 0.011289
231082882 | TAH7100 | 2025-05-21 | Q2 | 11:10 | 14:15 | 3:05 | 3 | 5 | 185.43 | 9 | 1668.6 |  | MANUALLY OPENED TRANSFORMER FUSE P90665 GRANLIBAKKEN RD-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 1621 | 0.0055521 | 1.0294 | 0.00018306 | 0.033939
120052203 | POR3200 | 2025-05-21 | Q2 | 12:25 | 19:40 | 7:15 | 7 | 15 | 435 | 15 | 6525 | PORTOLA | MANUALLY OPENED 11 AMP LINE FUSE P70989 N GULLING ST-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 1214 | 0.012356 | 5.3748 | 0.0003051 | 0.13272
231082932 | TAH7100 | 2025-05-21 | Q2 | 14:15 | 16:57 | 2:42 | 2 | 42 | 162 | 12 | 1944 |  | MANUALLY OPENED TRANSFORMER FUSE P90668 RAWHIDE DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 1621 | 0.0074028 | 1.1993 | 0.00024408 | 0.03954
231082939 | TAH7100 | 2025-05-21 | Q2 | 14:46 | 17:57 | 3:10 | 3 | 10 | 190.82 | 11 | 2098.8 |  | MANULLY OPENED TRANSFORMER FUSE P90670 RAWHIDE DR-REPLACED OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 1621 | 0.0067859 | 1.2948 | 0.00022374 | 0.042689
231082998 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 37 | 16834.8 |  | MANUALLY OPENED P68780 TREE REMOVAL - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 5 | 49165 | 4066 | 0.0090999 | 4.1404 | 0.00075257 | 0.34241
231083001 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:38 | 7:38 | 7 | 38 | 458 | 20 | 9160.2 |  | MANUALLY OPENED P68783 ELOSIE TREE REMOVAL - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 5 | 49165 | 4066 | 0.0049188 | 2.2529 | 0.00040679 | 0.18632
231083004 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 11 | 5005.2 | SOUTH LAKE TAHOE | MANUALLY OPENED P68784 ELOSIE TREE REMOVAL - PLANNED OUTAGE &#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 5 | 49165 | 4066 | 0.0027054 | 1.231 | 0.00022374 | 0.1018
231083007 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 28 | 12739.8 | SOUTH LAKE TAHOE | MANUALLY OPENED P68787 ELOSIE TREE REMOVAL - PLANNED OUTAGE &#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 5 | 49165 | 4066 | 0.0068864 | 3.1333 | 0.00056951 | 0.25912
231083014 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 13 | 5914.8 |  | MANUALLY OPENED P290425 ELOSIE TREE REMOVAL - PLANNED OUTAGE&#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 5 | 49165 | 4066 | 0.0031972 | 1.4547 | 0.00026442 | 0.12031
231083017 | MEY3400 | 2025-05-22 | Q2 | 10:00 | 17:35 | 7:35 | 7 | 35 | 455 | 4 | 1819.8 |  | MANUALLY OPENED P69852 12th ST TREE REMOVAL - PLANNED OUTAGE &#x0D; | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 5 | 49165 | 4066 | 0.00098377 | 0.44757 | 8.1359e-05 | 0.037014
120052436 | TAH5201 | 2025-05-22 | Q2 | 11:01 | 15:30 | 4:29 | 4 | 29 | 269.08 | 25 | 2490.6 | TAHOE CITY | BLOWN 10 AMP LINE FUSE P232266 &amp; P249279 BLOWN 11 AMP FUSE REPLACED U/G PADMOUNT TRANSFORMER 142 | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 5 | 2025 | 5 | 49165 | 3188 | 0.0078419 | 0.78124 | 0.00050849 | 0.050658
120052438 | KBH4202 | 2025-05-22 | Q2 | 11:09 | 13:17 | 2:07 | 2 | 7 | 127.55 | 36 | 4591.2 |  | MANUALLY OPENED TRANSFORMER FUSE P92263 GOLDEN AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 1348 | 0.026706 | 3.4059 | 0.00073223 | 0.093384
231083042 | MEY3400 | 2025-05-22 | Q2 | 11:17 | 19:23 | 8:06 | 8 | 6 | 486.32 | 4 | 1945.2 |  | MANUALLY OPENED 11K FUSE P234199 FOR PLANNED WORK | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 5 | 49165 | 4066 | 0.00098377 | 0.47841 | 8.1359e-05 | 0.039565
231083069 | KBH4202 | 2025-05-22 | Q2 | 13:37 | 15:50 | 2:13 | 2 | 13 | 133 | 17 | 2260.8 |  | MANUALLY OPENED P242138 REPLACE OPEN WIRE SALMON AVE - PLANNED OUTAGE | Planned | Other | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 1348 | 0.012611 | 1.6772 | 0.00034577 | 0.045984
231083070 | KBH4202 | 2025-05-22 | Q2 | 13:37 | 15:50 | 2:13 | 2 | 13 | 133 | 15 | 1995 |  | MANUALLY OPENED P81491 REPLACE OPEN WIRE SALMON AVE - PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 1348 | 0.011128 | 1.48 | 0.0003051 | 0.040578
231083108 | KBH4202 | 2025-05-22 | Q2 | 16:05 | 16:55 | 0:50 | 0 | 50 | 50 | 10 | 499.8 |  | MANUALLY OPENED P81487 CHIPMUNK REPLACE OPEN WIRE PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 1348 | 0.0074184 | 0.37077 | 0.0002034 | 0.010166
231083111 | KBH4202 | 2025-05-22 | Q2 | 16:05 | 16:55 | 0:50 | 0 | 50 | 50 | 6 | 300 |  | MANUALLY OPENED P81488 CHIPMUNK REPLACE OPEN WIRE PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 1348 | 0.004451 | 0.22255 | 0.00012204 | 0.0061019
120052595 | KBH4202 | 2025-05-23 | Q2 | 11:00 | 12:24 | 1:24 | 1 | 24 | 84 | 9 | 756 |  | MANUALLY OPENED TRANSFORMER FUSE P60543 SPEEDBOAT AVE-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 1348 | 0.0066766 | 0.56083 | 0.00018306 | 0.015377
231083240 | TAH7300 | 2025-05-23 | Q2 | 11:19 | 12:58 | 1:39 | 1 | 39 | 99 | 7 | 693 |  | MANUALLY OPENED XFMR FUSES P124755 GROUSE DR - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 4479 | 0.0015628 | 0.15472 | 0.00014238 | 0.014095
231083249 | TAH7300 | 2025-05-23 | Q2 | 12:37 | 14:15 | 1:38 | 1 | 38 | 98 | 10 | 979.8 |  | MANUALLY OPENED XFMRS P134312 GROUSE DR - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 4479 | 0.0022326 | 0.21875 | 0.0002034 | 0.019929
120052601 | KBH4203 | 2025-05-23 | Q2 | 12:45 | 14:26 | 1:41 | 1 | 41 | 101 | 14 | 1414.2 |  | MANUALLY OPENED TRANSFORMER FUSE P60529 BEAR ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 510 | 0.027451 | 2.7729 | 0.00028476 | 0.028764
231083254 | KBH4203 | 2025-05-23 | Q2 | 13:03 | 14:37 | 1:34 | 1 | 34 | 94 | 5 | 469.8 |  | MANUALLY OPENED XFMR FUSES P60526 BEAR ST - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 510 | 0.0098039 | 0.92118 | 0.0001017 | 0.0095556
231083284 | TAH7300 | 2025-05-23 | Q2 | 14:30 | 16:20 | 1:50 | 1 | 50 | 110 | 9 | 990 |  | MANUALLY OPENED XFMR FUSES P134316 CHUKAR CIR - CHANGING OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 4479 | 0.0020094 | 0.22103 | 0.00018306 | 0.020136
120052610 | KBH4203 | 2025-05-23 | Q2 | 15:00 | 15:34 | 0:34 | 0 | 34 | 34 | 12 | 408 |  | MANUALLY OPENED TRANSFORMER FUSE P35583 BEAR ST-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 6 | 49165 | 510 | 0.023529 | 0.8 | 0.00024408 | 0.0082986
120052723 | MULLER1296 | 2025-05-24 | Q2 | 11:13 | 11:46 | 0:33 | 0 | 33 | 33 | 632 | 20856 |  | NVE 112 LINE LOCKOUT ROUND HILL TO BUCKEYE - TRANSMISISON FAULT BETWEEN ROUND HILL AND MULLER | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | 5 | 2025 | 7 | 49165 | 641 | 0.98596 | 32.5367 | 0.012855 | 0.4242
231083680 | TAH7100 | 2025-05-27 | Q2 | 11:10 | 14:14 | 3:04 | 3 | 4 | 184 | 22 | 4048.2 | TAHOE CITY | MANUALLY OPENED TRANSFORMER FUSE P90692 VIRGINIA DR-REPLACE OPEN WIRE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 3 | 49165 | 1621 | 0.013572 | 2.4973 | 0.00044747 | 0.082339
231083855 | TAH7300 | 2025-05-28 | Q2 | 10:43 | 11:11 | 0:28 | 0 | 28 | 28 | 6 | 168 |  | MANUALLY OPENED TRANSFORMER FUSE P155487 STATE HWY 89-REPLACED CUTOUT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 5 | 2025 | 4 | 49165 | 4479 | 0.0013396 | 0.037508 | 0.00012204 | 0.0034171
120053128 | MEY3500 | 2025-05-28 | Q2 | 11:53 | 15:41 | 3:47 | 3 | 47 | 227.77 | 4 | 910.8 |  | MANUALLY DISCONNECTED PRIMARY P81961 &amp; P81962 RUBICON TRL-REPLACED PRIMARY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 4 | 49165 | 3852 | 0.0010384 | 0.23645 | 8.1359e-05 | 0.018525
120053171 | MEY3200 | 2025-05-28 | Q2 | 18:00 | 4:20 | 10:20 | 10 | 20 | 620.5 | 95 | 58947.6 | SOUTH LAKE TAHOE | MANUALLY OPENED VFI-3200-2 'E' POS-PRIMARY U/G REBUILD | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 5 | 2025 | 4 | 49165 | 3851 | 0.024669 | 15.3071 | 0.0019323 | 1.199
231084021 | TAH5201 | 2025-05-29 | Q2 | 13:01 | 13:14 | 0:13 | 0 | 13 | 13 | 17 | 220.8 |  | MANUALLY OPNED P281490 PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 3188 | 0.0053325 | 0.06926 | 0.00034577 | 0.004491
231084027 | TAH5201 | 2025-05-29 | Q2 | 13:23 | 13:32 | 0:09 | 0 | 9 | 9 | 10 | 90 |  | MANUALLY OPENED P61458 REPLACE CUTOUT -PLANNED OUTAGE | Planned | Maintenance |  | PLANNED OUTAGE | North Lake | 5 | 2025 | 5 | 49165 | 3188 | 0.0031368 | 0.028231 | 0.0002034 | 0.0018306
120053218 | STL3501 | 2025-05-29 | Q2 | 14:04 | 17:27 | 3:23 | 3 | 23 | 203 | 16 | 3247.8 | SOUTH LAKE TAHOE | BLOWN TRANSFORMER FUSE P71162 DEER PARK AVE - NO CAUSE FOUND. | Other | Unknown | Review Complete | NONE | South Lake | 5 | 2025 | 5 | 49165 | 2530 | 0.0063241 | 1.2837 | 0.00032543 | 0.066059
120053206 | MEY3300 | 2025-05-29 | Q2 | 14:06 | 15:26 | 1:19 | 1 | 19 | 79.63 | 14 | 1114.8 | SOUTH LAKE TAHOE | BLOWN TRANSFORMER FUSE P84216 NAVAHOE DR-SERVICE RIPPED DOWN BY TRUCK. CSP UNSAFE TO OPERATE | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | South Lake | 5 | 2025 | 5 | 49165 | 3628 | 0.0038589 | 0.30728 | 0.00028476 | 0.022675
120053223 | MEY3200 | 2025-05-29 | Q2 | 15:16 | 16:13 | 0:57 | 0 | 57 | 57 | 4 | 228 | SOUTH LAKE TAHOE | BLOWN TRANSFORMER FUSE P84634 ELOISE AVE-SERVICE RIPPED DOWN BY TRUCK | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | South Lake | 5 | 2025 | 5 | 49165 | 3851 | 0.0010387 | 0.059205 | 8.1359e-05 | 0.0046374
231084161 | KBH5200 | 2025-05-30 | Q2 | 13:23 | 13:35 | 0:12 | 0 | 12 | 12 | 6 | 72 |  | MANUALLY OPENED CUT OUTS AND REPLACED THEM AT P239496 CARNELIAN DR | Equipment | Other | Review Complete | NONE | North Lake | 5 | 2025 | 6 | 49165 | 2902 | 0.0020675 | 0.02481 | 0.00012204 | 0.0014645
120053420 | MEY3200 | 2025-05-31 | Q2 | 9:29 | 10:38 | 1:09 | 1 | 9 | 69 | 1 | 69 | SOUTH LAKE TAHOE | PARTIAL POWER P290767 TATA LN DUE TO BAD CONNECTIONS | Equipment | Other | Review Complete | NONE | South Lake | 5 | 2025 | 7 | 49165 | 3851 | 0.00025967 | 0.017917 | 2.034e-05 | 0.0014034
120053437 | TAH5201 | 2025-05-31 | Q2 | 13:03 | 14:10 | 1:07 | 1 | 7 | 67 | 48 | 3216 | TAHOE CITY | BLOWN 20 AMP FUSE P137671 GROVE ST - NO CAUSE FOUND; SUN SAID HE DIDNT FIND AN OBVIOUS CAUSE - SUSPECTS IT MIGHT HAVE BEEN A TREE LIMB TOUCH | Unknown |  | Review Complete | NONE | North Lake | 5 | 2025 | 7 | 49165 | 3188 | 0.015056 | 1.0088 | 0.0009763 | 0.065412
120053508 | MULLER1296 | 2025-06-01 | Q2 | 12:38 | 14:04 | 1:26 | 1 | 26 | 86 | 632 | 54352.2 | MARKLEEVILLE | NVE 112 LINE LOCKOUT ROUND HILL TO BUCKEYE - TRANSMISISON FAULT BETWEEN BUCKEYE (NVE) &amp; ROUNDHILL (NVE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | 6 | 2025 | 1 | 49165 | 641 | 0.98596 | 84.7928 | 0.012855 | 1.1055
231084420 | STL3501 | 2025-06-02 | Q2 | 0:00 | 19:30 | 19:30 | 19 | 30 | 1170 | 39 | 45630 |  | MANUALLY OPENED 25AMP LINE FUSE P291287 BLACKWOOD RD PULLED NEW UG | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 2 | 49165 | 2530 | 0.015415 | 18.0356 | 0.00079325 | 0.9281
231084424 | STL3501 | 2025-06-02 | Q2 | 11:00 | 19:30 | 8:30 | 8 | 30 | 510 | 19 | 9690 | SOUTH LAKE TAHOE | MANUALLY OPENED 25 AMP LINE FUSE P291288 PULLED NEW UG | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 2 | 49165 | 2530 | 0.0075099 | 3.83 | 0.00038645 | 0.19709
231084433 | KBH5200 | 2025-06-02 | Q2 | 12:01 | 12:10 | 0:09 | 0 | 9 | 9 | 5 | 45 |  | MANUALLY OPENED TRANSFORMER FUSE, REPLACED DAMAGED CUTOUT P206174 CARNELIAN BAY RD | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 6 | 2025 | 2 | 49165 | 2902 | 0.0017229 | 0.015507 | 0.0001017 | 0.00091529
120053556 | KBH4202 | 2025-06-02 | Q2 | 12:07 | 17:03 | 4:55 | 4 | 55 | 295.93 | 1 | 91.2 | KINGS BEACH | RAN MID SPAN TAP AND ELIMINATE APPROXIMATELY 35FT OF CABLE PARK LN | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 6 | 2025 | 2 | 49165 | 1348 | 0.00074184 | 0.067656 | 2.034e-05 | 0.001855
120053608 | MEY3400 | 2025-06-03 | Q2 | 11:44 | 15:59 | 4:15 | 4 | 15 | 255 | 15 | 3825 |  | MANUALLY OPENED LB 34-59 FOR PLANNED MAINTENANCE REPLACING SPAN GUY WITH DOWN GUY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 3 | 49165 | 4066 | 0.0036891 | 0.94073 | 0.0003051 | 0.077799
120053645 | TAH7300 | 2025-06-03 | Q2 | 18:39 | 8:56 | 14:17 | 14 | 17 | 857.47 | 784 | 113171.4 | MEEKS BAY | PTR 7300-R2 P291747 HWY 89 LOCKED OPEN / SWITCHING TO ISOLATE OUTAGE - BLOWN FUSES P134488 HWY 89 - FAILED CABLE BETWEEN HH @ XFMR 13523 TO NEXT HH TO NORTH | Equipment | Corrosion/Decay | Mismatch - Number of customers | NONE | North Lake | 6 | 2025 | 3 | 49165 | 4479 | 0.17504 | 25.2671 | 0.015946 | 2.3019
120053662 | MEY3200 | 2025-06-03 | Q2 | 21:14 | 3:39 | 6:25 | 6 | 25 | 385.37 | 12 | 4263.6 |  | MANUALLY OPENED OS-902-23 'A' POS @ CAPRI DR AND PADMOUNT XFMR 3938 TAHOE KEYS BLVD ELBOWS TOWARD VFI-3200-2 'E' POS FOR CREW WORKING ON TAHOE KEYS UG REBUILD / RETURNED MEY 3400 AND 3200 TO NORMAL CONFIG - FS-903-65 'A' POS IS NORMAL OPEN TIE SWITCH - PHASING ISSUE RESOLVED | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 3 | 49165 | 3851 | 0.0031161 | 1.1071 | 0.00024408 | 0.08672
120053823 | POR3200 | 2025-06-04 | Q2 | 12:41 | 15:33 | 2:52 | 2 | 52 | 172.55 | 32 | 5521.8 | PORTOLA | MANUALLY HUNG TEMPORARY CUTOUTS P155557 LADERA LN-REPLACE P130544 HUERTA WAY | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 4 | 49165 | 1214 | 0.026359 | 4.5484 | 0.00065087 | 0.11231
120053934 | TAH7100 | 2025-06-05 | Q2 | 15:11 | 16:30 | 1:18 | 1 | 18 | 78.87 | 25 | 1971 | TAHOE CITY | BLOWN 25K LINE FUSES P108875 BIG PINE DR-GARBAGE TRUCK CLIPPED PHONE LINE CAUSING PHASES TO BUMP | Act Of Man | Vehicle strike | Review Complete | THIRD PARTY | North Lake | 6 | 2025 | 5 | 49165 | 1621 | 0.015423 | 1.2159 | 0.00050849 | 0.040089
120053944 | MULLER1296 | 2025-06-05 | Q2 | 18:29 | 19:30 | 1:01 | 1 | 1 | 61 | 632 | 38551.8 | MARKLEEVILLE | 1296 CB @ MULLER (NVE) LOCKED OPEN - DUE TO DOWN WIRE AT NVE SIDE | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | 6 | 2025 | 5 | 49165 | 641 | 0.98596 | 60.1432 | 0.012855 | 0.78413
120053966 | CAL2501 | 2025-06-05 | Q2 | 21:57 | 22:53 | 0:56 | 0 | 56 | 56 | 96 | 5376 | VERDI | CALIFORNIA 2501 CB (NVE) LOCKED OPEN / FIRE MODE &amp; WEATHER | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 5 | 49165 | 97 | 0.98969 | 55.4227 | 0.0019526 | 0.10935
120053969 | WSH201 | 2025-06-05 | Q2 | 21:57 | 22:53 | 0:56 | 0 | 56 | 56 | 55 | 3079.8 | TRUCKEE | CALIFORNIA 2501 CB (NVE) LOCKED OPEN / FIRE MODE &amp; WEATHER | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 5 | 49165 | 58 | 0.94828 | 53.1 | 0.0011187 | 0.062642
120053976 | TPZ1202 | 2025-06-06 | Q2 | 1:01 | 3:44 | 2:43 | 2 | 43 | 163 | 595 | 96985.2 | COLEVILLE | MANUALLY OPENED LB# 1261-F @ P266658 HWY 395, REPLACED P# 128913 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 6 | 49165 | 727 | 0.81843 | 133.4047 | 0.012102 | 1.9726
120054056 | STL3501 | 2025-06-06 | Q2 | 11:39 | 11:52 | 0:13 | 0 | 13 | 13.43 | 38 | 510.6 |  | MANUALLY OPENED 25 AMP RISER FUSE P291287 BLACKWOOD RD-U/G SECONDARY MOLDINGS WERE MELTING | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | 6 | 2025 | 6 | 49165 | 2530 | 0.01502 | 0.20182 | 0.00077291 | 0.010385
231085189 | SQV8200 | 2025-06-06 | Q2 | 11:40 | 13:10 | 1:30 | 1 | 30 | 90 | 96 | 8640 |  | MANUALLY OPENED 65 AMP LINE FUSE P278419 WINDING CREEK RD-REPLACED CROSSARMS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 6 | 49165 | 888 | 0.10811 | 9.7297 | 0.0019526 | 0.17573
120054165 | TAH7300 | 2025-06-07 | Q2 | 11:07 | 18:34 | 7:27 | 7 | 27 | 447 | 6 | 2682 | TAHOE CITY | BLOWN TRANSFORMER FUSE P248973 QUAIL LN-REPLACED CUTOUT AND LEAKING TRANSFORMER | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 6 | 2025 | 7 | 49165 | 4479 | 0.0013396 | 0.59879 | 0.00012204 | 0.054551
120054499 | POR3200 | 2025-06-09 | Q2 | 11:00 | 13:20 | 2:20 | 2 | 20 | 140 | 11 | 1540.2 |  | MANUALLY OPENED LINE FUSE P193848 IDLE HOUR DR-REPLACE P155736 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 2 | 49165 | 1214 | 0.009061 | 1.2687 | 0.00022374 | 0.031327
231085484 | MEY3400 | 2025-06-09 | Q2 | 11:44 | 13:15 | 1:31 | 1 | 31 | 91 | 3 | 273 |  | MANUALLY OPENED CUTOUT AT P291674 FOR PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 2 | 49165 | 4066 | 0.00073783 | 0.067142 | 6.1019e-05 | 0.0055527
120054579 | MULLER1296 | 2025-06-09 | Q2 | 22:52 | 0:59 | 2:07 | 2 | 7 | 127 | 633 | 80391 | MARKLEEVILLE | LOSS OF SOURCE FROM NVE - FAILED LIGHTNING ARRESTORS ON 1296-R1 (NVE) - BYPASSED&#x0D; | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | South Lake | 6 | 2025 | 2 | 49165 | 641 | 0.98752 | 125.415 | 0.012875 | 1.6351
231085731 | GLS7400 | 2025-06-10 | Q2 | 13:41 | 14:45 | 1:04 | 1 | 4 | 64 | 10 | 640.2 |  | MANUALLY OPENED TRANSFORMER FUSE P161168 EDINBURGH DR-TRANSFORMER REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 3 | 49165 | 1234 | 0.0081037 | 0.5188 | 0.0002034 | 0.013021
231085795 | GLS7600 | 2025-06-10 | Q2 | 16:25 | 16:35 | 0:10 | 0 | 10 | 10 | 1 | 10.2 |  | MANUALLY OPENED TRANSFORMER FUSE P252953 HINTON DR-PLANNED OUTAGE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 3 | 49165 | 56 | 0.017857 | 0.18214 | 2.034e-05 | 0.00020746
120054673 | SLK257 | 2025-06-10 | Q2 | 21:35 | 21:52 | 0:17 | 0 | 17 | 17.35 | 3 | 52.2 | BORDERTOWN | LOSS OF SOURCE FROM NVE. CAUSE UNKNOWN | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 3 | 49165 | 3 | 1 | 17.4 | 6.1019e-05 | 0.0010617
231085854 | TAH5201 | 2025-06-11 | Q2 | 11:00 | 15:19 | 4:19 | 4 | 19 | 259 | 225 | 58275 | TAHOE CITY | MANUALLY OPENED 40 AMP LINE FUSE P92062 MAMMOTH DR-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 4 | 49165 | 3188 | 0.070577 | 18.2795 | 0.0045764 | 1.1853
231085950 | MEY3200 | 2025-06-12 | Q2 | 1:38 | 3:00 | 1:22 | 1 | 22 | 82 | 2 | 163.8 |  | MANUALLY OPENED LINE FUSES P84847 EMERALD BAY RD-REPLACE BROKEN CROSSARMS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 5 | 49165 | 3851 | 0.00051935 | 0.042534 | 4.0679e-05 | 0.0033316
120054941 | SQV7201 | 2025-06-13 | Q2 | 11:45 | 14:45 | 3:00 | 3 | 0 | 180.2 | 96 | 17299.2 |  | MANUALLY LIFTED TAPS P292066 ALPINE MEADOWS RD-REPLACE CROSSARM P201221 (CLIMB JOB) | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 6 | 49165 | 743 | 0.12921 | 23.2829 | 0.0019526 | 0.35186
120055062 | SQV8200 | 2025-06-15 | Q2 | 11:33 | 14:32 | 2:59 | 2 | 59 | 179 | 158 | 28282.2 | OLYMPIC VALLEY | BLOWN VFI 139- D POSTION VICTOR DR ANIMAL CONTACT P224075 VICTOR PLC | Animal | Squirrel | Review Complete | NONE | North Lake | 6 | 2025 | 1 | 49165 | 888 | 0.17793 | 31.8493 | 0.0032137 | 0.57525
120055088 | MEY3400 | 2025-06-15 | Q2 | 21:25 | 22:07 | 0:42 | 0 | 42 | 42.42 | 23 | 975.6 | SOUTH LAKE TAHOE | BLOWN 30A LINE FUSES (2) P90945 LAKE TAHOE BLVD-RAVEN MADE CONTACT WITH WIRE AT P98772 COYOTE RIDGE CIR | Animal | Bird | Review Complete | NONE | South Lake | 6 | 2025 | 1 | 49165 | 4066 | 0.0056567 | 0.23994 | 0.00046781 | 0.019843
231086422 | TRK7202 | 2025-06-16 | Q2 | 15:35 | 15:51 | 0:16 | 0 | 16 | 16 | 4 | 64.2 |  | MANUALLY OPENED TRANSFORMER FUSE P68748 RIVER RD-REPAIRS TO LIGHTNING ARRESTOR | Equipment | Vibration/Loose Connection | Review Complete | NONE | North Lake | 6 | 2025 | 2 | 49165 | 151 | 0.02649 | 0.42517 | 8.1359e-05 | 0.0013058
120055186 | STL3101 | 2025-06-17 | Q2 | 11:12 | 17:01 | 5:49 | 5 | 49 | 349.27 | 1 | 349.2 |  | MANUALLY OPENED 3101-R1 - MAINTENANCE ON CROSS ARMS AND JUMPERS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 3 | 49165 | 2316 | 0.00043178 | 0.15078 | 2.034e-05 | 0.0071026
120055392 | POR3100 | 2025-06-18 | Q2 | 11:35 | 17:28 | 5:52 | 5 | 52 | 352.78 | 201 | 70842 | PORTOLA | MANUALLY OPENED L./B# 31-4 AND FUSES P209782-MAINTENANCE REPLACING P215897 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 4 | 49165 | 748 | 0.26872 | 94.7086 | 0.0040883 | 1.4409
231086902 | TPZ1202 | 2025-06-19 | Q2 | 1:11 | 4:00 | 2:48 | 2 | 48 | 168.82 | 8 | 1350.6 | COLEVILLE | MANUALLY OPENED 15 AMP LINE FUSE P266630 US HWY 395-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 5 | 49165 | 727 | 0.011004 | 1.8578 | 0.00016272 | 0.027471
120055466 | POR3200 | 2025-06-19 | Q2 | 11:24 | 17:14 | 5:50 | 5 | 50 | 350.85 | 24 | 8420.4 |  | MANUALLY OPENED JUMPERS P215801 MANZANITA ST-REPLACE P150554 | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 5 | 49165 | 1214 | 0.019769 | 6.9361 | 0.00048815 | 0.17127
120055467 | STL3501 | 2025-06-19 | Q2 | 11:52 | 16:26 | 4:34 | 4 | 34 | 274.53 | 82 | 22512 |  | MANUALLY LIFTED TAPS AT P286998 JUNIPER AVE - MAINTENANCE POLE &amp; CROSS ARM REPLACEMENTS | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 5 | 49165 | 2530 | 0.032411 | 8.898 | 0.0016679 | 0.45789
120055576 | MEY3500 | 2025-06-20 | Q2 | 13:22 | 14:00 | 0:38 | 0 | 38 | 38 | 5 | 190.2 | SOUTH LAKE TAHOE | BLOWN 25A LINE FUSE P297961 LODI AVE-BIRD | Animal | Bird | Review Complete | NONE | South Lake | 6 | 2025 | 6 | 49165 | 3852 | 0.001298 | 0.049377 | 0.0001017 | 0.0038686
120055622 | TAH7300 | 2025-06-20 | Q2 | 21:38 | 5:47 | 8:09 | 8 | 9 | 489.25 | 1 | 489 | HOMEWOOD | REPLACED LOOSE HARDWARE AT THE CUTOUT 9291421 MOANA CIR | Equipment | Vibration/Loose Connection | Review Complete | NONE | North Lake | 6 | 2025 | 6 | 49165 | 4479 | 0.00022326 | 0.10918 | 2.034e-05 | 0.0099461
120055709 | KBH4202 | 2025-06-22 | Q2 | 19:16 | 0:09 | 4:53 | 4 | 53 | 293.43 | 1 | 293.4 | KINGS BEACH | BURNT SERVICE LINE AND CONNECTIONS P278531 BEAVER ST | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 6 | 2025 | 1 | 49165 | 1348 | 0.00074184 | 0.21766 | 2.034e-05 | 0.0059677
120055719 | MEY3200 | 2025-06-23 | Q2 | 11:21 | 13:20 | 1:58 | 1 | 58 | 118.58 | 41 | 4861.8 | SOUTH LAKE TAHOE | BLOWN RISER FUSE P87807 (1 OF 3). MANUALLY OPENED REMAINING 2 AT 10:31AM - REPLACED BAD UG CABLE | Equipment | Corrosion/Decay | Review Complete | NONE | South Lake | 6 | 2025 | 2 | 49165 | 3851 | 0.010647 | 1.2625 | 0.00083393 | 0.098887
231087482 | TRK7203 | 2025-06-23 | Q2 | 14:11 | 18:59 | 4:47 | 4 | 47 | 287.7 | 8 | 2301.6 |  | MANUALLY OPENED VFI -170 C POSTION -INSTALL TRANFORMER P10551 FILOLI | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 2 | 49165 | 1837 | 0.0043549 | 1.2529 | 0.00016272 | 0.046814
120055831 | POR3200 | 2025-06-24 | Q2 | 1:00 | 6:33 | 29:33 | 29 | 33 | 1773 | 3 | 1332 | PORTOLA | REPLACED FAILED TRANSFORMER P130541 LADERA LN | Equipment | Corrosion/Decay | Review Complete | NONE | North Lake | 6 | 2025 | 3 | 49165 | 1214 | 0.0024712 | 1.0972 | 6.1019e-05 | 0.027092
120055839 | MEY3300 | 2025-06-25 | Q2 | 0:19 | 2:18 | 1:59 | 1 | 59 | 119.37 | 139 | 16591.8 | SOUTH LAKE TAHOE | MANUALLY OPENED VFI-3300-21 'C' POS FUSES; REPLACING VAULT TOP SECTION SIDEWALK PROJECT NEAR P205200 APACHE AVE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 4 | 49165 | 3628 | 0.038313 | 4.5733 | 0.0028272 | 0.33747
120055834 | TPZ1202 | 2025-06-25 | Q2 | 0:20 | 2:05 | 1:44 | 1 | 44 | 104.97 | 2 | 210 | COLEVILLE | BLOWN 3A TRANSFORMER FUSE P294852 LARSON LN-NO PROBABLE CAUSE FOUND | UNKNOWN |  | Review Complete | NONE | South Lake | 6 | 2025 | 4 | 49165 | 727 | 0.002751 | 0.28886 | 4.0679e-05 | 0.0042713
231087895 | TAH7100 | 2025-06-26 | Q2 | 11:08 | 14:00 | 2:52 | 2 | 52 | 172 | 6 | 1032 |  | MANUALLY OPENED TRANSFORMER FUSE P124649 ALPINE WAY-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 5 | 49165 | 1621 | 0.0037014 | 0.63664 | 0.00012204 | 0.020991
120055997 | MEY3100 | 2025-06-26 | Q2 | 14:48 | 15:03 | 0:14 | 0 | 14 | 14.82 | 5 | 73.8 | SOUTH LAKE TAHOE | MANUALLY SWITCHED TO CREATE CLEARANCE ON 640 LINE AND 3100 FEEDER FOR MAINTENANCE ON POLE (G.O VIOLATIONS) | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 5 | 49165 | 2411 | 0.0020738 | 0.03061 | 0.0001017 | 0.0015011
120056194 | POR3200 | 2025-06-27 | Q2 | 12:00 | 18:17 | 6:17 | 6 | 17 | 377 | 13 | 4900.8 | PORTOLA | MANUALLY OPENED TRANSFORMER FUSE P66233 MAGNOLIA AVE- POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 6 | 49165 | 1214 | 0.010708 | 4.0369 | 0.00026442 | 0.099681
231088061 | MEY3300 | 2025-06-27 | Q2 | 12:08 | 14:00 | 1:52 | 1 | 52 | 112 | 9 | 1008 |  | MANUALLY OPENED TRANSFORMER FUSE P97014 ELF LN-POLE REPLACEMENT | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 6 | 49165 | 3628 | 0.0024807 | 0.27784 | 0.00018306 | 0.020502
231088214 | MEY3400 | 2025-06-28 | Q2 | 11:00 | 12:05 | 1:05 | 1 | 5 | 65 | 21 | 886.2 |  | MANUALLY OPENED TRANSFORMER FUSE P293729 12TH ST MANUALLY OPENED TRANSFORMER FUSE P69516 TAHOE ISLAND DR- TRANSFORMER UPGRADE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 7 | 49165 | 4066 | 0.0051648 | 0.21795 | 0.00042713 | 0.018025
120057355 | NST8400; NST8500; NST8600 | 2025-06-29 | Q2 | 0:18 | 0:44 | 24:26 | 24 | 26 | 1466 | 1564 | 45010.2 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 1 | 49165 | #N/A | #N/A | #N/A | 0.031811 | 0.91549
120057142 | TAH7300 | 2025-06-29 | Q2 | 20:58 | 23:30 | 2:32 | 2 | 32 | 152.47 | 1 | 152.4 | TAHOE CITY | REMOVED TREE AND REHUNG SERVICE, W LAKE BLVD | Vegetation | Fall In Tree | Review Complete | NONE | North Lake | 6 | 2025 | 1 | 49165 | 4479 | 0.00022326 | 0.034025 | 2.034e-05 | 0.0030998
120057225 | SQV8300 | 2025-06-29 | Q2 | 22:06 | 6:33 | 8:27 | 8 | 27 | 507.9 | 1 | 508.2 |  | MANUALLY OPENED OS-77 'B' POS, REPLACED 500' OF CABLE | Planned | Maintenance | Review Complete | PLANNED OUTAGE | North Lake | 6 | 2025 | 1 | 49165 | 257 | 0.0038911 | 1.9774 | 2.034e-05 | 0.010337
120057282 | CEM41; CEM42 | 2025-06-30 | Q2 | 0:18 | 3:43 | 3:25 | 3 | 25 | 205.25 | 482 | 98929.2 | LOYALTON | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | #N/A | #N/A | #N/A | 0.0098037 | 2.0122
120057288 | KBH4201; KBH4202 | 2025-06-30 | Q2 | 0:18 | 3:20 | 3:02 | 3 | 2 | 182.3 | 1868 | 339022.2 | KINGS BEACH | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | #N/A | #N/A | #N/A | 0.037995 | 6.8956
120057293 | POR3100 | 2025-06-30 | Q2 | 0:18 | 3:11 | 2:52 | 2 | 52 | 172.57 | 732 | 126318.6 | PORTOLA | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 748 | 0.97861 | 168.8751 | 0.014889 | 2.5693
120057296 | POR3200 | 2025-06-30 | Q2 | 0:18 | 3:11 | 2:52 | 2 | 52 | 172.75 | 1198 | 206973.6 | PORTOLA | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 1214 | 0.98682 | 170.489 | 0.024367 | 4.2098
120057380 | GLS7400 | 2025-06-30 | Q2 | 0:18 | 3:47 | 3:29 | 3 | 29 | 209.23 | 1232 | 257795.4 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 1234 | 0.99838 | 208.9104 | 0.025058 | 5.2435
120057405 | SQV7201; SQV8100; SQV8200; SQV8300 | 2025-06-30 | Q2 | 0:18 | 4:14 | 3:55 | 3 | 55 | 235.7 | 1952 | 421427.4 | OLYMPIC VALLEY | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | #N/A | #N/A | #N/A | 0.039703 | 8.5717
120057657 | KBH4203; KBH5100; KBH5200 | 2025-06-30 | Q2 | 0:18 | 3:22 | 3:03 | 3 | 3 | 183.77 | 3478 | 626472 | KINGS BEACH | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | #N/A | #N/A | #N/A | 0.070741 | 12.7422
120057661 | TAH7300 | 2025-06-30 | Q2 | 0:18 | 0:45 | 0:26 | 0 | 26 | 26.88 | 4447 | 119545.2 | TAHOMA | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 4479 | 0.99286 | 26.6902 | 0.090451 | 2.4315
120057663 | TAH5201; TAH7100; TAH7200 | 2025-06-30 | Q2 | 0:18 | 4:39 | 4:20 | 4 | 20 | 260.63 | 4858 | 1104498.6 | TAHOE CITY | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | #N/A | #N/A | #N/A | 0.09881 | 22.4651
120057670 | GLS7600 | 2025-06-30 | Q2 | 0:18 | 3:50 | 3:31 | 3 | 31 | 211.8 | 55 | 11649 |  | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 56 | 0.98214 | 208.0179 | 0.0011187 | 0.23694
120057671 | TRK7203 | 2025-06-30 | Q2 | 0:18 | 0:44 | 0:26 | 0 | 26 | 26 | 1836 | 47736 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 1837 | 0.99946 | 25.9858 | 0.037344 | 0.97093
120057672 | TRK7202 | 2025-06-30 | Q2 | 0:18 | 0:45 | 0:26 | 0 | 26 | 26.52 | 151 | 4006.8 | TAHOE CITY | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 151 | 1 | 26.5351 | 0.0030713 | 0.081497
120057673 | TRK7204 | 2025-06-30 | Q2 | 0:18 | 0:44 | 0:26 | 0 | 26 | 26.02 | 48 | 1248.6 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 48 | 1 | 26.0125 | 0.0009763 | 0.025396
120057674 | SRB51 | 2025-06-30 | Q2 | 0:18 | 0:44 | 0:26 | 0 | 26 | 26.4 | 243 | 6415.2 | LOYALTON | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 243 | 1 | 26.4 | 0.0049425 | 0.13048
120057675 | RUS7900 | 2025-06-30 | Q2 | 0:18 | 0:45 | 0:26 | 0 | 26 | 26.75 | 55 | 1472.4 | TRUCKEE | LOSS OF SOURCE (NVE) BLOWN ARRESTOR ON 106 LINE AT MT ROSE SUBSTATION (3-WAY LINE) | Loss of Supply | Supplier outage | Review Complete | LOSS OF SUPPLY | North Lake | 6 | 2025 | 2 | 49165 | 55 | 1 | 26.7709 | 0.0011187 | 0.029948
120057735 | TAH7100 | 2025-06-30 | Q2 | 9:35 | 12:44 | 3:09 | 3 | 9 | 189 | 7 | 1323 | TAHOE CITY | BLOWN 6AMP TRANSFORMER FUSE P120577 CHAPEL LN-CAUSE UNKNOWN | UNKNOWN |  | Review Complete | NONE | North Lake | 6 | 2025 | 2 | 49165 | 1621 | 0.0043183 | 0.81616 | 0.00014238 | 0.026909
120057792 | MEY3100 | 2025-06-30 | Q2 | 13:04 | 13:26 | 0:22 | 0 | 22 | 22.57 | 5 | 112.8 |  | RESTORE SWITCHING FOR LUCA25-1110 - MULTIPLE REPAIRS ON 3100 FEEDER | Planned | Maintenance | Review Complete | PLANNED OUTAGE | South Lake | 6 | 2025 | 2 | 49165 | 2411 | 0.0020738 | 0.046786 | 0.0001017 | 0.0022943
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
|  |  | Q1 |  |  | 0:00 | 0 | 0 | #DIV/0! |  | 0 | [6 empty] | #N/A | 1 | 1900 | 7 | 48925 | #N/A | #N/A | #N/A | 0 | 0
Note on Q1: Joel Rivera: Wil be renamed to Construction Type (from OMS)

## CAUSE
Month | (All)
E2_Exclusion | None
Year | 2025
Row Labels | Count of ID | Sum of CI | Sum of CMI
Unknown | 2 | 49 | 3262.2
Other | 10 | 215 | 22564.8
Animal | 5 | 306 | 38502.6
Vegetation | 15 | 3677 | 1219176.6
Weather | 32 | 8376 | 966963
Equipment | 32 | 6269 | 640807.8
Grand Total | 96 | 18892 | 2891277

## Historical Data
Year | Month | No Of Events | Customers Inter | Customers Minutes | CAIDI (Min) | SAIDI (Min) | SAIFI | Cust Served | CIII
2020 | January |  |  |  | 48.4764 | 0.9259 | 0.0191
2020 | February |  |  |  | 354.6933 | 2.6602 | 0.0075
2020 | March |  |  |  | 43.7333 | 4.1328 | 0.0945
2020 | April |  |  |  | 115.2927 | 0.9454 | 0.0082
2020 | May |  |  |  | 120.9565 | 0.2782 | 0.0023
2020 | June |  |  |  | 166.4006 | 11.2154 | 0.0674
2020 | July |  |  |  | 53.3246 | 33.7971 | 0.6338
2020 | August |  |  |  | 60.0104 | 15.5607 | 0.2593
2020 | September |  |  |  | 48.5316 | 8.6095 | 0.1774
2020 | October |  |  |  | 254.3656 | 30.7528 | 0.1209
2020 | November |  |  |  | 576.8256 | 66.1619 | 0.1147
2020 | December |  |  |  | 92.5877 | 6.6015 | 0.0713 |  |  | 181.6414 | 1.5764
2021 | January |  |  |  | 190.5296 | 36.6577 | 0.1924
2021 | February |  |  |  | 192.9609 | 30.8809 | 0.16004
2021 | March |  |  |  | 573.7153 | 7.3327 | 0.012781
2021 | April |  |  |  | 309.4571 | 3.1531 | 0.010189
2021 | May |  |  |  | 91.9463 | 3.0672 | 0.033359
2021 | June |  |  |  | 137.6732 | 3.9695 | 0.028833
2021 | July |  |  |  | 97.5537 | 36.0406 | 0.36944
2021 | August |  |  |  | 155.6877 | 5.544 | 0.03561
2021 | September |  |  |  | 225.4407 | 32.1859 | 0.14277
2021 | October |  |  |  | 206.545 | 83.3124 | 0.40336
2021 | November |  |  |  | 21.8066 | 1.8675 | 0.085641
2021 | December |  |  |  | 290.7238 | 211.6472 | 0.728 |  |  | 455.6588 | 2.2024
2022 | January |  |  |  | 109.5485 | 36.5031 | 0.33321
2022 | February |  |  |  | 276.8458 | 0.74527 | 0.002692
2022 | March |  |  |  | 219.3545 | 3.6128 | 0.01647
2022 | April |  |  |  | 125.7471 | 14.7283 | 0.11713
2022 | May |  |  |  | 178.4688 | 22.5297 | 0.12624
2022 | June |  |  |  | 140.4578 | 49.3343 | 0.35124
2022 | July |  |  |  | 144.1905 | 32.5177 | 0.22552
2022 | August |  |  |  | 98.7195 | 30.8948 | 0.31295
2022 | September |  |  |  | 60.5973 | 11.7809 | 0.19441
2022 | October |  |  |  | 75.3811 | 8.5859 | 0.1139
2022 | November |  |  |  | 99.9957 | 4.9508 | 0.04951
2022 | December |  |  |  | 349.3223 | 162.365 | 0.4648 |  |  | 378.5484 | 2.3081
2023 | January |  |  |  | 147.2102 | 115.928 | 0.7875
2023 | February |  |  |  | 335.4268 | 5.501 | 0.0164
2023 | March |  |  |  | 154.0591 | 18.256 | 0.1185
2023 | April |  |  |  | 99.4094 | 3.3998 | 0.0342
2023 | May |  |  |  | 185.6492 | 15.5574 | 0.0838
2023 | June |  |  |  | 66.1396 | 3.221 | 0.0487
2023 | July |  |  |  | 116.8173 | 11.635 | 0.0996
2023 | August |  |  |  | 184.8824 | 2.2001 | 0.0119
2023 | September |  |  |  | 90.0781 | 9.224 | 0.1024
2023 | October |  |  |  | 117.09 | 5.7257 | 0.0489
2023 | November |  |  |  | 307.426 | 26.992 | 0.0878
2023 | December |  |  |  | 142.7407 | 1.927 | 0.0135 |  |  | 219.567 | 1.4532
2024 | January |  |  |  | 54.1879 | 6.1991 | 0.1144
2024 | February |  |  |  | 56.9862 | 11.591 | 0.2034
2024 | March |  |  |  | 229.5266 | 96.8843 | 0.42211
2024 | April |  |  |  | 135.4083 | 13.195 | 0.097446
2024 | May |  |  |  | 217.1286 | 1.2513 | 0.005763
2024 | June |  |  |  | 101.7441 | 5.4391 | 0.053459
2024 | July |  |  |  | 163.3705 | 14.506 | 0.088792
2024 | August |  |  |  | 179.7638 | 9.1153 | 0.050707
2024 | September |  |  |  | 109.973 | 13.8214 | 0.12568
2024 | October |  |  |  | 48.642 | 3.6265 | 0.074555
2024 | November |  |  |  | 135.3853 | 25.4649 | 0.18809
2024 | December |  |  |  | 159.1837 | 6.4847 | 0.040737 |  |  | 207.5786 | 1.4651 | 288.5989 | 1.801
5Yr Sum |  | 0 | 0 | 0 | 9846.096 | 1442.9943 | 9.0052
[6 empty] | 288.5989 | 1.801 |  | 5 Year Average SAIDI AND SAIFI Targets
[7 empty] | #DIV/0! |  | 5 Year CII
[7 empty] | #DIV/0! |  | 5 Year CAIDI
2019-2023 | SAIFI 5 Yr Average | SAIDI 5 Yr Average | CAIDI 5 Yr Average | Events | CI | CMI | CS | CIII
JAN | 0.28932 | 39.2428 | 109.9905 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
FEB | 0.078006 | 10.2757 | 243.3826 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAR | 0.13287 | 26.0437 | 244.0778 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
APR | 0.053432 | 7.0843 | 157.0629 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAY | 0.050292 | 8.5368 | 158.8299 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
JUN | 0.10993 | 14.6359 | 122.4831 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
JUL | 0.28343 | 25.6993 | 115.0513 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
AUG | 0.13409 | 12.663 | 135.8128 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
SEP | 0.14853 | 15.1244 | 106.9241 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
OCT | 0.15232 | 26.4007 | 140.4047 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
NOV | 0.10515 | 25.0874 | 228.2878 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
DEC | 0.26367 | 77.8051 | 206.9116 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
TOTAL | 1.801 | 288.5989 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Lists (hidden)
Feeder | Date | Quarter | From | To | Elapsed | Hr | Min | Duration | CI | CMI | Town | Comments | Cause | E2_Exclusion | Wind | Weather | Follow Up Required? | District | Legacy Feeder | Column1
CAL2501 |  | Q4 | [10 empty] | UNKNOWN | NONE |  |  |  | NORTH LAKE TAHOE | CAL2501 | NORTH LAKE TAHOE
CEM41 |  | Q3 | [10 empty] | ANIMAL | CUSTOMER OWNED |  |  |  | SOUTH LAKE TAHOE | CEM41 | NORTH LAKE TAHOE
CEM42 |  | Q2 | [10 empty] | CONSTRUCTION BY COMPANY | FIRE/POLICE REQUEST |  |  |  |  | CEM42 | NORTH LAKE TAHOE
GLS7400 |  | Q1 | [10 empty] | CONSTRUCTION BY COMPANY CONTRACTOR | LOAD SHEDDING |  |  |  |  | GLS7400 | NORTH LAKE TAHOE
GLS7600 | [12 empty] | CONTAMINATION | LOSS OF SUPPLY |  |  |  |  | GLS7600 | NORTH LAKE TAHOE
HOB7700 | [12 empty] | CONTROL TROUBLE | IEEE MED |  |  |  |  | HOB7700 | NORTH LAKE TAHOE
KBH4203 | [12 empty] | DETERIORATION | THIRD PARTY |  |  |  |  | KBH4203 | NORTH LAKE TAHOE
KBH5100 | [12 empty] | DEVICE FAILED | TRANSMISSION |  |  |  |  | KBH5100 | NORTH LAKE TAHOE
KBH5200 | [12 empty] | DISTRIBUTION TRANSFORMER OVERLOAD | UNKNOWN |  |  |  |  | KBH5200 | NORTH LAKE TAHOE
KBH4201 | [12 empty] | FEEDER OVERLOAD | PLANNED OUTAGE |  |  |  |  | KBH4201 | NORTH LAKE TAHOE
KBH4202 | [12 empty] | FEEDER UNBALANCE | [5 empty] | KBH4202 | NORTH LAKE TAHOE
NST8400 | [12 empty] | FIRE ON COMPANY EQUIPMENT | [5 empty] | NST8400 | NORTH LAKE TAHOE
NST8500 | [12 empty] | FLOODING | [5 empty] | NST8500 | NORTH LAKE TAHOE
NST8600 | [12 empty] | FLYING DEBRIS | [5 empty] | NST8600 | NORTH LAKE TAHOE
POR3100 | [12 empty] | HUMAN CONTACT | [5 empty] | POR3100 | NORTH LAKE TAHOE
POR3200 | [12 empty] | IMPROPER APPLICATION | [5 empty] | POR3200 | NORTH LAKE TAHOE
RUS7900 | [12 empty] | IMPROPER INSTALLATION | [5 empty] | RUS7900 | NORTH LAKE TAHOE
SRB51 | [12 empty] | INSULATION FAILURE - CABLE | [5 empty] | SRB51 | NORTH LAKE TAHOE
SLK257 | [12 empty] | INSULATION FAILURE - OTHER | [5 empty] | SLK257 | NORTH LAKE TAHOE
SQV7201 | [12 empty] | LIGHTNING | [5 empty] | SQV7201 | NORTH LAKE TAHOE
SQV8300 | [12 empty] | MOISTURE | [5 empty] | SQV8300 | NORTH LAKE TAHOE
SQV8100 | [12 empty] | NON-COMPANY ACTIVITIES | [5 empty] | SQV8100 | NORTH LAKE TAHOE
SQV8200 | [12 empty] | NON-OUTAGE | [5 empty] | SQV8200 | NORTH LAKE TAHOE
SMP8700 | [12 empty] | OPERATING/TESTING ERROR | [5 empty] | SMP8700 | NORTH LAKE TAHOE
TAH7300 | [12 empty] | OTHER COMPANY ACTIVITIES | [5 empty] | TAH7300 | NORTH LAKE TAHOE
TAH5201 | [12 empty] | PLANNED OUTAGE | [5 empty] | TAH5201 | NORTH LAKE TAHOE
TAH7100 | [12 empty] | TREE - BROKEN LIMB | [5 empty] | TAH7100 | NORTH LAKE TAHOE
TAH7200 | [12 empty] | TREE FELL | [5 empty] | TAH7200 | NORTH LAKE TAHOE
608 | [12 empty] | TREE GROWTH | [5 empty] | 608 | NORTH LAKE TAHOE
619 | [12 empty] | UNDER FREQUENCY | [5 empty] | 619 | NORTH LAKE TAHOE
TRK7202 | [12 empty] | UNDER VOLTAGE | [5 empty] | TRK7202 | NORTH LAKE TAHOE
TRK7203 | [12 empty] | VANDALISM | [5 empty] | TRK7203 | NORTH LAKE TAHOE
TRK7204 | [12 empty] | VEHICLE | [5 empty] | TRK7204 | NORTH LAKE TAHOE
WSH201 | [12 empty] | VINES | [5 empty] | WSH201 | NORTH LAKE TAHOE
KNG2800 | [18 empty] | KNG2800 | SOUTH LAKE TAHOE
MEY3100 | [18 empty] | MEY3100 | SOUTH LAKE TAHOE
MEY3200 | [18 empty] | MEY3200 | SOUTH LAKE TAHOE
MEY3300 | [18 empty] | MEY3300 | SOUTH LAKE TAHOE
MEY3400 | [18 empty] | MEY3400 | SOUTH LAKE TAHOE
MEY3500 | [18 empty] | MEY3500 | SOUTH LAKE TAHOE
MULLER1296 | [18 empty] | MULLER1296 | SOUTH LAKE TAHOE
RHL1502 | [18 empty] | RHL1502 | SOUTH LAKE TAHOE
STL2200 | [18 empty] | STL2200 | SOUTH LAKE TAHOE
STL2300 | [18 empty] | STL2300 | SOUTH LAKE TAHOE
STL3501 | [18 empty] | STL3501 | SOUTH LAKE TAHOE
STL3101 | [18 empty] | STL3101 | SOUTH LAKE TAHOE
TPZ1202 | [18 empty] | TPZ1202 | SOUTH LAKE TAHOE

## E38 (hidden)
E38 Report Q1 |  |  | E38 Report Q2
V. | Customer Average Interruption Duration Index (CAIDI) |  | V. | Customer Average Interruption Duration Index (CAIDI)
a. | Sum of all customer interruption durations | 1786588.8 | a. | Sum of all customer interruption durations | 1258637.4
b. | Total number of customer interruptions | 12324 | b. | Total number of customer interruptions | 7639
c. | CAIDI | 144.9683 | c. | CAIDI | 164.7647
VI. | System Average Interruption Frequency Index (SAIFI) |  | VI. | System Average Interruption Frequency Index (SAIFI)
a. | Total number of customer interruptions | 12324 | a. | Total number of customer interruptions | 7639
b. | Total number of customers served | 49165 | b. | Total number of customers served | 49165
c. | SAIFI | 0.25067 | c. | SAIFI | 0.15537
VII. | System Average Interruption Duration Index (SAIDI) |  | VII. | System Average Interruption Duration Index (SAIDI)
a. | SAIDI | 36.3386 | a. | SAIDI | 25.6003
VIII. | Average number of customers without power per interruption as determined by deviing the number of customers interrupted by the number of interruptions (CIII) |  | VIII. | Average number of customers without power per interruption as determined by deviing the number of customers interrupted by the number of interruptions (CIII)
a. | Total number of customers interrupted | 12324 | a. | Total number of customers interrupted | 7639
b. | Total number of customer interruptions | 67 | b. | Total number of customer interruptions | 47
c. | CIII (VIII. a. / VIII. B.) | 183.9403 | c. | CIII (VIII. a. / VIII. B.) | 162.5319
E38 Report Q3 |  |  | E38 Report Q4
V. | Customer Average Interruption Duration Index (CAIDI) |  | V. | Customer Average Interruption Duration Index (CAIDI)
a. | Sum of all customer interruption durations | 0 | a. | Sum of all customer interruption durations | 0
b. | Total number of customer interruptions | 0 | b. | Total number of customer interruptions | 0
c. | CAIDI | #DIV/0! | c. | CAIDI | #DIV/0!
VI. | System Average Interruption Frequency Index (SAIFI) |  | VI. | System Average Interruption Frequency Index (SAIFI)
a. | Total number of customer interruptions | 0 | a. | Total number of customer interruptions | 0
b. | Total number of customers served | 47485 | b. | Total number of customers served | 47953
c. | SAIFI | 0 | c. | SAIFI | 0
VII. | System Average Interruption Duration Index (SAIDI) |  | VII. | System Average Interruption Duration Index (SAIDI)
a. | SAIDI | #DIV/0! | a. | SAIDI | #DIV/0!
VIII. | Average number of customers without power per interruption as determined by deviing the number of customers interrupted by the number of interruptions (CIII) |  | VIII. | Average number of customers without power per interruption as determined by deviing the number of customers interrupted by the number of interruptions (CIII)
a. | Total number of customers interrupted | 0 | a. | Total number of customers interrupted | 0
b. | Total number of customer interruptions | 0 | b. | Total number of customer interruptions | 0
c. | CIII (VIII. a. / VIII. B.) | #DIV/0! | c. | CIII (VIII. a. / VIII. B.) | #DIV/0!

## Feeder Count
MONTH | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
COLUMN # 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
CAL2501 | 96 | 97 | 97 | 97 | 97 | 97
CEM41 | 271 | 272 | 272 | 272 | 272 | 272
CEM42 | 214 | 214 | 214 | 214 | 214 | 214
GLS7400 | 1234 | 1234 | 1234 | 1234 | 1234 | 1234
GLS7600 | 56 | 56 | 56 | 56 | 56 | 56
HOB7700 | 30 | 32 | 32 | 32 | 32 | 32
KBH4203 | 509 | 510 | 510 | 510 | 510 | 510
KBH5100 | 96 | 96 | 96 | 96 | 96 | 96
KBH5200 | 2894 | 2902 | 2902 | 2902 | 2902 | 2902
KBH4201 | 541 | 541 | 541 | 541 | 541 | 541
KBH4202 | 1343 | 1348 | 1348 | 1348 | 1348 | 1348
NST8400 | 587 | 587 | 587 | 587 | 587 | 587
NST8500 | 973 | 974 | 974 | 974 | 974 | 974
NST8600 | 7 | 7 | 7 | 7 | 7 | 7
POR3100 | 745 | 748 | 748 | 748 | 748 | 748
POR3200 | 1211 | 1214 | 1214 | 1214 | 1214 | 1214
RUS7900 | 55 | 55 | 55 | 55 | 55 | 55
SRB51 | 242 | 243 | 243 | 243 | 243 | 243
SLK257 | 3 | 3 | 3 | 3 | 3 | 3
SQV7201 | 540 | 743 | 743 | 743 | 743 | 743
SQV8300 | 257 | 257 | 257 | 257 | 257 | 257
SQV8100 | 70 | 70 | 70 | 70 | 70 | 70
SQV8200 | 885 | 888 | 888 | 888 | 888 | 888
SMP8700 | 6 | 6 | 6 | 6 | 6 | 6
TAH7300 | 4455 | 4479 | 4479 | 4479 | 4479 | 4479
TAH5201 | 3185 | 3188 | 3188 | 3188 | 3188 | 3188
TAH7100 | 1823 | 1621 | 1621 | 1621 | 1621 | 1621
TAH7200 | 78 | 80 | 80 | 80 | 80 | 80
608 | 1 | 1 | 1 | 1 | 1 | 1
619 | 2 | 2 | 2 | 2 | 2 | 2
TRK7202 | 151 | 151 | 151 | 151 | 151 | 151
TRK7203 | 1825 | 1837 | 1837 | 1837 | 1837 | 1837
TRK7204 | 48 | 48 | 48 | 48 | 48 | 48
WSH201 | 58 | 58 | 58 | 58 | 58 | 58
KNG2800 | 2 | 2 | 2 | 2 | 2 | 2
MEY3100 | 2391 | 2411 | 2411 | 2411 | 2411 | 2411
MEY3200 | 3837 | 3851 | 3851 | 3851 | 3851 | 3851
MEY3300 | 3580 | 3628 | 3628 | 3628 | 3628 | 3628
MEY3400 | 4051 | 4066 | 4066 | 4066 | 4066 | 4066
MEY3500 | 3820 | 3852 | 3852 | 3852 | 3852 | 3852
MULLER1296 | 635 | 641 | 641 | 641 | 641 | 641
RHL1502 | 1 | 1 | 1 | 1 | 1 | 1
STL2200 | 98 | 98 | 98 | 98 | 98 | 98
STL2300 | 473 | 480 | 480 | 480 | 480 | 480
STL3501 | 2521 | 2530 | 2530 | 2530 | 2530 | 2530
STL3101 | 2312 | 2316 | 2316 | 2316 | 2316 | 2316
TPZ1202 | 713 | 727 | 727 | 727 | 727 | 727
Total | 48925 | 49165 | 49165 | 49165 | 49165 | 49165 | 0 | 0 | 0 | 0 | 0 | 0

## Performance Chart
Reliability Indices: System-Wide by Month |  |  |  |  | 5
Report Date: |  | 2025-02-03
First Interruption: |  | 2025-01-01 07:05
Last Interruption: |  | 2025-01-31 19:53
TMED = 96.33 (2025) SAIDI/day (min)
Month | Incidents | CI | CMI | SAIFI | TARGET | SAIDI | TARGET
5 | 24 | 2798 | 711115.8 | 0.05691 | 0.050292 | 14.4639 | 8.5368
|  |  | YTD ACTUAL | 0.38409 |  | 58.7953
|  |  | YTD TARGET | 0.60392 |  | 91.1832

## Email Image
SAIFI
[15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Total
[15 empty] | 0.051853 | 0.043588 | 0.061537 | 0.073449 | 0.034242 | 0.062228 | 0.10444 | 0.069604 | 0.095035 | 0.035181 | 0.038291 | 0.055438 | 0.72489
SAIDI
[15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Total
[15 empty] | 6.7508 | 5.6961 | 8.3947 | 9.3057 | 5.3764 | 4.3199 | 14.1909 | 12.6283 | 13.9819 | 3.6857 | 5.5054 | 6.3371 | 96.1727
Corporate Goal
SAIFI
[13 empty] | 2024 |  | 0.73
Reliability Indices: System-Wide by Month |  |  |  |  | 5 |  |  | Metric | Annual Goal | Annual Projected | Projected % | Projected Annual Performance
[8 empty] | SAIDI | 288.5989 | 244.7211 | -15.2% | Pass
Report Date: |  | 2025-02-03 | [5 empty] | SAIFI | 1.801 | 1.4933 | -17.09% | Pass
First Interruption: |  | 2025-01-01 07:05
Last Interruption: |  | 2025-01-31 19:53
TMED = 96.33 (2025) SAIDI/day (min) | [7 empty] | Metric | Corporate Goal | Annual Projected | Projected % | Projected Annual Performance
[8 empty] | SAIFI | 0.73 | 1.4933 | 104.6% | Fail
Month | Incidents | CI | CMI | SAIFI | TARGET | SAIDI | TARGET
|  |  | Minutes | [5 empty] | * Need to update Corporate goal once it becomes available
5 | 24 | 2798 | 711115.8 | 0.05691 | 0.050292 | 14.4639 | 8.5368
|  |  | YTD ACTUAL | 0.38409 |  | 58.7953
|  |  | YTD TARGET | 0.60392 |  | 91.1832

## SAIDI-SAIFI (hidden)
SAIFI - TOTAL
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection | MON
2025 Results | 0.0035769 | 0.21448 | 0.032625 | 0.076498 | 0.05691 | 0.021967 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40606 | 1.4933 | Jan
2024 Results | 0.1144 | 0.2034 | 0.42211 | 0.097446 | 0.005763 | 0.053459 | 0.088792 | 0.050707 | 0.12568 | 0.074555 | 0.18809 | 0.040737 | 1.4651 |  | Jan
5 Year Average | 0.28932 | 0.078006 | 0.13287 | 0.053432 | 0.050292 | 0.10993 | 0.28343 | 0.13409 | 0.14853 | 0.15232 | 0.10515 | 0.26367 | 1.801 |  | Jan
Projection | 0.0035769 | 0.21448 | 0.032625 | 0.076498 | 0.05691 | 0.021967 | 0.28343 | 0.13409 | 0.14853 | 0.15232 | 0.10515 | 0.26367
YTD Projection | 0.0035769 | 0.21806 | 0.25068 | 0.32718 | 0.38409 | 0.40606 | 0.68949 | 0.82358 | 0.97212 | 1.1244 | 1.2296 | 1.4933
Year to date target | 0.28932 | 0.36733 | 0.5002 | 0.55363 | 0.60392 | 0.71385 | 0.99728 | 1.1314 | 1.2799 | 1.4322 | 1.5374 | 1.801
Year to date actual | 0.0035769 | 0.21806 | 0.25068 | 0.32718 | 0.38409 | 0.40606 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SAIFI - SALEM
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 0.034165 | 0.0098181 | 0.017501 | 0.0092489 | 0.01891 | 0.0013124 | 0.027692 | 0.029944 | 0.053414 | 0.017017 | 0.020342 | 0.020955 | 0.26032 | 0.26032 | Jan
2022 Results | 0.022308 | 0.0059026 | 0.024175 | 0.054818 | 0.0056208 | 0.042387 | 0.022363 | 0.03808 | 0.038183 | 0.0096169 | 0.0047586 | 0.0050024 | 0.27321 |  | Jan
5 Year Average | 0.023375 | 0.019458 | 0.081273 | 0.038559 | 0.020624 | 0.033596 | 0.038046 | 0.021718 | 0.067675 | 0.017118 | 0.023763 | 0.021761 | 0.40697 |  | Jan
Projection | 0.034165 | 0.0098181 | 0.017501 | 0.0092489 | 0.01891 | 0.0013124 | 0.027692 | 0.029944 | 0.053414 | 0.017017 | 0.020342 | 0.020955
Year to date | 0.023375 | 0.042832 | 0.12411 | 0.16266 | 0.18329 | 0.21688 | 0.25493 | 0.27665 | 0.34432 | 0.36144 | 0.3852 | 0.40697
SAIFI - LEBANON
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 0.02529 | 0.030879 | 0.00081349 | 0.012706 | 0.008441 | 0.0078961 | 0.049849 | 0.027845 | 0.05687 | 0.0046371 | 0.0045934 | 0.01063 | 0.24045 | 0.24045 | Jan
2022 Results | 0.017086 | 0.0032914 | 0.0039168 | 0.02848 | 0.010126 | 0.038231 | 0.015011 | 0.026387 | 0.010844 | 0.0068129 | 0.0058989 | 0.0027087 | 0.16879 |  | Jan
5 Year Average | 0.017823 | 0.0055855 | 0.018288 | 0.014925 | 0.013725 | 0.027363 | 0.036425 | 0.024954 | 0.0091535 | 0.01897 | 0.023117 | 0.012541 | 0.22287 |  | Jan
Projection | 0.02529 | 0.030879 | 0.00081349 | 0.012706 | 0.008441 | 0.0078961 | 0.049849 | 0.027845 | 0.05687 | 0.0046371 | 0.0045934 | 0.01063
Year to date | 0.017823 | 0.023409 | 0.041697 | 0.056622 | 0.070347 | 0.09771 | 0.13413 | 0.15909 | 0.16824 | 0.18721 | 0.21033 | 0.22287
SAIFI - CHARLESTOWN
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 0.022441 | 0.0018628 | 0.0026823 | 0.0021581 | 0.035262 | 0.027078 | 0.01063 | 0.019248 | 0.020692 | 0.044337 | 0.036113 | 0.0018811 | 0.22439 | 0.22439 | January
2022 Results | 0.0083463 | 0.036952 | 0.030225 | 0.0042622 | 0.0053802 | 0.010761 | 0.040787 | 0.0034817 | 0.0069881 | 0.0017087 | 0.0067979 | 0.0016602 | 0.15735 |  | January
5 Year Average | 0.0041477 | 0.011085 | 0.009347 | 0.019519 | 0.0091322 | 0.043026 | 0.033214 | 0.016199 | 0.02702 | 0.0036303 | 0.0059109 | 0.016472 | 0.1987 |  | January
Projection | 0.022441 | 0.0018628 | 0.0026823 | 0.0021581 | 0.035262 | 0.027078 | 0.01063 | 0.019248 | 0.020692 | 0.044337 | 0.036113 | 0.0018811
Year to date | 0.0041477 | 0.015233 | 0.02458 | 0.044099 | 0.053231 | 0.096257 | 0.12947 | 0.14567 | 0.17269 | 0.17632 | 0.18223 | 0.1987
SAIDI - TOTAL
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection | MON
2025 Results | 0.50043 | 33.0237 | 2.817 | 7.9904 | 14.4639 | 3.146 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9413 | 244.7211 | Jan
2024 Results | 6.1991 | 11.591 | 96.8843 | 13.195 | 1.2513 | 5.4391 | 14.506 | 9.1153 | 13.8214 | 3.6265 | 25.4649 | 6.4847 | 207.5786 |  | Jan
5 Year Average | 39.2428 | 10.2757 | 26.0437 | 7.0843 | 8.5368 | 14.6359 | 25.6993 | 12.663 | 15.1244 | 26.4007 | 25.0874 | 77.8051 | 288.5989 |  | Jan
Projection | 0.50043 | 33.0237 | 2.817 | 7.9904 | 14.4639 | 3.146 | 25.6993 | 12.663 | 15.1244 | 26.4007 | 25.0874 | 77.8051
YTD Projection | 0.50043 | 33.5241 | 36.3411 | 44.3315 | 58.7953 | 61.9413 | 87.6406 | 100.3036 | 115.428 | 141.8286 | 166.916 | 244.7211
Year to date target | 39.2428 | 49.5184 | 75.5621 | 82.6464 | 91.1832 | 105.8191 | 131.5184 | 144.1814 | 159.3057 | 185.7064 | 210.7938 | 288.5989
Year to date actual | 0.50043 | 33.5241 | 36.3411 | 44.3315 | 58.7953 | 61.9413 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SAIDI - SALEM
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 2.661 | 0.951 | 1.5879 | 0.74618 | 1.7634 | 0.18741 | 4.4192 | 2.0881 | 6.7453 | 2.1833 | 3.7073 | 1.0188 | 28.0588 | 28.0588 | Jan
2022 Results | 1.8169 | 0.99287 | 1.4532 | 6.1889 | 1.0209 | 1.3062 | 2.3261 | 4.5924 | 5.304 | 1.0398 | 0.88207 | 0.87739 | 27.8008 |  | Jan
5 Year Average | 2.3099 | 1.7898 | 6.7214 | 3.9112 | 2.0803 | 2.3332 | 4.3634 | 3.2787 | 6.1839 | 1.7781 | 2.3191 | 2.2826 | 39.3516 |  | Jan
Projection | 2.661 | 0.951 | 1.5879 | 0.74618 | 1.7634 | 0.18741 | 4.4192 | 2.0881 | 6.7453 | 2.1833 | 3.7073 | 1.0188
Year to date | 2.3099 | 4.0997 | 10.8211 | 14.7323 | 16.8127 | 19.1458 | 23.5092 | 26.7879 | 32.9718 | 34.7499 | 37.069 | 39.3516
SAIDI - LEBANON
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 1.3639 | 3.257 | 0.058307 | 2.8615 | 0.77315 | 0.88867 | 5.7446 | 3.6325 | 12.7916 | 0.56189 | 0.55562 | 1.6823 | 34.1709 | 34.1709 | Jan
2022 Results | 4.5903 | 0.74101 | 0.73216 | 4.9189 | 1.9242 | 2.7107 | 3.4838 | 2.5671 | 1.2871 | 0.65555 | 0.67655 | 0.36002 | 24.6476 |  | Jan
5 Year Average | 2.8051 | 0.52862 | 2.5263 | 2.2373 | 1.9414 | 2.4349 | 4.8613 | 2.8009 | 1.1584 | 2.6803 | 3.0906 | 0.93026 | 27.9953 |  | Jan
Projection | 1.3639 | 3.257 | 0.058307 | 2.8615 | 0.77315 | 0.88867 | 5.7446 | 3.6325 | 12.7916 | 0.56189 | 0.55562 | 1.6823
Year to date | 2.8051 | 3.3338 | 5.86 | 8.0973 | 10.0387 | 12.4737 | 17.3349 | 20.1358 | 21.2942 | 23.9745 | 27.0651 | 27.9953
SAIDI - CHARLESTOWN
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 3.0702 | 0.14751 | 0.20612 | 0.29176 | 9.1075 | 0.8482 | 1.9793 | 2.579 | 4.1072 | 4.3981 | 6.0037 | 0.16388 | 32.9024 | 32.9024 | Jan
2022 Results | 2.8787 | 9.7634 | 2.3363 | 0.8284 | 1.086 | 0.86879 | 9.5227 | 0.26991 | 0.943 | 0.13792 | 1.2207 | 0.36116 | 30.217 |  | Jan
5 Year Average | 0.97456 | 2.6537 | 1.6583 | 3.2661 | 4.1964 | 6.3287 | 6.6686 | 6.0444 | 6.9824 | 0.44575 | 1.521 | 2.8749 | 43.6146 |  | Jan
Projection | 3.0702 | 0.14751 | 0.20612 | 0.29176 | 9.1075 | 0.8482 | 1.9793 | 2.579 | 4.1072 | 4.3981 | 6.0037 | 0.16388
Year to date | 0.97456 | 3.6283 | 5.2865 | 8.5526 | 12.7489 | 19.0776 | 25.7462 | 31.7906 | 38.773 | 39.2188 | 40.7397 | 43.6146
EVENTS - TOTAL
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection | MON
2025 Results | 10 | 45 | 12 | 7 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 403.8 | Jan
2024 Results | 38 | 33 | 32 | 25 | 26 | 86 | 62 | 67 | 35 | 41 | 82 | 34 | 561 |  | Jan
5 Year Average | 42.2 | 30 | 38.8 | 35.2 | 35.2 | 60.2 | 73.8 | 53.2 | 49.8 | 34 | 47.2 | 31.8 | 531.4 |  | Jan
Projection | 10 | 45 | 12 | 7 | 24 | 16 | 73.8 | 53.2 | 49.8 | 34 | 47.2 | 31.8
Year to date target | 42.2 | 72.2 | 111 | 146.2 | 181.4 | 241.6 | 315.4 | 368.6 | 418.4 | 452.4 | 499.6 | 531.4
Year to date actual | 10 | 55 | 67 | 74 | 98 | 114 | 114 | 114 | 114 | 114 | 114 | 114
EVENTS - SALEM
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 30 | 21 | 13 | 10 | 9 | 13 | 30 | 18 | 18 | 8 | 11 | 8 | 189 | 189 | Jan
2022 Results | 12 | 14 | 6 | 22 | 14 | 9 | 17 | 31 | 18 | 14 | 11 | 4 | 172 |  | Jan
5 Year Average | 17.4 | 14.4 | 19.6 | 18.2 | 16.4 | 20.2 | 26.8 | 21.6 | 22 | 20.4 | 22.6 | 11.4 | 231 |  | Jan
Projection | 30 | 21 | 13 | 10 | 9 | 13 | 30 | 18 | 18 | 8 | 11 | 8
Year to date | 17.4 | 31.8 | 51.4 | 69.6 | 86 | 106.2 | 133 | 154.6 | 176.6 | 197 | 219.6 | 231
EVENTS - LEBANON
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 10 | 9 | 2 | 8 | 15 | 14 | 37 | 15 | 33 | 10 | 11 | 14 | 178 | 178 | Jan
2022 Results | 17 | 9 | 15 | 26 | 23 | 33 | 36 | 24 | 19 | 8 | 12 | 12 | 234 |  | Jan
5 Year Average | 12.6 | 10.4 | 14.8 | 18.4 | 21 | 24.2 | 29.8 | 24 | 20.6 | 18.2 | 26.6 | 13.6 | 234.2 |  | Jan
Projection | 10 | 9 | 2 | 8 | 15 | 14 | 37 | 15 | 33 | 10 | 11 | 14
Year to date | 12.6 | 23 | 37.8 | 56.2 | 77.2 | 101.4 | 131.2 | 155.2 | 175.8 | 194 | 220.6 | 234.2
EVENTS - CHARLESTOWN
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 27 | 9 | 10 | 6 | 11 | 16 | 14 | 12 | 15 | 5 | 7 | 5 | 137 | 137 | Jan
2022 Results | 13 | 15 | 12 | 13 | 14 | 16 | 13 | 17 | 9 | 6 | 17 | 9 | 154 |  | Jan
5 Year Average | 10.2 | 7.8 | 7 | 12.4 | 14.4 | 19.8 | 22.8 | 12.2 | 17.8 | 8.2 | 12.6 | 10.2 | 155.4 |  | Jan
Projection | 27 | 9 | 10 | 6 | 11 | 16 | 14 | 12 | 15 | 5 | 7 | 5
Year to date | 10.2 | 18 | 25 | 37.4 | 51.8 | 71.6 | 94.4 | 106.6 | 124.4 | 132.6 | 145.2 | 155.4
CUSTOMERS INTERRUPTED - TOTAL
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection | MON
2025 Results | 175 | 10545 | 1604 | 3761 | 2798 | 1080 | 0 | 0 | 0 | 0 | 0 | 0 | 19963 | 19963 | Jan
2024 Results | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Jan
5 Year Average | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Jan
Projection | 175 | 10545 | 1604 | 3761 | 2798 | 1080 | 0 | 0 | 0 | 0 | 0 | 0
Year to date target | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CUSTOMERS INTERRUPTED - SALEM
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 1559 | 448 | 796 | 420 | 858 | 60 | 1266 | 1369 | 2442 | 778 | 930 | 958 | 11884 | 11884 | Jan
2022 Results | 1021 | 269 | 1111 | 2508 | 257 | 1938 | 1022 | 1739 | 1743 | 439 | 217 | 229 | 12493 |  | Jan
5 Year Average | 1046.6 | 871.6 | 3644.2 | 1740.4 | 925.4 | 1513.6 | 1714.4 | 985.2 | 3070.8 | 774.4 | 1072.6 | 986.8 | 18346 |  | Jan
Projection | 1559 | 448 | 796 | 420 | 858 | 60 | 1266 | 1369 | 2442 | 778 | 930 | 958
Year to date | 1046.6 | 1918.2 | 5562.4 | 7302.8 | 8228.2 | 9741.8 | 11456.2 | 12441.4 | 15512.2 | 16286.6 | 17359.2 | 18346
CUSTOMERS INTERRUPTED - LEBANON
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 1154 | 1409 | 37 | 577 | 383 | 361 | 2279 | 1273 | 2600 | 212 | 210 | 486 | 10981 | 10981 | Jan
2022 Results | 782 | 150 | 180 | 1303 | 463 | 1748 | 686 | 1205 | 495 | 311 | 269 | 124 | 7716 |  | Jan
5 Year Average | 799.6 | 250.8 | 822 | 674.6 | 614 | 1231 | 1638.8 | 1131.4 | 416 | 855.6 | 1040.6 | 568 | 10042.4 |  | Jan
Projection | 1154 | 1409 | 37 | 577 | 383 | 361 | 2279 | 1273 | 2600 | 212 | 210 | 486
Year to date | 799.6 | 1050.4 | 1872.4 | 2547 | 3161 | 4392 | 6030.8 | 7162.2 | 7578.2 | 8433.8 | 9474.4 | 10042.4
CUSTOMERS INTERRUPTED - CHARLESTOWN
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2022 Projection | MON
2023 Results | 1024 | 85 | 122 | 98 | 1600 | 1238 | 486 | 880 | 946 | 2027 | 1651 | 86 | 10243 | 10243 | Jan
2022 Results | 382 | 1684 | 1389 | 195 | 246 | 492 | 1864 | 159 | 319 | 78 | 310 | 76 | 7194 |  | Jan
5 Year Average | 188.4 | 502.6 | 426.4 | 875 | 408.6 | 1916.4 | 1497 | 734.2 | 1223 | 163.6 | 267.4 | 750.6 | 8953.2 |  | Jan
Projection | 1024 | 85 | 122 | 98 | 1600 | 1238 | 486 | 880 | 946 | 2027 | 1651 | 86
Year to date | 188.4 | 691 | 1117.4 | 1992.4 | 2401 | 4317.4 | 5814.4 | 6548.6 | 7771.6 | 7935.2 | 8202.6 | 8953.2
CUSTOMERS MINUTES INTERRUPTED - TOTAL
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | 2025 Projection
2025 Results | 24483.6 | 1623609.6 | 138495.6 | 392847.6 | 711115.8 | 154674 | 0 | 0 | 0 | 0 | 0 | 0 | 3045226.2 | 3045226.2
2024 Results | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 Year Average | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Projection | 24483.6 | 1623609.6 | 138495.6 | 392847.6 | 711115.8 | 154674 | 0 | 0 | 0 | 0 | 0 | 0
Year to date target | 0 | 1650772.6 | 1790934 | 2186747 | 2902272.4 | 3064418.2 | 3072215.6 | 3080378.4 | 3090319 | 3100444.8 | 3110565.8 | 3120355.6
CUSTOMERS MINUTES INTERRUPTED - TOTAL Apr: PUC Regulatory Criteria Only | [12 empty] | SAIDI | SAIFI | SAIDI | SAIFI | SAIDI | SAIDI | SAIFI | SAIFI
Exclusions | Period Type | Year | Period Value | ACTUAL SAIFI | ACTUAL SAIDI | TARGET SAIFI | TARGET SAIDI | 12Mo SAIFI | 12Mo SAIFI | 12Mo SAIFI | 12Mo SAIFI |  | Exclusions | Period Type | Year | Period Value | ACTUAL SAIFI | ACTUAL SAIDI | TARGET SAIFI | TARGET SAIDI | MTD SAIFI | MTD SAIDI | ACTUAL EVENTS | ACTUAL CI | ACTUAL CMI | YTD Actual | YTD Actual | YTD Target | YTD Target | YTD Actual + Projected | YTD Projected | YTD Actual + Projected | YTD Projected | Exclusions | Period Type | Year | Period Value | % ACHIEVED | TARGET | Exclusions | Period Type | Year | Year | Period Value | % ACHIEVED | TARGET | CAIDI MONTHLY CALCULATION
PUC CRITERIA | Quarter | 2016 | 1 | 0.73991 | 25.812 | 0.171 | 17.56 | ending Q1 | ending Q2 | ending Q3 | ending Q4 |  | PUC CRITERIA | Monthly | 2017 | 1 | 0.103 | 9.018 | 0.037276 | 4.6606 | [13 empty] | COMPANY GOAL | Quarter | 2017 | 1 | 2.48 | 3.75 | COMPANY GOAL | Monthly | 2017 | April | #REF! | #REF! | 100% | Division | MONTH | YEAR | INTERRUPTIONS | SAIFI | SAIDI | CAIDI
PUC CRITERIA | Quarter |  | 2 | 0.15667 | 27.702 | 0.426 | 39.53 | 1.0077 |  |  |  |  | PUC CRITERIA | Monthly |  | 2 | 0.0415 | 10.052 | 0.037339 | 3.9917 | [13 empty] | COMPANY GOAL | Quarter |  | 2 | 3.75 | 3.75 | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100% | Bellows Falls | #REF! | 2019 | #REF! | #REF! | #REF! | #REF!
PUC CRITERIA | Quarter |  | 3 | 0.26518 | 43.044 | 0.421 | 45.13 |  | 1.1996 |  |  |  | PUC CRITERIA | Monthly |  | 3 | 0.138 | 15.605 | 0.13216 | 9.9897 | [13 empty] | COMPANY GOAL | Quarter |  | 3 | 3.75 | 3.75 | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100% | Lebanon |  |  | #REF! | #REF! | #REF! | #REF!
PUC CRITERIA | Quarter |  | 4 | 0.30338 | 21.581 | 0.308 | 28.8 |  |  | 1.0915 |  |  | PUC CRITERIA | Monthly |  | 4 | 0.1285 | 24.8149 | 0.10214 | 12.1901 | [13 empty] | COMPANY GOAL | Quarter |  | 4 | 2.9 | 3.75 | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100% | Salem |  |  | #REF! | #REF! | #REF! | #REF!
PUC CRITERIA | Quarter | 2017 | 1 | 0.2825 | 34.675 | 0.20677 | 18.642 |  |  |  | 0.90824 |  | PUC CRITERIA | Monthly |  | 5 | 0.097 | 14.5744 | 0.12033 | 9.4552 | [13 empty] | COMPANY GOAL | Quarter | 2018 | 1 |  | 3.75 | COMPANY GOAL | Monthly | 2017 | May | #REF! | #REF! | 100% | System Total |  |  | #REF! | #REF! | #REF! | #REF!
PUC CRITERIA | Quarter |  | 2 | 0.34851 | 52.8803 | 0.41508 | 38.8833 | 0.7789 |  |  |  |  | PUC CRITERIA | Monthly |  | 6 | 0.12301 | 13.491 | 0.19262 | 17.2379 | [13 empty] | COMPANY GOAL | Quarter |  | 2 |  | 3.75 | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
PUC CRITERIA | Quarter |  | 3 | 0.1571 | 18.1705 | 0.45408 | 47.0762 |  | 0.65202 |  |  |  | PUC CRITERIA | Monthly |  | 7 | 0.0632 | 8.9375 | 0.16184 | 21.2563 | [13 empty] | COMPANY GOAL | Quarter |  | 3 |  | 3.75 | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
PUC CRITERIA | Quarter |  | 4 | 0.12013 | 12.028 | 0.27779 | 26.1284 |  |  | 0.6663 |  |  | PUC CRITERIA | Monthly |  | 8 | 0.0629 | 5.633 | 0.20382 | 15.443 | [13 empty] | COMPANY GOAL | Quarter |  | 4 |  | 3.75 | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100% | CAIDI MONTHLY CALCULATION
PUC CRITERIA | Quarter | 2018 | 1 | 0.15315 | 9.8976 | 0.24327 | 24.0449 |  |  |  | 0.73714 |  | PUC CRITERIA | Monthly |  | 9 | 0.031 | 3.6 | 0.088419 | 10.3769 | [13 empty] | COMPANY GOAL | Quarter | 2019 | 1 |  | 3.75 | COMPANY GOAL | Monthly | 2017 | June | #REF! | #REF! | 100% | Division | MONTH | YEAR | INTERRUPTIONS | SAIFI | SAIDI | CAIDI
PUC CRITERIA | Quarter |  | 2 | 0.22163 | 54.2819 | 0.34081 | 38.6199 | 0.7736 |  |  |  |  | PUC CRITERIA | Monthly |  | 10 | 0.022 | 2.353 | 0.1348 | 10.277 | [13 empty] | COMPANY GOAL | Quarter |  | 2 |  | 3.75 | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100% | Bellows Falls | Jan - Aprl | 2020 | 137 | 0.22439 | 32.9024 | 146.6325
PUC CRITERIA | Quarter |  | 3 | 0.17139 | 26.9811 | 0.38161 | 41.1069 |  | 0.77639 |  |  |  | PUC CRITERIA | Monthly |  | 11 | 0.067507 | 4.9509 | 0.050173 | 5.3403 | [13 empty] | COMPANY GOAL | Quarter |  | 3 |  | 3.75 | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100% | Lebanon |  |  | 178 | 0.24045 | 34.1709 | 142.1123
PUC CRITERIA | Quarter |  | 4 | 0.19097 | 30.624 | 0.22981 | 22.4934 |  |  | 0.68966 |  |  | PUC CRITERIA | Monthly |  | 12 | 0.030623 | 4.7241 | 0.092822 | 10.511 | [13 empty] | COMPANY GOAL | Quarter |  | 4 |  | 3.75 | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100% | Salem |  |  | 189 | 0.26032 | 28.0588 | 107.7861
PUC CRITERIA | Quarter | 2019 | 1 | 0.18962 | 20.5491 | 0.2319 | 22.6527 |  |  |  | 0.60931 |  | PUC CRITERIA | Monthly | 2018 | 1 | 0.045462 | 3.3367 | 0.055796 | 6.2182 | [19 empty] | COMPANY GOAL | Monthly | 2017 | July | #REF! | #REF! | 100% | System Total |  |  | 504 | 0.40606 | 61.9413 | 152.543
PUC CRITERIA | Quarter |  | 2 | 0.22442 | 30.9034 | 0.33514 | 44.5423 | 0.67037 |  |  |  |  | PUC CRITERIA | Monthly |  | 2 | 0.0027134 | 0.47003 | 0.041648 | 5.354 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
PUC CRITERIA | Quarter |  | 3 | 0.084657 | 10.2903 | 0.28925 | 32.7867 |  | 0.60132 |  |  |  | PUC CRITERIA | Monthly |  | 3 | 0.10498 | 6.0908 | 0.14582 | 12.4727 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
PUC CRITERIA | Quarter |  | 4 | 0.11061 | 8.9197 | 0.158 | 18.1842 |  |  | 0.51667 |  |  | PUC CRITERIA | Monthly |  | 4 | 0.018878 | 3.9988 | 0.091852 | 13.0486 | [19 empty] | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100%
PUC CRITERIA | Quarter | 2020 | 1 | 0.25068 | 36.3411 | 0.5002 | 75.5621 |  |  |  | 0.40606 |  | PUC CRITERIA | Monthly |  | 5 | 0.10536 | 25.3019 | 0.075739 | 9.1833 | [19 empty] | COMPANY GOAL | Monthly | 2017 | August | #REF! | #REF! | 100%
PUC CRITERIA | Quarter |  | 2 | 0.15537 | 25.6003 | 0.21365 | 30.2569 | 0.15537 |  |  |  |  | PUC CRITERIA | Monthly |  | 6 | 0.0974 | 24.9812 | 0.17322 | 16.3881 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
PUC CRITERIA | Quarter |  | 3 | 0 | 0 | 0.56606 | 53.4866 |  | 0 |  |  |  | PUC CRITERIA | Monthly |  | 7 | 0.079443 | 15.9367 | 0.15648 | 19.8958 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
PUC CRITERIA | Quarter |  | 4 | 0 | 0 | 0.52114 | 129.2932 |  |  | 0 |  |  | PUC CRITERIA | Monthly |  | 8 | 0.032343 | 4.7415 | 0.13841 | 11.1416 | [19 empty] | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Nov: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 9 | 0.0596 | 6.3029 | 0.086716 | 10.0695 | [19 empty] | COMPANY GOAL | Monthly | 2017 | September | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Aug: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 10 | 0.0625 | 12.6664 | 0.09927 | 8.3116 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Sep: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 11 | 0.12076 | 16.5167 | 0.061588 | 6.222 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Oct: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 12 | 0.0077097 | 1.4409 | 0.068947 | 7.9598 | [19 empty] | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Nov: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly | 2019 | 1 | 0.080552 | 11.2478 | 0.050889 | 5.2578 | [19 empty] | COMPANY GOAL | Monthly | 2017 | October | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Aug: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 2 | 0.086282 | 7.5457 | 0.034191 | 5.072 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Sep: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 3 | 0.022785 | 1.7556 | 0.14682 | 12.3229 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Oct: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 4 | 0.1107 | 21.5907 | 0.091628 | 13.6844 | [19 empty] | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Nov: 0; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 5 | 0.027686 | 4.6093 | 0.07881 | 13.5777 | [19 empty] | COMPANY GOAL | Monthly | 2017 | November | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 6 | 0.086036 | 4.7034 | 0.1647 | 17.2803 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 7 | 0.02888 | 3.3744 | 0.09974 | 14.1327 | [19 empty] | COMPANY GOAL | Monthly |  |  | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 8 | 0.036597 | 5.5178 | 0.10488 | 9.6639 | [19 empty] | COMPANY GOAL | Monthly |  |  | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 9 | 0.019179 | 1.3981 | 0.084636 | 8.9901 | [21 empty] | 2018 | January | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 10 | 0.014184 | 1.5465 | 0.05977 | 7.3928 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 11 | 0.012359 | 2.383 | 0.063739 | 6.7894 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 12 | 0.084065 | 4.9903 | 0.034489 | 4.002 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly | 2021 | 1 | 0.042527 | 5.1286 | 0.055 | 5.826 | [21 empty] | 2018 | February | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 2 | 0.0081656 | 0.86527 | 0.034 | 4.54 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 3 | 0.10787 | 18.1105 | 0.094 | 11.441 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 4 | 0.053959 | 4.5986 | 0.081 | 11.894 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 5 | 0.044315 | 4.868 | 0.057 | 10.168 | [21 empty] | 2018 | March | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 6 | 0.044293 | 4.0192 | 0.081 | 10.64 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 7 | 0.12493 | 16.9952 | 0.1 | 13.731 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 8 | 0.073224 | 28.0084 | 0.059 | 11.462 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 9 | 0.16488 | 18.4031 | 0.048 | 7.491 | [21 empty] | 2018 | April | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 10 | 0.056697 | 5.3812 | 0.039 | 4.883 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 11 | 0.029677 | 3.9085 | 0.06 | 7.14 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 12 | 0.09993 | 17.5916 | 0.054 | 6.666 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly | 2022 | 1 | 0.04774 | 9.286 | 0.054822 | 5.8259 | [21 empty] | 2018 | May | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 2 | 0.046146 | 11.4973 | 0.034015 | 4.5402 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 3 | 0.058317 | 4.5217 | 0.094209 | 11.4409 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 4 | 0.087561 | 11.9362 | 0.0805 | 11.8941 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 5 | 0.021127 | 4.0311 | 0.057131 | 10.1677 | [21 empty] | 2018 | June | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 6 | 0.091378 | 4.8857 | 0.080663 | 10.6397 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 7 | 0.07816 | 15.3326 | 0.099627 | 13.7307 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 8 | 0.067948 | 7.4295 | 0.0588 | 11.4624 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 9 | 0.056014 | 7.5342 | 0.048289 | 7.4909 | [21 empty] | 2018 | July | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 10 | 0.018138 | 1.8333 | 0.038624 | 4.8825 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 11 | 0.017455 | 2.7793 | 0.059603 | 7.1405 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 12 | 0.0093713 | 1.5986 | 0.054465 | 6.6659 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly | 2023 | 1 | 0.083978 | 7.5446 | 0.044102 | 5.9038 | [21 empty] | 2018 | August | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 2 | 0.04256 | 4.3555 | 0.035619 | 4.919 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 3 | 0.020997 | 1.8523 | 0.078333 | 9.2424 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 4 | 0.024113 | 3.8995 | 0.072402 | 9.3255 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 5 | 0.062613 | 11.6441 | 0.042791 | 8.108 | [21 empty] | 2018 | September | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 6 | 0.036287 | 1.9243 | 0.074459 | 8.9354 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 7 | 0.088171 | 12.1432 | 0.1027 | 15.0192 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 8 | 0.077037 | 8.2995 | 0.060666 | 11.9781 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 9 | 0.13098 | 23.644 | 0.080773 | 10.5182 | [21 empty] | 2018 | October | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 10 | 0.065992 | 7.1432 | 0.037833 | 4.7904 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 11 | 0.061048 | 10.2666 | 0.050281 | 6.7597 | [23 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 12 | 0.033466 | 2.865 | 0.050287 | 6.0523 | [23 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly | 2025 | 1 | 0.0035769 | 0.50043 | 0.28932 | 39.2428 |  |  | 10 | 175 | 24483.6 | 0.50043 | 0.0035769 | 39.2428 | 0.28932 | 0.50043 | #N/A | 0.0035769 | #N/A | [8 empty] | 2018 | November | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 2 | 0.21448 | 33.0237 | 0.078006 | 10.2757 |  |  | 45 | 10545 | 1623609.6 | 33.5241 | 0.21806 | 49.5184 | 0.36733 | 33.5241 | #N/A | 0.21806 | #N/A | [10 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 3 | 0.032625 | 2.817 | 0.13287 | 26.0437 |  |  | 12 | 1604 | 138495.6 | 36.3411 | 0.25068 | 75.5621 | 0.5002 | 36.3411 | #N/A | 0.25068 | #N/A | [10 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 4 | 0.076498 | 7.9904 | 0.053432 | 7.0843 |  |  | 7 | 3761 | 392847.6 | 44.3315 | 0.32718 | 82.6464 | 0.55363 | 44.3315 | #N/A | 0.32718 | #N/A | [10 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 5 | 0.05691 | 14.4639 | 0.050292 | 8.5368 |  |  | 24 | 2798 | 711115.8 | 58.7953 | 0.38409 | 91.1832 | 0.60392 | 58.7953 | #N/A | 0.38409 | #N/A | [8 empty] | 2018 | December | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 6 | 0.021967 | 3.146 | 0.10993 | 14.6359 |  |  | 16 | 1080 | 154674 | 61.9413 | 0.40606 | 105.8191 | 0.71385 | 61.9413 | #N/A | 0.40606 | #N/A | [10 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 7 | 0 | 0 | 0.28343 | 25.6993 |  |  | 0 | 0 | 0 | #N/A | #N/A | 131.5184 | 0.99728 | 87.6406 | 87.6406 | 0.68949 | 0.68949 | [10 empty] | #REF! | #REF! | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 8 | 0 | 0 | 0.13409 | 12.663 |  |  | 0 | 0 | 0 | #N/A | #N/A | 144.1814 | 1.1314 | 100.3036 | 100.3036 | 0.82358 | 0.82358 | [10 empty] | Final Score | 100% | 100%
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 9 | 0 | 0 | 0.14853 | 15.1244 |  |  | 0 | 0 | 0 | #N/A | #N/A | 159.3057 | 1.2799 | 115.428 | 115.428 | 0.97212 | 0.97212
CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 10 | 0 | 0 | 0.15232 | 26.4007 |  |  | 0 | 0 | 0 | #N/A | #N/A | 185.7064 | 1.4322 | 141.8286 | 141.8286 | 1.1244 | 1.1244
CUSTOMERS MINUTES INTERRUPTED - TOTAL Nov: SAIDI; CUSTOMERS MINUTES INTERRUPTED - TOTAL Dec: SAIFI; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 11 | 0 | 0 | 0.10515 | 25.0874 |  |  | 0 | 0 | 0 | #N/A | #N/A | 210.7938 | 1.5374 | 166.916 | 166.916 | 1.2296 | 1.2296
CUSTOMERS MINUTES INTERRUPTED - TOTAL Nov: 4.3555; CUSTOMERS MINUTES INTERRUPTED - TOTAL Dec: 0.04256; CUSTOMERS MINUTES INTERRUPTED - TOTAL Total: PUC CRITERIA | Monthly |  | 12 | 0 | 0 | 0.26367 | 77.8051 |  |  | 0 | 0 | 0 | #N/A | #N/A | 288.5989 | 1.801 | 244.7211 | 244.7211 | 1.4933 | 1.4933
[16 empty] | Total | 0.40606 | 61.9413 | 1.801 | 288.5989

## Tmed check (hidden)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025
SAIDI All | 151.74 | 165.28 | 201.6 | 237.02 | 365.58
SAIFI All | 1.183 | 1.043 | 1.14 | 1.151 | 1.544
CAIDI All | 128.24 | 158.45 | 176.9 | 205.89 | 236.81
SAIDI IEEE | 102.39 | 108.7 | 84.29 | 99.21 | 92.23
SAIFI IEEE | 1.001 | 0.854 | 0.635 | 0.772 | 0.822
CAIDI IEEE | 102.25 | 127.22 | 132.71 | 128.48 | 112.25
alpha | -2.8188 | -2.8104 | -2.8472 | -2.8403 | -2.8681 | -2.8402
beta | 2.2023 | 2.2161 | 2.2078 | 2.2 | 2.1815 | 2.2174
e(a+2.5b) = Tmed | 14.6853 | 15.3311 | 14.4742 | 14.2928 | 13.272 | 14.929
Number of MEDs | 2 | 2 | 3 | 2 | 5
Number of Zero Days | 115 | 104 | 126 | 117 | 136

## WPF (hidden)
E2_Exclusion | (Multiple Items) | E2_Exclusion | (Multiple Items)
Year | (Multiple Items) | Year | (Multiple Items)
Sum of FEEDER SAIDI | Column Labels | Sum of FEEDER SAIFI | Column Labels
| Grand Total |  | Grand Total |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Grand Total |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Grand Total
Row Labels |  | Row Labels |  | Row Labels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row Labels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total |  | Grand Total |  | Grand Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Grand Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E2_Exclusion | (Multiple Items) | E2_Exclusion | (Multiple Items)
Year | (Multiple Items) | Year | (Multiple Items) | 5YR AVE. SAIDI | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Grand Total | 5YR AVE. SAIFI | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Grand Total
|  |  |  | Row Labels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Row Labels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sum of FEEDER SAIDI | Column Labels | Sum of FEEDER SAIFI | Column Labels | Grand Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Grand Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grand Total |  | Grand Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Row Labels |  | Row Labels |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total |  | Grand Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Dec: mean | 0 | [12 empty] | mean | 0
[5 empty] | Dec: variance | 0 | [12 empty] | variance | 0
[5 empty] | Dec: std dev | 0 | [12 empty] | std dev | 0
[17 empty] | 0 | [13 empty] | 0
[60 empty] | 2015 |  | 2016 |  | 2017 |  | 2018 |  | 2019 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  |  | 2015 |  | 2016 |  | 2017 |  | 2018 |  | 2019 |  | 2021 |  | 2022 |  | 2023 |  | 2024
[19 empty] | Row Labels | Sum of FEEDER SAIDI | Sum of FEEDER SAIFI | [5 empty] | Row Labels | Sum of FEEDER SAIDI | Sum of FEEDER SAIFI | CKAIDI RANK | CKAIFI RANK | RANK | 2014 WORST CKAIDI | 2015 WORST CKAIDI | 2016 WORST CKAIDI | 2017 WORST CKAIDI | 2018 WORST CKAIDI | 2019 WORST CKAIDI | 2020 WORST CKAIDI | 2021 WORST CKAIDI | 2022 WORST CKAIDI | 2023 WORST CKAIDI | 2024 WORST CKAIDI | 2014 WORST CKAIFI | 2015 WORST CKAIFI | 2016 WORST CKAIFI | 2017 WORST CKAIFI | 2018 WORST CKAIFI | 2020 WORST CKAIFI | 2021 WORST CKAIFI | 2022 WORST CKAIFI | 2023 WORST CKAIFI | 2024 WORST CKAIFI | RANK | WORST CKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | Feeder | cKAIDI | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI | Feeder | cKAIFI
[19 empty] | 2024 | [7 empty] | 2024 - 5 year average |  |  |  |  | 1 | 41-7L1 | 42-14L2 | 41-7L2 | 41-15H1 | 43-12L2 | 41-7L1 | 43-12L2 | 43-12L2 | 43-12L2 | 43-12L2 | 12L1 | 41-7L1 | 42-18L1 | 41-7L2 | 42-14L3 | 43-12L2 | 43-12L2 | 43-12L2 | 43-12L2 | 43-12L2 | 12L1 | 1 | 41-7L1 | 42-14L2 | 274.7507 | 41-7L2 | 436.2259 | 41-15H1 | 742.1902 | 43-12L2 | 639.2192 | 41-7L1 | 257.1161 | 43-12L2 | 415.8638 | 43-12L2 | 415.8638 | 43-12L2 | 415.8638 | 43-12L2 | 415.8638 | 42-18L1 | 41-7L1 | 12L1 | 1052.1002 | 3.4418 | 42-14L3 | 3.2252 | 43-12L2 | 1.6014 | 41-7L1 | 1.5861 | 43-12L2 | 1.9083 | 43-12L2 | 1.9083 | 43-12L2 | 1.9083 | 43-12L2 | 1.9083 | 43-12L2 | 2.0558 | 12L1 | 10.288
[19 empty] | Row Labels | 0 | 0 | 1 | 1 |  |  |  | Row Labels | 0 | 0 | 1 | 1 | 2 | 42-9L1 | 42-9L2 | 43-12L2 | 41-6L4 | 43-12L1 | 43-12L1 | 41-7L1 | 43-12L1 | 43-12L1 | 43-12L1 | 11L1 | 42-14L2 | 42-14L2 | 41-1L1 | 41-39L2 | 41-7L2 | 41-7L1 | 42-14L2 | 41-7L1 | 41-16L1 | 7L1 | 2 | 42-9L1 | 42-9L2 | 140.6002 | 43-12L2 | 303.8196 | 41-6L4 | 352.5906 | 43-12L1 | 548.5981 | 43-12L1 | 227.4918 | 43-12L1 | 379.8864 | 43-12L1 | 379.8864 | 43-12L1 | 379.8864 | 43-12L1 | 379.8864 | 42-14L2 | 42-14L2 | 11L1 | 320.9872 | 3.3812 | 41-39L2 | 2.7463 | 41-7L2 | 1.5834 | 42-14L3 | 1.5573 | 42-14L2 | 1.361 | 42-14L2 | 1.361 | 42-14L2 | 1.361 | 42-14L2 | 1.361 | 41-16L1 | 1.6133 | 7L1 | 6.7848
[19 empty] | Grand Total | 0 | 0 | 1 | 1 |  |  |  | Grand Total | 0 | 0 | 1 | 1 | 3 | 42-14L2 | 42-18L1 | 42-13L2 | 41-39L2 | 41-16L1 | 43-12L2 | 43-12L1 | 41-16L1 | 41-16L1 | 41-16L1 | 12L2 | 41-16L1 | 42-9L2 | 42-13L2 | 41-6L4 | 42-14L4 | 42-14L2 | 42-14L3 | 42-14L2 | 43-12L1 | 11L1 | 3 | 42-14L2 | 42-18L1 | 139.0139 | 42-13L2 | 296.5234 | 41-39L2 | 307.1248 | 41-16L1 | 451.7511 | 43-12L2 | 205.8723 | 41-16L1 | 181.0913 | 41-16L1 | 181.0913 | 41-16L1 | 181.0913 | 41-16L1 | 181.0913 | 42-9L2 | 41-16L1 | 12L2 | 254.27 | 3.363 | 41-6L4 | 2.2617 | 42-14L4 | 1.5156 | 41-1L1 | 1.3684 | 42-14L3 | 1.3434 | 42-14L3 | 1.3434 | 42-14L3 | 1.3434 | 42-14L3 | 1.3434 | 43-12L1 | 1.3402 | 11L1 | 2.9556
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | 4 | 42-9L3 | 41-16L1 | 41-1L1 | 41-6L3 | 42-9L3 | 42-9L3 | 41-6L3 | 41-39L2 | 41-7L1 | 41-7L1 | 14L2 | 42-13L2 | 41-16L1 | 43-12L2 | 41-6L2 | 41-6L3 | 42-9L2 | 43-12L1 | 43-40L3 | 41-7L1 | 14L2 | 4 | 42-9L3 | 41-16L1 | 137.0012 | 41-1L1 | 262.5718 | 41-6L3 | 298.0885 | 42-9L3 | 240.5452 | 42-9L3 | 146.8118 | 41-39L2 | 171.0417 | 41-39L2 | 171.0417 | 41-39L2 | 171.0417 | 41-39L2 | 171.0417 | 41-16L1 | 42-13L2 | 14L2 | 203.3924 | 2.9745 | 41-6L2 | 2.1716 | 41-6L3 | 1.3868 | 41-39L2 | 1.2814 | 43-12L1 | 1.3134 | 43-12L1 | 1.3134 | 43-12L1 | 1.3134 | 43-12L1 | 1.3134 | 41-7L1 | 1.2802 | 14L2 | 2.5525
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | 5 | 42-9L2 | 41-6L3 | 41-6L4 | 41-6L2 | 41-39L2 | 42-14L3 | 42-14L4 | 41-7L1 | 41-39L2 | 41-39L2 | 7L1 | 43-12L1 | 41-6L3 | 42-18L4 | 43-12L2 | 42-14L2 | 42-13L1 | 41-7L1 | 43-12L1 | 42-14L2 | 18L2 | 5 | 42-9L2 | 41-6L3 | 136.9593 | 41-6L4 | 228.6577 | 41-6L2 | 269.4658 | 41-39L2 | 235.803 | 42-14L3 | 136.9047 | 41-7L1 | 170.1328 | 41-7L1 | 170.1328 | 41-7L1 | 170.1328 | 41-7L1 | 170.1328 | 41-6L3 | 43-12L1 | 7L1 | 161.514 | 2.5296 | 43-12L2 | 2.1053 | 42-14L2 | 1.3596 | 43-12L1 | 1.1843 | 41-7L1 | 1.2879 | 41-7L1 | 1.2879 | 41-7L1 | 1.2879 | 41-7L1 | 1.2879 | 42-14L2 | 1.1128 | 18L2 | 1.6226
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | POOR PERFORMING FEEDER MEANS ANY DISTRIBUTION CIRCUIT THAT POSSESSES A CKAIDI OR CKAIFI VALUE FOR A REPORTING YEAR THAT IS AMONG THE HIGHEST FIVE OF ALL OF LIBERTY'S FEEDERS.
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | PROBLEM CIRCUIT MEANS ANY FEEDER THAT POSSESSES A CKAIDI OR CKAIFI VALUE FOR A REPORTING YEAR THAT IS AMONG THE HIGHEST FIVE OF ALL OF LIBERTY'S FEEDERS CKAIDI AND CKAIFI VALUES FOR ANY TWO CONSECUTIVE YEARS
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | CHRONIC CIRCUIT MEANS ANY FEEDER THAT POSSESSES A CKAIDI OR CKAIFI VALUE FOR A REPORTING YEAR THAT IS AMONG THE HIGHEST FIVE OF ALL OF LIBERTY'S FEEDERS CKAIDI AND CKAIFI VALUES FOR ANY THREE CONSECUTIVE YEARS
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | CKAIDI/CKAIFI ANNUAL BENCHMARKS VALUES TO BE SET AS THE AVERAGE OF THE CKAIDI AND CKAIFI VALUES FOR ALL LIBERTY FEEDERS IN THAT GIVEN YEAR PLUS TWO STANDARD DEVIATIONS.
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | THE AVERAGE CKAIDI AND CKAIFI VALUES OF CHRONIC FEEDERS TO BE COMPARED TO THE ANNUAL CKAIDI AND CKAIFI BENCHMARKS
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | 2021 NOTES
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | FOR CKAIDI, 12L1 AND 12L2 ARE WORST PERFORMERS FOR THE LAST 4 YEARS, 7L1 IS A CHRONIC FEEDER (3 YEARS IN A ROW)
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | FOR CKAIFI, 12L2 IS A WORST PERFORMING FEEDER FOR THE PAST 4 YEARS AND 14L2 AND 7L1 ARE PROBLEM FEEDERS (2 YEARS IN A ROW)
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1 | ** NEED TO VERIFY AND CORRECT WPF FOR PREVIOUS YEARS. USE ACTUAL FEEDER RESULTS FOR THE YEAR FOR RANKING AND NOT 5 YEAR AVERAGE. 5 YEAR AVERAGE IS USED TO DETERMINE THESHOLD. THRESHOLD FOR 2025 IS 290 MINUTES AND SAIFI OF 2
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[19 empty] | 0 | 0 | 0 | 1 | 1 |  |  |  | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1
[27 empty] | 0 | 0 | 0 | 1 | 1

## Pivot
IEEE MED without Planned Outage
E2_Exclusion | (Multiple Items)
Cause | (All)
SubCause | (All)
Year | (All)
Row Labels | Count of ID | Sum of CI | Sum of CMI | Average of Cust Serv | Sum of SAIFI | Sum of SAIDI
Jan | 12 | 209 | 25206 | 48925 | 0.0042718 | 0.5152
Feb | 50 | 12580 | 1677480.6 | 49165 | 0.25587 | 34.1194
Mar | 19 | 1802 | 155072.4 | 49165 | 0.036652 | 3.1541
Apr | 8 | 3773 | 398470.2 | 49165 | 0.076742 | 8.1048
May | 28 | 3490 | 745242.6 | 49165 | 0.070985 | 15.158
Jun | 39 | 27355 | 3756968.4 | 49165 | 0.55639 | 76.4155
Grand Total | 156 | 49209 | 6758440.2 | 49146.5385 | 1.0009 | 137.467