## Discovery Log
**This Discovery Log reflects Data Requests completed as of 05:00PM each Wednesday
SDG&E 2026 WMP Discovery Log
Question Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Response | Requestor | Date Rec'd | Final Due Date | Date Sent | Link | Number of Atchs | NDA Required | WMP Section | Category | Sub Category
1 | OEIS | 2 | OEIS-2 | 1 | OEIS-2.1 | Regarding Vegetation Management Inspections: On page 209 of its 2026-2028 Base WMP, SDG&E lists the Area Inspected for all Vegetation Management Inspection programs as “HFTD.” On pages 57-60 of its 2026-2028 Base WMP, SDG&E describes evaluating high fire areas outside of the HFTD and explains why SDG&E has not proposed adding these areas to the HFTD. SDG&E states that some of these areas are of a lower priority for grid-hardening initiatives but does not mention other WMP activities. a. Explain SDG&E’s decision-making process for excluding the WUI and coastal canyons from SDG&E’s 2026-2028 WMP Vegetation Management Inspection Programs and associated targets. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). b. Does SDG&E plan to perform Detailed Inspection (WMP.494) in the WUI and coastal canyons during the 2026-2028 WMP cycle? i. If not, provide the estimated risk reduction achieved by performing Detailed Inspections to: 1. The WUI 2. Coastal canyons c. Does SDG&E plan to perform Off-Cycle Patrols (WMP.508) in the WUI and coastal canyons during the 2026-2028 WMP cycle? i. If not, provide the estimated risk reduction achieved by adding Off-Cycle Patrols to: 1. The WUI 2. Coastal canyons | a. The targets presented for Vegetation Management inspections are limited to the HFTD to remain consistent with the approach taken in SDG&E’s Test Year 2024 GRC Decision.1 SDG&E clarifies that Detailed Inspection (WMP.494) activities and Off-Cycle patrols, such as targeted species patrols, are performed outside the HFTD throughout its entire service territory, but these inspections are no longer in scope for WMP. b. Yes, as described above, SDG&E plans to perform Detailed Inspection in the WUI and coastal canyons during the 2026-2028 WMP cycle. b.i. N/A c. Yes, as described above, SDG&E plans to perform Off-Cycle Patrols in the WUI and coastal canyons during the 2026-2028 WMP cycle. c.i. N/A | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5 | 5 Risk Methodology and Assessment | 5.6.2 | 5.6.2 Model Controls, Design, and Review
2 | OEIS | 2 | OEIS-2 | 2 | OEIS-2.2 | Regarding Integrated Vegetation Management Activities: In SDG&E's 2023-2025 Base WMP (pages 284-286), sections 8.2.3.6 High-Risk Species and 8.2.3.7 Fire-Resilient Right-of-Ways SDG&E includes four integrated vegetation management activities: Right Tree, Right Place (WMP.1325), Community Tree Rebate Program (WMP.1326), Land Services Vegetation Abatement (WMP.1327) and Fire Coordination Fuels Reduction MOU & Grant (WMP.1328). On page 215 of its 2026-2028 Base WMP, SDG&E lists Fuels Management (WMP.497) as its only IVM activity. SDG&E states that “because of the relative lack of vegetation density along its major transmission corridors, SDG&E does not engage in these traditional integrated vegetation management activities.” a. Does SDG&E plan to perform all or some of the activities that its 2023-2025 Base WMP describes for WMP.1325, WMP.1326, WMP.1327, and WMP.1328 during the 2026-2028 WMP cycle? i. If yes, describe which activities SDG&E plans to perform and which it will discontinue during the 2026-2028 Base WMP cycle. ii. For each of these activities its plans to perform during the 2026-2028 WMP cycle, explain why SDG&E excludes these activities from its 2026-2028 Base WMP. iii. For each of these activities it will not perform during the 2026-2028 WMP cycle, explain SDG&E’s decision-making process for discontinuing the activity. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). | a. SDG&E does plan to perform some of the activities described for WMP.1325, WMP.1326, WMP.1327, and WMP.1328 during its 2023-2025 Base WMP during the 2026-2028 Base WMP cycle. i. SDG&E plans to perform Right Tree, Right Place; Land Services Vegetation Management Abatement; and Fire Coordination Fuels Reduction & Grant activities during the 2026-2028 Base WMP. SDG&E plans to discontinue the Community Tree Rebate Program during the 2026-2026 Base WMP cycle. ii. As stated in its 2023-2025 Base WMP, SDG&E’s Right Tree, Right Place (WMP.1325) is part of its tree removal program (see page 277). SDG&E primarily engages customers with the option to remove incompatible trees during the inspection activity or during the tree pruning activity. In its 2026-2028 Base WMP Guidelines, Energy Safety created two new initiatives for Vegetation Management: IVM and Pruning and Right Place within IVM, and instead to reserve IVM solely for the activity of Fuels Management. SDG&E will continue to engage customers on the option to remove incompatible trees using the concept of Right Tree, Right Place during the inspection and tree pruning and removal activities during the 2026-2028 Base WMP. Land Services Vegetation Management Abatement, and Fire Coordination Fuels Reduction & Grant are not categorized as activities within IVM in the 2026-2026 Base WMP. However, both activities are described under the new WMP section titled Partnerships 9.8 and will continue during the 2026-2028 Base WMP. iii. SDG&E’s Community Tree Rebate Program (WMP.1326) has been discontinued in 2025 to promote customer affordability and reflect SDG&E’s authorized revenue requirements. SDG&E also believes it has substantively met the overall goal of the program to engage those customers eligible to participate in the program. The cessation of the program does not negatively impact the company’s risk mitigation measures as the program is not primarily aimed at risk reduction. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 9 | 9 Vegetation Management and Inspections | 9.7.1 | 9.7.1 Overview
3 | OEIS | 2 | OEIS-2 | 3 | OEIS-2.3 | Regarding Vegetation Management Quality Assurance and Quality Control: On page 224 of its 2026-2028 WMP, SDG&E combines Detailed Inspections (WMP.494), Prune and Removal (Clearance)(WMP.501), and Pole Clearing (WMP.512) into a single quality check activity/row in Table 9-6: Vegetation Management QA and QC Activity Targets. a. Complete the table below with a separate row for each activity containing activityspecific quantitative values for population/sample unit, annual population size, annual sample size, confidence level, and margin of error (MOE). i. In the “Annual Sample Size” column, list the number of individual sample units that make up the sample rather than listing a percentage of the population. | SDG&E performs QA/QC throughout the calendar year following the completion of the scheduled vegetation management activities (Detailed Inspections; Pruning and Removal; Pole Clearing). SDG&E strives to complete a 15% audit for each activity. The sample population for each audit is dependent on the number of units completed for each respective activity, thus calculated based on historical averages. Note that Prune and Removal is dependent on the Detailed Inspection, therefore, an accurate method to calculate annual population size or sample size is not available. SDG&E includes in the table provided above an approximate value of the Annual Sample Size for each of the three activities. Initiative/Activity Being Audited Population / Sample Unit Annual Population Size Annual Sample Size Confide nce Level Margin of Error (MOE) Detailed Inspections (WMP.494) Number of Trees Inspected 255,000 38,250 99% 3% Initiative/Activity Being Audited Population / Sample Unit Annual Population Size Annual Sample Size Confide nce Level Margin of Error (MOE) Prune and Removal (Clearance) (WMP.501) Number of Trees Pruned/Remo ved N/A N/A N/A N/A Pole Clearing (WMP.512) Number of Poles Brushed 22,000 3,300 99% 3% | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 9 | 9 Vegetation Management and Inspections | OEIS Table 9-6 | Vegetation Management QA and QC Activity Targets
4 | OEIS | 2 | OEIS-2 | 4 | OEIS-2.4 | Regarding Larger QA/QC Sample Sizes for Enhanced Vegetation Management Activities in the HFTD: On page 289 of its 2023-2025 WMP, SDG&E indicates that "a higher sampling percentage is used for some enhanced vegetation management activities in the HFTD, including a 100 percent post-trim audit of all completed trim and removal work generated from the off-cycle patrol (WMP.508) activities… Additionally, audits are performed on 100 percent of all work completed on tree trim “Memo” work orders." SDG&E’s audit of a higher percentage of “some enhanced vegetation management activities in the HFTD” is absent from its 2026-2028 Base WMP. a. Does SDG&E plan to perform a post-trim audit of completed trim and removal work generated from off-cycle patrol activities during the 2026-2028 WMP cycle? i. If so, explain why SDG&E excludes this audit from its 2026-2028 Base WMP. ii. If not, explain SDG&E’s decision-making process for discontinuing this audit. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). b. Does SDG&E plan to audit work completed on tree trim “Memo” work orders during the 2026-2028 WMP cycle? i. If so, explain why SDG&E excludes this audit from its 2026-2028 Base WMP. ii. If not, explain SDG&E’s decision-making process for discontinuing this audit. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). | a. Yes, SDG&E plans to perform post-trim audits of completed pruning and removal work generated from off-cycle patrol activities during the 2026-2028 WMP cycle. i. For the 2026-2028 Base WMP, SDG&E will integrate a post-trim audit of work generated from the off-cycle patrols into its standard auditing processes. Doing so will align overall audit practices and provide procedural consistency. Upon further evaluation of its audit scope, SDG&E believes that utilizing a representative sample population to perform its audits is effective in determining contractor compliance and work quality. SDG&E may elect to conduct a higher percentage of audits on work generated from the off cycle HFTD patrol than the standard 15%. However, this may be the same VMA, and the most efficient and effective utilization of contractor resources. ii. Please see the response to i. above. b. Yes, SDG&E plans to audit work completed on tree trim “Memo” work orders during the 2026-2028 WMP cycle. i. For the 2026-2028 Base WMP, SDG&E will integrate a post-trim audit of work generated from the off-cycle patrols into its standard auditing processes. Doing so will align overall audit practices and provide procedural consistency. Upon further evaluation of its audit scope, SDG&E believes that utilizing a representative sample population to perform its audits is effective in determining contractor compliance and work quality. SDG&E may elect to conduct a higher percentage of audits on work generated from the off cycle HFTD patrol than the standard 15%. However, this may be influenced by other vegetation management activities concurrently in process within the same VMA, and the most efficient and effective utilization of contractor resources. ii. Please see the response to i. above. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | N/A | Absence Enhanced vegetation management activities in the HFTD in 2026-2028 Base WMP | N/A | N/A
5 | OEIS | 2 | OEIS-2 | 5 | OEIS-2.5 | Regarding Benchmarking Performance of Vegetation Management Operations Across Multiple VMAs: On page 290 of its 2023-2025 Base WMP, SDG&E states it “is considering the development of compliance-based audits as a measure of system status and reliability. Such audits may be performed across multiple VMAs and create benchmarking for the performance of vegetation management operations. The anticipated timeline to implement compliance-based audits is 2 to 3 years.” a. Provide an update on the progress of using audits to benchmark the performance of vegetation management operations across multiple VMAs. b. Provide a summary of findings, lessons learned, and improvements to vegetation operations that SDG&E has implemented as a result of considering compliance-based audits as a measure of system status and reliability. | a. SDG&E continues to explore the possibility of expanding its audit program to include a compliance-based component for the activity of tree pruning. In its current state the posttrim audit program is scaled and scoped to occur at the individual Vegetation Management Area (VMA) level focusing on contractor performance and work quality. A compliancebased audit would target instances of non-compliant tree clearances and incorporate rootcause analysis as part of the procedure. Compliance-based audits could be conducted throughout the year exclusive of the schedule for routine tree trimming activities. b. Developing a compliance audit would require enhancements to SDG&E’s current work management system (Cityworks) including the design, development, and testing of integrating multiple VMAs into the system’s randomization tool, creation of new electronic forms to support data entry, and back-end reporting to track audit results, among others. Other considerations in expanding the audit scope include the required increase in contractor staffing resources and additional costs for the program. SDG&E has also considered employing the use of remote sensing technology as a potential tool in a compliance-driven audit. For example, LiDAR could be used on a broad scale and as a mechanism in accurately identifying non-compliant trees. Cost and frequency of LiDAR capture and the timeliness of data processing are additional considerations for viability. SDG&E will continue to explore this issue and currently continues to anticipate a timeline of 2 to 3 years to complete its evaluation of possible implementation of a compliance-based audits in its vegetation management program. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 2023-2025 Base WMP | Benchmarking Performance of Vegetation Management Operations Across | N/A | N/A
6 | OEIS | 2 | OEIS-2 | 6 | OEIS-2.6 | Regarding Past Due Work Order Quantities and Constraint Types: On page 228 of its 2026-2028 Base WMP, SDG&E lists 9,916 past due work orders in Tables 9-7 and 9-8. On page 292 of its 2023-2025 Base WMP, SDG&E lists 981 past due work orders. a. Describe the factors that have primarily led to an approximately 900 percent increase in past due work orders from the time of 2023-2025 Base WMP submission to the time of the 2026-2028 Base WMP submission. | The difference in the number of past due work orders provided in the 2023-2025 Base WMP compared with the numbers of past due work orders provided in the 2026-2028 Base WMP can be attributed to the differences in the methodology of deriving the data, and not the result of a substantial increase in past due work orders. In its 2026-2028 Base WMP, SDG&E reported the total number of open work orders, not past due work orders. SDG&E makes the correction in tables provided below. SDG&E will additionally provide these corrected tables in its forthcoming errata. OEIS Table 9-7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier HFTD Area 0-30 days 31-90 days 91-180 days 181+ days HFTD Tier 2 75 225 5 1 HFTD Tier 3 300 29 1 0 OEIS Table 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels Priority Level 0-30 days 31-90 days 91-180 days 181+ days High Priority 40 12 2 0 Low Priority 335 242 4 1 | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 9.12.3 | 9.12.3 Trends . | Table 9-7 | Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier HTFD Area 0-30 Days 31-90 Days 91-180
7 | OEIS | 2 | OEIS-2 | 7 | OEIS-2.7 | Regarding Financial Attribute Components: On page 29 of SDG&E’s 2026-2028 Base WMP, SDG&E discusses two general components of the financial attribute: societal damage and utility repair costs. a. Provide information on the magnitude of these two components in comparison to one another, including the following individual portions for each component: i. Physical damage, lost wages, and relocation costs for societal damage ii. Labor and materials for utility repair b. Provide an example of how total cost is calculated showing the various societal damage and utility repair monetization components. | In accordance with CPUC Decision (D.) 22-12-027, SDG&E is shifting from its previous reliance on the Multi-Attribute Value Framework (MAVF) to a Cost-Benefit Analysis (CBA) approach. Section 5.1 introduces this new methodology, offering an initial outline that will be further developed in SDG&E’s upcoming 2025 Risk Assessment Mitigation Phase (RAMP) filing. This section serves to bridge the Wildfire Mitigation Plan (WMP) with broader enterprise risk management efforts. This section introduces the financial attribute and explains how it can be used to capture two general categories of costs: societal damage (e.g., including physical damages, lost wages, and relocation costs) and utility repair costs (e.g., labor, materials). This approach is intended to reflect how financial impacts may be consistently calculated and applied across SDG&E. Specifically for this WMP, SDG&E’s wildfire consequence model estimates societal damages by assigning monetary values to projected structure losses and acres burned, based on outputs from Technosylva wildfire simulations. SDG&E’s wildfire consequence model does not estimate utility repair costs, because of the difficulty of estimating the number of assets impacted and the severity of the impact and because the high-level dollar estimates for utility repairs would be relatively insignificant when compared to the more substantial costs associated with structural losses and acres burned. In the PSPS Risk Model, the financial impact of a de-energization event is estimated based on several key factors: the assumed duration of the PSPS event, the number and types of customers affected, and cost proxies informed by the federal per diem rates for lodging, meals, and incidentals applicable to San Diego County. a) Not applicable – see explanation above. b) The following is an example of how SDG&E quantifies wildfire risk. This example was originally shared during the Risk Modeling Working Group session held on March 26, 2025. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5.2 | 5.2 Risk Analysis Framework | N/A | N/A
8 | OEIS | 2 | OEIS-2 | 8 | OEIS-2.8 | Regarding Climate Change Projections: On page 30 of SDG&E’s 2026-2028 Base WMP, SDG&E notes that a system-wide climate adaptation vulnerability assessment (CAVA) is being analyzed to examine mid- and endcentury climate change projections. SDG&E notes that it plans to update its risk modeling methodology when new data becomes available. a. Provide a timeline for the completion of this examination and its implementation into the risk modeling methodology. This timeline must include: i. Discreet steps within the timeline for implementation ii. Expected completion dates for each step, down to quarter granularity (i.e., Q4 2025) | SDG&E is actively exploring multiple methodologies to model future wildfire risk, with particular emphasis on projecting potential increases in acres burned relative to historical baseline. A key objective is to align these projections as closely as possible with the latest climate science, specifically the CMIP6 (Coupled Model Intercomparison Project Phase 6) simulation outputs, which will inform California’s upcoming Fifth Climate Change Assessment, scheduled for release in 2026. Currently, the most recent wildfire projection dataset available on Cal-Adapt is based on earlier CMIP5 simulations, specifically the work by Westerling (2018). However, this dataset is now considered outdated. In response, the UC Merced research team is actively working to update wildfire projections using CMIP6 data. These updated projections will provide a more accurate and forward-looking foundation for assessing wildfire risk under future climate scenarios and will be incorporated into the 2026 Assessment. Once the CMIP6-based wildfire projections are made available, SDG&E will review, validate, and incorporate the data into its risk modeling framework, pending approval by its internal subject matter experts (SMEs). | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5.2 | 5.2 Risk Analysis Framework | N/A | N/A
9 | OEIS | 2 | OEIS-2 | 9 | OEIS-2.9 | Regarding Consequence Models: On page 36 of SDG&E’s 2026-2028 Base WMP, Figure 5-6 depicts the differences between the WiNGS-Ops and WiNGS-Planning consequence models. a. Provide a description of any additional differences between the two models not captured within Figure 5-6. b. Explain why egress is only included as a part of the WiNGS-Planning model. c. Explain how the egress factor is calculated. | a) Figure 5-6 depicts all major model source and process step differences between the consequence models across both the operational and planning versions of the WiNGS model. Additional differences of each model exist and are summarized within the model technical documentation. For more details, please refer to Appendix B: Supporting Documentation For Risk Methodology and Assessment, Section 2: Summary Documentation. The notable difference related to the consequence models not captured directly in Figure 5-6 between the two versions of the WiNGS is the risk unit utilized. WiNGS-Planning uses a cost-benefit ratio (CBR) framework unit as described in the up-coming filing for the 2025 Risk Assessment and Mitigation Phase (RAMP) report for its risk score, whereas WiNGS-Ops will upgrade to leverage the same framework in the future and currently uses a weighted risk score approach using a risk spend efficient (RSE) framework as described by SDGE’s 2021 Risk Assessment and Mitigation Phase (RAMP) report. WiNGS-Ops is expected to align with the cost-benefit framework by end of Q3-2025. b) As the WiNGS-Ops model is focused on PSPS and emergency decision making, SDG&E does not incorporate egress modeling into its WINGS-Ops model, based on the operational roles and responsibilities defined during wildfire and PSPS de-energization events. This decision reflects both the utility’s limited authority in evacuation matters and the established structure of emergency response coordination within California. Primarily, SDG&E does not intend to use egress model outputs during PSPS activations or active wildfire incidents. This is because utility personnel do not have the authority to initiate or request evacuations, nor are they part of the formal decision-making process regarding evacuation orders. These decisions are made by the Incident Commander, who operates within a Unified Command structure composed of first responder agencies, most notably fire and law enforcement authorities. Utilities, including SDG&E, typically serve as cooperators in these incidents, providing support with utility knowledge but not directing public safety actions. The decision to evacuate is multifaceted and considers a range of dynamic factors such as fire behavior, weather conditions, terrain, and population density. Utilities are generally not a significant factor in this analysis. Law enforcement agencies are the primary leads for executing evacuations, and their decisions are informed by real-time situational awareness and public safety priorities. While SDG&E recognizes the value of egress modeling as a tool for understanding potential evacuation challenges, it does not currently view it as a best practice for utility-led operational platforms. Instead, SDG&E focuses on strengthening partnerships with fire and law enforcement agencies to enhance coordination and public safety. This includes participating in joint training exercises, leveraging shared communication platforms, and supporting public messaging during emergencies. By maintaining clear boundaries around its operational role and deferring evacuation decisions to the appropriate authorities, SDG&E ensures that its wildfire and PSPS response efforts remain aligned with the broader emergency management framework in California. c) The Egress model is intended to be included in the wildfire consequence model (safety attribute) of WiNGS-Planning. The egress model is a relative ranking model that helps in identifying areas in SDG&E service territory that are most vulnerable to evacuation constraints during a wildfire event. SDG&E completed the first iteration of the model by the end of 2022 and adoption in WiNGS-Planning was completed in 2023. At any given location, the model simulates different (stochastic) potential scenarios of movements of people considering road capacity constraints during the evacuation process. Each scenario is triggered by a simulated match-drop ignition (spread, direction, duration), predefined evacuation routes, and evacuation travel times. Random scenarios are created based on a set of Subject Matter Expert assumptions, 8-hour unsuppressed wildfire simulations created by Technosylva, historical weather conditions, population information, and road-street networks and geometries. SDG&E’s egress model is predominantly influenced by these two papers: - Grajdura, Sarah, Sachraa Borjigin, and Deb Niemeier. "Fast-moving dire wildfire evacuation simulation." Transportation research part D: transport and environment 104 (2022): 103190. - Kim, Sangho, Betsy George, and Shashi Shekhar. "Evacuation route planning: scalable heuristics." Proceedings of the 15th annual ACM international symposium on Advances in geographic information systems. 2007. SDG&E emphasizes that this model is for mitigation planning and scoping only and is not intended to be used during an evacuation planning or during an active real-evacuation event. This model is not used to create a set of strategies or define best practices to ensure the safe and efficient evacuation of communities in the path of an advancing wildfire. In the event of a wildfire evacuation event, SDG&E will work closely with local authorities, emergency responders, law enforcement, and other stakeholders to assist with evacuation efforts based on known real time conditions and available information. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf | 0 | No | 5.5.2 | 5.5.2 Top Risk-Contributing Circuits/Segments/Spans | Figure 5-6 | WiNGS-Planning and Ops Calculation Schematic
10 | OEIS | 2 | OEIS-2 | 10 | OEIS-2.10 | Regarding Attributes for Wildfire Consequence: a. On page 38 of SDG&E’s 2026-2028 Base WMP, SDG&E Table 5-4 provides estimates used to calculate various risk components. i. For the safety component, SDG&E states that it is using an assumption of a 0.00617 factor to estimate the total number of equivalent fatalities per structure destroyed. Provide documentation justifying the basis for this assumption, including the analysis conducted on the CAL FIRE data set as discussed within SDG&E Table 5-4. ii. For the financial component, SDG&E states that it is using an assumption of $2,350 per acre burned for suppression and restoration cost. Provide documentation justifying the basis for this assumption, including any analysis performed. b. On pages 39 and 40 of SDG&E’s 2026-2028 Base WMP, the financial attributes for PSPS and PEDS consequences are discussed in SDG&E Table 5-5 and SDG&E Table 5-6, respectively. Provide additional discussion and justification on the motivation and basis for the differences in financial attribute assumptions used for PSPS and PEDS.Include any supporting documentation and analysis that led to the financial attribute assumptions used. | a) i) Refer to “SDGE_Wildfire_Fatality_Structures_ratios_2025_05_12.xlsx” for details on how this assumption is calculated a) ii) Refer to “SDGE_Cost_per_acre_2025_05_09.xlsx” for details on how this assumption is calculated b) The differences in how financial estimates are calculated for PSPS and PEDS events are based on the assumption that PSPS events typically involve longer restoration times, with an assumed duration of approximately 24 hours per event. Due to this extended duration, a per-diem cost estimation method is applied. This approach accounts for additional customer impacts, including the need for meals and lodging during the de-energization period. In contrast, PEDS events are typically shorter in duration and occur with less predictability, often being characterized as “random” in nature. Due to their limited duration, it is assumed that these events are less likely to necessitate extended accommodations or meal provisions. As a result, the financial estimates for PEDS events do not include per-diem costs for meals and lodging, leading to lower overall cost assumptions. To estimate the financial impact of a PEDS event, SDG&E applies a simplified cost assumption equivalent to 10% of the expected reliability impact. This percentage is derived from a high-level approximation of post-patrol costs associated with overhead line inspections conducted during elevated or extreme fire weather conditions. While this estimate is not event-specific, SDG&E subject matter experts consider it as a reasonable proxy to reflect the variability in financial impacts across different PEDS events. This approach acknowledges that not all PEDS events incur the same level of cost. With this approach, the financial estimate is intended to scale proportionally with the simulated PEDS event duration and the number of customers affected by a given PEDS outage, providing a consistent approach for estimating financial impact in the absence of detailed event-level data. | Zhenying Shao | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-02_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE_Cost_per_acre_2025_05_09_0.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE_Wildfire_Fatality_Structures_ratios_2025_05_12_0.xlsx | 2 | No | 5.2.2.2.1 | Wildfire CoRE | Table 5-4 | Attributes for Wildfire Consequence
11 | MGRA | 3 | MGRA-3 | 1 | MGRA-3.1 | With regard to Figure 1-1: 2026-2028 Expected risk Reduction: a. Does the risk reduction indicated include SDG&E's convex risk weighting function/attitude? b. If the answer to a) is yes, please provide an equivalent figure using a neutral risk attitude. | a) No. Figure 1-1 does not include SDG&E’s risk aversion. b) Not applicable | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 1.2 | 1.2 Objectives | Figure 1-1 | 2026-2028 Expected Risk Reduction
12 | MGRA | 3 | MGRA-3 | 2 | MGRA-3.2 | With regard to “Wind Gust Weight” described on p. 13, how is this weighting determined and the driver normalized? | To distinguish and quantify the wildfire risk for a given risk driver that occurred at locations prone to wildfire conditions, the 99th percentile wind gust for a given location is compared to the 25th, 50th, 75th of the overall 99th percentile wind guests for all HFTD locations. The weight (WRwind) of the wind component for a risk event is calculated using 20, 21, 22, and 23, respectively. The frequency of the ignition events (Rfreq) is aggregated by the FPI level, wind gust category, and consequence category. For drivers that do not have CPUC reportable ignitions, this multiply factor (n_ignition_events_normalized) would be 1. For example, if 5 animal-contact caused ignitions occurred at locations where the 99th wind gust falls between 25th to 50th percentiles of the overall 99th wind gust (WRwind = 21) and where the 50th consequence is above the overall 50th percentile threshold, the Rfreq is calculated as follow: Rfreq = n_ignition_events_normalized × WRwind × Wcon × Σn Rcon The ignition events are normalized using the min-max scaling normalization formula: | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 3.4 | 3.4 Prioritized List of Wildfire Risks and Risk Drivers . | N/A | N/A
13 | MGRA | 3 | MGRA-3 | 3 | MGRA-3.3 | Please provide technical documentation for the risk driver statistical analysis and testing mentioned on page 14: “Topographical and climatological risk factors, which include factors include FPI, temperature, humidity, wind gust, elevation, slope, and aspect associated with the location where risk events were observed, were evaluated. Test statistics method Mann Whitney Test was used to compare the sample mean of a risk driver to the sample mean of the other risk drivers. If the difference was statistically significant, this risk factor is noted in OEIS Table 3-1 as influential for a risk driver. These factors are evaluated based on the historical climatological data and current topographical characteristics of the locations associated with each risk driver.” | SDG&E objects to the request to the extent is seeks information that is publicly available and equally available to the requestor. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not have technical documentation regarding this Mann Whitney Test but abundant explanations can be found online. The goal is to test the statistical significance of a risk factor for a given risk driver. Risk events for each diver category are not normally distributed, which is the main reason Mann Whitney Test is used to run the statistical test instead of using T test. The data used for this test are processed in python, mannwhitneyu() function under “scipy.stats” library. The underlying data have risk factors mapped to individual risk event observations. The data field, FPI value, is spatially and temporally mapped to each observation; whereas other risk factors, such as temperature and slope, are mapped spatially to the asset where the risk events were observed. The data are sampled into two groups, a given risk driver and all other observations before running this test. The OEIS table 3-1 shows the result of the test for each risk driver category when compared with all the other risk drivers. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 3.4 | 3.4 Prioritized List of Wildfire Risks and Risk Drivers . | N/A | N/A
14 | MGRA | 3 | MGRA-3 | 4 | MGRA-3.4 | With regard to SDG&E Table 5-7, p. 42, please provide the justification and modeling that leads to the P100 percentile of a potential $211B loss in the SDG&E service area. | As illustrated in Table 5-7, Wildfire risk constitutes the majority of the Overall Utility Risk, significantly outweighing the contributions from PSPS and PEDS risks. Over the course of the 5 million simulated years, the most extreme wildfire scenario, resulting in an estimated cost of approximately $211 billion, was driven by two ignition events that coincidentally occurred under the same simulation seed ID. The table below shows how the maximum values are derived based on the Monte Carlo simulation: Ignition 1 Ignition 2 Total Sim Weather Conditions Date 11/12/2018 11/17/2014 --- Ignition ID 403589 1012407 --- Seed ID 11792465 11792465 --- Total Acres Burned 43,703 35,934 79,637 Total Structures Destroyed 6,029 4,042 10,071 Sim Max Wind Gust Conditions 62 55 --- SCADA Sect. Device 907-1562AE 909-451 --- Feeder ID 907 909 --- Wildfire Total Risk (with Risk Aversion) [M$] $136,729.33 $74,237.73 $210,967.06 Wildfire Total Risk (without Risk Aversion) [M$] $7,559.78 $4,989.72 $12,549.50 Wildfire Safety Risk (without Risk Aversion) [M$] $1,427.77 $863.42 $2,291.19 Wildfire Financial Risk (without Risk Aversion) [M$] $6,132.00 $4,126.24 $10,258.25 Wildfire Reliability Risk (without Risk Aversion) [M$] $0.01 $0.05 $0.06 | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 5.2.2.3 | 5.2.2.3 Risk | SDGE Table 5-7 | 5-7: Pre-Mitigation Wildfire, PSPS, PEDS, and Overall Utility Risk estimates for the Service Territory . 42
15 | MGRA | 3 | MGRA-3 | 5 | MGRA-3.5 | Please provide a list of the 125 worst fire weather days (p. 45) and associated wildfire hazard intensity data. | Please see attached spreadsheet titled “SDGE Response MGRA-2026-8- 03_Q5_SDGE_125_worst_fire_days_stats_2025_05_15.xlsx” for the list of 125 days and percentile values of acres burned and structure destroyed for each day. This is the data as referenced on page 45 of SDG&E’s 2026-2028 WMP. This list is currently under review by the Meteorology and Risk Analytics teams. Given the extreme fire weather conditions experienced within SDG&E’s service territory between November 2024 and January 2025, SDG&E is evaluating the inclusion of these recent dates in future analyses. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03_Q5_SDGE_125_worst_fire_days_stats_2025_05_15.xlsx | 1 | No | 5.2.3 | 5.2.3 Key Assumptions and Limitations . | N/A | N/A
16 | MGRA | 3 | MGRA-3 | 6 | MGRA-3.6 | With regard to OEIS Table 4-3, and corresponding Excel table (MGRA-3-9 b), please break out customers into Residential, Small C&I, and Medium/Large C&I. | SDG&E objects to the request to the extent it is unduly burdensome and calls on SDG&E to perform studies or analysis that do not currently exist. Subject to and without waving the foregoing objections, SDG&E responds as follows: Commercial and Industrial customers are split based on their kW demand. SDG&E does not have C&I broken down by small, medium or large. The documentation provided includes customer hours broken out into Residential and C&I. Please see the attached spreadsheet titled “SDGE Response MGRA-2026-8-03_Q06-OEIS-Table- 4-3.xlsx.” | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03_Q06-OEIS-Table-4-3.xlsx | 1 | No | OEIS Table 4-3 | 4-3: Frequently De-energized Circuits 23 | N/A | N/A
17 | MGRA | 3 | MGRA-3 | 7 | MGRA-3.7 | WiNGS-Planning still incorporate a decision tree that will default to underground if the Cost/benefit characteristics meet certain criteria, as was described in the SDG&E GRC? Or are all combinations evaluated as options prior to the decision tree? a. If the answer is yes decision tree is prior to CBR calculation does the CBR use SDG&E’s convex risk function/attitude for the decision tree? | SDG&E objects to the request to the extent it is argumentative and mischaracterizes SDG&E’s modeling functions. SDG&E further objects to the request to the extent it is vague and ambiguous, and fails to identify with specificity the information requested. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not default to undergrounding as the preferred mitigation strategy. For each feeder segment, SDG&E evaluates risk reduction and cost-benefit ratios for both Combined Covered Conductor and Strategic Undergrounding mitigation options. As stated in the 2026-2028 WMP filing, mitigations are selected by considering their Cost Benefit Ratio (CBR) estimates which encompass risk reduction estimates, as well as both upfront installation and lifecycle costs. Lifecycle costs are essential to making informed and cost-effective decisions in infrastructure investments. They encompass not only the initial investment in mitigation measures but also the ongoing costs of maintenance, operations, and potential upgrades. See section 6.1.3 of the 2026-2028 WMP filing for further details. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | N/A | WiNGS-Planning | N/A | N/A
18 | MGRA | 3 | MGRA-3 | 8 | MGRA-3.8 | SDG&E describes significant changes to the covered conductor management structure that are now ongoing (p. 98). Will covered conductor deployment continue unabated while SDG&E reorganizes the management process? | Yes, the covered conductor deployment is expected to continue unabated while SDG&E reorganizes the Project Management Office (PMO) services. There will be some overlap between the incumbent PMO service provider and the new PMO service provider to ensure a smooth transition. The new PMO service provider may also subcontract some of their services with the incumbent to ensure there are no disruptions in the program. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | 6.1.3.2 | 6.1.3.2 Activity Prioritization . | 6.1.3.2.3 | Resource Optimization
19 | MGRA | 3 | MGRA-3 | 9 | MGRA-3.9 | Please provide tabular data in Excel spreadsheet format for the following figures: a. OEIS Table 3-1: List of Risks and Risk Drivers to Prioritize b. OEIS Table 4-3: Frequently De-energized Circuits c. OEIS Table 6-1 and Appendix F, List of Prioritized Areas d. SDG&E Table 6-1 Potential Mitigation Activities for Risk Drivers e. OEIS Table 6-3 Risk Impact of Activities f. Appendix G refers to a dead web link. Please provide the data in Excel spreadsheet as well as fix the weblink. | For a-f all the requested tables are available on SDG&E’s website at https://www.sdge.com/2026- 2028-wildfire-mitigation-plan | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | OEIS Table 3-1 | 3-1: List of Risks and Risk Drivers to Prioritize 11 | N/A | N/A
20 | MGRA | 3 | MGRA-3 | 10 | MGRA-3.10 | Please provide GIS data in the form of shapefiles or geodatabases that support the following figures (if these have not already been provided). a. Figure 4-3: Frequently De-energized circuits, p. 22. | Please see the attached gdb titled, “SDGE_Frequently_De-energized_circuits.gdb.” | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE_Frequently_De-energized_circuits.gdb_.zip | 1 | No | Figure 4-3 | 4-3: Frequently De-energized Circuits . 22 | N/A | N/A
21 | MGRA | 3 | MGRA-3 | 11 | MGRA-3.11 | Is FPI historic geographic data available, if so is it available through a public interface and if not how difficult would it to be to produce? a. If SDG&E were asked to produce FPI estimates given a set of geographic points and date/time, how far back into history could SDG&E provide FPI data? | SDGE divides the service territory into 8 operational districts. The FPI is computed daily for each operational district using live fuel moisture values, dead fuel moisture values, grass NDVI values, dewpoint depression and sustained wind speed forecast. The output is not gridded, and each district receives an FPI value from 1-17. Historical values are archived in a spreadsheet and are not posted publicly. a. For operational FPI values, SDGE started keeping daily records of the data in April 2013 but there exists intermittent values as far back as late September 2012. Again, the FPI values are calculated per district and not for a set of otherwise specified geographic points. | Joseph Mitchell | 2025-05-12 | 2025-05-15 | 2025-05-15 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-03.pdf | 0 | No | N/A | FPI historic geographic data | N/A | N/A
22 | OEIS | 3 | OEIS-3 | 1 | OEIS-3.1 | Regarding Contractor Employees with Minimum Qualifications On pages 229 through 231 of its 2026-2028 Base WMP, SDG&E lists the worker titles, qualifications, and training associated with its vegetation management workforce. SDG&E indicates that for several positions (Pre-Inspector, Tree Trim General Foreperson/Supervisor, and Tree Trimmer), the total number of employees with each position is greater than the number of minimally qualified employees. This suggests that some employees holding the Pre-Inspector, Tree Trim General Foreperson/Supervisor, or Tree Trimmer title do not possess minimum qualifications. a. Are there employees with each of the above worker titles who do not hold the minimum qualifications for their position? i. If yes, list other factors associated with each worker title that contribute to a hiring decision for an employee who does not possess minimum qualifications. ii. If no, explain why there is a difference between the number of employees with minimum qualifications and the total number of employees. | After further investigation with its contractors, SDG&E has determined that it erred in its initial reporting of the number of contracted employees who possess minimum qualifications compared to the total number of employees. SDG&E can confirm that all contracted employee positions including Pre-Inspector, Tree Trim General Foreperson/Supervisor, and Tree Trimmer possess the minimum qualifications. The error was related to the number of employees who possess specific certifications, which are not a requirement of employment. SDG&E will update the number of contracted employees in Revision 1 of the 2026-2028 WMP. | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 0 | No | 9.13 | 9.13 Workforce Planning (WMP.506) | N/A | N/A
23 | OEIS | 3 | OEIS-3 | 2 | OEIS-3.2 | Regarding Fire Potential Index for Action Initiation On page 252 of its 2026-2028 Base WMP SDG&E states that, “The FPI reflects key variables such as the state of native grasses across the service territory (‘green-up’), fuels (ratio of DFM component to LFM component), and weather (sustained wind speed and dew point depression). Each of these variables is assigned to a numeric value. Those numeric values are summed up to generate a Fire Potential Index value from 0 to 17 that expresses the degree of fire threat expected for each of the seven days in the forecast. The numeric values are grouped as ‘Normal’, ‘Elevated’, or ‘Extreme’.” a. Provide the following information regarding the Fire Potential Index (FPI) breakpoints and how each is used in the initiation of PSPS events. i. A detailed description of the weather conditions associated with each level of the FPI breakpoint (i.e., Normal, Elevated, and Extreme). ii. The initiation criteria for PSPS events for FPI breakpoint (i.e., Normal, Elevated, and Extreme). b. Provide the following information regarding the FPI breakpoints and how they are used for actions taken in the field. i. A detailed description of actions taken in the field that are associated with each FPI breakpoint (i.e., Normal, Elevated, and Extreme). | a.i. Please reference the attached document titled “SDGE Response OEIS-P-WMP_2025-SDGE-03_Q2_Fire Potential Index (FPI).pdf.” Weather conditions are a function of dewpoint depression and sustained wind speeds. Since each break point is a function of dead fuel moisture, live fuel moisture, grass NDVI, dewpoint depression and sustained wind speeds, no single value of wind or dewpoint depression defines each breakpoint - they are defined by the combination of all variables and are based on a backcast against historical fires as shown in the figures below. a.ii. The FPI is a consideration for PSPS but not the only one. The following outlines the procedure for initializing a PSPS from a Meteorology perspective: 1. Has the National Weather Service (NWS) provided any indication in their forecast discussion, forecast products or social media communications that a Red Flag Warning or critical fire weather conditions may be possible during the forecast period? 2.Has the GACC in Riverside, CA given any indication in their forecast discussion/products or social media communications of a “High Risk Day” or any Santa Ana Wildfire Threat Index rating may be issued? 3. Does the SDG&E Fire Potential Index show that a combination of fuel dryness and Santa Ana winds may lead to the potential for large wildfire (FPI 14 or above)? 4. Do initial wind speed forecasts generated by SDG&E meteorology models (WRF and AI forecasting) indicate a reasonable probability of reaching alert speeds for any of the SDG&E weather stations? 5. Do the forecasted weather conditions warrant a convening of executive leadership to discuss the potential for PSPS Protocols? b.i. SDG&E has several procedures that outline company responsibilities and action required for each breakpoint. Electric Distribution Operations (EDO) has procedures during SDG&E fire conditions that outline the distribution operating restrictions and notifications required for overhead facilities during various operating condition levels, to include operating under NORMAL conditions (1-11), ELEVATED Conditions (12-14), and EXTREME Conditions (15-17).Electric Grid Operations at SDG&E has fire preparedness and transmission restrictions that outline the transmission operating restrictions and notifications required for overhead facilities during various operating condition levels, to include operating under NORMAL conditions (1-11), ELEVATED Conditions (12-14) , and EXTREME Conditions (15-17). SDG&E operations and maintenance has a wildland fire prevention plan that outlines the minimum wildland fire prevention standards for all system Operations & Maintenance work conducted in wildland areas of our service territory. The plan provides a wildland fire risk and mitigation matrix based on work activity within Fire Potential Index (FPI) or Project Activity Level (PAL) areas to set a level for minimum fire prevention and suppression tools. The Fire Potential Index (FPI) (1-17) is a comprehensive assessment of fire risk, used as a tool for making operation & maintenance decisions related to fire prevention. The tool converts environmental, statistical, and scientific data into an easily understood forecast of short-term fire threat. The 7-day forecast is used for planning purposes, while the daily FPI is used for work activities. The FPI is used to determine the fire potential for each day (Normal, Elevated, or Extreme). | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_Q2_Fire%20Potential%20Index%20%28FPI%29.pdf | 1 | No | 10.6 | 10.6 Fire Potential Index (WMP.450) | 10.6.1 | 10.6.1 Existing Calculation Approach and Use
24 | OEIS | 3 | OEIS-3 | 3 | OEIS-3.3 | Regarding SDG&E’s Response to SDGE-25U-01 In Appendix D, pages 1-2, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-25U-01. Calculating Risk Scores Using Maximum Consequence Values. a. In its response, SDG&E states that “Moving forward, the new risk event probability distribution outputs, along with statistical distribution metrics such as mean and various percentiles, will be used to inform future optimal mitigation prioritization decisions.” i. When does SDG&E intend to start using the new outputs? ii. If the new outputs have been implemented already, provide a detailed description of how the new risk event probability distributions impacted SDG&E’s risk model scores. This must include, at a minimum: (1) A list showing any shifts to risk ranking prioritizations. (2) Heatmaps of risk distributions across SDG&E’s territory showing changes in risk scores. b. In its response, SDG&E states that “the wildfire risk modeling approach will continue to be updated” and that “assumptions and inputs used in the models will be continuously reviewed and enhanced.” i. What frequency does SDG&E plan on updating its risk models? ii. What frequency does SDG&E plan on reviewing and enhancing assumptions and inputs? iii. Provide SDG&E’s timeline including concrete milestones and associated dates for future risk modeling updates. | a. i. SDG&E has begun adopting risk event probability distribution outputs from its WiNGS-Planning model as of Q1 2025 and first reported on them in the 2026-2028 WMP base filing. ii. The new risk event probability distributions, derived from the WiNGS-Planning model, have been implemented in alignment with the Cost-Benefit Ratio (CBR) framework outlined in SDG&E’s forthcoming 2025 Risk Assessment and Mitigation Phase (RAMP) filing. This represents a significant methodological shift from the Risk Spend Efficiency (RSE) framework used in the 2021 RAMP filing—as required by the CPUC. Under the new framework, risk is quantified in monetary terms, replacing the Multi-Attribute Value Framework (MAVF) previously used. The updated model outputs include comprehensive statistical distribution metrics—such as mean, P95, P99, and maximum values—providing a probabilistic view of risk events. This contrasts with the earlier approach, which relied on a single deterministic risk score per asset. Key impacts of this upgrade include: - The probabilistic modeling approach offers greater transparency into the range and likelihood of potential risk events, rather than a single-point estimate. - The use of trained predictive models to estimate ignition events introduces a more data-driven and forward-looking risk assessment capability. - Technosylva simulation data used in the old model uses a 8 hour run simulation, whereas the new model uses a 24 hour run simulation Due to the change in risk units and modeling methodology, direct comparisons of risk scores between the old and new frameworks are not feasible. Instead, changes in risk rankings could provide a lens through which to assess the impact of the new model. However, comparing ranking outputs from the two models is further complicated due to differences in GIS data snapshots associated with the official model runs dates, which reflect changes in the electric infrastructure over time, such as installation of new sectionalizing devices, undergrounding of overhead lines, covered conductor of existing bare wires, thereby introducing variability unrelated to the modeling framework change itself. For a list of segment ranking comparisons, please see attached file titled “SDGE Response OEIS-P-WMP_2025-SDGE-03__Q3_rank_summary.xlsx.” (2) SDG&E does not currently have a comparison between risk scores generated under the previous MAVF methodology and those produced using the new Cost-Benefit framework. Developing a meaningful comparison would require substantial resources and the application of several assumptions. However, SDG&E could generate heatmaps illustrating shifts in risk rankings across feeder segments within its service territory, but it would take several weeks to complete. SDG&E can begin this work, once OEIS confirms that it would like SDG&E to spend weeks creating these heatmaps. b. i. SDG&E’s risk models are continuously in the process of development and review for potential enhancements and currently follow a minimum yearly cadence of release of new production versions. ii. SDG&E’s review and enhancement of assumptions and inputs for its risk models coincide with the release of each new production version. iii. SDG&E maintains a proactive and iterative approach to enhancing its risk modeling capabilities. As part of our commitment to continuous improvement, SDG&E reviews its risk models annually. This process includes a thorough evaluation of model performance, integration of new data, and consideration of feedback from both intervenors and the Office of Energy Infrastructure Safety (OEIS). SDG&E prioritizes and execute updates based on this feedback to ensure our models remain robust, transparent, and aligned with evolving risk landscapes. Looking ahead, SDG&E’s roadmap for future risk modeling enhancements is guided by the Risk Modeling Improvement Plan outlined in the 2026–2028 WMP, Section 5, OEIS Table 5-6: Utility Risk Assessment Improvement Plan, as well as any feedback collected in the Risk Modeling Working Groups where SDG&E is actively participating | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03__Q3_rank_summary.xlsx | 1 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
25 | OEIS | 3 | OEIS-3 | 4 | OEIS-3.4 | Regarding SDG&E’s Response to SDGE-23B-04 In Appendix D, pages 3-4, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-23B-04. Incorporation of Extreme Weather Scenarios into Planning Models. a. In SDG&E’s response, SDG&E states that its latest model methodology estimates “upper tail risk, which includes rare and extreme scenarios.” On page 51 of SDG&E’s 2026-2028 Base WMP, SDG&E states that it “does not currently analyze extreme events or highly uncertain scenarios” and that “the WiNGS-Planning model is designed to incorporate historical weather conditions experienced within the service territory.” i. Describe how “rare and extreme scenarios” differ from “extreme events or highly uncertain scenarios” in these two instances. b. On page 51 of SDG&E’s 2026-2028 Base WMP, SDG&E states that “the potential incorporation of climate change scenarios based on the latest climate modeling projection datasets that are being produced with the support from California Energy Commission are currently being evaluated.” i. Provide a timeline with concrete milestones and dates for SDG&E’s evaluation for integration of climate change scenarios. c. In SDG&E’s response, SDG&E states that the framework allows SDG&E to “generate statistical estimates of potential wind events over the maximum asset life of its system.” i. What estimates did SDG&E use for maximum asset life, given that the fire behavior scenarios used span the years 2013 to 2021? ii. Describe how SDG&E integrated and estimated the maximum asset life into risk modeling. | a) i. In the context of the reference on page 3 of Appendix D, SDGE-23B-04. Incorporation of Extreme Weather Scenarios into Planning Models, “rare and extreme scenarios” is referring to the upper tail risk interval of the probabilistic distribution that accounts for rare but catastrophic risk events. The full probabilistic distribution of risk events leveraging Technosylva’s outputs calculated under extreme fire weather days are currently accounted for in SDG&E’s risk modeling framework. The reference on page 51 of the 2026-2028 Base WMP, from Section 5.3.2 Extreme-Event/High Uncertainty Scenarios, is in the context of rare and extreme risk event hazards that are not accounted for in SDG&E’s current risk modeling, including black swan events such as acts of terrorism, multi-hazard scenarios such as ignitions from another source during a PSPS, extended drought, etc. b) i. SDG&E is exploring multiple methodologies to model future wildfire risk, with particular emphasis on projecting potential increases in acres burned relative to historical baseline. A key objective is to align these projections with the latest climate science, specifically the CMIP6 (Coupled Model Intercomparison Project Phase 6) simulation outputs, which will inform California’s upcoming Fifth Climate Change Assessment, scheduled for release in 2026. Currently, the most recent wildfire projection dataset available on Cal-Adapt is based on earlier CMIP5 simulations, specifically the work by Westerling (2018). However, this dataset is now considered outdated. In response, the UC Merced research team is actively working to update wildfire projections using CMIP6 data. These updated projections will aim to reflect a more accurate and forward-looking foundation for assessing wildfire risk under future climate scenarios and will be incorporated into the 2026 Assessment. Once the CMIP6-based wildfire projections are made available, SDG&E will review, validate, and incorporate the data into its risk modeling framework, pending approval by its internal subject matter experts (SMEs). c) i. A 5 million simulation run was performed leveraging Probability of Ignition (POI) model outputs and fire behavior scenarios from Technosylva’s WRRM model that include weather conditions observed from 2013 to 2021 to simulate annual wildfire risk event scenarios, effectively equating 5 million years being simulated. The maximum asset life is modeled for Combined Covered Conductor and Undergrounding with an assumed lifespan of 55 years in alignment with guidance from the with the Electric Undergrounding Program (EUP) risk modeling reporting requirements established by Energy Safety pursuant to Senate Bill 884. ii. Maximum asset life is utilized to estimate projected risk reduction benefits over the life of the asset as part of the calculation of Cost Benefit Ratio (CBR) metrics for each mitigation type, which account for annual inflation and various benefit discount rates scenarios over that lifetime. For further details on how CBR metrics are calculated, see Section 6.2.1.2 Risk Impact of Activities in SDG&E’s 2026-2028 WMP report. | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 0 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
26 | OEIS | 3 | OEIS-3 | 5 | OEIS-3.5 | Regarding SDG&E’s response to SDGE-25U-02 In Appendix D, pages 5-6, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-25U-02 Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety. In SDG&E’s response, SDG&E describes monthly meetings held focusing on WMP activities and topics. Provide the dates and topics associated with each meeting held. | Please see attached document titled, “SDGE Response OEIS-P-WMP_2025-SDGE-03_Q5.pdf.” | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 1 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
27 | OEIS | 3 | OEIS-3 | 6 | OEIS-3.6 | Regarding SDG&E’s response to SDGE-25U-03 In Appendix D, pages 7-29, of SDG&E’s 2026-2028 Base WMP, SDG&E provides its response to SDGE-25U-03. Third-Party Recommendations for Model Improvements. In Table 4-1: WiNGS-Planning Risk Model Updates, SDG&E provides a status of “Not Applicable” for the following recommendations: CHI Update and Mean Value Assessment. Explain why these recommendations are listed as “Not Applicable.” | In Table 4-1: WiNGS-Planning Risk Model Updates, SDG&E initially marked the CHI Update and Mean Value Assessment recommendations as “Not Applicable” incorrectly. These entries will be corrected to reflect their true status: - The CHI update has been completed and subsequently removed from the WiNGS-Planning model, as the integration of WiNGS-Ops into WiNGS-Planning now captures this information. - The Mean Value Assessment is currently underway, with completion anticipated before 2027. With the transition to a probabilistic risk assessment framework, SDG&E considers this requirement to be almost completed through the enhanced modeling approach. | Zhenying Shao | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-03_0.pdf | 0 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
28 | OEIS | 4 | OEIS-4 | 1 | OEIS-4.1 | Regarding reduction in 2025 targets/expenditure for Lightning Arrestor Removal/Replacement (WMP.550) and Avian Protection (WMP.972) In its Petition to Amend, SDG&E requests to reduce its 2025 targets for Lightning Arrestor Removal/Replacement (WMP.550) from 1,848 to 90 and for Avian Protection (WMP.972) from 200 to 95 poles.1 SDG&E revised its projected 2025 capital expenditure for Lightning Arrestor Removal/Replacement (WMP.550) from $3.483 million to $0, and for Avian Protection (WMP.972) from $1.512 million to $0.2 In its General Rate Case (GRC) decision, the California Public Utilities Commission (CPUC) adopted a capital forecast of $3.2 million for SDG&E’s lightning arrestor replacement and avian protection programs.3,4 The CPUC adopted forecast is $0.357 million lower than SDG&E’s proposal in the GRC application. a. Explain why its projected expenditure in its Petition to Amend for the Lightning Arrestor Removal/Replacement (WMP.550) and Avian Protection (WMP.972) initiatives are $0 even though the CPUC adopted a capital forecast of $3.2 million. b. Provide the unit cost of lightning arrestor removal and replacement in High Fire Threat district (HFTD) Tier 2 and Tier 3 and the number of lightning arrestors SDG&E plans to remove/replace in Tier 2 and Tier 3, respectively. i. If the total annual cost is higher than that adopted by the CPUC, provide justification for the higher unit cost. c. Explain why SDG&E’s 2025 Avian Protection (WMP.972) target is reduced even though the category is uncontested in the GRC decision. | As discussed in the Petition to Amend, SDG&E must manage expenditures for the entire portfolio of wildfire mitigation initiatives and across all four years of the TY 2024 GRC cycle, 2024-2027.As stated on page 5 of the Petition to Amend, “To stay within the authorized revenue requirement and because SDG&E exceeded its capital expenditures in 2024, it is necessary to reduce SDG&E’s wildfire mitigation spending for 2025, 2026, and 2027.” For this reason, SDG&E elected to reduce program scope for some of its uncontested programs, thereby reducing program spend and overall portfolio spend, for the initiatives in question. SDG&E carefully considered every initiative in its WMP portfolio with specific focus on the impacts on wildfire and PSPS risk reduction to determine the scope and scale of program reductions. Regarding target changes requested for 2024, the Commission did not issue a final decision in the GRC until the last week of the year. In the absence of that final decision, SDG&E used reasonable judgement at the time to reduce programs in alignment with its proposed Settlement Agreement with CalPA, both to adhere to the terms of that proposed agreement and in an effort to find cost savings and efficiencies while maintaining an appropriate level of risk reduction. For example, SDG&E continued implementation of its grid hardening initiatives, mandatory asset and vegetation management inspections, and maintained situational awareness and emergency preparedness. As a result, SDG&E elected to reduce the uncontested programs that would not achieve as much risk reduction, and further explanations for each are provided below. Regarding target and expenditure changes for 2025, SDG&E first considered how to implement the explicitly authorized undergrounding and covered conductor initiatives, and then how to make further adjustments to portfolio level spend while not introducing or increasing additional wildfire and PSPS risk. The resulting portfolio includes reductions to uncontested programs in question, and further explanations are provided below and in response to other questions. a. SDG&E elected to reduce program budgets for Lightning Arrestor Removal/Replacement (WMP.550) and Avian Protection (WMP.972) to $0 and reallocate those budgets to wildfire mitigation activities that are expected to reduce more wildfire risk. As discussed in its Change Order submitted January 27, 2025 and rejected by Energy Safety and again in the Petition to Amend, SDG&E intends to continue replacing and installing these assets alongside covered conductor deployment. For this reason, the program targets have not been completely reduced to zero but instead are aligned with the intended covered conductor mileage planned for 2025. SDG&E also notes that the GRC Decision adopted TURN’s recommendation for cost per unit of covered conductor at $800,000/mile, which was a significant reduction from SDG&E’s request and reduced available funds for associated asset replacements such as structures, lightning arrestors, fuses, avian protection, etc. Reallocating the costs in the manner described in the authorized spend for lightning arrestors and avian protection to Covered Conductor (WMP.455) is reasonable because it will continue to replace those assets as it deploys covered conductor and to increase its Covered Conductor program budget to account for a more realistic and reasonable unit cost.b. SDG&E is not calculating a projected cost per unit for lightning arrestors and avian protection as those replacements are included in the cost/mile and projected spend for Covered Conductor. The targeted units for lightning arrestors and avian protection were forecasted based on estimating a number of widgets needed for an average number of structures per circuit mile. This methodology yields 90 lightning arrestors and 95 poles with avian protection, respectively. Applying the percentage of planned miles for covered conductor deployment in Tier 2 and Tier 3 in 2025, SDG&E estimates that it will install the following: Tier 2 Tier 3 Lightning arrestors 54 36 Avian protection 57 38 c. See response to part a. above. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
29 | OEIS | 4 | OEIS-4 | 2 | OEIS-4.2 | Regarding reduction in 2025 targets/expenditure for Detailed Vegetation Inspections (WMP.494) In its Petition to Amend, SDG&E seeks to reduce its 2025 Detailed Vegetation Inspections (WMP.494) target from 485,400 inspections to 255,000 inspections in the HFTD.5 Correspondingly, SDG&E requested to reduce its HFTD expenditure from $32.639 million to $30.854 million.6 For the category of Vegetation Management and Inspection – Tree Trimming only, the GRC decision authorized $26.612 million for the work in the HFTD, which is $0.62 million lower than SDG&E’s proposal ($27.232 million) due to lower unit ($97 in Tier 2 and Tier 3) cost adopted.7 CPUC also authorized $15.269 million in the non-HFTD for the 2024 test year, which is consistent with SDG&E’s proposal.8 For the category of Vegetation Management and Inspection, the GRC decision authorized $ 12.481 million, which is $3.552 million less than SDG&E’s request ($ 16.033 million, post-Update Testimony forecast).9 The GRC decision did not discuss the number of inspections for this category.10 a. Provide the number of inspections SDG&E planned in its GRC application that formed the basis for the $41.881 million CPUC authorization in both HFTD and non-HFTD.11 Include a reference (from its GRC filing, include the URL and page number) for the number of inspections. i. If the number of inspections SDG&E plans to conduct in its GRC application is not consistent with the target changes in the Petition to Amend, provide justification for the difference in the scope of work. b. Explain why inspections are only performed in the HFTD when there is an authorized non-HFTD forecast. c. Provide unit costs for Detailed Vegetation Inspections (WMP.494) in the HFTD and non- HFTD. i. If SDG&E’s unit cost calculates to a higher total cost than $26.612 million (HFTD) and $15.269 million (non-HFTD) authorized by the CPUC, provide justification for the higher unit costs. | a. In its 2024 GRC, SDG&E anticipated performing 491,822 tree inspections throughout its service territory, with 149,228 trees in Tier 2, 123,772 trees in Tier 3, and 218,822 trees in the non-HFTD. Tree Trimming’s number of trees inspected are discussed in 1WM005.001 (pages 106-107) in 2024 GRC Application Exhibit SDG&E-13-WP-2R-E: SDGE-13-WP-2R-E_Jonathan T Woldemariam_EOWM.pdf. b. SDG&E clarifies that there is no change to its planned vegetation management activities across its entire service territory and it will continue to perform vegetation management inspections and follow up activities throughout its service territory. Rather, to remain consistent with other wildfire mitigation activities that address wildfire risk in the most consequential areas, SDG&E elected to limit the WMP scope of vegetation management activities to the HFTD. This approach is consistent with the approach taken in the GRC Decision authorizing the use of the Vegetation Management Balancing Account (VMBA), and authorizing vegetation management HFTD costs distinctly from non-HFTD costs. In addition, it develops more transparency for vegetation management related activities and costs in the HFTD and not have the data comingled with the non-HFTD work. c. SDG&E’s current projected unit cost for vegetation management inspections and tree trimming activities in the HFTD is ~$121/tree, which totals $30.854 million for 255,000 trees. The unit cost reflected in the GRC Decision for vegetation management inspections and tree trimming activities in the HFTD is ~$97.50/tree. The projected cost of $30.854 million is higher than the CPUC authorized HFTD costs of $26.612 million for various reasons. SDG&E developed its 2024 GRC in the latter half of 2021 and early 2022, and at the time forecasted spend for the category of Vegetation Management and Inspection – Tree Trimming only using a base-year forecast that assumed 2021 levels of work and spend and simply escalated to 2024 dollars. The base year forecast was flawed in thatit fails to reflect current market conditions and competitive solicitations for contracted workforce performing these activities. There are significant market increases due to union wages and benefits guided by Senate Bill 247, overhead expenses, equipment costs, and contractor liability insurance that influence SDG&E’s current cost forecasts. SDG&E continues to manage a safe and compliant vegetation management program to prevent wildfires and tree-caused outages. SDG&E will continue to seek opportunities to reduce program costs through undergrounding projects, leveraging technology and risk modeling, and removing fast-growing tree species to modify the tree inventory near overhead electrical lines. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
30 | OEIS | 4 | OEIS-4 | 3 | OEIS-4.3 | Regarding reduction in 2025 targets/expenditure for Pole Clearing (WMP.512) In its Petition to Amend, SDG&E seeks to reduce its 2025 Pole Clearing (WMP.512) target from 33,010 poles to 22,000 poles.12 SDG&E requests to reduce its operations expenditure for Pole Clearing (WMP.512) from $8.13 million to $6.427 million.13 The GRC decision adopts a 2024 forecast of $5.369 million for Pole Brushing/Clearing with the same number of poles SDG&E stated in its GRC application.14 CPUC’s authorization is $2.524 million less than SDG&E’s request ($7.893 million) in its GRC application.15 a. From its GRC application, provide the number of poles SDG&E planned to clear that formed the basis for the $7.893 million requested by SDG&E.16 Include a reference (from its GRC filing, include the URL and page number) for the number of poles. b. Provide the unit cost for Pole Clearing (WMP.512) in HFTD Tier 2 and Tier 3, and the number of poles SDG&E plans to brush in each tier. i. If the unit cost amounts to a total cost higher than the $5.369 million authorized by the CPUC, provide justification for the higher unit cost. c. Provide justification for reduced target request given that the GRC decision does not discuss the scope of pole brushing/clearing. The acceptance of Cal Advocate’s recommendation implicitly endorses workloads per year; the workloads forecast by SDGE and recommended by Cal Advocates are equal – it’s only the unit cost that differs.17 i. If the number of poles SDG&E plans to clear is not consistent with the number provided in its GRC application, provide justification for the difference in the scope of work. | a. In its 2024 GRC, SDG&E anticipated performing pole clearing activities around 34,000 poles.18 Pole Brushing’s number of poles brushed are discussed in 1WM005.000 (pages 93-94) in 2024 GRC Application Exhibit SDG&E-13-WP-2R-E: SDGE-13-WP-2R-E_Jonathan T Woldemariam_EOWM.pdf. b. SDG&E’s current projected unit cost for pole clearing activities is ~$292/pole, which totals $6.427 million for 22,000 poles. The unit cost reflected in the GRC Decision for pole clearing activities is ~$158/pole, which totals $5.369 million for 34,000 poles. SDG&E’s requested unit cost in its GRC request is ~$232/pole, which totals the requested $7.893 million for 34,000 poles. SDG&E’s current cost projection is higher than both its requested costs and CPUC authorized costs for reasons described in response to question 2c. above. c. As discussed in its Petition to Amend, consistent with the GRC Decision authorizing $2.54 million less than requested, and in an effort to align program budget with authorized spend, SDG&E elected to reduce the scope of this program, thereby reducing total program costs, by eliminating pole clearing activities around poles with exempt equipment that are not required by Public Resources Code (PRC) § 4292. Although SDG&E’s current projected spend of $6.427 million remains $1.058 million higher than authorized, the corresponding change in program scope demonstrates SDG&E’s commitment to performing mandatory pole clearing activities in compliance with PRC § 4292 with the ultimate goal of reducing wildfire risk. As stated previously, SDG&E continues to manage a safe and compliant vegetation management program to prevent both likelihood and consequence of ignition. SDG&E will continue to seek opportunities to reduce program costs through undergrounding projects that will eliminate the need for these activities where overhead lines are undergrounded. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
31 | OEIS | 4 | OEIS-4 | 4 | OEIS-4.4 | Regarding reduction in 2024 targets for Fuels Management (WMP.497) In its Petition to Amend, SDG&E seeks to reduce its 2024 Fuel Management (WMP.497) target from 500 poles to 150 poles.18 The GRC decision adopts a 2024 forecast of $5.246 million with the same number of structures SDG&E stated in its GRC application. CPUC’s authorization is $1.028 million less than SDG&E’s request ($6.274 million) in its GRC application. a. From SDG&E’s GRC application, provide the number of structures SDG&E planned to clear in 2024 that formed the basis for the $6.274 million forecast proposed by the SDG&E.19 SDG&E must include a reference to a GRC filing (including URL and page number) for the number of structures. b. Provide the unit cost for Fuels Management (WMP.497) in HFTD Tier 2 and Tier 3, , and the number of structures SDG&E cleared in each Tier from its GRC application. i. If the unit cost amounts to a total annual cost higher than the $5.246 million authorized by the CPUC, provide justification for the higher unit cost. c. Provide justification for reducing its 2024 target given that the GRC decision did not reduce the scope of the program. i. If the request to reduce its target to 150 poles for 2024 is not consistent with the number provided in the GRC application, provide justification to the difference in the scope of work. | a. In its 2024 GRC, SDG&E anticipated performing fuels management activities around 550 poles. The total cost for Fuels Management includes the activities of structure clearing, fuels grants program, and fuel abatement within easements. SDG&E’s unit target for Fuels Management pertains only to the activity of structure clearing (550 poles). Fuels Management’s number of structures cleared are discussed in 1WM005.000 (pages 91-92) in 2024 GRC Application Exhibit SDG&E-13-WP-2R-E: SDGE-13-WP-2R-E_Jonathan T Woldemariam_EOWM.pdf. b. Embedded in the GRC Decision and the GRC request for Fuels Management are the costs for structure clearing, fuels grants program and fuel abatement program. When separating the cost of these programs by activity, the relative portion for the structure clearing (unit cost) isdetermined. In 2024, the total cost for structure clearing was $1.563 million. In 2024, SDG&E cleared 26 poles in Tier 2 and 121 poles in Tier 3. This yields a unit cost of ~$10,631/pole. The unit cost shown in SDG&E’s GRC request and the GRC Decision includes all three Fuels Management activities. The unit cost reflected in SDG&E’s GRC request was $11,407/pole. The unit cost reflected in the GRC Decision was $9,538/pole. The approximate annual cost for the fuels grants program and the fuel abatement program is $1.5 million. Removing these costs from the GRC request would modify the unit cost for structural clearing to $8,679/pole. The higher actual unit cost in 2024 can be attributed to a proportional increase in the number of poles that were cleared for the first time. Initial pole clearing requires additional time to complete the work at each site, requires additional environmental review and on-site monitoring, and increases the costs associated with project management. c. Given that SDG&E was not issued its GRC Decision until December 23, 2024, it elected to make informed decisions regarding its then-pending GRC Decision earlier in 2024 as it implemented its 2024 WMP initiatives. Absent the GRC Decision, which ultimately authorized some spend for these activities, and in a position to make operational decisions in anticipation of the Decision, SDG&E aligned program budgets with its then-pending Settlement Agreement with CalPA and elected to reduce the scope of this program in 2024. The election to reduce the scope was informed by the knowledge that the remaining poles in the fuels management initiative would be addressed by other risk-reducing vegetation management measures such as pole brushing. Ultimately, the reduced scope of the program is supported by the Decision’s reduction to authorized spend for this activity. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
32 | OEIS | 4 | OEIS-4 | 5 | OEIS-4.5 | Regarding reduction in 2025 targets and expenditures for Distribution Vegetation Inspections (WMP.494) and Pole Clearing (WMP.512) a. Complete the table below by listing the proposed target in SDG&E’s Petition to Amend, unit costs, and total costs in 2021 dollars. i. If any of the expenditures in the “2025 Total Cost” column are different from the expenditures in the “GRC Authorized Cost” column explain why. Data Request OEIS-P-WMP_2025-SDGE-04 7 Initiative Location Unit 2025 Target in Petition to Amend 2025 Unit Cost (2021 $/unit) 2025 Total Cost (millions of 2021 $) GRC Authorized Cost (millions of 2021 $) Distribution Vegetation Inspections (WMP.494) Non-HFTD Inspections 15.269 Distribution Vegetation Inspections (WMP.494) HFTD Inspections 26.612 Pole Clearing (WMP.512) HFTD Poles 5.369 | Initiative Location Unit 2025 Target in Petition to Amend 2025 Unit Cost (2021 $/unit) 2025 Total Cost (millions of 2021 $) GRC Authorized Cost (millions of 2021 $) Distribution Vegetation Inspections (WMP.494) Non-HFTD Inspections 0 15.269 Distribution Vegetation Inspections (WMP.494) HFTD Inspections 255,000 $121/tree $30.854 26.612 Pole Clearing (WMP.512) HFTD + non-HFTD Poles 22,000 $292/pole $6.427 5.369 GRC costs are derived from forecasts developed several years in advance of the applicable years and based on estimates and historical costs. Thus, SDG&E’s current 2025 projected costs for vegetation management activities are inevitably different from the GRC authorized costs for various reasons. SDG&E’s TY 2024 GRC was developed in 2021 with a base-year forecasting methodology that did not account for variations in contracted labor costs per Senate Bill 247, overhead expenses, equipment costs, and contractor liability insurance. The base-year forecasting methodology assumes levels of work and spend to be very close to the previous year’s levels of work and spend. These variations in costs are the contributing factors to increased unit costs SDG&E is experiencing with implementing these activities. Second, as discussed in responses to questions 2 and 3, SDG&E is requesting to reduce program targets, thereby reducing program spend, in an effort to align as closely as possible with GRC authorized amounts. However, SDG&E is committed to performing mandatory vegetation management activities, which are reflected with the targets requested, in compliance with PRC § 4292. The mandatory, targeted work at the current unit costs are therefore different from the GRC authorized costs. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
33 | OEIS | 4 | OEIS-4 | 6 | OEIS-4.6 | Regarding reduction in 2024 targets and expenditure for Fuels Management (WMP.497) a. Complete the table below by listing the proposed target in SDG&E’s Petition to Amend, unit costs, and total costs in 2021 dollars. i. If any of the expenditures in the “2024 Total Cost” column are different from the expenditures in the “GRC Authorized Cost” column explain why. Initiative Location Unit 2024 Target in Petition to Amend 2024 Unit Cost (2021 $/unit) 2024 Total Cost (millions of 2021 $) GRC Authorized Cost (millions of 2021 $) Fuels Management (WMP.497) HFTD Poles 5.264 | Initiative Location Unit 2024 Target in Petition to Amend 2024 Unit Cost (2021 $/unit) 2024 Total Cost (millions of 2021 $) GRC Authorized Cost (millions of 2021 $) Fuels Management (WMP.497) HFTD Poles 150 $21,490/pole $3.159 5.264 d. As stated in response to question 4c. above, given that SDG&E was not issued its GRC Decision until December 23, 2024, it elected to make informed decisions regarding its then-pending GRC Decision earlier in 2024 as it implemented its 2024 WMP initiatives. Absent the GRC Decision, which ultimately authorized some spend for this activity, and in a position to make operational decisions in anticipation of the Decision, SDG&E aligned program budgets with its then-pending Settlement Agreement with CalPA and elected to reduce the scope of this program. The election to reduce the scope was informed by the knowledge that the remaining poles in the fuels management initiative would be addressed by other risk-reducing vegetation management measures such as pole brushing. Ultimately, the reduced scope of the program is supported by the Decision’s reduction to authorized spend for this activity. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
34 | OEIS | 4 | OEIS-4 | 7 | OEIS-4.7 | Regarding reduction in 2025 target for Covered Conductor (WMP.455) In its Petition to Amend, SDG&E seeks to increase its 2025 target from 40 miles to 50 miles with the capital expenditure increased from $67.63 million to $81.43 million.20 SDG&E’s petition produces a unit cost of $1.623 million per mile. In the GRC decision, the CPUC adopted $71.9 million for 100 miles of covered conductor, for an average cost of less than $1 million per mile.21 Explain the $1.623 million unit cost for covered conductor. Present the historic unit cost data and itemize the key expenses included when estimating the unit cost for covered conductor. | The Commission adopted TURN’s recommendation of $800,000/mile of covered conductor installation, which was informed by average unit costs across California utilities. This unit cost is flawed in that it does not consider SDG&E’s full scope of covered conductor deployment, which includes replacing other assets such as structures, crossarms, lightning arrestors and avian protection (as discussed in question 1), fuses, etc. Additionally, SDG&E leverages LiDAR survey pre-construction (design) and post-construction (True-Up Analysis). It engineers and designs facilities using PLS-CADD, not OCalc Pro or SpidaCalc. PLS-CADD is the most robust and accurate way to ensure poles, crossarms, guys, anchors, and wire sag/tension/clearances are built correctly and meet or exceed GO95 or internal SDG&E Standards. OCalc Pro and SpidaCalc are not as accurate when it comes to loading calculation nor do they perform wire sag/tension/clearance analysis. SDG&E also has a robust post-construction QA/QC process where each facility is inspected by a Qualified Electrical Worker. These are all contributing factors to SDG&E’s higher unit cost than was authorized in the Decision. Furthermore, the costs incurred in any given year do not directly correlate to the miles energized in the same year. The installation of covered conductor is complex work that requires many months, sometimes spanning multiple years, for project initiation through construction and energization. Consistent with the Commission’s authorization for covered conductor units in the Decision, SDG&E plans to increase its covered conductor deployment in future years, which is reflected in its 2026-2028 WMP. Therefore, the 2025 projected spend of $81.43 million includes costs for work planned to be completed in 2025, 2026, and 2027, and it is inappropriate to unitize these costs across the 50 miles planned in 2025. Key expenses that influence the cost forecast for covered conductor include pre-construction activities (project management, scheduling, engineering and design, GIS, surveying, permitting, public relations, etc) and construction activities (labor, equipment, and materials). These costs can be incurred in multiple years during the life of a project depending on when the project is initiated and the project schedule. The table below presents average, historical direct costs, program-to-date for key cost elements: Direct Costs Category $ Amount Labor (Internal) $ 278,000 Materials $ 197,000 Contractor $ 260,000 Overhead (division, corporate, etc.) $ 350,000 Total Direct Cost per Mile 2023 $ $ 1,085,000 | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
35 | OEIS | 4 | OEIS-4 | 8 | OEIS-4.8 | Regarding reduction in 2025 targets/expenditure for Strategic Pole Replacement Program (WMP.1189) In its Petition to Amend, SDG&E seeks to decrease its 2025 target from 291 poles to 200 poles while requesting to increase its capital expenditure from $6.948 million to $7.923 million. As provided in SDG&E’s response to Data Request OEIS-P-WMP_2025-SDGE-01,22 the Strategic Pole Replacement Program initiative (WMP.1189) is part of the High Risk Pole Replacement Program in the GRC decision, which is an uncontested category in the GRC decision.23 a. Provide an explanation for the reduced target and increased expenditure. b. Provide an explanation for increased unit cost for the initiative, given the increased expenditure and decrease in target. | a. SDG&E increased its target from 200 poles to 291 poles in its 2025 WMP Update (Update) submitted on July 5, 2024. At the time it prepared and submitted the Update, it had limited program experience and cost data to accurately inform an updated cost forecast. Consequently and as filed in the Update, it only increased its forecasted costs from $6.701 million to $6.948 million, a 4% increase inconsistent with the target increase of 46%. This discrepancy is due in large part to the challenges posed by Energy Safety’s Process and Evaluation Guidelines requiring the utilities to transition to the year-ahead process for submitting annual WMP updates. SDG&E’s annual capital planning process typically occurs in quarter 4 of the year preceding the planning year. In this case, SDG&E developed its 2025 WMP initiative targets in late 2023 in preparation to submit its Update in early 2024, a year in advance of 2025. Because SDG&E’s annual planning process did not align with the newly introduced year-ahead WMP process, this cost forecast was likely overlooked. Subsequently, the Petition to Amend reflects a target reduction back down to 200 poles, which is a result of SDG&E aligning its capital planning process for the entire WMP portfolio given the GRC Decision. If SDG&E had continued with 291 poles targeted, the forecasted spend would have exceeded authorized and increased overall portfolio spend to levels beyond authorized. The projected 2025 spend of $7.923 million reflects the current cost forecast for the200 poles initially planned and reasonably aligns with overall WMP portfolio authorized levels. b. Unit costs for this initiative did not increase. Rather, there was an inadvertent and discrepant units to costs ratio presented in SDG&E’s 2025 WMP Update as described above. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
36 | OEIS | 4 | OEIS-4 | 9 | OEIS-4.9 | Regarding reduction in targets for uncontested initiatives and for initiatives that the GRC decision adopted SDG&E’s proposal In its Petition to Amend, SDG&E requested target changes for nine initiatives and accompanying expenditure reductions for initiatives that were not contested in the GRC.24 • 2024 target changes o Distribution Communications Reliability Improvements (WMP.549) o Distribution Infrared Inspections (WMP.481) o Standby Power Program (WMP.468)  The GRC decision adopted SDG&E’s proposal.25 • 2024 and 2025 target changes o Drone Assessments (WMP.552) • 2025 target changes o Strategic Pole Replacement Program (WMP.1189) o Transmission OH Hardening (WMP.543) o Distribution Communications Reliability Improvements (WMP.549) o Connectors, including hotline clamps (WMP.464) o Expulsion Fuse Replacement (WMP.459) Provide explanations for each of the target and expenditure reductions for the above initiatives. | 2024 Target Changes Distribution Communications Reliability Improvements (WMP.549) SDG&E elected to transition from a high-volume deployment of this program to a more targeted deployment while continuing to assess the benefit of this program and where additional efficiencies could be achieved through refined practices and alternative technology. This change will result in a delay to some of the communications reliability improvements expected from the SDG&E-owned private LTE network that supports some of SDG&E’s Advanced Protection Programs (APP), including Falling Conductor Protection (FCP) and Early Fault Detection (EFD). FCP and EFD work will continue to be deployed on this new network where available, and will utilize alternate technologies for support when necessary. Distribution Infrared Inspections (WMP.481) SDG&E transitioned this program to a risk-informed approach in an effort to optimize outcomes. In prior years, structures selected for this program were based on previous inspections, to ensureinspections were not repeated in consecutive years, and were informed by subject matter expert recommendations. However, SDG&E found that this inspection program yielded only a 0.2 percent find rate. To optimize the program for 2024, specific areas were targeted during peak load season and structures were selected using a risk-informed strategy comprised of SDG&E’s Asset 360 models, risk analytics models, and Intelligent Image Processing (IIP). This program will continue with the risk-informed approach in 2025, and inspections will be performed on 300 structures, as approved in SDG&E’s 2025 WMP Update. Standby Power Program (WMP.468) SDG&E elected to scale back on the scope of this program because no new customers had been identified to include in scope of the program due to the lack of PSPS de-energizations from 2021 to mid-2024. SDG&E will continue to explore additional PSPS mitigation approaches for its customers and expects this program to evolve in the 2026-2028 WMP cycle. Drone Assessments (WMP.552) SDG&E reevaluated the program to optimize the number of inspections based on further risk assessment. This reevaluation aimed to balance expected risk reduction with expected repair and replacement costs and timelines. The historical number and severity of findings from the first year of program implementation (2023), along with historical repair and replacement costs, were evaluated against the expected wildfire risk consequences at each asset location. This resulted in a determination to perform 6,500 inspections, which represented a balanced approach that still maximized risk reduction. 2025 Target Changes Drone Assessments (WMP.552) SDG&E reevaluated the program to optimize the number of inspections based on further risk assessment. This reevaluation aimed to balance expected risk reduction with expected repair and replacement costs and timelines. The historical number and severity of findings from the first year of program implementation (2023), along with historical repair and replacement costs, were evaluated against the expected wildfire risk consequences at each asset location. This resulted in a determination to perform 6,500 inspections, which represented a balanced approach that still maximized risk reduction. Strategic Pole Replacement Program (WMP.1189) SDG&E is not descoping work for this program; rather, it is extending the timeframe for which it will complete the scoped work to achieve cost relief in 2025. There is no impact to expected risk reduction as these poles will continue to be maintained with routine inspections, including wood pole intrusive inspections, which determine the integrity of the pole. Findings will be corrected in timeframes determined by the severity and in compliance with GO 95. Transmission OH Hardening (WMP.543) This reduction is due to a dependency on distribution underbuild that was previously scoped for strategic undergrounding but will no longer be performed in 2025 due to the undergrounding program reductions. Therefore, the transmission hardening work requires either a re-design to account for the distribution underbuild or will be shifted to future years when the distribution underbuild is undergrounded. Distribution Communications Reliability Improvements (WMP.549) SDG&E elected to continue projects in construction, and then pause this program. This program has no direct impact to risk reduction and therefore will not change SDG&E’s risk profile. Connectors, including hotline clamps (WMP.464) Rather than proactive, high-volume deployment of these assets, SDG&E will strategically deploy these assets with the deployment of covered conductor and continue to replace them as needed as part of its Corrective Maintenance Program (CMP). This deployment plan will achieve cost efficiencies and prioritize higher risk circuit segments in tandem with covered conductor. The program target has not been completely reduced to zero but instead is aligned with the intended covered conductor mileage planned for 2025. SDG&E also notes that the GRC Decision adopted TURN’s recommendation for cost per unit of covered conductor at $800,000/mile, which SDG&E finds unreasonable and rebuts given its historical cost per unit that incorporates not only reconductor work, but also associated asset replacements such as structures, connectors, lightning arrestors, fuses, avian protection, etc. SDG&E finds it reasonable to reallocate the authorized spend for this program to Covered Conductor (WMP.455) because it will continue to replace those assets as it deploys covered conductor and to increase its Covered Conductor program budget to account for a more realistic and reasonable unit cost. Expulsion Fuse Replacement (WMP.459) Rather than proactive, high-volume deployment of these assets, SDG&E will strategically deploy these assets with the deployment of covered conductor and continue to replace them as needed as part of its Corrective Maintenance Program (CMP). This deployment plan will achieve cost efficiencies and prioritize higher risk circuit segments in tandem with covered conductor. The program target has not been completely reduced to zero but instead is aligned with the intended covered conductor mileage planned for 2025. SDG&E also notes that the GRC Decision adopted TURN’s recommendation for cost per unit of covered conductor at $800,000/mile, which SDG&E finds unreasonable and rebuts given its historical cost per unit that incorporates not only reconductor work, but also associated asset replacements such as structures, connectors, lightning arrestors, fuses, avian protection, etc. SDG&E finds it reasonable to reallocate the authorized spend for this program to Covered Conductor (WMP.455) because it will continue to replace those assets as it deploys covered conductor and to increase its Covered Conductor program budget to account for a more realistic and reasonable unit cost. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
37 | OEIS | 4 | OEIS-4 | 10 | OEIS-4.10 | Regarding revenue requirement and capital expenditure In its Petition to Amend, SDG&E indicated that there is a “Revenue Requirement Shortfall” of $0.148 billion to complete the GRC-authorized capital expenditure (Capex).26 In addition, SDG&E stated the total “Actual/Forecasted Capex” is $1.045 billion while the total “Adjusted Capex Target” is $1.086 billion.27 The GRC decision stated that the CPUC adopted “…a base margin revenue (O&M and capital revenue requirement) increase of 3 percent each year for 2025, 2026, and 2027 plus certain wildfire mitigations, including undergrounding and covered conductor” which allows SDG&E to “fund incremental capital additions for wildfire mitigation programs that are important for infrastructure safety.”28 The GRC decision goes on to state that it provides “… both just and reasonable returns for the utilities and affordable rates for ratepayers.”29 a. Provide a reference from the GRC decision (include a URL and page number) for the in the “Authorized Capital Expenditures (Capex)” values SDG&E provides in its Petition to Amend.30 b. Provide explanations for the “Revenue Requirement Shortfall”. c. Provide high-level explanation on the calculation of “Adjusted Capex Target”. d. Provide explanations to the $41 million difference between the total “Actual/Forecasted Capex” and “Adjusted Capex.” 31 | a. Capital expenditures for Wildfire Mitigation are discussed in Section 19.3.5 (pages 471-486) in 2024 GRC Decision: https://docs.cpuc.ca.gov/PublishedDocs/Published/G000/M550/K485/550485071.pdf. The "Authorized Capital Expenditures (Capex)" values denote direct dollar amounts that include escalation. Conversely, the data presented in our 2024 General Rate Case (2024 GRC) decision reflects direct dollar amounts in 2021 base year dollars (excludes escalation). For instance, the 2024 Authorized Capital Expenditures value of $396 million, as indicated in the table, corresponds to the $321 million total for WMVM Capital Costs for the 2024 Test Year, found in Table 19.18 on page 495 of SDG&E’s 2024 GRC Final Decision. The $396 million in capital for 2024, is escalated directly in SDG&E’s RO Model, that supports the 2024 GRC Final Decision revenue requirement. The 2025-2027 capital values are imputed for the purposes of the RSAR and are consistent with the adopted post-test year mechanism. b. The 2024 GRC Decision does not calculate revenue requirement separately for all of Wildfire Mitigation. Thus, SDG&E performed the revenue requirement calculations noted below for purposes of the Petition to Amend. To calculate the revenue requirement shortfall, SDG&E calculated the revenue requirement, using a combination of the Results of Operations Model adopted in the 2024 GRC Decision and the Project Evaluation Tool (SDG&E’s internal financial model used to calculate revenue requirements) for two scenarios: Scenario No. 1 (“Authorized Revenue Requirement”): The “Authorized Revenue Requirement” represents what was approved in the 2024 GRC and adopted PTY mechanism, which implemented several substantial reductions to SDG&E’s requested wildfire mitigation costs. This “Authorized Revenue Requirement” encompasses: 1) the revenue requirements for covered conductor and strategic undergrounding for each year of the GRC cycle, as explicitly authorized by the CPUC, and 2) an approximate 3 percent annual revenue requirement increase for all other wildfire mitigation programs. However, this authorized revenue requirement falls significantly short of the revenue requirement necessary to fulfill the authorized capital expenditures indicated in the first row of the table. Scenario No. 2 (“Revenue Requirement necessary to complete Authorized Capex”): In accordance with the CPUC’s 2024 GRC Final Decision, SDG&E was authorized capital expenditure forecasts for wildfire mitigation initiatives for Test Year 2024. This level of 2024 spending, and the corresponding imputed figures for the post-test years (2025-2027), are presented in the first row of the table, “Authorized Capital Expenditures (Capex)”. Thecalculated revenue requirement tied to this level of expenditure is reflected in the “Revenue Requirement necessary to complete Authorized Capex” row of the table. The difference between the two scenarios represents the “Revenue Requirement Shortfall”. To reiterate, given that the GRC Decision was issued at the conclusion of Test Year 2024, SDG&E had essentially completed its WMP-related activities for 2024 without definitive funding guidance. As previously mentioned, in the absence of such guidance, SDG&E relied on the Settlement Agreement with Cal Advocates to inform its wildfire mitigation expenditures for 2024. However, this agreement was ultimately rejected by the CPUC, who further reduced the authorized funding for WMP-related activities. The resulting 3 percent annual revenue requirement increase authorized by the CPUC for all other wildfire mitigation programs outside of covered conductor and undergrounding results in SDG&E not being able to invest in new capital. Instead, it allows SDG&E to continue servicing the assets placed into service in 2024. Consequently, if SDG&E were to spend its authorized O&M and capital expenditures each year of the GRC cycle, SDG&E would exceed its authorized revenue requirement. This situation arises because the capital funding required to perform the necessary work exceeds the approximately 3 percent annual revenue requirement increase approved in the 2024 GRC. c. The “Adjusted Capex Target” represents the level of spending required to adhere to the revenue requirement authorized for the overall wildfire mitigation program in accordance with the 2024 GRC Final Decision. To remain within the authorized revenue requirement and because SDG&E exceeded its capital expenditures in 2024, it is necessary to reduce SDG&E’s wildfire mitigation spending for 2025, 2026, and 2027. d. As noted above, the “Adjusted Capex Target” represents the level of spending required to adhere to the revenue requirement authorized for the overall wildfire mitigation program in accordance with SDG&E’s 2024 GRC Final Decision. The “Actual/Forecasted Capex” represents the revised forecasted spending outlined in SDG&E’s Petition to Amend, aimed at ensuring alignment with the costs authorized with SDG&E’s 2024 GRC Final Decision. Ideally, the total for these two rows are identical. However, the $41M delta represents less than a four percent difference relative to the “Adjusted Capex Target” total. It should be noted that the “Adjusted Capex Target” was derived based on a number of financial assumptions. Any deviations from these assumptions in practice may result in the revenue requirement being subject to change. | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
38 | OEIS | 4 | OEIS-4 | 11 | OEIS-4.11 | Q11. Regarding memorandum accounts In the GRC decision, the CPUC decided not to modify the Wildfire Mitigation Plan Memorandum Account (WMPMA).32,33 The decision also converted the existing two-way Tree Trimming Balancing Account into a one-way Vegetation Management Balancing Account (WMBA) with an accompanying Vegetation Management Memorandum Account (VMMA) for spend above the VMBA authorization. Provide the table from pages 2 and 3 of the Petition to Amend listing the initiatives. For each, identify whether the initiative is eligible to be booked in the WMPMA, the VMBA, or the VMMA. | RESPONSE 11 WMP Initiative Unit Original Target Requested Target WMPMA, VMBA or VMMA 2024 Requested Changes Distribution Communications Reliability Improvements (WMP.549) base stations 60 5 WMPMA Standby Power Program (WMP.468) generators 300 58 WMPMA Drone Assessments (WMP.552) inspections 13,500 6,500 WMPMA Distribution Infrared Inspections (WMP.481) inspections 9,532 300 WMPMA Fuels Management (WMP.497) poles 500 150 VMBA/VMMA 2025 Requested Changes Strategic Undergrounding (WMP.473) miles 125 28 WMPMA Covered Conductor (WMP.455) miles 40 50 WMPMA Strategic Pole Replacement Program (WMP.1189) Poles 291 200 WMPMA Transmission OH Hardening Miles 4.64 2 WMPMA Distribution Communications Reliability Improvements (WMP.549) base stations 42 5 WMPMA Drone Assessments (WMP.552) inspections 13,500 6,500 WMPMA Lightning Arrester Removal/Replacement (WMP.550) lightning arresters 1,848 90 WMPMA Connectors, including hotline clamps (WMP.464) hotline clamps 950 100 WMPMA Avian Protection (WMP.972) poles 200 95 WMPMA Expulsion Fuse Replacement (WMP.459) fuses 700 80 WMPMA Detailed Vegetation Inspections (WMP.494) inspections 485,400 255,000 VMBA/VMMA Pole Clearing (WMP.512) poles 33,010 22,000 VMBA/VMMA | Zhenying Shao | 2025-05-15 | 2025-05-21 | 2025-05-22 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-04.pdf | 0 | No | N/A | SDGE 2025 Petition to Amend | N/A | N/A
39 | OEIS | 5 | OEIS-5 | 1 | OEIS-5.1 | Regarding Database(s) Used for Data Storage: On page 288 of its 2026-2028 Base WMP, SDG&E lists the different databases used for data storage among its various enterprise systems. SDG&E indicates several databases that are in use (Oracle, SAP Hana, Azure, AWS, Proprietary Databases, etc.). a. Provide an overview of any data governance plan that SDG&E has in place. b. Provide a description of SDG&E’s ability to migrate data across systems, such as between third-party software and internal proprietary databases, if any. i. If migration of data across systems is not possible, what internal plan does SDG&E have to ensure complete data migration in the future? | a. The Enterprise Data Governance Office provides strategies to promote clean, organized, and easily accessible data. Data governance processes and controls are documented for the enterprise systems leveraged in the WMP Data Platform. The Enterprise Data Catalog is comprised of two main components, SAP Hana and AWS. Collibra, DataZone, and Glue, are used for creating data asset inventories, data stewardship, metadata capture, and governance. The WMP Data Platform provides a centralized data repository that enables consistent, reliable, and automated reporting of mandated OEIS reporting requirements, along with other data consumption needs. Data is ingested into the Data Foundation from multiple Data Sources including asset systems, asset management systems, outage systems, vegetation management systems, and other internal and external systems, enabling one source of truth for the WMP Data Platform. Data Consumption includes regulatory reporting, internal reporting, efficacy studies, and advanced analytics. The Data Governance program ensures WMP data is governed by management oversight, policies and procedures, education, and tool standards. An overview of the WMP Data Platform is in Figure 1 shown below. b. SDG&E has successfully centralized its data from Oracle to SAP HANA. The data is organized using HANA Views, making it easily accessible. SAP HANA is utilized for producing SDG&E’s Quarterly Data Reports and for responding to data requests, demonstrating the system's efficiency and reliability. In addition, we have plans for cloud migration as shown by the annual goals below. This initiative is focused on creating high-quality, reusable solutions that support better, faster decision-making across the board. 2026 Goals: • Establish data migration patterns. • Successfully migrate data sets, including grid hardening, assets, and PSPS/risk events. • Implement data validation, integrity, and governance processes. 2027 Goals: • Execute data integration from the upgraded SAP S/4 HANA platform for ERP, transitioning from the legacy SAP ECC system. • Implement data ingestion processes for the new Transmission SAP S/4 HANA system. • Maintain enterprise data quality standards. 2028 Goals: • Integrate and ingest critical data from all newly implemented systems across the organization. • Establish data pipelines, security protocols, and ETL processes. • Prioritize data quality and system compatibility while maintaining compliance standards. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDG%26E%20Efficacy%20Studies%20Documentation.pdf | 1 | No | 12.2 | 12.2 Summary of Enterprise Systems . | N/A | N/A
40 | OEIS | 5 | OEIS-5 | 2 | OEIS-5.2 | Regarding SDG&E’s response to SDG&E-25U-08: In response to SDGE-25U-08, SDG&E lists findings resulting from its 2024 IR inspections in Table 9-1. In 2024, thermography findings were created on the structures listed in the table below. a. For each structure, indicate in the adjacent columns if the structure was observed by continuous monitoring technology as of April 1, 2024. For each structure that was monitored by any continuous monitoring technology (ARFS, PQ, or other) as of April 1, 2024, indicate whether any inspections were triggered as a result of the continuous monitoring technology, provide the type of inspection that was performed, and provide the date the inspection was performed. Structure ID Monitored By Advanced Radio Frequency Sensors (ARFS) April 1, 2024 (yes/no) Monitored By Power Quality (PQ) Sensors April 1, 2024 (yes/no) Monitored By Other Condition Monitoring Device/Technology as of April 1, 2024 (specify device or technology name) Inspection(s) Triggered By Continuous Monitoring Technology (yes/no) Triggered Inspection Date(s) P192125 P737707 P192259 P479712 P192287 P570385 P11850 P192306 P474064 P201281 P279981 P379031 Z245659 Z731331 P227944 Z118778 Z473088 Z229374 P839538 P734600 P933220 P2135672414 P313295 P2157171985 P174771 | Structure ID Monitored By Advanced Radio Frequency Sensors (ARFS) April 1, 2024 (yes/no) Monitored By Power Quality (PQ) Sensors April 1, 2024 (yes/no) Monitored By Other Condition Monitoring Device/Technology as of April 1, 2024 (specify device or technology name) Inspection(s) Triggered By Continuous Monitoring Technology (yes/no) Triggered Inspection Date(s) P192125 No Yes* No No N/A P737707 No Yes* No No N/A P192259 No Yes* No No N/A P479712 No Yes* No No N/A P192287 No Yes* No No N/A P570385 No Yes* No No N/A Structure ID Monitored By Advanced Radio Frequency Sensors (ARFS) April 1, 2024 (yes/no) Monitored By Power Quality (PQ) Sensors April 1, 2024 (yes/no) Monitored By Other Condition Monitoring Device/Technology as of April 1, 2024 (specify device or technology name) Inspection(s) Triggered By Continuous Monitoring Technology (yes/no) Triggered Inspection Date(s) P11850 No Yes* No No N/A P192306 No No No N/A N/A P474064 No Yes* No No N/A P201281 No Yes* No No N/A P279981 No Yes* No No N/A P379031 No Yes* No No N/A Z245659 No Yes* No No N/A Z731331 No Yes No No N/A P227944 No Yes No No N/A Z118778 No Yes* No No N/A Z473088 No Yes* No No N/A Z229374 No Yes* No No N/A P839538 No Yes* No No N/A P734600 No Yes* No No N/A P933220 No No No N/A N/A P2135672414 No Yes No No N/A P313295 No Yes* No No N/A P2157171985 No Yes* No No N/A P174771 No Yes* No No N/A * Monitor is at the substation bank or bus level and does not distinguish between circuits | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | SDG&E findings resulting from its 2024 IR inspections in Table 9-1 | N/A | N/A
41 | OEIS | 5 | OEIS-5 | 3 | OEIS-5.3 | Regarding Continuous Monitoring Technology Deployment: a. Provide the total number of structures in SDG&E’s HFTD/HFRA. b. Provide the number of structures in SDG&E’s HFTD/HRA continuously monitored by both PQ sensors and ARFS as of Jan 1, 2025. c. Provide the number of structures in SDG&E’s HFTD/HFRA continuously monitored by PQ sensors but not ARFS as of Jan 1, 2025. d. Provide the number of structures in SDG&E’s HFTD/HFRA continuously monitored by ARFS but not PQ sensors as of Jan 1, 2025. e. List any other continuous monitoring sensors or technologies deployed by SDG&E that have been used or are planned for use to inform grid inspections and/or corrective grid work. | a. 85,639 distribution structures in the HFTD b. 6,932 distribution structures in the HFTD monitored by both PQ and ARFS c. 59,445 distribution structures in the HFTD monitored by PQ but not ARFS d. 7,649 distribution structures in the HFTD monitored by ARFS but not PQ e. The EFD Program aims to utilize the PQ and ARFS monitoring technologies to detect and prevent significant equipment failures in order to address fire risk while also gaining the benefits of reducing customer forced outages. Sensors that are a part of this program have the potential to be used to inform grid inspections and/or corrective grid work. To accomplish this SDG&E is looking at the process changes needed to integrate the two processes that are currently separate. At this time the integration is still in its early stages. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | Continuous Monitoring Technology Deployment | N/A | N/A
42 | OEIS | 5 | OEIS-5 | 4 | OEIS-5.4 | Regarding Inspections Trigged by Continuous Monitoring Technology: a. Describe the process for initiating an inspection due to ARFS data. Include how assets are flagged for potential inspection, confirmed for inspection, the type of inspection is determined (i.e. patrol, infrared, detailed), and the inspection due date is determined. i. Provide supporting documentation including written processes, guidance, and/or job aids related to initiating and performing inspections as a result of ARFS data. b. Describe the process for initiating an inspection due to PQ sensor data. Include how assets are flagged for potential inspection, confirmed for inspection, the type of inspection is determined (i.e. patrol, infrared, detailed), and the inspection due date is determined. i. Provide supporting documentation including written processes, guidance, and/or job aids related to initiating and performing inspections as a result of PQ sensor data. c. Provide the total number of inspections initiated in 2024 as a result of ARFS data. i. Provide the number of such inspections that resulted in level 1 findings. ii. Provide the number of such inspections that resulted in level 2 findings. d. Provide the total number of inspections initiated in 2024 as a result of PQ sensor data. i. Provide the number of such inspections that resulted in level 1 findings. ii. Provide the number of such inspections that resulted in level 2 findings. | a. SDG&E receives a bi-monthly report from the manufacturer of ARFS equipment containing locations of interest with data showing RF energy dispersion signal groupings. After analyzing that data, SDG&E will issue a patrol for any locations with a concerning amount of disturbance energy. The patrol is performed by SDG&E’s drone pilots, who capture high-resolution images from all angles of the location in question. Additionally, the drone pilot may capture infrared images of the location in question. Images are reviewed, then the asset is field verified by an engineer and a qualified electrical worker to determine severity and remediation work needed. Drone inspections are typically completed within two weeks of issuance, depending on resource availability. Currently there is no formal documentation of this process as this is still in the R&D space and SDG&E is continually improving and altering the process. b. SDG&E received a weekly report of all new precursor events captured by PQ sensors. This data is then reviewed by engineers to determine severity and if a known location can be identified. For overhead-related assets, the same process described in item 4a is followed. For underground-related assets, the engineer will issue an underground patrol request to be completed by a qualified electrical worker. Underground patrols involve a visual inspection as well as an infrared camera to locate hot connections. Depending on findings, remediation work is determined by the field personnel. Underground patrols are requested to be completed within three days. Currently there is no formal documentation of this process as this is still in the R&D space and SDG&E is continually improving and altering the process. c. 40 inspections initiated in 2024 as a result of ARFS data i. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 1 findings. ii. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 2 findings. d. 20 inspections initiated in 2024 as a result of PQ data i. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 1 findings. ii. Due to the focus of the EFD program not being compliance, SDG&E currently does not track level 2 findings. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | Inspections Trigged by Continuous Monitoring Technology: | N/A | N/A
43 | OEIS | 5 | OEIS-5 | 5 | OEIS-5.5 | Regarding Transmission Inspection QA/QC a. Provide a copy of SDG&E document TCM 807, Section 5.2: Condition Assessment, Version 8G. | See attached document titled “TCM807 Version 8G Section 5.2-Condition Assessment.pdf.” | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/TCM807%20Version%208G%20Section%205.2-Condition%20Assessment.pdf | 1 | No |  | #N/A |  | #N/A
44 | OEIS | 5 | OEIS-5 | 6 | OEIS-5.6 | Regarding Weather Station Maintenance and Calibration In section 10.5.5 of the Wildfire Mitigation Plan Guidelines on page 136, the utility companies must provide an “acceptable percentage of weather station outages as defined by the electric corporation.” Page 252 of the 2026-2028 Base SDG&E WMP Submission states, “although SDG&E does not have a set acceptable outage percentage, the stations have consistently maintained a 99 percent communication rate.” a. Provide an acceptable percentage of weather station outages in which SDG&E will still be able to operate without an increase in risk or impact to the PSPS decision making as outlined in the Wildfire Mitigation Plan Guidelines. i. If SDG&E cannot provide what percentage of weather station outages is defined as acceptable, provide an explanation why it cannot. | SDGE weather stations have consistently maintained a 99 percent communication rate. SDG&E does not have a set acceptable outage percentage because it is nearly impossible to ascertain an acceptable percentage. All weather stations operate independently of distribution circuits and are powered by batteries that are recharged by solar panels. Each high-risk circuit has a weather station associated with that circuit. However, some circuits are very long and have multiple weather stations associated with that circuit. Additionally, not all areas of the HFTD are affected the same way during Santa Ana wind events. Thus, picking weather stations that are inconsequential because other circuit associated stations that could be used as a proxy is event and weather dependent and cannot be answered in a holistic manner. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 10.5 | 10.5 Weather Forecasting | 10.5 | 10.5 Weather Forecasting
45 | OEIS | 5 | OEIS-5 | 7 | OEIS-5.7 | Regarding Vegetation Inspections and Pole Clearing Targets: Page 104 of the Wildfire Mitigation Plan Guidelines states “Targets for inspection activities (programs) of overhead electrical assets must use circuit miles as the unit.” a. Provide all quarterly and year-end targets from Table 9-2 for the following programs in circuit miles: i. Detailed Inspection (WMP.494) ii. Off-Cycle Patrol (WMP.508) | Targets by circuit mile are provided below. Historically, Detailed Inspections have been reported by inspections complete, and Off-Cycle Patrol by Vegetation Management Area (VMA) complete. While able to pivot and report by circuit line mile, this unit of measure provides a less granular understanding of the work completed. SDG&E will comply with updating to the new unit requirement in the 2026-2028 WMP and associated QDR data tables when OEIS allows a mechanism to do so. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | N/A | Vegetation Inspections and Pole Clearing Targets | N/A | N/A
46 | OEIS | 5 | OEIS-5 | 8 | OEIS-5.8 | Regarding Vegetation Management QA/QC Pass Rate Targets: On page 224 of its 2026-2028 Base WMP, SDG&E targets a 90% pass rate for its “Quality assurance/quality control of Vegetation Management” (WMP.505) initiative. On page 290 of its 2023-2025 Base WMP, SDG&E targets a pass rate of 95% for all three of its QA/QC audits. SDG&E states that in 2022 it achieved a pass rate of 94% for pre-inspection, 99% for tree trimming, and 97% for pole clearing activities. a. Explain why SDG&E has lowered its pass rate target for QA/QC in its 2026-2028 Base WMP. b. Describe any obstacles to SDG&E increasing the QA/QC pass rate target each year from 2026-2028 (e.g., need for additional training, longer time to complete vegetation management work, human error, etc.). | a. After further review of historical QA/QC findings and pass rates, SDG&E determined that a 90% pass rate is a reasonable and representative target and threshold for work quality performance of the vegetation management contractors. b. SDG&E anticipates no obstacles to potentially increasing its QA/QC pass rate target in the future. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 9.11 | 9.11 Quality Assurance and Quality Control of Vegetation Management (WMP.505) | 9.11.1 | 9.11.1 Overview, Objectives, and Targets
47 | OEIS | 5 | OEIS-5 | 9 | OEIS-5.9 | Regarding the Granularity of Priority Levels in Past Due Vegetation Management Work Orders: On page 228 of its 2026-2028 Base WMP, SDG&E categorizes past due work orders by “Low Priority” and “High Priority.” On page 227 of its 2026-2028 WMP, SDG&E sets work completion timelines for routine pruning and removal of “60 to 120 days following inspections,” and “Memo” work order timelines of “the same day the condition is observed, the next day, or within 30 days.” a. Complete the table below, in the format of Table 9-8, to disaggregate low and high priority past due pruning and removal work into the following priority levels: 60-120 days, within 30 days, next day, same day. Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels Priority Level 0-30 Days 31-90 Days 91-180 Days 181+ Days 60-120 Days Within 30 Days Next Day Same Day | Priority Level 0-30 Days 31-90 Days 91-180 Days 181+ Days 60-120 Days 335 242 4 1 Within 30 Days 40 12 2 0 Next Day 0 0 0 0 Same Day 0 0 0 0 | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 9.12 | 9.12 Work Orders | 9.12.3 | 9.12.3 Trends .
48 | OEIS | 5 | OEIS-5 | 10 | OEIS-5.10 | Regarding SDG&E’s Pole Clearing Program: On page 213 of its 2026-2028 Base WMP, SDG&E states, "The determination to stop clearing poles with exempt equipment was made due to the evaluation of cost efficiencies,environmental impacts, impacts to customers, and the general absence of ignition data associated with exempt equipment." a. Did SDG&E consult with other electrical corporations before deciding to stop clearing vegetation around poles with Public Resource Code (PRC) 4292 exempt equipment? i. List all electrical corporations that SDG&E consulted in making this decision. ii. Provide summaries of any discussions with these electrical corporations that informed SDG&E’s evaluation and decision-making process. iii. Did SDG&E request ignition data associate with PRC 4292 exempt equipment from other electrical corporations? 1. If ignition data was requested, provide a summary of the ignition data received from each electrical corporation SDG&E consulted. iv. If SDG&E did not consult with other electrical corporations, explain why. b. Provide the ignition data that was used to support SDG&E's claim that there is a general absence of ignition data associated with PRC 4292 exempt equipment. i. What time period did the ignition data cover? ii. How many ignitions, if any, were identified as being associated with PRC 4292 exempt equipment? c. Were customer opinions solicited or considered when evaluating the customer impacts of clearing vegetation around poles with PRC 4292 exempt equipment? i. If so, provide a summary of the customer feedback received regarding this activity. ii. If customer input was not solicited, explain the basis of SDG&E’s determination that clearing vegetation around PRC 4292 exempt equipment has customer impacts. d. Were environmental experts or formal assessments used in evaluating the environmental impacts of clearing vegetation around poles with PRC 4292 exempt equipment? i. If so, provide a summary of the findings from those environmental assessments regarding this activity. ii. If environmental experts or assessments were not used, explain SDG&E’s decision-making process for determining that clearing around PRC 4292 exempt poles has environmental impacts. | a. SDG&E did not directly consult with other electrical corporations before deciding to stop clearing vegetation around poles with exempt PRC 4292 equipment. i. NA ii. NA iii. NA 1. NA iv. SDG&E did not consult with other electrical corporations on this decision based on the differences in the geography, topography and vegetation types between the service territories, and the internal considerations specific to SDG&E (e.g., cost efficiencies, no known prior ignitions associated with exempt hardware, additional environmental review). A primary driver for SDG&E stopping the clearing of vegetation around poles is based on Cal Fire’s classification of the equipment as exempt which was determined through field testing. b. As required by the CPUC, utilities must report ignitions involving their equipment that meet the criteria per D.14-02-015. Please see https://www.cpuc.ca.gov/industries-and-topics/wildfires for the ignition data related to SDG&E. i. The time-period the data ignition covers is 2014-2024. ii. There were no ignitions that were directly associated with PRC 4292 exempt equipment. c. Customers were not separately and specifically solicited when SDG&E evaluated the impacts of clearing vegetation around poles with PRC 4292 exempt equipment. However, customer impacts are derived through historical, anecdotal interactions with Vegetation Management, and are described further below in response to Question ii. i. NA ii. Customers can be impacted by vegetation clearing for PRC 4292 in multiple ways. 1) Customers often must provide physical access to a property for the contractor to perform pole clearing; 2) Pole clearing often requires two or more visits annually to a property for mechanical, herbicide, and/or re-clear activities; 3) Post-clearing audit activities may necessitate additional property visits by the contractor; 4) Pole clearing requires removal of vegetation down to bare mineral soil within a 10 foot radius, and the removal of tree branches within the radius up to the height of the conductors. Ground clearing could promote soil erosion at the base of the pole and would require the removal of healthy landscaping maintained by the customer. These impacts are a necessary result of pole clearing where required by law, however, they can be seen as an unnecessary burden to customers where it’s not required by law. d. Yes. All poles that receive pole brushing for PRC 4292 are annually screened for environmental and cultural review. i. Please see attached document titled, “OEIS-2025-05_Q10(d)(i)_Redacted.pdf”. SDG&E is providing an example of an annual environmental release for poles that are scheduled for pole brushing. SDG&E is providing a redacted version that contains personal names and phone numbers that are not directly relevant to the question. ii. N/A | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2025-05_Q10%28d%29%28i%29_Redacted.pdf | 1 | No | 9.4 | 9.4 Pole Clearing (WMP.512) | 9.4.4 | 9.4.4 Updates .
49 | OEIS | 5 | OEIS-5 | 11 | OEIS-5.11 | Regarding SDG&E’s Pole Clearing Target (WMP.512): On page 208 of its 2026-2028 Base WMP, SDG&E sets annual targets in 2026, 2027, and 2028 of 22,000 poles. On page 257 of its 2023-2025 Base WMP, SDG&E set annual targets for 2023, 2024, and 2025 of 33,010 poles. The delta between SDG&E’s targets in the 2026-2028 Base WMP and SDG&E’s 2023-2025 Base WMP is 11,010 poles. On page 211 of its 2026-2028 Base WMP, SDG&E states that “Since the 2023-2025 Base WMP, SDG&E has ceased performing pole clearing on poles with exempt equipment, such as hotline clamps (HLC).” a. Of the 11,010 poles that SDG&E no longer plans to clear, provide the number of those poles that hold exempt equipment and do not hold any non-exempt equipment. b. If some of the 11,010 poles that SDG&E no longer plans to clear hold non-exempt equipment, describe the other operational decisions that led to SDG&E’s plan to no longer clear these poles. c. Provide details of any risk reduction measures that will compensate for the reduced volume of pole clearing work. | a. All 11,010 of the poles SDG&E no longer plans to clear hold exempt equipment. b. N/A. See response to a. above. c. The risk reduction measures that compensate for the reduced volume of pole clearing work include locations where non-exempt hardware is replaced by exempt hardware. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 9.1 | 9.1 Targets. | 9.1.2 | 9.1.2 Quantitative Targets .
50 | OEIS | 5 | OEIS-5 | 12 | OEIS-5.12 | Regarding SDG&E’s Early Fault Detection Third Party Evaluation: In its response to the Early Fault Detection Implementation (SDGE-25U-05) ACI on page 32 of Appendix D in SDG&E's 2026-2028 WMP, SDG&E stated: "A third party was engaged to evaluate its effectiveness, and based on their analysis, several changes were implemented to accommodate system tracing and ensure the accurate coverage of the installed devices." a. Provide a copy of this third-party evaluation and analysis. b. Provide a summary of the types of issues missed that resulted in the ten false negatives. | A. See attached PDF document titled “EFD Study Document.pdf” for the early fault detection third-party evaluation and analysis. b. SDGE found the below 10 false negative with EFD devices. Issue# Outage ID Circuit Cause 1 220223E253449 211 Wire slap/pole down/wire down (severe weather) 2 230601E286128 350 Pole - contact/damage/broke/rotted/on fire 3 230316E280845 445 Arrester failure 4 230113E276229 448 Crossarm failure/contact 5 230111E276108 448 Hardware failure 6 230731E290189 448 Transformer (station) failure/contact 7 230607E286603 524 OH connector failure (jumper/splice/squeeze-on) 8 240613E313709 211 Pole - contact/damage/broke/rotted/on fire 9 240319E307337 350 Transformer (station) failure/contact 10 240109E301776 217 Cutout failure | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/EFD%20Study%20Document.pdf | 1 | No | Appendix D | Areas for Continued Improvement | N/A | N/A
51 | OEIS | 5 | OEIS-5 | 13 | OEIS-5.13 | Regarding SDG&E’s Risk Reduction in OEIS Table 8-1: Energy Safety’s understanding of the expected risk reduction for the activities is Section 8 Grid Design & System Hardening and Grid Operations reported in OEIS Table 8-1 of SDG&E's 2026-2028 WMP is currently calculated at a segment/circuit level in which work is being completed. However, the expected risk reduction to be reported in Table 8-1 should reflect the reduction in SDG&E's overall wildfire and PSPS risk – in other words, the impact of each activity on the enterprise-wide risk. a. Is the expected risk reduction for activities reported in OEIS Table 8-1 calculated at a segment/circuit level in which work is being completed? If not, explain how SDG&E calculated the expected risk reduction values in Table 8-1. b. Provide the updated risk reduction percentages for each activity reported in OEIS Table 8-1 for the years 2026, 2027, and 2028, calculated at the overall enterprise level. c. Provide the updated expected risk reduction percentages for each activity reported in OEIS Table 6-3 using the same update to the calculation as Table 8-1 in part (b). | a) The expected risk reduction for activities reported in OEIS Table 8-1 are calculated at a segment level on which activity is going to be completed in the WMP years 2026-2028. b) Please refer to the attached spreadsheet titled “2026_OEIS Guideline Tables.xlsx” for updated table 8-1 risk reduction. c) Please refer to the attached spreadsheet titled “2026_OEIS Guideline Tables.xlsx” for updated table 6-3 risk reduction. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/2026_OEIS%20Guideline%20Tables.xlsx | 1 | No | OEIS Table 8-1 | 8-1: Grid Design, Operations, and Maintenance Targets by Year 126 | N/A | N/A
52 | OEIS | 5 | OEIS-5 | 14 | OEIS-5.14 | Regarding OEIS Table 6-4: a. Provide an updated version of OEIS Table 6-4 (SDG&E’s 2026-2028 Base WMP, p. 116; and Appendix F, pp. 58-73) via Excel with the following additional columns for each circuit/circuit segment: i. Total Circuit Mileage Undergrounded as of EOY 2025 ii. Total Circuit Mileage of Covered Conductor as of EOY 2025 iii. Total Circuit Mileage Planned for Undergrounding (for 2026, 2027, and 2028, respectively) iv. Total Circuit Mileage Planned for Covered Conductor (for 2026, 2027, and 2028, respectively) | Please refer to the attached spreadsheet titled “2026_OEIS Guideline Table 6-4.xlsx” for the updated OEIS 6-4 Table with the additional requested columns included. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/2026_OEIS%20Guideline%20Table%206-4.xlsx | 1 | No | OEIS Table 6-4 | 6-4: Summary of Risk Reduction for Top-Risk Circuits .. 116 | N/A | N/A
53 | OEIS | 5 | OEIS-5 | 15 | OEIS-5.15 | Regarding OEIS Table 6-1: a. Provide the total overall utility risk value used to calculate the percentage of overall utility risk percentages shown in OEIS Table 6-1 (SDG&E’s 2026-2028 Base WMP, p. 84 Appendix F, pp. 12-55) b. Provide an updated version of OEIS Table 6-1 via Excel with the following additional columns for each circuit/circuit segment: i. Safety Risk Score Component of Wildfire Risk Score ii. Reliability Risk Score Component of Wildfire Risk Score iii. Financial Risk Score Component of Wildfire Risk Score iv. PSPS Risk Score v. PEDS Risk Score | a) The percentage of overall utility risk is calculated from the total overall utility risk across the full territory, which includes circuit-segments that do not have overhead in the HFTD territory. These were not included in the OEIS 6-1 Table, since SDG&E’s risk prioritization is focused primarily in the HFTD territory. The total overall utility risk value calculated from the full list of circuit-segments in the territory is $3,032,480,966. b) Please refer to the attached spreadsheet titled “2026_OEIS Guideline Table 6-1.xlsx” for the updated OEIS 6-1 Table with the additional requested columns included. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf https://www.sdge.com/sites/default/files/regulatory/2026_OEIS%20Guideline%20Table%206-1.xlsx | 1 | No | OEIS Table 6-1 | 6-1: List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk 84 | N/A | N/A
54 | OEIS | 5 | OEIS-5 | 16 | OEIS-5.16 | Regarding OEIS Table 6-3: a. Provide a detailed explanation of the analysis used to calculate the activity effectiveness for each activity in OEIS Table 6-3 (SDG&E’s 2026-2028 Base WMP, pp. 111-112). Include copies of any relevant workpapers and supporting documentation used for this analysis. b. Provide a detailed explanation of the analysis used to calculate expected % risk reduction for each activity in OEIS Table 6-3. Include copies of any relevant workpapers (i.e. the “CCC Risk & Cost Benefit” Excel sheet) and supporting documentation used for this analysis. | a) Please see attached PDF titled “SDG&E Efficacy Study Documentation.pdf” for effectiveness calculation explanation. b) Please refer to Appendix G of WMP 2026-2028 for detail % risk reduction calculation, which is available on SDG&E’s 2026-2028 WMP website at: https://www.sdge.com/2026-2028-wildfire-mitigation-plan. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | OEIS Table 6-3 | 6-3: Risk Impact of Activities .. 111 | N/A | N/A
55 | OEIS | 5 | OEIS-5 | 17 | OEIS-5.17 | Regarding SDG&E’s Mitigation Initiative Prioritization On page 100 of SDG&E’s 2026-2028 Base WMP, in Figure 6-2, SDG&E depicts a flowchart showing its high-level mitigation prioritization. a. As part of the “develop draft hardening scope” portion, SDG&E includes a bullet point to “Optimize survey.” Describe what is included in this step of prioritization and provide any supporting documentation and procedures outlining this step. b. SDG&E includes a step to “prioritize Wildfire Risk reduction benefit” as part of developing its draft hardening scope. Describe what factors and thresholds are used as part SDG&E’s measuring and determining reduction benefit and provide any supporting documentation and procedures. c. SDG&E includes a step to determine whether “hardening scoping plan ready for release.” Describe what instances would lead to a “no” at this step and therefore run through development of a draft hardening scope and review again. | See updated Figure 6-2: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk as submitted in the WMP substantive and non-substantive errata, which is available on the OEIS docket as well as SDG&E’s website at https://www.sdge.com/2026-2028-wildfire-mitigation-plan. a. “Optimize survey” was removed from the figure as it is not a primary consideration in this step of prioritization. Rather, SDG&E evaluates the advantages of “bundling” the hardening of upstream feeder segments to optimize PSPS risk reduction and leverage economies of scale by reducing permitting and mobilization costs b. “Prioritize Wildfire Risk reduction benefit” was modified to be “Analyze Wildfire, PSPS, and PEDS risk reduction benefit.” The primary drivers for selecting a circuit-segment mitigation project are wildfire risk (a direct output from WiNGS-Planning) and the PSPS de-energization history and risk of the circuit. The PSPS review considers both upstream and downstream topography, wind speeds, and recommended mitigations to optimize the overall mitigation plan for the circuit. The WiNGS-Planning model is used to calculate wildfire, PSPS, and PEDS risk used in the aggregated overall wildfire and overall outage program risk components. The model estimates the baseline risk and quantifies the expected risk reduction for both Combined Covered Conductor and Strategic Undergrounding for each feeder segment. For more details around prioritization analysis and ranking of circuit-segments, see Section 6.1.2 Risk-Informed Prioritization. c. Subject matter expertise review may identify projects or components of projects that are infeasible. For example, covered conductor installation is not permitted above certain elevations due to the negative impacts of ice loading. Another example may include property ownership, land access, or environmental constraints that require significant revisions to the routing of a proposed SUG project. | Zhenying Shao | 2025-05-16 | 2025-05-21 | 2025-05-21 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-05_0.pdf | 0 | No | 6.1.3.2.5 | Activity Prioritization | 6.1.3.2.6 | Mitigation Initiative Prioritization to Reduce Wildfire and PSPS Risk
56 | OEIS | 6 | OEIS-6 | 1 | OEIS-6.1 | Regarding Injuries/Fatalities Conversion: Page 53 of SDG&E's 2026-2028 Base WMP, “OEIS Table 5-4: Summary of Risk Models,” notes that SDG&E uses “number of acres burned conversion factors to estimate the number of serious injuries and fatalities from customers impacted.” However, page 38 of SDG&E’s 2026-2028 Base WMP, “SDGE Table 5-4: Attributes for Wildfire Consequence,” notes that SDG&E uses a fatalities per structure destroyed factor. a. Clarify if the injuries/fatalities conversion is based on acres burned (per OEIS Table 5-4) or structures destroyed (per SDGE Table 5-4). Explain the differences between the factors in each table. | The data presented in OEIS Table 5-4 is incorrect and should be revised to align with the information provided in SDG&E’s Table 5-4. In previous versions, Technosylva outputs included only estimates of acres burned and structures impacted. However, the latest model output now provides estimates for both acres burned and structures destroyed. Estimates of structures destroyed are used to estimate the number of serious injuries and fatalities. | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | 5.4 | 5.4 Summary of Risk Models . | N/A | N/A
57 | OEIS | 6 | OEIS-6 | 2 | OEIS-6.2 | Regarding Monte Carlo Simulations: On page 46 of SDG&E's 2026-2028 Base WMP, SDG&E notes that Monte Carlo simulations are used to assess risk outcomes on the grid. On page 3 of “Appendix D: Areas for Continued Improvement,” SDG&E describes the intent of the Monte Carlo simulations, but methods are not provided in “Appendix B: Supporting Documentation for Risk Methodology and Assessment.” a. Provide a detailed description of the methodology and framework for Monte Carlo simulations used within SDG&E’s risk modeling. Include any documentation, procedures, and policies which describe the methods. | For a detailed description of the Monte Carlo simulation methodology used in SDG&E’s Wildfire and PSPS risk modeling framework, please see the 2025 Risk Assessment and Mitigation Phase (RAMP), SDGE-4 Wildfire and PSPS, Section III: “Pre-Mitigation Risk Value”, starting on page 16. This section outlines the structure, assumptions, and implementation of Monte Carlo simulations as applied to SDG&E’s risk assessment processes. The document includes relevant methodological details and supports the statements made in the 2026–2028 Base WMP and its appendices. The full document is publicly available at the following link: https://www.sdge.com/sites/default/files/regulatory/SDG%26E%20-Risk-4%20Wildfire%20%26%20PSPS_0.pdf | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | 5.3 | 5.3 Risk Scenarios . | N/A | N/A
58 | OEIS | 6 | OEIS-6 | 3 | OEIS-6.3 | Regarding WiNGS-Ops Consequence Risk Metrics: On page 47 of SDG&E's 2026-2028 Base WMP, SDG&E notes that the WiNGS-Ops visualization platform displays the worst-case estimates of acres burned. a. Is the only consequence risk metric for WiNGS-Ops acres burned? i. If yes, discuss why other consequence risk metrics are not used. ii. If not, provide a list of other consequence risk metrics used. b. Provide a detailed description of how the safety, reliability, and financial attributes for consequence are displayed and analyzed for operations. | a. No, users of the WiNGS-Ops visualization platform have the ability to toggle between estimates of acres burned and buildings destroyed. While SDG&E receives additional estimates from Technosylva that are stored in SDG&E’s database, only these two metrics are displayed in the platform. Additionally, users can select and view estimates from different times across multiple days to visualize consequence estimates at different points in time. b. Currently, Safety, Reliability, and Financial consequence estimates are not displayed or utilized in operational decision-making during PSPS activations under extreme fire weather conditions. However, an overall risk score, based on the now-obsolete MAVF, is still presented. SDG&E anticipates transitioning WiNGS-Ops to incorporate monetized values by the end of Q3 2025. Operational decisions involve an assessment by a cross-functional team of SMEs (including Meteorology, Electric Commodity Liaisons, Risk Analytics, Emergency Management, Electric Operations, and others) through the analysis of dynamic information, such as detailed meteorological forecasts, real-time observed weather conditions, local fuel conditions, situational awareness, and the following risk modeling outputs from WiNGS-Ops. The following details how information that allows for the assessment of potential wildfire consequences is currently displayed in WiNGS-Ops and reviewed during a PSPS event, as detailed in processes like those outlined in Section 2 of SDG&E's PSPS Post-Event Reports 1. • Dynamic Risk Modeling Outputs: o Information from the WiNGS-Ops tool provides evolving wildfire and PSPS risk estimates. It is important to note that WiNGS-Ops operates based on a set of defined enterprise and event-specific assumptions (as mentioned in Section 2.4 of the Post-Event Report), which are continuously reviewed and refined. Wildfire risk is calculated based on forecasted weather conditions. o The wildfire consequence estimates incorporate the outputs of Technosylva Fire-Sight, which takes into account weather variables, advanced fuel layers, and an 8-hour unsuppressed fire spread model and provides detailed insights into potential fire behavior, spread, and impact under the forecasted weather conditions. For more information around how Safety, Reliability, and Financial attributes are considered in SDG&E’s risk analysis framework, see Section 5.2.2.2.1 of SDG&E’s 2026-2028 Wildfire Mitigation Base Plan. | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | 5.3 | 5.3 Risk Scenarios . | N/A | N/A
59 | OEIS | 6 | OEIS-6 | 4 | OEIS-6.4 | Regarding Technical Documentation for Risk Models: a. On page 49 of SDG&E's 2026-2028 Base WMP, SDG&E mentions the “statistical and machine learning models detailed in Appendix B,” but Appendix B lacks documentation on these models. Provide technical documentation for the statistical and machine learning models used for Wings-Planning and Wings-Ops models. b. On page 61 and 62 of SDG&E's 2026-2028 Base WMP, SDG&E mentions usage of Amazon Web Services (AWS). Provide technical documentation showing how and where SDG&E uses AWS in its statistical and machine learning models used for Wings-Planning and Wings-Ops. | a. Refer to “Appendix B Table – Detailed Model Documentation_5_23_25” excel spreadsheet with detailed information about the models. b. Amazon Web Services (AWS) is used at each layer of the data science lifecycle outside of the initial business problem identification. For Data Collection, WiNGS Ops and WiNGS planning both leverage SDGE's internal AWS based data mesh. In this system distributed AWS accounts generate data through Athena / DataZone the WMP teams can discover, gather, and consume data for each model. This system is used in conjunction with flat files and other data sources to form the inputs to both models. After collecting from external sources, data is then stored in S3 within AWS. For Data Cleaning and Preparation programming languages like Python, along with domain-specific programming languages like SQL are used to clean and prepare data. These preparations leverage AWS resources like Glue, and Sagemaker processing jobs to efficiently deliver clean data for EDA. This step is done as a hybrid approach leveraging both AWS resources and local development. For Exploratory Data Analysis (EDA), Sagemaker studio is used to consume cleaned data and create model features. Additionally, the Modeling step also leverages the Sagemaker Model Registry and various additional Sagemaker features. These two steps are also done as a hybrid approach leveraging both AWS resources and local development For Deployment and Monitoring this is done through 3 AWS accounts separated into development, quality assurance, and production. Automated testing is performed using dbt, glue failurenotifications, and additional monitoring. These steps are done purely through AWS although some monitoring is done in external BI tools like Microsoft's Power BI Our front end for both WiNGS Ops and Wings Planning also leverages AWS. We deliver each model as an S3 single-page website (or S3 static website). We use additional AWS services like route53, cognito user groups, and API gateways for traffic, access, and data delivery. See attached document titled “OEIS-P-WMP_2025-SDGE-06_Q4_WINGS.pdf.” Pade 2 is related to Wings Ops. Slide 3 is related to WiNGS Planning. Slide 3 is related to WiNGS Front-End. | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf https://www.sdge.com/sites/default/files/regulatory/Appendix%20B%20Table%20-%20Detailed%20Model%20Documentation_5_23_25.xlsx https://www.sdge.com/sites/default/files/regulatory/OEIS-P-WMP_2025-SDGE-06_Q4_WINGS.pdf | 2 | No | 5.3 | 5.3 Risk Scenarios . | 5.3.1 | 5.3.1 Design Basis Scenarios
60 | OEIS | 6 | OEIS-6 | 5 | OEIS-6.5 | Regarding Design Scenarios: a. On page 49 of SDG&E's 2026-2028 Base WMP, SDG&E mentions that it uses a 2-year history for historical weather and fuel data. Describe why a longer weather history is not used. Include any supporting analysis and documentation showing how and why SDG&E chose to use a 2-year history. b. Page 50 of SDG&E's 2026-2028 Base WMP, “OEIS Table 5-2: Summary of Design Scenarios,” mentions the "WV1" scenario ID. i. Specify if this WV1 scenario ID is intended to address "Weather Condition 1" from the WMP Guidelines. ii. If it is not, discuss: (1) Why SDG&E includes “WV1” as a design scenario. (2) How “WV1” differs from “Weather Condition 1.” (3) How “Weather Condition 1” is otherwise captured within the design scenarios in OEIS Table 5-2, or why it is excluded. | a. SDG&E’s use of a 2-year historical period for weather and fuel data in its 2026–2028 Base WMP is primarily driven by computational constraints. The modeling and simulation processes that support wildfire mitigation planning, particularly those involving hourly wind gust estimates, fuel conditions, and fire behavior, are extremely resource-intensive. Extending the historical period would substantially increase the volume of data to be processed, resulting in longer runtimes and significantly higher computational demands. These limitations have constrained the development, validation, and refinement of risk models within the required timelines. The two years selected for weather analysis were chosen as representative years because they reflect a range of fire weather conditions and fuel states that are representative of recent trends in SDG&E’s service territory. These years include periods of elevated fire risk, including extreme wind events and dry fuel conditions, which are critical for evaluating the effectiveness of wildfire mitigation strategies. The two selected years are also incorporated into a broader Monte Carlo simulation framework. To account for the natural variation in extreme weather conditions, SDG&E integrates weather conditions from those years with a set of 125 extreme fire weather days spanning 2013-2022. The conditions from these days are sampled in alignment with the historical average of approximately16 high fire-risk days per year in SDG&E’s service territory. This approach ensures that the model realistically reflects both the frequency and distribution of extreme weather events. b. i. Yes, Scenario ID WV1 models anticipated weather conditions within the service territory as defined by the “Weather Condition 1” scenario detailed from the WMP guidelines Section 5.3.1. Design Basis Scenarios, leveraging historical data from two representative years to inform ignition probability modeling results. While this approach captures short-term weather variability, longer-term and more extreme risk scenarios are incorporated through a Monte Carlo simulation. This probabilistic framework enables the assessment of a broader distribution of potential outcomes, including high-consequence events that extend beyond the range of historically observed weather conditions. ii. N/A | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | 5.3 | 5.3 Risk Scenarios . | 5.3.1 | 5.3.1 Design Basis Scenarios
61 | OEIS | 6 | OEIS-6 | 6 | OEIS-6.6 | Regarding AFN Scaling Factors: Page 53 of SDG&E's 2026-2028 Base WMP, “OEIS Table 5-4: Summary of Risk Models,” notes the input of "Scaling factors for AFN customer impacts." a. Clarify if SDG&E uses scaling based on AFN for PSPS consequences only, or for wildfire consequences as well. | AFN Customer scaling is applied only to PSPS Consequence calculations (safety attribute) and not for Wildfire Consequence. Wildfire Consequence simulations are performed by Technosylva and do not include population demographics, including but not limited to AFN customer types. Specific customer counts and type demographics is a data source tied to customer meters maintained by SDG&E. | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | 5.4 | 5.4 Summary of Risk Models . | N/A | N/A
62 | OEIS | 6 | OEIS-6 | 7 | OEIS-6.7 | Regarding Proposed Updates to the HFTD: On page 59 of SDG&E's 2026-2028 Base WMP, SDG&E states: “To date, SDG&E has not suggested any adjustments to the HFTD. Recent modeling initiatives evaluated the wildfire risk of coastal canyons and the WUI for mitigation. Both efforts resulted in the exclusion of each proposed addition.” a. SDG&E also states that “The analysis found that wildfire risk associated with coastal canyons was lower than that associated with current HFTD segments.” Provide a detailed description of the analysis performed, and associated documentation and conclusions demonstrating the lower wildfire risk, including any associated risk scores in comparison to those within the HFTD. b. For analysis of the WUI, SDG&E also states that “While this layer may serve to prioritize the adjacent developed areas for fire infrastructure and suppression planning, it does not yield a usable layer for identifying areas where an energized wire down could spark a wildfire, or areas at heightened risk for ignition due to interference from vegetation.” i. Describe how this layer is used to prioritize fire infrastructure. ii. Explain why this layer is not a “usable layer” for evaluating wildfire risk as described. | a. In 2022, a preliminary analysis was conducted to compare existing High Fire-Threat District (HFTD) prioritized circuit segments with additional non-HFTD coastal canyon circuit segments. The objective was to better understand the relative wildfire risk at a circuit-segment level and to assess potential risk exposure beyond the currently designated HFTD boundaries. This assessment focused on key wildfire risk indicators—namely, Wildfire Likelihood of Risk Event (WF LoRE), Wildfire Consequence of Risk Event (WF CoRE), and overall Wildfire Risk. These metrics were evaluated across all circuit segments in both groups, along with their respective statistical averages. The findings revealed that while certain coastal canyon segments exhibited higher risk levels than some of the lower-risk HFTD segments, the average wildfire risk across coastal canyon segments was significantly lower than that of HFTD segments. Notably, the highest-risk coastal canyon segment still ranked below the top 200 riskiest segments within the HFTD.b. i. The US Fire Administration defines the WUI as “the zone of transition between unoccupied land and human development.” This can be used by local, state, and federal fire agencies to create strategy around their fire infrastructure and defense plans. Per CALFIRE (https://osfm.fire.ca.gov/what-we-do/code-development-and-analysis/wildland-hazards-and-building-codes ) this zone may also have impact on building construction methods or defensible space requirements that are designed to prevent negative impacts from fires on communities that are adjacent to wildland fuels. The fire infrastructure referenced is that of the fire agencies and how they choose to utilize the information is outside of the utilities scope. ii. The WUI map is designed to display zones between unoccupied land and human development mix. Even though some of the same variables may be used to develop the WUI and the HFTD the WUI is not designed to quantify the risk of an ignition from utility equipment. The HFTD is also not designed to address areas where urbanization has begun to mix with wildland fuels. For the HFTD the Independent Review Team utilized the Integrated Utility Threat Index Model to validate the risk associated with an ignition location (Process history: https://docs.cpuc.ca.gov/PublishedDocs/Efile/G000/M199/K508/199508442.PDF ). During SDG&E’s annual review of the HFTD, the WUI map and the associated variables are reviewed and discussed for potential changes to the HFTD. This process will continue to ensure the level of mitigation utilized by the utility to mitigate the risk of a large fire originating from equipment are addressed. New information is regularly incorporated into the discussion of the HFTD shape, with the risk of ignition existing inside and outside of the HFTD (36% of SDG&E’s CPUC reportable fires have been outside the HFTD). Based on the models (7a answer) and the process associated with the creation of the HFTD, SDG&E believes that the risks associated with ignitions within the HFTD (93% of acres associated with SDG&E ignitions have been within the HFTD) are in most cases greater than those of areas outside tiers 2 & 3, even if those areas fall into WUI. | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | 5.5 | 5.5 Risk Analysis Results and Presentation . | 5.5.1.2 | 5.5.1.2 Proposed Updates to the HFTD
63 | OEIS | 6 | OEIS-6 | 8 | OEIS-6.8 | Regarding Third-Party Risk Model Recommendations to Models: Pages 62-66 of SDG&E's 2026-2028 Base WMP, “SDGE Table 5-8: WiNGS-Planning Third Party Recommendations,” and “SDGE Table 5-9: WiNGS-Ops Risk Modeling Updates,” show third-party recommendations for SDG&E’s models. a. Multiple recommendations state that SDG&E’s model documentation is lacking, with a 2026 target deadline to provide documentation. Explain what efforts have been made to start creating each documentation recommended. b. One recommendation states that a report that tracks compliance with OIR requirements would help prevent potential violations. i. Provide a copy of this report, if it has been created. ii. If such a report has not been created, discuss SDG&E’s progress on creating this report. | a. The latest drafted technical documentation has been provided in response to QUESTION 4 above. This documentation will continue to be refined through 2026 as mentioned in SDGE Tables 5-8 and 5-9. b. A formalized report that tracks OIR requirements has not been developed yet. With a “low” severity level, this has been deferred and will continue to be explored through 2026. Alternatively, SDG&E does regularly track and roadmap risk modeling regulatory requirements stemming from the WMP, Maturity Model, ACIs, etc., which are included in OEIS Table 5-6: Utility Risk Assessment Improvement Plan. | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | 5.6 | 5.6 Quality Assurance and Quality Control | 5.6.1 | 5.6.1 Independent Review
64 | OEIS | 6 | OEIS-6 | 9 | OEIS-6.9 | Regarding Climate Change: a. Provide a detailed description and relevant supporting documentation on how climate change is currently accounted for in SDG&E’s risk models. | Currently, Climate Change is not accounted for in SDG&E’s wildfire, PSPS, and PEDS risk models. | Zhenying Shao | 2025-05-20 | 2025-05-23 | 2025-05-23 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-06.pdf | 0 | No | N/A | Climate Change in Risk Models | N/A | N/A
65 | MGRA | 4 | MGRA-4 | 1 | MGRA-4.1 | With regard to SDG&E Data Request Response MGRA-2026-8-03-2: “For example, if 5 animal-contact caused ignitions occurred at locations where the 99th wind gust falls between 25th to 50th percentiles of the overall 99th wind gust (WRwind = 21) and where the 50th consequence is above the overall 50th percentile threshold, the Rfreq is calculated as follow:”[sic] a. Does SDG&E use a wind-gust adjustment for animal contact? b. If the answer to a is yes, what is the justification for adjusting the frequency of animal contact ignitions as a function of wind gust speed? c. Does SDG&E apply the same wind gust weight adjustment to all ignition drivers? d. If the answer to c is no, which ignition drivers have a wind gust adjustment applied, and what is the basis for the application of the weighting and its magnitude? | a. Yes. SDG&E applied a wind gust weight factor (WRwind) to ignition events, including those caused by animal contact when calculating the Rfreq b. By applying a wind-based weighting, SDG&E accounts for the elevated wildfire risk associated with ignition events occurring in locations prone to high wind gusts. This approach enables a location-specific quantification of risk, even for ignition causes not directly influenced by wind, such as animal contact. c. Yes d. N/A | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | MGRA-2026-8-03-2 | N/A | N/A
66 | MGRA | 4 | MGRA-4 | 2 | MGRA-4.2 | With regard to SDG&E Data Request Response MGRA-2026-8-03-3: a. For risk factors such as wind gust, humidity, and temperature, were these sampled at the time of the risk event or does the analysis use aggregated data (i.e. averages, peaks, etc.)? b. If sampled at the time of the was this based on climatology models or weather station data? c. If aggregated describe the source of the data, aggregation period method. | a. For this analysis, the risk factors other than Fire Potential Index (FPI) such as wind gust, humidity, and temperature, were aggregated for a given location. b. N/A c. Historical wind gust, humidity and temperature were aggregated at the weather station level. For each station, wind gust was aggregated using the 99th percentile, and both temperature and humidity were aggregated using minimum, median and maximum values. All risk events (outages and ignitions) were then spatially tied to their associated weather station to incorporate these localized climatological factors into the risk driver prioritization analysis. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | MGRA-2026-8-03-3 | N/A | N/A
67 | MGRA | 4 | MGRA-4 | 3 | MGRA-4.3 | With regard to SDG&E Data Request Response MGRA-2026-8-03-4: In SDG&E’s most extreme wildfire scenario, the total risk with SDG&E’s risk aversion applied is 16 times larger than without risk aversion. In Section 5.2.2.3 of its WMP SDG&E explains this adjustment comes from applying a power law with an exponent of 1.47. a. Provide the basis for choosing a power law for the risk aversion function. b. Provide the method by which the exponent of 1.47 was determined. c. Does SDG&E agree that wildfire loss statistics, in particular wildfire size, generally follow a power law distribution? d. If the answer to c is yes, then please provide an explanation of why it is appropriate to adjust a power law distribution by multiplying by another power law distribution. | in SDG&E’s existing filings and regulatory submissions. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. Refer to “Risk-Averse Scaling Function” detailed discussion in SDG&E’s recent RAMP submission at “SCG/SDG&E RAMP-3 Risk Quantification Framework-24” https://www.sdge.com/sites/default/files/regulatory/Vol1_Ch3_Joint_ERM_Risk_Quantification.pdf b. Refer to the answer given in 3a. c. Yes, SDG&E agrees with this statement. Refer to “Consequence of a Risk Event” discussion in SDG&E’s recent RAMP submission, starting in “SDGE-Risk-4 Wildfire and PSPS-25” https://www.sdge.com/sites/default/files/regulatory/SDG%26E%20-Risk-4%20Wildfire%20%26%20PSPS_0.pdf d. SDG&E’s wildfire risk modeling framework demonstrates that wildfire consequences within its service territory exhibit a heavy-tailed loss distribution, underscoring the significant role that infrequent yet high-impact events play in overall risk assessment. By modeling tail events, this approach ensures that rare but severe losses are appropriately accounted for in decision-making, leading to a more precise risk characterization and the development of more effective mitigation strategies. To further refine its wildfire consequence modeling, SDG&E has transitioned its wildfire consequence model to Technosylva’s 24-hour unsuppressed simulations.1 These simulations validate the previously observed heavy-tailed behavior while offering a site-specific, asset / span, level analysis of wildfire impact across varying observed weather conditions within SDG&E’s service territory. While statistical models such as power-law distributions and/or Technosylva simulations effectively describe the potential scale of wildfire-related losses, they do not inherently account for any risk attitude, whether risk-seeking or risk-averse. These models provide a robust quantitative foundation for understanding wildfire impacts but lack the dimension necessary to capture SDG&E’s reasonable approach to wildfire risk management. Risk aversion plays a critical role in regulatory and operational decision-making, shaping how SDG&E evaluates, plans for, and responds to wildfire threats. It influences mitigation strategies, infrastructure investments, emergency response protocols, and stakeholder engagement. To ensure wildfire risk is managed in accordance with regulatory requirements and community safety priorities, additional modeling techniques, such as incorporating a risk-aversion scaling function, are essential. These adjustments help integrate both statistical projections and the practical, economic sensitivities of utilities, regulators, and communities, ensuring that extreme loss scenarios receive appropriate consideration in planning and risk mitigation efforts. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | MGRA-2026-8-03-4 | N/A | N/A
68 | MGRA | 4 | MGRA-4 | 4 | MGRA-4.4 | With regard to SDG&E Data Request Response MGRA-2026-8-03-5: Please provide a version of the table MGRA-2026-8-03_Q06-OEIS-Table-4-3.xlsx with three additional columns listing the total number of customers current as of 2025 on each listed circuit for each of the customer classes: a. Large/Medium commercial b. Small commercial c. Residential | SDG&E objects to the request to the extent it is unduly burdensome and calls on SDG&E to perform studies or analysis that do not currently exist. Subject to and without waving the foregoing objections, SDG&E responds as follows: Commercial and Industrial customers are split based on their kW demand. SDG&E does not have C&I broken down by small, medium or large. The documentation provided includes customers broken out into total, residential and C&I based on current circuit customer counts. Please see the attached spreadsheet titled “SDGE Response MGRA-2026-8-04_Q04-OEIS-Table-4-3.xlsx.” | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04_Q04-OEIS-Table-4-3.xlsx | 1 | No | N/A | MGRA-2026-8-03-5 | N/A | N/A
69 | MGRA | 4 | MGRA-4 | 5 | MGRA-4.5 | With regard to SDG&E Data Request Response MGRA-2026-8-03-7: SDG&E states that it “does not default to undergrounding as the preferred mitigation strategy. For each feeder segment, SDG&E evaluates risk reduction and cost-benefit ratios for both Combined Covered Conductor and Strategic Undergrounding mitigation options.” In SDG&E’s last GRC, the WiNGS Planning suite used a decision tree (see GRC DR request responses SDG&E DR Response MGRA-3-13, SDG&E DR Response MGRA-4-1, and SDG&E DR Response TURN-SEU-056-1). a. Please confirm whether the methodology used during the GRC has been replaced and whether a decision tree is still used at any point in the mitigation decision process. b. Since SDG&E evaluates both risk reduction and cost-benefit ratios to evaluate mitigation options, please provide the quantitative and qualitative process by which both risk reduction and CBR go into the mitigation decision. | a. The current mitigation decision process has evolved from the methodology used in previous WiNGS-Planning versions. While a structured framework still guides mitigation selection, the process now incorporates a more dynamic, data-driven approach. After the Risk Analytics team reviews and approves the feeder-segment outputs from WiNGS-Planning, a multidisciplinary group of subject matter experts, including Electric System Hardening engineers, fire coordination staff, meteorologists, risk data scientists, and construction engineers, conducts a comprehensive evaluation. This team assesses the WiNGS-Planning model results and associated cost-benefit ratios, considering feasibility, expected risk reduction, and residual risks for each mitigation option, such as Combined Covered Conductor or Strategic Undergrounding. They also factor in both upfront installation and lifecycle costs, which are modeled over a 55-year lifespan, to ensure long-term cost-effectiveness. Additionally, the team evaluates opportunities to “bundle” upstream feeder segment hardening projects to enhance PSPS risk reduction and achieve cost efficiencies through reduced permitting and mobilization efforts. This integrated, expert-driven process reflects a refinement of earlier methodologies, allowing for more nuanced and context-sensitive mitigation decisions. For further details, please refer to Figure 6.1.3.2.6, Mitigation Initiative Prioritization to Reduce Wildfire and PSPS Risk in the 2026–2028 WMP. b. SDG&E performs a cost-benefit analysis to compare the expected risk reduction and lifecycle costs of Strategic Undergrounding and Combined Covered Conductor. This analysis informs the prioritization of grid hardening mitigations. The WiNGS-Planning model estimates reductions in wildfire, PSPS, and PEDS risks for each feeder segment located in Tier 2 and Tier 3 of the High Fire-Threat District (HFTD). Based on these risk reduction estimates, SDG&E recommends a mitigation strategy for each feeder segment. These recommendations are then reviewed by the Electric System Hardening team for further evaluation. As part of the scoping process, a desktop feasibility study is conducted to assess the practicality of the proposed mitigation. Adjacent upstream and downstream segments are also evaluated to determine whether Strategic Undergrounding or Combined Covered Conductor is the more effective solution (see Section 6.1.2, Risk-Informed Prioritization). Where appropriate, consecutive segments may be bundled to maximize PSPS risk reduction and realize economies of scale. Additionally, Electric Distribution Planning engineers review wildfire mitigation projects for any capacity-related grid needs identified on the associated circuits. These needs, along with any required upgrades, are identified through the annual Distribution Planning Process. As part of their review, engineers verify the results of the Distribution Planning Process and assess whether any changes in scope have occurred since its completion. If necessary, upgrades or reconfigurations are incorporated into the wildfire mitigation project scope. For further details, please refer to Figure 6.1.3.2.6, Mitigation Initiative Prioritization to Reduce Wildfire and PSPS Risk in the 2026–2028 WMP. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | MGRA-2026-8-03-7 | N/A | N/A
70 | MGRA | 4 | MGRA-4 | 6 | MGRA-4.6 | With regard to SDG&E Data Request Response MGRA-2026-8-03-11: Please provide: a. An Excel spreadsheet listing all FPI daily records going back to April 2013, listing FPI value, date, and operational district. b. A shapefile or geodatabase representing SDG&E’s operational districts. | SDG&E objects to the request to the extent it is overly broad and unduly burdensome, particularly in that it seeks information dating back more than 10 years. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. See attached spreadsheet titled “SDGE Response MGRA-2026-8-04_Q6_Operational FPI - 2012-Current.xlsx.” b. See attached zipped folder titled “SDGE Response MGRA-2026-8-04_Q6_District Shapefiles.zip.” | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04_Q6_Operational%20FPI%20-%202012-Current.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04_Q6_District%20Shapefiles.zip | 2 | No | N/A | MGRA-2026-8-03-11 | N/A | N/A
71 | MGRA | 4 | MGRA-4 | 7 | MGRA-4.7 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: Define “Combined Covered Conductor” and why this is different from the traditional term “Covered Conductor. | The term “Covered Conductor” previously referred solely to replacing bare conductor with covered conductor manufactured with an internal semiconducting layer and external insulating ultraviolet-resistant layers to provide incidental contact protection. The “Combined Covered Conductor” Program (WMP.455) refers to the replacement of bare conductors with covered conductors in the HFTD and, as needed, combining additional equipment replacements and installations such as structures, lighting arrestors, fuses, connectors, and avian protection. Furthermore, advanced protection solutions like Early Fault Detection (EFD) and Falling Conductor Protection (FCP) are assessed and implemented to enhance the system's effectiveness against various risk drivers. A revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
72 | MGRA | 4 | MGRA-4 | 8 | MGRA-4.8 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: Does the “CCC_RA_RAMP” tab calculate the effectiveness of covered conductor alone or does it include EFD and FCD? | All calculations related to Combined Covered Conductor include effectiveness of EFD and FCP. A revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan.. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
73 | MGRA | 4 | MGRA-4 | 9 | MGRA-4.9 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: Why is Expected Risk Reduction dramatically less than Activity Effectiveness for combined covered conductor? Section 6.2.1.2 does not clarify why this would be the case. | The expected risk reduction for combined covered conductor may appear lower than the stated activity effectiveness due to two key factors: baseline asset condition and the probabilistic nature of risk reduction modeling. First, the effectiveness of any mitigation activity is calculated relative to the baseline condition of the asset. Assets that have already received traditional hardening measures will experience less additional benefit from the application of covered conductor compared to assets that are currently unhardened. In SDG&E’s modeling framework, this means that the marginal risk reduction is lower where the baseline already includes some degree of risk mitigation. Second, expected risk reduction is derived through stochastic simulation in which ignition events are probabilistically sampled out based on the modeled efficacy of the mitigation. For example, a mitigation effectiveness of 0.58 implies that, on average, 58 out of 100 ignition events are prevented on an unhardened asset. However, because wildfire risk is highly skewed (tail risk, where a small number of events can drive a large share of total expected dollar impact) the removal of events does not necessarily translate to a proportional reduction in overall risk. The events that are sampled out may be lower impact on average, and therefore the total expected risk (in dollar terms) may be reduced by less than the raw event count suggests. This distinction between activity effectiveness and expected risk reduction is an intentional aspect of the model design, ensuring that mitigation impacts are realistically scaled to both the existing system state and the asymmetric nature of wildfire consequences. A revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
74 | MGRA | 4 | MGRA-4 | 10 | MGRA-4.10 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: While the Excel file is interactive and relatively transparent, changing the Mitigation Effectiveness value in cell K10 on the CCC_RA_RAMP page has no effect on the calculated mitigation values. a. Why is this the case? b. Is there a way to adjust the table in order to insert user-defined efficiencies? c. If not, please provide an alternative version of SDG&E_2026-2028_Base-WMP_Appendix G Supporting Data_R0.xlsx with the CCC efficiency set to 85%. | SDG&E objects to the request on the grounds it calls for SDG&E to conduct studies or analysis that do not currently exist and are inconsistent with SDG&E’s existing risk models. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. Modifying the effectiveness does not affect risk reduction because SDG&E incorporates mitigation effectiveness into its risk reduction calculations within the WiNGS-Planning tool, where millions of stochastic simulations are performed to ensure accurate risk reduction assessments at the feeder-segment level. WiNGS-Planning outputs can be reviewed in tab “raw_WiNGS_Planning”. b. User-defined mitigation efficiencies can be modified in all tabs except CCC and SUG, where this functionality is not available due to risk reductions being calculated within the WiNGS-Planning tool. c. See attached file titled “SDGE Response MGRA-2026-8-04_Q10c.xlsx” with 85% CC efficacy rate. A revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04_Q10c.xlsx | 1 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
75 | MGRA | 4 | MGRA-4 | 11 | MGRA-4.11 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: Do the cost benefit calculations derived from the file incorporate SDG&E’s risk attitude function? | Yes, the cost benefit calculations derived from the file incorporate SDG&E’s risk attitude function. A revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
76 | MGRA | 4 | MGRA-4 | 12 | MGRA-4.12 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: SDG&E states that “Currently, SDG&E does not calculate a Mitigation Effectiveness metric for PSPS and PEDS risk reductions.” Does SDG&E calculate a wildfire risk reduction metric for PSPS and PEDS? | SDG&E does not establish a wildfire risk reduction metric for PSPS and PEDS, as its approach to risk assessment focuses on analyzing the likelihood and potential consequences of risk events both before and after mitigation. For each mitigation effort, risk reduction is determined by calculating the difference between the total baseline risk and the total post-mitigation risk. Since both PSPS and PEDS events are highly dependent on weather conditions, SDG&E cannot precisely identify the locations where these protocols will be activated within a three-year period. As a result, SDG&E is unable to calculate risk reduction specific to the WMP years for PEDS and PSPS. A revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
77 | MGRA | 4 | MGRA-4 | 13 | MGRA-4.13 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: Figure 6.5 shows that the residual risk after SDG&E hardening programs, PSPS and PEDS is 1.5%. a. What is the estimated combined net estimated residual risk from the portfolio CCC+FCD+ESD+PEDS+PSPS b. Please provide a version of SDG&E_2026-2028_Base-WMP_Appendix G Supporting Data_R0.xlsx with a tab representing this portfolio risk if it is not already incorporated into the CCC tab. c. If the tab in b) is onerous to produce, provide a date by which such a portfolio could be generated. | a. “Figure 6-5: Estimated Wildfire Risk Reduction 2007–2037” is derived from current grid hardening initiatives and the projected mileage outlined in “Figure 6-4: Wildfire Hardening Targets”. In developing these estimates, an average risk reduction factor is applied to both SUG and CC scenarios, regardless of the specific location of the feeder segment. Currently, SDG&E has not scoped the exact feeder segments beyond 2027. Consequently, the risk reduction estimates provided are indicative and reflect preliminary risk reduction estimates. These high-level risk reduction estimates serve as an initial assessment to support wildfire and PSPS risk strategy efforts, and they are expected to be refined and updated as more detailed feeder segmentation data becomes available. Modeling only CCC (CC+ Inspections + EFD + FCP+PSPS) the resulting residual risk is 2.22% with a 38.89% risk reduction provided by PSPS de-energizations. b. Refer to tab “CCC” where risk reduction for 139 miles are presented for the given portfolio. Note that a revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan c. N/A | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
78 | MGRA | 4 | MGRA-4 | 14 | MGRA-4.14 | With regard to Appendix G and the file SDG&E_2026-2028_Base- WMP_Appendix G Supporting Data_R0.xlsx: Are advanced protections planned for circuits that may be in SDG&E's long term undergrounding plans? | The current method for scoping advanced protection projects includes analysis based on SDG&E’s strategy and cost consideration in selecting circuits for strategic undergrounding of electric lines and aims to provide protection on circuits where no other mitigation exists before implementing a combined mitigation of Falling Conductor Protection (FCP) and long term undergrounding scope. The goal is to gain immediate risk reduction on circuits expected to remain overhead before installing additional mitigation measures on circuits which already have had risk reduced via undergrounding. Some circuits may not be completely undergrounded due to construction complexity or lower calculated risk on those segments. In this case, advanced protection deployments may be scoped to provide additional risk reduction by installing advanced protection downstream of where the underground segment ends and returns to the overhead plant. A revised version of these calculations can be found in SDG&E’s non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
79 | MGRA | 4 | MGRA-4 | 15 | MGRA-4.15 | Consequence Modeling: With regard to SDG&E Data Request Response OEIS-P-WMP_2025-SDGE-02-Q7 and Q9: Provide available technical details of the structure loss model including citations to supporting literature. | SDG&E objects to the request to the extent it seeks information that contains confidential trade secret or proprietary information. SDG&E objects to providing such information absent an appropriate protective order. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E utilizes Technosylva’s proprietary software to estimate potential wildfire impacts, including acres burned and structures destroyed. To ensure clarity and transparency on the methodology used, SDG&E has formally requested Technosylva’s latest documentation detailing the methodology used to determine structures destroyed based on those located within the fire footprint in their simulations. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | OEIS-P-WMP_2025-SDGE-02-Q7 and Q9 | N/A | N/A
80 | MGRA | 4 | MGRA-4 | 16 | MGRA-4.16 | Consequence Modeling: With regard to SDG&E Data Request Response OEIS-P-WMP_2025-SDGE-02-Q7 and Q9: What assumptions do the structure loss model make regarding the fractions of structures burned within the fire perimeter? | See response to Question 15. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | OEIS-P-WMP_2025-SDGE-02-Q7 and Q9 | N/A | N/A
81 | MGRA | 4 | MGRA-4 | 17 | MGRA-4.17 | Consequence Modeling: With regard to SDG&E Data Request Response OEIS-P-WMP_2025-SDGE-02-Q7 and Q9: Does the structure loss model use Technosylva's TDI calculation to estimate home losses? If so what is the relationship between TDI and fraction of structures burned? | See response to Question 15. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | OEIS-P-WMP_2025-SDGE-02-Q7 and Q9 | N/A | N/A
82 | MGRA | 4 | MGRA-4 | 18 | MGRA-4.18 | Consequence Modeling: With regard to SDG&E Data Request Response OEIS-P-WMP_2025-SDGE-02-Q7 and Q9: Provide additional technical detail regarding SDG&E’s egress model. | The wildfire egress modeling framework developed by SDG&E is a simulation system designed to evaluate evacuation feasibility and understand potential egress strategies in the event of a wildfire. The model integrates multi-source geospatial and temporal data to simulate fire progression, population movement, and traffic dynamics. It leverages a combination of deterministic fire spread modeling, graph-based network optimization, and behavioral simulation to identify evacuation bottlenecks and high-risk communities. At its core, the model treats each utility pole as a potential ignition point, associating it with the nearest weather station and Technosylva fire simulation data to parameterize fire behavior. Fire spread is modeled as an elliptical function, where the major and minor axes are dynamically determined by wind gust magnitude and direction. This allows the model to simulate the temporal evolution of fire perimeters across a heterogeneous landscape. The fire footprint is discretized into five concentric zones, each representing a different level of threat, and road segments are dynamically assigned to these zones as the fire advances. Population data is spatially resolved using smart meter locations, with each meter’s population assigned to the nearest road segment. This enables fine-grained estimation of evacuee density and supports the identification of critical evacuation corridors. The road network is derived from OpenStreetMap (OSM) via OSMNx python library, incorporating attributes such as speed limits and lane capacities. These are used to construct a weighted graph for network flow analysis, where evacuation routes are identified using shortest-path algorithms that account for dynamic fire encroachment and traffic congestion. The simulation pipeline consists of several stages: ignition point initialization, fire spread simulation, safe zone identification, egress route computation, and behavioral modeling. Safe zones are predefined based on geographic and infrastructural criteria, and the model computes optimal paths from each populated node to the nearest safe zone, updating routes in response to fire progression. Human behavior is modeled probabilistically, incorporating compliance rates with evacuation orders and potential deviations from optimal routes. The model also supports dynamic rerouting and capacity adjustments, such as contraflow lane usage, to reflect real-world emergency response strategies.To manage computational complexity, the model employs spatial clustering using hexagonal binning. This reduces the number of required simulations by aggregating ignition points with similar fire spread characteristics. For instance, out of over 216,000 potential ignition points, only 30,283 simulations are necessary after filtering out those locations with simulated zero rate of spread and applying hexagonal aggregation. This optimization significantly reduces runtime while preserving spatial resolution and ensuring the predictions remain relevant and accurate. Egress modeling is a complex and technically challenging process, and its accuracy depends on a several factors and necessary assumptions that are intrinsically extremely difficult to model. SDG&E is constantly working on model enhancements and more effective incorporation of modeling inputs into its larger risk assessment framework to help support a more accurate predictive and prescriptive modeling output, with the intent to more effectively support wildfire mitigation efforts and situational awareness to benefit the community at large. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf | 0 | No | N/A | OEIS-P-WMP_2025-SDGE-02-Q7 and Q9 | N/A | N/A
83 | MGRA | 4 | MGRA-4 | 19 | MGRA-4.19 | GIS Data: Please provide GIS data in the form of geodatabase used in Figure 5-12. RESPONSE 19 | Please see attached zip file titled “base_risk_data_GDB.zip” containing the base_risk_geodatabase.gdb file. The .gdb file includes all 3 geospatial layers visualized in Figure 5-12, namely circuit-segment overall risk hexagons, San Diego County line boundaries, and High Fire Threat District (HFTD) line boundaries. | Joseph Mitchell | 2025-05-21 | 2025-05-28 | 2025-05-28 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-04.pdf https://www.sdge.com/sites/default/files/regulatory/base_risk_data_GDB.zip | 1 | No | N/A | N/A | N/A | N/A
84 | OEIS | 7 | OEIS-7 | 1 | OEIS-7.1 | Regarding Worse Weather Days: a. In response to MGRA Data Request 3 Question 5, SDG&E provided a list of the 125 worst fire weather days. Provide an updated list of these weather days with the following information for each day: i. Wind speed (mph) ii. Wind gust (mph) iii. Temperature (F) iv. Humidity levels (%) v. FPI rating | Refer to the attached spreadsheet titled “SDGE Response OEIS-P-WMP_2025-SDGE-07_Q1&Q4.xlsx” for daily FPI data and hourly wind gust measurements across the SDG&E service territory, Tier-2 and Tier-3 areas. The slicer allows toggling between mean and maximum hourly values. | Zhenying Shao | 2025-05-23 | 2025-05-29 | 2025-05-29 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07_Q1%26Q4.xlsx | 1 | No | N/A | MGRA DR3.5 | N/A | N/A
85 | OEIS | 7 | OEIS-7 | 2 | OEIS-7.2 | Regarding OEIS Table 6-4: a. In response to OEIS-P-WMP_2025-SDGE-05, Question 14, SDG&E provided an updated “OEIS Table 6-4: Summary of Risk Reduction for Top-Risk Circuits,” that included additional columns for completed and planned hardening. Provide an expanded version of OEIS Table 6-4 with the following additional columns: i. 2026 planned undergrounding (circuit mileage) ii. 2027 planned undergrounding (circuit mileage) iii. 2028 planned undergrounding (circuit mileage) iv. 2026 planned covered conductor (circuit mileage) v. 2027 planned covered conductor (circuit mileage) vi. 2028 planned covered conductor (circuit mileage) vii. 2026 planned traditional hardening (circuit mileage) viii. 2027 planned traditional hardening (circuit mileage) ix. 2028 planned traditional hardening (circuit mileage) | Please refer to the tab titled “Question 2” in the attached spreadsheet titled “SDGE Response OEIS-P-WMP_2025-SDGE-07_Q2&Q3.xlsx” for the requested table 6-4 in the Question 2 tab. | Zhenying Shao | 2025-05-23 | 2025-05-29 | 2025-05-29 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07_Q2%26Q3.xlsx | 1 | No | N/A | OEIS DR5.14 | N/A | N/A
86 | OEIS | 7 | OEIS-7 | 3 | OEIS-7.3 | Regarding Cost Benefit Ratios (CBR): a. Provide a list via Excel of all undergrounding and combined covered conductor projects planned for 2026-2028 with the following columns: i. Circuit/circuit segment ID ii. Type of hardening (undergrounding or combined covered conductor) iii. Year for planned project (2026, 2027, or 2028) iv. Circuit mileage of project v. Overall utility risk score vi. CBR for undergrounding used for decision-making vii. Risk reduction for undergrounding used for decision-making viii. CBR for combined covered conductor used for decision-making ix. Risk reduction for covered conductor used for decision-making x. HFTD designation (Tier 2 or Tier 3) | Please refer to the tab titled “Question 3” in the attached spreadsheet titled “SDGE Response OEIS-P-WMP_2025-SDGE-07_Q2&Q3.xlsx.” | Zhenying Shao | 2025-05-23 | 2025-05-29 | 2025-05-29 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07_Q2%26Q3.xlsx | 1 | No | N/A | Covered Conductor List | N/A | N/A
87 | OEIS | 7 | OEIS-7 | 4 | OEIS-7.4 | Regarding Financial Risk: a. In response to OEIS-P-WMP_2025-SDGE-05, Question 15, SDG&E provided an updated version of “OEIS Table 6-1: List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk,” breaking out risk score components. Building upon the updated table provided in the response, provide an updated version of OEIS Table 6-1 via Excel with the following additional columns: i. Financial Risk Score Component of Wildfire Risk Score attributed to buildings burned. ii. Financial Risk Score Component of Wildfire Risk Score attributed to acres burned. | Refer to the "Acres-Structure %" tab in the attached spreadsheet titled “SDGE Response OEIS-P-WMP_2025-SDGE-07_Q1&Q4.xlsx” to review the risk distribution for approximately 164,000 structures, based on SDG&E’s assumptions of $1 million per structure lost and $2,350 per acre burned. | Zhenying Shao | 2025-05-23 | 2025-05-29 | 2025-05-29 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-07_Q1%26Q4.xlsx | 1 | No | N/A | OEIS DR5.15 | N/A | N/A
88 | SPD | 1 | SPD-1 | 1 | SPD-1.1 | Provide SPD with the confidential versions of SDG&E’s 2026-2028 Wildfire Mitigation Plan (WMP) and any confidential associated documents or attachments submitted to the Office of Energy Infrastructure and Safety (Energy Safety). a. Provide SPD with any confidential responses to data requests that SDG&E sent to Energy Safety or any other party since May 2, 2025. Include any attachments, appendices or datasets in the native format that were sent to Energy Safety or any other party with the confidential data requests. Submit all of the materials to Kiteworks packaged in a single zip file and organized according to the following folder structure: i. Party Name (i.e. Energy Safety, Cal Advocates, MGRA, TURN etc.) ii. DR Name (i.e. SPD-SDGE-WMP2026-001) 1. Place the original data request in this folder 2. Place the confidential data request responses in this folder. iii. Attachments 1. Place any confidential attachments to the data request responses in this folder. | SDG&E does not have a confidential version of its 2026-2028 WMP and has not provided any confidential responses to data requests received thus far. | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf | 0 | No | N/A | Confidential versions of SDG&E’s 2026-2028 Wildfire Mitigation Plan | N/A | N/A
89 | SPD | 1 | SPD-1 | 2 | SPD-1.2 | SDG&E submitted an Errata workpaper titled TN15872_20250516T165458_SDGE_20262028_BaseWMP_Appendix_G_Supporting_Data_Errata .xlsx on May 16 2025. a. Provide SPD with a description of each of the fields found in the following spreadsheets of this workpaper: i. raw_WiNGS_Planning ii. TrancheID iii. FeederSegment miles iv. SUG&CCC_Lifecycle_cost v. Capital_Units&Cost vi. O&M_Units&Cost b. For each of the fields described in SDG&E’s response to Question 2a., SDG&E must explain how each field is calculated. i. If the data comes from an external dataset, provide SPD with that dataset. For instance, in the SUG&CCC_Lifecycle_cost spreadsheet, the field avg_yearly_if_ug_cost_per_mile records values that appear to have been calculated from another dataset. Provide SPD with that dataset. | a.i-iv. Please see the attached file titled “SPD-SDGE-WMP2026-001-Q02.Metadata.xlsx” for complete information on column outputs for information pertaining to raw_WiNGS_Planning, TrancheID, FeederSegment miles, and SUG&CCC_Lifecycle_cost. Additionally, see attached WiNGS Planning Consequence Simulation Data Dictionary.docx for a complete data dictionary on all WiNGS-Planning related simulation outputs. v-vi. Capital_Units&Cost and O&M_Units&Cost The capital unit cost represents the capital expense required to perform work each year. It is a combination of Actuals and forecasted cost. Although these costs are documented, thedata in these sheets is not directly used within the work paper formulas. Its inclusion is intended to align the calculations used for SDG&E’s 2025 RAMP filing and 2026-2028 WMP cost-benefit ratios; however, it was not used for WMP cost-benefit ratio calculations, and is therefore irrelevant. b. Please see the attached file titled “SPD-SDGE-WMP2026-001-Q02.Metadata.xlsx” for information pertaining to the calculation of column data. i. The dataset used to generate Columns A-Q in SUG&CCC_Lifecycle_cost has been provided in the attached file titled “SDGE Response SPD-SDGE-WMP2026-001-Q02.b.Lifecycle Cost Dataset.xlsx”. | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001-Q02.Metadata.xlsx https://www.sdge.com/sites/default/files/regulatory/WiNGS%20Planning%20Consequence%20Simulation%20Data%20Dictionary.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001-Q02.b.Lifecycle%20Cost%20Dataset.xlsx | 3 | No | N/A | Errata Workpapers | N/A | N/A
90 | SPD | 1 | SPD-1 | 3 | SPD-1.3 | During the 2026-2028 Base Wildfire Mitigation Plan Workshop hosted by Energy Safety on May 21 2025, SDG&E presented a series of slides (slides 81-114 of the Workshop Slides). Provide SPD with all of the SDG&E slides in its native ppt format. a. All figures and textboxes should remain editable b. Any workbooks that were embedded in the ppt should remain embedded in the ppt. | See attached slide deck titled “SDGE WMP 2026-2028_Presentation.pptx.” | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20WMP%202026-2028_Presentation.pdf | 1 | No | N/A | 2026-2028 Base Wildfire Mitigation Plan Workshop | N/A | N/A
91 | SPD | 1 | SPD-1 | 4 | SPD-1.4 | During the 2026-2028 Base Wildfire Mitigation Plan Workshop hosted by Energy Safety on May 21 2025, SDG&E presented the unit cost of covered conductor as approximately $1.44 million ($1M for Installation and $.44M for Foundational) on slide 96 of the Workshop Slides. In SDG&E’s 2026- 2028 Base WMP Table 6-1 presents Combined Covered Conductor (WMP.455) as having an Expected Implementation Cost of $212,401,000. Table 8-1 presents the 3-year total for Combined Covered Conductor (WMP.455) miles as 130. This amounts to a unit cost of $1,633,853. a. Provide all workpapers that support how SDG&E arrived at the Expected Implementation Cost of Combined Covered Conductor of $212,401,000. i. If an incorrect value was input into Table 6-1, provide the correct value and explain why the value was incorrectly recorded in Table 6-1. b. Confirm that the 3-year total for Combined Covered Conductor (WMP.455) presented in Table 8-1 is 130 miles. i. If it is not, provide the correct value and explain why the value was incorrectly recorded in Table 8-1. c. Provide all workpapers that support how SDG&E arrived at the unit cost for covered conductor as presented in the May 21 2025 2026-2028 Base Wildfire Mitigation Plan Workshop on slide 96. i. The workpaper(s) must explain how each of the five components (Installation, Inspections+, Vegetation Management, PSPS and Foundational) were calculated. ii. Explain if the Installation costs included estimates for replacing cross arms and poles. iii. Provide a detailed description of the PSPS costs. iv. Provide a detailed description of the Inspections+ costs. v. How might the PSPS and Inspections+ costs overlap? If they do not overlap, explain why. vi. Do any of the five categories include the cost for replacement of the asset after its55 year use life is complete? 1.If yes, explain how that was calculated. 2.If not, explain why not. 3.If not, provide an estimate of the replacement cost/mile of covered conductor vii. Do any of the five categories include the cost for decommissioning or disposing(i.e.net negative salvage) of the asset after its 55 year use life is complete? 1.If yes, explain how that was calculated. 2.If not, explain why not. 3.If not, provide an estimate of the decommissioning cost/mile of covered conductor viii. Explain the discrepancy between the unit cost of $1,633,853 in the WMP and what was presented at the Workshop. d. In SDGE’s Response to Question 15 of the data request SPD-SDGE-SB884-07, SDG&E provided the SDGE Response SPD-SDGE-SB884-07_Q15_CC.xlsx workbook. The total cost per mile presented in this workbook presents SDG&E’s unit cost for covered conductor as$1,551,882. i. Explain the discrepancy between the unit cost of $1,633,853 in the WMP and what was presented in the SDGE Response SPD-SDGE-SB884-07_Q15_CC.xlsxworkbook. ii. Explain the discrepancy between the unit cost of approximately $1.44M presented in the May 21 2025 2026-2028 Base Wildfire Mitigation Plan Workshop on slide 96 and what was presented in the SDGE Response SPD-SDGE-SB884-07_Q15_CC.xlsxworkbook. iii. Explain why in the SDGE Response SPD-SDGE-SB884-07_Q15_CC.xlsx workbook three Project IDs0157-A-CC,0157-P-CC, and0157-S-CCalong with all of their associated data are duplicated. iv. If there is an update to the SDGE ResponseSPD-SDGE-SB884-07_Q15_CC.xlsx workbook that was used in the WMP, provide SPD with a copy of that workbook. v. If there is an update to the SDGE Response SPD-SDGE-SB884-07_Q15_CC.xlsx workbook that was used to prepare slide 96 2026-2028 Base Wildfire Mitigation Plan Workshop slide deck, provide SPD with a copy of that workbook. | a. In responding to this data request, SDG&E found that the cost estimates presented in Table 6-1 were erroneously derived from its 2025 RAMP workpapers, encompassing both Capital and O&M expenses. SDG&E will correct Table 6-1 in its WMP at the next available opportunity provided by Energy Safety guidelines. Expected Implementation Cost of Covered Conductor for the 3-year WMP cycle $183.10 million. The workpaper supporting this cost forecast is provided in the attached spreadsheet titled “SDGE Response SPD-SDGE-WMP2026-001-Q04a_Q05a.xlsx” b. Yes, the 3-year target for Combined Covered Conductor (WMP.455) presented in Table 8-1 is 130 miles. c. [Regarding unit costs presented at Workshop  Lifecycle costs] i. The dataset used to generate the average cost per mile used in the workshop is included in the attached file titled “SDGE Response SPD-SDGE-WMP2026-001-Q04.c.Lifecycle Cost Dataset hftd only.xlsx”. ii. The estimated installation cost of $1M/mile includes estimates for replacing all associated equipment, including, but not limited to, cross arms and poles, as needed and determined in design. iii. Lifecycle PSPS Cost = PSPS Activation Cost + PSPS Comm. Cust Outreach Cost PSPS Activation Cost = (baseline cost/mile + activation cost/mile × simulated frequency) × Overhead HFTD miles × 55 years PSPS Comm. Cust Outreach Cost = baseline cost/mile × Overhead HFTD miles × 55 years iv. [Overhead] Inspections + = Asset Inspection Costs + Asset Repair/Replacement Costs Overhead Asset Inspection Costs = (Detailed Inspection Cost per pole + Patrol Inspection Cost per pole + Wood Pole Intrusive Cost per pole + Drone Inspection Cost per pole) × ∫ frequency per year 1 × 55 years Overhead Asset Repair/Replacement Cost = (Replacement Capital cost + Repair Capital + Repair and Replacement O&M) × frequency × 55 years Veg Management Lifecycle Cost = tree related costs + pole related costs + fuel management Tree related costs = (inspections + trim/removal + audit) × ∫ frequency per year × 55 years Pole related costs = (inspections + clearing + audit) × ∫ frequency per year × 55 years Fuel management costs = cost per year × 55 years When assets are undergrounded, the cost for community outreach and emergency management costs are estimated to be reduced, 50% reduction is used in the current lifecycle model. v. There is no overlap between Inspections + and PSPS costs because the activities included in each are unique activities. vi. [Cost of replacement after 55 yrs. for five categories] 1. The current version 2.0 of the lifecycle model assumes that the life of the covered conductor and undergrounding asset is 55 years, therefore the replacement cost of these installations is not included in the 55-year lifecycle analysis. However, the replacement cost of existing equipment as a result of asset inspection corrective action is included. The purpose of the lifecycle model is to compare the cost difference in the next 55 years between covered conductor and underground mitigation alternatives. 2. N/A. 3. SDG&E has not replaced any covered conductor and therefore has no cost estimation at this time. However, replacing bare conductor with covered conductor is estimated at $1M/mile. vii. [Decommissioning costs for five categories] 1. The current version 2.0 of the lifecycle model assumes that the life of the covered conductor and underground asset is 55 years, therefore decommissioning cost is not included in the 55-year lifecycle analysis. The purpose of the lifecycle model is to compare the cost difference in the next 55 years between covered conductor and undergrounding mitigation alternatives. 2. N/A 3. The purpose of the lifecycle model is to compare the cost difference between covered conductor and underground mitigation options. Decommission related cost would be part of the project that grants the action of decommissioning after 55 years should better energy solution become available. viii. As explained in part a. above, the total 3-year cost to implement covered conductor in the 2026-2028 WMP cycle is $183.10 million. Furthermore, and as discussed prior, the total costs for the 3-year cycle also include costs for work potentially completed in years ahead of the cycle and years following the cycle. Therefore, it is inappropriate to derive unit costs using annual/cyclical costs and only the miles energized in that year/cycle. Additionally, the unit costs presented during the workshop of $1.44M in direct costs comprise $1M/mile for installation and $0.44M/mile for foundational elements, whereas the total cost to implement in the 3-year cycle is for installation only. These two costs are not comparable in that one includes lifecycle foundational costs and the other does not. d. Relevant to all responses below, SDG&E clarifies that the direct unit cost for covered conductor provided in response SPD-SDGE-SB884-07_Q15_CC.xlsx workbook is $1,037,000. i. As discussed in part a. above, the correct Table 6-1 Expected Implementation Cost of covered conductor for the 3-year cycle is $183.10 million. Again, it is inappropriate to derive a unit cost based on total cyclical costs. ii. The unit costs presented during the workshop of $1.44M/mile in direct costs comprise $1M/mile for installation and $0.44M/mile for foundational elements, whereas the cost of $1.037 million presented in SPD-SDGE-SB884-07_Q15_CC.xlsx is for installation only. These two costs are not comparable in that one includes lifecycle foundational costs and the other does not. However, SDG&E points out that the installation cost of $1M/mile in both the workshop slides and SPD-SDGE-SB884-07_Q15_CC.xlsx is comparable. iii. The three Project IDs – 0157-A-CC, 0157-P-CC, and 0157-S-CC along with their associated data, were inadvertently duplicated in the originally provided SPD-SDGE-SB884-07_Q15_CC.xlsx workbook. The duplicates have been removed, and the file was reuploaded with no further changes to SDG&E’s 884 website at https://www.sdge.com/rates-and-regulations/proceedings/SB-884-Expedited-Undergrounding-Program-Discovery-Data-Requests. iv. SDGE did not use SPD-SDGE-SB884-07_Q15_CC.xlsx workbook for the WMP. v. SDGE did not use SPD-SDGE-SB884-07_Q15_CC.xlsx workbook for the 2026-2028 Base Wildfire Mitigation Plan Workshop slide deck. | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001-Q04.c.Lifecycle%20Cost%20Dataset%20hftd%20only.xlsx | 1 | No | N/A | 2026-2028 Base Wildfire Mitigation Plan Workshop | N/A | N/A
92 | SPD | 1 | SPD-1 | 5 | SPD-1.5 | During the 2026-2028 Base Wildfire Mitigation Plan Workshop hosted by Energy Safety on May 21 2025, SDG&E presented slides describing the unit cost of undergrounding as approximately $2.18 million. In SDG&E’s 2026-2028 Base WMP Table 6-1 presents Strategic Undergrounding (WMP.473) as having an Expected Implementation Cost of $435,575,000. Table 8-1 presents the 3-year total for Strategic Undergrounding (WMP.473) miles as 50. This amounts to a unit cost of $8,711,500. a. Provide all workpapers that support how SDG&E arrived at the Expected Implementation Cost of Strategic Undergrounding of $435,575,000. i. If an incorrect value was input into Table 6-1, provide the correct value and explain why the value was incorrectly recorded in Table 6-1. b. Confirm that the 3-year total for Strategic Undergrounding (WMP.473) is 130 miles. i. If it is not, provide the correct value and explain why the value was incorrectly recorded in Table 8-1. c. Provide all workpapers that support how SDG&E arrived at the unit cost for strategic undergrounding as presented in the May 21 2025 2026-2028 Base Wildfire Mitigation Plan Workshop on slide 96. i. The workpaper(s) must explain how each of the four components (Installation, Inspections+, PSPS and Foundational) were calculated. ii. Provide a detailed description of the PSPS costs. iii. Provide a detailed description of the Inspections+ costs. iv. How might the PSPS and Inspections+ costs overlap? If they do not overlap, explain why. v. Do any of the five categories include the cost for replacement of the asset after its 55 year use life is complete? 1.If yes, explain how that was calculated. 2.If not, explain why not. 3.If not, provide an estimate of the replacement cost/mile of covered conductor vi. Do any of the five categories include the cost for decommissioning or disposing (i.e. net negative salvage) of the asset after its 55 year use life is complete? 1.If yes, explain how that was calculated. 2.If not, explain why not. 3.If not, provide an estimate of the decommissioning cost/mile of covered conductor vii. Explain the discrepancy between the unit cost of $8,711,500 in the WMP and what was presented at the Workshop. d. In SDGE’s Response to Question 15 of the data request SPD-SDGE-SB884-07, SDG&E provided the SDGE Response SPD-SDGE-SB884-07_Q15_UG.xlsx workbook. The total cost per energized mile and total cost per trench mile presented in this workbook presents SDG&E’s unit cost for strategic undergrounding as $2,300,569 and $2,834,747 respectively. i. Explain the distinction between energized mile and trench mile as presented in the SDGE Response SPD-SDGE-SB884-07_Q15_UG.xlsx workbook. ii. Does the unit cost of $8,711,500 included in the WMP represent a cost per energized mile or a cost per trench mile? Explain. iii. Does the unit cost of approximately $2.18M that was included in the May 21 2025 2026-2028 Base Wildfire Mitigation Plan Workshop on slide 96 represent a cost per energized mile or a cost per trench mile? Explain. iv. Explain the discrepancy between the unit cost of $8,711,500 in the WMP and what was presented in the SDGE Response SPD-SDGE-SB884-07_Q15_UG.xlsx. v. Explain the discrepancy between the unit cost of approximately $2.18M presented in the May 21 2025 2026-2028 Base Wildfire Mitigation Plan Workshop on slide 96 and what was presented in the SDGE Response SPD-SDGE-SB884- 07_Q15_UG.xlsx. vi. If there is an update to the SDGE Response SPD-SDGE-SB884-07_Q15_UG.xlsx workbook that was used in the WMP, provide SPD with a copy of that workbook. vii. If there is an update to the SDGE Response SPD-SDGE-SB884-07_Q15_UG.xlsx workbook that was used to prepare slide 96 2026-2028 Base Wildfire Mitigation Plan Workshop slidedeck, provide SPD with a copy of that workbook. | a. In responding to this data request, SDG&E found that the cost estimates presented in Table 6-1 were erroneously derived from its 2025 RAMP workpapers, encompassing both Capital and O&M expenses. SDG&E will correct Table 6-1 in its WMP at the next available opportunity provided by Energy Safety guidelines. Expected Implementation Cost of Strategic Undergrounding (SUG) for the 3-year WMP cycle is $150.824 million. The workpaper supporting this cost forecast is provided in the attached spreadsheet titled “SDGE Response SPD-SDGE-WMP2026-001-Q04a_Q05a.xlsx.” b. The 3-year SUG target is 50 miles and is correctly presented in WMP Table 8-1. c. [Regarding workshop slides cost of $2.18M/mile, installation + foundational] SDG&E clarifies that the lifecycle unit cost of SUG presented in the workshop slides to which this question pertains is $2.59M/mile, which includes installation costs, inspections and maintenance costs, PSPS costs, and foundational costs over 55 years. i. The dataset used to generate the average cost per mile used in the workshop has been provided in the attached file titled “SDGE Response SPD-SDGE-WMP2026-001-Q04.c.Lifecycle Cost Dataset hftd only.xlsx”. ii. Lifecycle PSPS Cost = PSPS Activation Cost + PSPS Comm. Cust Outreach Cost PSPS Activation Cost = (baseline cost/mile + activation cost/mile × simulated frequency) × Overhead HFTD miles × 55 years PSPS Comm. Cust Outreach Cost = baseline cost/mile × Overhead HFTD miles × 55 years iii. Underground Asset Lifecycle Cost = Underground Asset Inspection Costs + Underground Repair and Replacement Costs Underground Asset Inspection Costs = (SS10 Inspection (Subsurface) + AGI/E Inspection (Padmount)) × ∫ frequency per year × 55 years Underground Repair and Replacement Costs = (Replacement Capital + Repair Capital + Repair and Replacement O&M) × ∫ frequency per year × 55 years iv. There is no overlap between Inspections + and PSPS costs because the activities included in each are unique activities. v. [Cost of replacement after 55 yrs. for five categories] 1. The current version 2.0 of the lifecycle model assumes that the life of the covered conductor and undergrounding asset is 55 years, therefore the replacement cost of these installations is not included in the 55-year lifecycle analysis. However, the replacement cost of existing equipment as a result of asset inspections corrective action is included. The purpose of the lifecycle model is to compare the cost difference in the next 55 years between covered conductor and underground mitigation alternatives. 2. N/A. 3. SDG&E has not replaced any newly installed, WMP-related undergrounded cable and therefore has no cost estimation at this time. vi. [Decommissioning costs for five categories] 1. The current version 2.0 of the lifecycle model assumes that the life of the covered conductor and underground asset is 55 years, therefore decommissioning cost is not included in the 55-year lifecycle analysis. However, the repair/replace/decommission cost of existing equipment as a result of asset inspections corrective action is included. The purpose of the lifecycle model is to compare the cost difference in the next 55 years between covered conductor and undergrounding mitigation alternatives. 2. N/A 3. The purpose of the lifecycle model is to compare the cost difference between covered conductor and underground mitigation alternatives. SDG&E does not have an estimate for decommissioning costs for undergrounded cable. vii. As explained in part a. above, the total 3-year cost to implement undergrounding in the 2026-2028 WMP cycle is $150.824 million. Furthermore, and as discussed prior, the total costs for the 3-year cycle also include costs for work potentially completed in years ahead of the cycle and years following the cycle. Therefore, it is inappropriate to derive unit costs using annual/cyclical costs and only the miles energized in that year/cycle. Additionally, the unit costs presented during the workshop of $2.18 million in direct costs comprise $2 million/mile for installation and $0.18 million/mile for foundational elements, whereas the total cost to implement in the 3-year cycle is for installation only. These two costs are not comparable in that one includes lifecycle foundational costs and the other does not. d. SDG&E clarifies that the direct unit cost for undergrounding provided in Response SPD-SDGE-SB884-07_Q15_UG.xlsx workbook is $1.930 million for energized miles and $2.379 million for trench miles. i. Trench mile is a unit of measure which includes civil construction (digging the trench & sub-structure locations, placement of conduit, etc.) required to complete a project(s), whereas Energized Mile is a unit of measure that includes the use of existing underground facilities (spare conduit) that were cabled as part of the project(s). ii. SDG&E clarifies that the unit cost of $8,711,500 is incorrect for two reasons. First, it was calculated with an erroneous Expected Implementation Cost in Table 6-1, and second, it is inappropriate to calculate unit costs using total annual/cyclical costs and annual/cyclical miles. That said, all costs presented by SDG&E refer to energized mile costs. iii. The unit cost of approximately $2.18M that was included in the May 21, 2025 2026-2028 Base Wildfire Mitigation Plan Workshop on slide 96 represents a cost per energized mile. iv. SDG&E clarifies that the unit cost of $8,711,500 is incorrect for two reasons. First, it was calculated with an erroneous Expected Implementation Cost in Table 6-1, and second, it is inappropriate to calculate unit costs using total annual/cyclical costs and annual/cyclical miles. Therefore, the costs in question are not comparable. v. The unit costs presented during the workshop of $2.18M/mile in direct costs comprise $2M/mile for installation and $0.18M/mile for foundational elements, whereas the cost of $1.93 million presented in SPD-SDGE-SB884-07_Q15_CC.xlsx is for installation only. These two costs are not comparable in that one includes lifecycle foundational costs and the other does not. However, SDG&E points out that the installation cost of $2M/mile in the workshop slides is comparable to $1.93M/mile in SPD-SDGE-SB884-07_Q15_CC.xlsx. vi. SDGE Response SPD-SDGE-SB884-07_Q15_UG.xlsx workbook was not used in the WMP. vii. SDGE Response SPD-SDGE-SB884-07_Q15_UG.xlsx workbook was not used in the workshop. | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001-Q04a_Q05a.xlsx | 1 | No | N/A | 2026-2028 Base Wildfire Mitigation Plan Workshop | N/A | N/A
93 | SPD | 1 | SPD-1 | 6 | SPD-1.6 | Did SDG&E incorporate the “savings” of operational mitigations like vegetation management when it cal-culated the cost-benefit ratio of strategic undergrounding in its 2026-2028 Base Wildfire Mitigation Plan? a. If so, provide a step-by-step explanation of how “savings” were integrated into the formula or calculat-ing a CBR in the WMP. | a. No. SDG&E does not incorporate the savings of operational mitigations not performed. | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf | 0 | No | N/A | Cost-benefit ratio in WMP Plan | N/A | N/A
94 | SPD | 1 | SPD-1 | 7 | SPD-1.7 | Did SDG&E incorporate the “savings” of operational mitigations like vegetation management when it calculated the cost-benefit ratio of undergrounding in its RAMP Application filed on May 15 2025? a. If so, is it synonymous with what was done in the WMP? i. If it is not synonymous, provide a step-by-step explanation of how “savings” were integrated into the formula for calculating a CBR in the RAMP. | No. SDG&E does not incorporate the savings of operational mitigations not performed. | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf | 0 | No | N/A | Cost-benefit ratio in WMP Plan | N/A | N/A
95 | SPD | 1 | SPD-1 | 8 | SPD-1.8 | On page 83 of SDG&E’s 2026-2028 Base Wildfire Mitigation Plan, it is mentioned that an optimization al-gorithm is being developed that “selects feeder segment bundles that, when upgraded, would minimize the anticipated residual wildfire and PSPS risks while maintaining a cost-benefit ratio greater than 1 (i.e., a net benefit) for the upgraded bundle”. Provide any documentation related to this optimization algorithm that currently exists. a. If the optimization algorithm is still being developed, explain how mitigations were selected for feeder segments presented in SDG&E’s 2026-2028 Base Wildfire Mitigation Plan. b. According to the SUG_2028_comp and CC_2028_comp spreadsheets within the SDGE_20262028_BaseWMP_Appendix_G_Supporting_Data_Errata.xlsx workpaper, the 211-312R feeder segment currently exhibits a CBR of below 1 for the WACC and Hybrid Discount Scenar-ios for undergrounding and for covered conductor for all of the discount scenarios. Does that mean the optimization algorithm would not recommend hardening the 211-312R feeder segment? i. If the algorithm would not recommend hardening, what other mitigations would SDG&E employ to ad-dress the risk on this feeder segment? ii. If would still recommend hardening, explain why. | a. Yes, the algorithm used to support mitigation selection is still under development and thus no documentation exists at this time. In the interim, SDG&E’s subject matter experts manually selected feeder segments by reviewing baseline risk, risk reduction potential, residual risk, and cost-benefit analysis across consecutive upstream and downstream segments. b. No, the algorithm does not automatically exclude feeder segments with a cost-benefit ratio (CBR) below 1. Instead, it is designed to optimize mitigation selection by evaluating combinations or “bundles” of consecutive upstream and downstream feeder segments. The goal of this bundling process is to minimize anticipated residual wildfire PSPS risks while ensuring that the overall bundled mitigation maintains a CBR greater than 1. Feeder segments with individual CBRs below 1 are still within the scope of the optimization algorithm. These segments may be included in a bundled mitigation package if their inclusion contributes to a net risk reduction that justifies the investment when considered alongside adjacent segments with higher CBRs. This approach allows the algorithm to account for system-level benefits and interdependencies that may not be realized when evaluating segments in isolation. i. The algorithm is designed solely to calculate bundled mitigation metrics and does not generate recommendations on whether to harden or not harden individual feeder segments. ii. Refer to response “i” above. | Edwin Schmitt | 2025-05-27 | 2025-05-30 | 2025-06-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-001.pdf | 0 | No | 6.1.2 | 6.1.2 Risk-Informed Prioritization . | N/A | N/A
96 | MGRA | 5 | MGRA-5 | 1 | MGRA-5.1 | With regard to SDG&E Data Request Response MGRA-2026-8-03-4 and MGRA-2026-8-04-3: SDG&E states that it applies its risk aversion function to all attributes related to wildfire, and that the power law correction for wildfire uses an exponent of 1.47. a. Under what conditions, if any, will this risk aversion function affect the choice of mitigation set used, and if there are differences how do they come about? b. Is cost/benefit ratio used explicitly used as a threshold to make decisions in any wildfire safety process, for spending requests, or in the choice of mitigations? If so state specifically where and how cost/benefit threshold is used. (That comparisons of CBRs is used is clear and need not be discussed.) | a) Risk aversion is integrated into the assessment of baseline risk, risk reduction potential, residual risk, and cost-benefit evaluations. SDG&E’s subject matter experts, including specialists in risk analytics, fire coordination, meteorology, and engineering, utilize these metrics to inform the selection of grid hardening strategies at the feeder-segment level. Final mitigation strategies are determined through detailed, site-specific scoping of each feeder segment. b) Cost-benefit ratio (CBR) is not used as a strict threshold or cutoff for decision-making in wildfire safety processes, spending requests, or mitigation selection. Rather, CBR is one of several key metrics used to inform prioritization and comparative evaluation of mitigation options. SDG&E’s wildfire mitigation planning process incorporates CBR analyses to assess the relative efficiency of different mitigation strategies, particularly at the feeder-segment level. However, final decisions also consider additional factors such as: - Operational feasibility and constructability, - Geographic and environmental constraints, and - Expert judgment from interdisciplinary teams (including fire science, engineering, and meteorology). Thus, while CBR comparisons are explicitly used to guide and support decision-making, they are not applied as absolute thresholds that determine whether a mitigation is approved or rejected. | Joseph Mitchell | 2025-05-30 | 2025-06-04 | 2025-06-04 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-05.pdf | 0 | No | N/A | MGRA-2026-8-03-4 and MGRA- 2026-8-04-3 | N/A | N/A
97 | MGRA | 5 | MGRA-5 | 2 | MGRA-5.2 | With regard to SDG&E Data Request Response MGRA-2026-8-04-11, CPUC rules state that when a utility uses a convex function to calculate fix, their analysis should be accompanied by a neutral function as well. a. Has SDG&E prepared a neutral risk analysis and presented in SDG&E_2026-2028_Base-WMP_Appendix G Supporting Data_R0.xlsx or elsewhere in public data, and if not can it provide one? | SDG&E’s neutral risk analysis is presented in the attached file titled “SDGE Response MGRA-2026-8-05_Q2”.xlsx. A revised version of risk aversion cost benefit calculations can be found in SDG&E’s substantive and non-substantive errata folder, dated May 16, at the following link: https://www.sdge.com/2026-2028-wildfire-mitigation-plan.. | Joseph Mitchell | 2025-05-30 | 2025-06-04 | 2025-06-04 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-05.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-05_Q2.xlsx | 1 | No | N/A | MGRA-2026-8-04-11 | N/A | N/A
98 | OEIS | 8 | OEIS-8 | 1 | OEIS-8.1 | Regarding Weather Station Outage Procedures SDG&E states on page 252 of its 2026-2028 Base WMP that the weather stations, “...have consistently maintained a 99 percent communication rate.” a. Provide the procedures utilized for the emergency repair and maintenance of the 217 weather stations owned and operated by SDG&E. Include the following: i. Average time from repair ticket initiation to completed repair and device back “in service.” ii. Procedure for maintenance/repair for other than communication rate issues. iii. Procedure for maintenance/repair for communication rate issues. iv. Acceptable percentage of stations “out of service” for other than communication rate issues that allow SDG&E to develop the daily/hourly weather forecasts and FPI values for the service area. | a. i. SDG&E does not have a formalized emergency repair procedure for its 217 weather stations; however, emergency maintenance is addressed through regular coordination with its contracted repair and calibration crews based out of the Kearny Maintenance & Operations District. Weather station issues are prioritized during weekly communications, and in the event of an emergency, the Kearny manager is contacted directly to initiate repair efforts. Additional meetings may be convened as needed to expedite resolution. Repair timelines are dependent on crew availability and the specific nature of the issue. As such, SDG&E does not maintain a standardized average repair time. Based on recent experience, emergency repairs have been completed within approximately one week from issue identification to the station being returned to service. ii. Maintenance and repairs follow a required maintenance schedule managed by Kearny Maintenance & Operations personnel. See attached document titled: OEIS-P_2025-08_Q1_532.075 Weather Station Inspection,Testing, Maintenance. iii. When communication rate issues arise, the first step is to contact the weather station and data vendor, Western Weather Group (WWG), for remote troubleshooting. If additional support is needed, Kearny Maintenance & Operations personnel are contacted. WWG and Kearny work collaboratively to diagnose and resolve communication rate problems. If the issue cannot resolved remotely, WWG will coordinate with a field technician to perform on-site maintenance or repairs. iv. SDG&E Meteorology does not use weather station observations to make weather forecasts or to produce the FPI. Model output is used for those tasks. | Zhenying Shao | 2025-05-30 | 2025-06-04 | 2025-06-04 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-08.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-P_2025-08_Q1_532.075%20Weather%20Station%20Inspection%2CTesting%2C%20Maintenance.pdf | 1 | No | 10.5 | 10.5 Weather Forecasting | 10.5.5 | 10.5.5 Weather Station Maintenance and Calibration .
99 | OEIS | 8 | OEIS-8 | 2 | OEIS-8.2 | Regarding SDG&E’s Right Tree, Right Place Mitigation Activity On page 285 of its 2023-2025 Base WMP, SDG&E sets a “target goal” to distribute 10,000 trees each year as a part of it’s Right Tree, Right Place (RTRP) mitigation activity. RTRP may encourage customers to replace powerline incompatible tree species with powerline compatible tree species. SDG&E did not include its RTRP mitigation activity in its 2026-2028 Base WMP, but did indicate in OEIS-P-WMP_2025_SDGE-002, question 02, that it “will continue to engage customers on the option to remove incompatible trees using the concept of Right Tree, Right Place during the inspection and tree pruning and removal activities during the 2026-2028 Base WMP.” a. Discuss how SDG&E will continue to promote incompatible tree replacement during the 2026-2028 Base WMP cycle. In doing so, address: i. How SDG&E encourages customer participation in its RTRP program (e.g., through pamphlets, information booths, vegetation management workers actively offering tree replacement, etc.). ii. How SDG&E considers which tree species to offer RTRP program participants and aims to replace non-native trees with native trees (e.g., through consultation with nurseries, arborists, master gardeners, etc.). iii. How SDG&E ensures its RTRP program retains its scope from year-to-year. | SDG&E encourages customer participation in the RTRP program in multiple ways, beginning with the Pre-Inspection activity. When an inspector identifies a tree that is incompatible with the power lines based on species, growth rate or other characteristics, they will contact the customer to discuss the benefits of tree removal and replacement. This discussion usually involves safety, compliance and reliability benefits of compatible trees near power lines. SDG&E also engages customers and the community on the RTRP concept and program during tree planting events, wildfire safety fairs, and other outreach venues and collateral. Additionally, SDG&E’s Vegetation Management website provides information, links, and appropriate suggested species for planting near powerlines. ii. SDG&E considers compatible trees for the RTRP program those whose mature canopy height does not require pruning for power line safety. RTRP is a mature concept and program within the utility vegetation management industry including multiple resources for identifying proper species selection. Additional components of the program include the utilization of native species where applicable and appropriate. The application of the program within SDG&E is made by Certified Arborists whose education and background provide the necessary knowledge to apply RTRP. iii. The scope of the RTRP fluctuates year to year and is based directly on the number of incompatible trees that are removed. This program is also an element of SDG&E’s sustainability initiative which includes targeted goals over multiple years. | Zhenying Shao | 2025-05-30 | 2025-06-04 | 2025-06-04 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-08.pdf | 0 | No | N/A | 2023-2025 WMP RTRP | N/A | N/A
100 | OEIS | 8 | OEIS-8 | 3 | OEIS-8.3 | Regarding Past Due Vegetation Management Work Orders On page 232 of its 2026-2028 Base WMP Substantive and Non-substantive Errata, SDG&E includes an updated version of OEIS Table 9-8. The errata version of OEIS Table 9-8 switches low priority and high priority row values relative to the version of OEIS Table 9-8 that SDG&E included in its response to OEIS-P-WMP_2025-SDGE-002, question 06. Thus, it is not clear which table is accurate. a. Provide the correct version of OEIS Table 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels. | OEIS Table 9-8 is accurate as presented in the response to OEIS-P-WMP_2025-SDGE-002, submitted on 14 May 2025, and as provided in the 2026-2028 Substantive and Non-substantive Errata, submitted on 16 May 2025. OEIS Table 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels. Priority Level 0-30 days 31-90 days 91-180 days 181+ days High Priority 40 12 2 0 Low Priority 335 242 4 1 | Zhenying Shao | 2025-05-30 | 2025-06-04 | 2025-06-04 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-08.pdf | 0 | No | 9.12.3 | 9.12.3 Trends . | OEIS Table 9-8 | 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels . 228
101 | OEIS | 8 | OEIS-8 | 4 | OEIS-8.4 | Regarding Top Risk Circuits a. On page 60 of SDG&E’s 2026-2028 Base WMP, SDG&E states that OEIS Table 5-5 “also includes segments that contribute to more than 1 percent of the Overall Utility risk”. Provide a list of these circuit segments, including the overall utility risk score and riskper- mile score associated with those circuit segments. b. On page 116 of SDG&E’s 2026-2028 Base WMP, SDG&E presents OEIS Table 6-4 showing the top-risk circuits. Describe how these top risk circuits were determined (i.e., top percentage, overall risk, or risk per mile). i. If not already the case, provide an updated version of OEIS Table 6-4 sorted using the same risk-per-mile methodology as OEIS Table 5-5, with the following additional columns: 1) Undergrounding planned for 2026 (circuit mileage) 2) Undergrounding planned for 2027 (circuit mileage) 3) Undergrounding planned for 2028 (circuit mileage) 4) Covered conductor planned for 2026 (circuit mileage) 5) Covered conductor planned for 2027 (circuit mileage) 6) Covered conductor planned for 2028 (circuit mileage) | a) See table below showing circuit-segments that exceed top 1% of the total risk across all circuit-segments upstreamardfacilityid overall_utility_risk_per_mile 222-1986R $ 3,725,802 222-1990R $ 3,168,165 358-682F $ 3,006,265 909-451 $ 2,682,718 909-805R $ 2,408,131 1458-601R $ 2,400,175 908-2038R $ 2,301,533 1021-1748F $ 1,983,191 upstreamardfacilityid overall_utility_risk_per_mile 237-30R $ 1,957,370 237-2R $ 1,847,268 524-69R $ 1,181,539 b) Refer to the following excel file with updated OEIS Table 6-4 sorted using the same risk-per-mile methodology as OEIS Table 5-5. This list is unfiltered and includes all segments in the territory. SDGE Response OEIS-P-WMP_2025-SDGE-08_Q4.xlsx | Zhenying Shao | 2025-05-30 | 2025-06-04 | 2025-06-04 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-08.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-08_Q4.xlsx | 1 | No | 5.5 | 5.5 Risk Analysis Results and Presentation . | 5.5.2 | 5.5.2 Top Risk-Contributing Circuits/Segments/Spans
102 | OEIS | 8 | OEIS-8 | 5 | OEIS-8.5 | Regarding Cost Benefit Ratio (CBR) In response to Energy Safety Data Request OEIS-P-WMP_2025-SDGE-07 Question 3, Energy Safety requested that SDG&E provide the CBR and risk reduction for both undergrounding and covered conductor for each project as used for decision-making, as specified by including columns (vi)-(ix). However, SDG&E only provided the CBR and risk reduction of the chosen hardening methodology for each project. a. Provide an updated response via Excel that includes two additional columns for each project provided for the CBR and risk reduction so that each project has values for both covered conductor and undergrounding. | The response is updated in the attached file “SDGE Response OEIS-P-WMP_2025-SDGE-08_Q5.xlsx.” | Zhenying Shao | 2025-05-30 | 2025-06-04 | 2025-06-04 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-08.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-08_Q5.xlsx | 1 | No | N/A | OEIS-P-WMP_2025-SDGE-07 Question 3 | N/A | N/A
103 | MGRA | 6 | MGRA-6 | 1 | MGRA-6.1 | For each of the risk drivers listed in OEIS Table 3-1 which has x% of either ignitions or overhead faults greater than 0.5%, please provide in tabular form the percentage reduction in risk events from the specified risk driver by applying the following mitigations: a. Covered conductor b. Combined covered conductor (CCC) with FCP and ESD c. CCC + PEDS | The percentage reduction in risk events for drivers with either ignition or overhead fault greater than 0.5% by mitigations has been provided in the attached spreadsheet titled “SDGE Response MGRA-2026-8-06.xlsx”. a. Covered Conductor: Can be found in Column H in the above-mentioned sheet b. CCC with FCP and EFD: Can be found in Column I in the above-mentioned sheet. SDG&E doesn’t have calculated effectiveness by driver for FCP and EFD. The risk reduction provided is an SME estimation of effectiveness. c. Protective Equipment and Devices Settings (PEDS), known within SDG&E as the Sensitive Relay Profile (SRP), serves as a reactive ignition mitigation strategy. These settings respond to fault currents without differentiating between various risk events, resulting in a consistent risk reduction percentage across all incidents. Historically, SDG&E has applied SRP selectively, activating it only during periods of heightened wildfire risk—approximately 7% of the year on average. While SDG&E does not measure efficacy by specific risk drivers, PEDS is 100% effective whenever it is enabled, as SDG&E has not experienced any downstream ignitions on SRP-enabled devices regardless of CCC installation. | Joseph Mitchell | 2025-06-06 | 2025-06-11 | 2025-06-11 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-06.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-06.xlsx | 1 | No | OEIS Table 3-1 | 3-1: List of Risks and Risk Drivers to Prioritize 11 | N/A | N/A
104 | OEIS | 9 | OEIS-9 | 1 | OEIS-9.1 | Regarding Weather Station Outage Percentage SDG&E states on page 252 of its 2026-2028 Base WMP that the weather stations, “...have consistently maintained a 99 percent communication rate.” a. Provide SDG&E’s established acceptable daily percentage of weather stations “out of service” for issues other than communication rate issues. | As stated in SDG&E’s response to question 6 of Data Request OEIS-P-WMP_2025-SDGE-05: SDG&E weather stations have consistently maintained a 99 percent communication rate. SDG&E does not have a set acceptable outage percentage because it is nearly impossible to ascertain an acceptable percentage. All weather stations operate independently of distribution circuits and are powered by batteries that are recharged by solar panels. Each high-risk circuit has a weather station associated with that circuit. However, some circuits are very long and have multiple weather stations associated with that circuit. Additionally, not all areas of the HFTD are affected the same way during Santa Ana wind events. Thus, picking weather stations that are inconsequential because other circuit associated stations could be used as a proxy is event and weather dependent and cannot be answered in a holistic manner. | Zhenying Shao | 2025-06-06 | 2025-06-11 | 2025-06-09 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-09.pdf | 0 | No | 10.5 | 10.5 Weather Forecasting | 10.5.5 | 10.5.5 Weather Station Maintenance and Calibration .
105 | OEIS | 10 | OEIS-10 | 1 | OEIS-10.1 | Regarding Idle Transmission Power Lines: a. How many circuit miles of idle transmission lines does SDG&E currently have located within the HFTD and HFRA? b. Do any of these idle, deenergized transmission lines run parallel to and in close proximity (within 1,000 feet) with energized transmission lines? i. If so, provide the number of circuit miles, and describe the spacing characteristics and location of each instance. c. Provide a preliminary estimate of idle transmission line miles planned for removal between 2026 and 2028. d. Provide SDG&E’s latest findings or studies on whether idle transmission lines present a potential induction risk that could result in unintended energization. e. Describe any procedures, policies, or future planned projects to mitigate the ignition risk of idle transmission lines that SDG&E is considering. | SDG&E objects to the request to the extent it seeks information that is protected by the attorney-client privilege and/or constitutes attorney work product. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. SDG&E currently maintains 14.69 circuit miles of idle transmission lines within Tier 2 and Tier 3 HFTD. b. Yes. SDG&E maintains 3 idle transmission lines within HFTD that share structures with or parallel (within 1,000 feet) existing energized transmission lines. b.i. - TL99925 shares structures with (1) transmission line and parallels (4) existing energized transmission lines across its entirety of 0.32 circuit miles. TL99925 parallel separation distances range from being on a shared structure to 280 feet apart. Distance Between (feet) Parallel Length (Circuit Miles) Same Structure – 230kV Same Structure 0.32 Parallel 1 - 138kV 100 0.32 Parallel 2 - 138kV 100 0.32 Parallel 3 - 69kV 180 0.32 Parallel 4 - 230kV 280 0.32 - TL99901 parallels (4) existing energized transmission lines. TL99901 totals 7.63 idle circuit miles. A breakdown of distances and parallel lengths is included below: Distance Between (feet) Parallel Length (Circuit Miles) Parallel 1 - 69kV 77 0.24 Parallel 2 - 69kV 60 5.54 Parallel 3 - 69kV 280 0.55 Parallel 4 - 230kV 60 5.53 - TL99904 parallels (4) existing energized transmission lines and also briefly parallels various non-SDGE lines. TL99904 totals 6.74 idle circuit miles. A breakdown of distances and parallel lengths is included below: Distance Between (feet) Parallel Length (Circuit Miles) Parallel 1 - 69kV 278 0.76 Parallel 2 - 230kV 55 0.03 Parallel 3 - 230kV 175 3.90 Parallel 4 - 230kV 175 3.91 Various Non - SDGE 130 3.27 c. SDG&E does not have any proposed plans to remove existing idle transmission lines within the HFTD. Portions of these lines are currently identified in future projects to be reused for new energized transmission lines. Approximately 4.7 miles of the existing idle TL99901 and 2.6 miles of the existing idle TL99904 are being evaluated for reuse or replacement as new energized transmission lines. d. See attached documents titled “OutOfServiceSummary.pdf” and “OOServiceCircuitSummary-AppendixA.pdf.” e. SDGE maintains a limited number of transmission lines that are currently out of service. The idle transmission lines are isolated and not grounded. These lines undergo regular inspections and are maintained in accordance with all applicable standards and requirements, as if they were energized. | Zhenying Shao | 2025-06-24 | 6/27/2025 7/3/2025 | 2025-07-03 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-10.pdf https://www.sdge.com/sites/default/files/regulatory/OutOfServiceSummary.pdf https://www.sdge.com/sites/default/files/regulatory/OOServiceCircuitSummary-AppendixA.pdf | 2 | No | N/A | Regarding Idle Transmission Power Lines: | N/A | N/A
106 | OEIS | 11 | OEIS-11 | 1 | OEIS-11.1 | On page 281 of its 2023-2025 Base WMP, SDG&E stated “In addition to the approximately 34,000 poles SDG&E clears every year for compliance and fire prevention, approximately 2,475 poles are cleared in the Local Responsibility Area (LRA). This includes poles located in areas of dense and/or highly flammable vegetation and/or located near steep topography.” On page 213 of its 2026–2028 Base WMP, SDG&E explains its decision to stop clearing poles with exempt equipment during the 2026–2028 WMP cycle, but it does not clarify why it decided to stop clearing poles in the LRA. a. Explain SDG&E’s decision-making process for no longer clearing poles in the LRA including locations with dense and/or highly flammable vegetation and/or located near steep topography. b. Provide details of any risk reduction measures that will compensate for the reduced volume of pole clearing work. | a. SDG&E breaks its service territory into discrete, geographical Vegetation Management Areas (VMA) for the purpose of performing all its vegetation management activities, including pole clearing. The VMA boundaries may be determined by several factors including but not limited to SDG&E Operational District boundaries, city boundaries, and geographical features. In most instances the VMAs are not delineated by the dividing line between the State Responsibility Area (SRA) and Local Responsibility Area (LRA). Therefore, the SRA/LRA boundary often intersects VMA boundaries resulting in VMAs that are entirely within SRA, LRA, or a blend of the two. Historically, in VMAs that contain SRA and LRA, SDG&E has also brushed the poles located within the LRA portion of the VMA to be consistent in the scope and application of PRC 4292. SDG&E will continue this approach moving forward. However, where SDG&E plans to halt pole clearing activities are in those VMAs that exist fully within the LRA. The approximate 2,475 poles described in the 2026-2028 WMP cycle are those that are located in VMAs that are entirely within the LRA. SDG&E’s decision to adjust its work practice and halt pole clearing activities in VMAs located entirely within the LRA was to ensure an appropriate balance between risk-mitigation and affordability for SDG&E ratepayers, consistent with the spirit of SDG&E’s applicable General Rate Case. Based on SDG&E’s ongoing wildfire mitigation work throughout the HFTD, SDG&E concluded that pole clearing within the entire LRA has limited additional risk mitigation value, given that SDG&E already has a robust pole clearing and fuels management program within the HFTD and the SRA. Additional factors contributing to the decision for no longer clearing poles within the LRA were the potential for negative environmental impacts caused by pole clearing, and to reduce impacts to customers. b. As stated in response to (a) above, SDG&E will continue to perform pole clearing within those VMAs whose boundary includes both LRA and SRA. For those VMAs that are entirely within the LRA, Vegetation Management will continue its annual pre-inspection activity which includes a visual foot patrol of each span to assess the relationship between trees and the overhead conductors. The electronic records that represent the LRA poles will remain visible to the inspectors who can report ground vegetation conditions that may warrant follow-on action. Additionally, through routine maintenance operations, where applicable, SDG&E replaces old pole hardware with Cal Fire-approved equipment. Such action removes the threat of ignition and negates the need to perform vegetation clearing at the base of the pole. | Zhenying Shao | 2025-06-24 | 6/27/2025 7/3/2025 | 2025-07-03 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-11.pdf | 0 | No | 9.4.4 | Updates | N/A | N/A
107 | OEIS | 11 | OEIS-11 | 2 | OEIS-11.2 | Regarding Public Resource Code section 4292 Non-Exempt and Exempt Pole Clearing: On page 272 of its 2023-2025 Base WMP, SDG&E stated that “Pole clearing (brushing) (WMP.512) is performed on approximately 34,000 poles located in the [State Responsibility Area (SRA)] of the service territory subject to PRC § 4292.” a. Complete the table below regarding SDG&E’s pole clearing work in the SRA during its 2023-2025 Base WMP cycle: State Responsibility Area (SRA) PRC 4292 Exempt/Non-Exempt Pole Statistics b. Complete the table below regarding SDG&E’s pole clearing work in the LRA during its 2023-2025 Base WMP cycle: Local Responsibility Area (LRA) PRC 4292 Exempt/Non-Exempt Pole Statistics c. Complete the table below regarding SDG&E’s pole clearing work in the FRA during its 2023-2025 Base WMP cycle: Federal Responsibility Area (FRA) PRC 4292 Exempt/Non-Exempt Pole Statistics | a. State Responsibility Area (SRA) PRC 4292 Exempt/Non-Exempt Pole Statistics 2023 2024 Total Number of Poles with PRC 4292 Exempt and Non-Exempt Equipment 35,507 34,826 Number of Poles with PRC 4292 Exempt Equipment 10,162 10,162 Number of Brushed Poles with PRC 4292 Exempt Equipment 8,293 8,361 Number of Poles with PRC 4292 Non-Exempt Equipment 25,345 24,664 Number of Brushed Poles with PRC 4292 Non-Exempt Equipment 21,933 21,856 b. Local Responsibility Area (LRA) PRC 4292 Exempt/Non-Exempt Pole Statistics 2023 2024 Total Number of Poles with PRC 4292 Exempt and Non-Exempt Equipment 2,645 3,440 Number of Poles with PRC 4292 Exempt Equipment 1,266 1,266 Number of Brushed Poles with PRC 4292 Exempt Equipment 409 584 Number of Poles with PRC 4292 Non-Exempt Equipment 1,379 2,174 Number of Brushed Poles with PRC 4292 Non-Exempt Equipment 882 1,078 c. Federal Responsibility Area (FRA) PRC 4292 Exempt/Non-Exempt Pole Statistics 2023 2024 Total Number of Poles with PRC 4292 Exempt and Non-Exempt Equipment 1,957 1,847 Number of Poles with PRC 4292 Exempt Equipment 328 328 Number of Brushed Poles with PRC 4292 Exempt Equipment 255 261 Number of Poles with PRC 4292 Non-Exempt Equipment 1,629 1,519 Number of Brushed Poles with PRC 4292 Non-Exempt Equipment 1,386 1,500 | Zhenying Shao | 2025-06-24 | 6/27/2025 7/3/2025 | 2025-07-03 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf | 0 | No | N/A | 2023-2025 Base WMP | N/A | N/A
108 | SPD | 2 | SPD-2 | 1 | SPD-2.1 | In response to Question 3 of SPD-SDG&E-WMP 2026-001 SDG&E submitted a slide deck called “SDGE WMP 2026-2028_Presentation.” On slide 20, SDG&E presented its strategic undergrounding mitigation effectiveness calculation. The following are questions regarding the slide: a. SDG&E estimates that undergrounding is 95% effective at mitigating the risk of drivers related ignitions on the underground system. i. Would it be correct to interpret this as SDG&E estimates that an ignition associated with underground lines is 95% less risky than an overhead ignitions? 1. Provide any SDG&E studies to justify that an underground ignition is less risky than an overhead ignition. 2. SDG&E states that ignitions associated with the underground system are unlikely to cause wildfires due to underground assets’ enclosed and protected nature. What proof exists that this is correct? 3. SDG&E is reporting non-reportable and reportable ignitions in the data set. What percentage of ignitions are reportable for each of the drivers? 4. SDG&E’s four largest CPUC-reportable ignitions between 2015 and 2024 (ignitions on 4/12/2015, 7/6/2018, 5/22/2018, 7/1/2024) were each located in rural areas with a relative abundance of fuel sources. Many of the underground or padmounted reportable ignitions appear to be near more densely populated areas with limited fuel sources. How can SDG&E ensure that the reason for undergrounded ignitions appearing to be less risky is not that they are less risky but instead that undergrounded lines are in areas with less fuels as compared to the overhead lines which result in the more impactful overhead ignitions? b. Correct the mitigation effectiveness calculation to fix the arithmetic error which conflates the drivers for outage ignitions. The chart computes the mitigation effectiveness of undergrounding by comparing the number of ignitions from drivers before versus after being mitigated. However, the chart adds the drivers of underground ignitions to the drivers overhead ignitions, as an “ignition being mitigated.” These drivers of undergrounding ignitions will not be mitigated by undergrounding. In fact – the newly undergrounded lines will now be subject to these new set of underground ignition drivers – and so the number of undergrounding related ignitions to increase as lines are undergrounded. c. Provide a workpaper which computes the strategic undergrounding mitigation effectiveness calculation, but only includes ignitions that occurred the HFTD. | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional con-cerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the is-sues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 | 7/2/2025 7/16/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q1c_HFTD_CPUC_Reportable_Ignitions_for_SUG_2025_07_16.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf | 1 | N/A | N/A | SPD-SDG&E-WMP 2026-001 | N/A | N/A
109 | SPD | 2 | SPD-2 | 2 | SPD-2.2 | Provide a workpaper which shows the study which demonstrates how the estimated effectiveness of covered conductor has degraded overtime as discussed on page 11 of “Joint IOU Grid Hardening Working Group Report: Update for 2026-2028 Wildfire Mitigation Plan.” a. How many of the equipment failures used on the “traditionally (bare conductor) hardening” related to non-exempt equipment? | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 7/2/2025 7/16/2025 7/24/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02__Q2_Hardening%20Efficacy.xlsx | 0 | N/A | Attachment A | Attachment A: Joint IOU Grid Hardening Working Group Report: Update for 2026-2028 Wildfire Mitigation Plan | N/A | N/A
110 | SPD | 2 | SPD-2 | 3 | SPD-2.3 | Provide an update ignition dataset through 2024 to the one previously provided as part of, “WSPS-SDGE-2023WMP-02 SDG&E RESPONSE.” a. Provide non-reportable ignitions used in the covered conductor and undergrounding mitigation effectiveness study under the same format. b. Include an additional column which classifies each ignition as one of the drivers used in the underground ignitions analysis slide 20 of “SDGE WMP 2026-2028_Presentation.” c. Include an additional column which classifies each ignition as the driver used for the covered conductor ignition mitigation effectiveness study on slide 21 of “SDGE WMP 2026-2028_Presentation.” d. Include a column which indicates which ignitions were used to determine the reduction in 10-year effectiveness of system hardening as described on page 11 of “Joint IOU Grid Hardening Working Group Report: Update for 2026-2028 Wildfire Mitigation Plan” e. Include a column which classifies if the “equipment involved with ignition” was exempt or non-exempt. | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 7/2/2025 7/16/2025 7/24/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02__Q3.xlsx | 0 | N/A | N/A | WSPS-SDGE-2023WMP-02 | N/A | N/A
111 | SPD | 2 | SPD-2 | 4 | SPD-2.4 | SPD understands SDG&E uses its “OH CMP Detailed Inspection Instructor Guide” to provide guide to its overhead inspectors. The guide provides little information as to how to prioritize corrective actions as level 1s, level 2s or level 3 per Rule 18 of General Order 95. What other guidance does SDG&E give its inspectors to ensure consistency between inspectors? a. For instance – one can imagine a pole that is split at the top, which may need a different priority depending on the severity. How does SDG&E ensure their inspectors assign a similar priority level for these types of condi-tions? Does SDG&E provide pictures to its inspectors showing different priority levels? | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 | 7/2/2025 7/16/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf | 0 | N/A | N/A | OH CMP Detailed Inspection Instructor Guide | N/A | N/A
112 | SPD | 2 | SPD-2 | 5 | SPD-2.5 | What steps has SDG&E taken to archive any data or models related to current and past risk models? a. Have any aspects of the current version of the Wings-Planning risk framework not been archived? If so, explain why they were not archived. i. If any aspects of the current version of the Wings-Planning risk framework were not archived, would this prevent a party from asking for data analysis the current version of the Wings-Planning risk framework in the future? b. How long will SDG&E maintain its archive of the data or models related to the current version of the Wings-Planning risk framework? c. What data is SDG&E maintaining of its previous asset data? What data would be missing if SDG&E wanted to backcast the risk in pre-2023 years using the current version of the Wings-Planning risk framework? d. How is SDG&E working to ensure that future models have the data necessary to backcast the risk to current system configurations? | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 | 7/2/2025 7/16/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_0.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf | 0 | N/A | N/A | Archive data or models related to current and past risk models | N/A | N/A
113 | SPD | 2 | SPD-2 | 6 | SPD-2.6 | In Response to Question 5.d.i of “SPD-SDGE-WMP2026-001,” SDG&E stated the following: Trench mile is a unit of measure which includes civil construction (digging the trench & sub-structure locations, placement of conduit, etc.) required to complete a project(s), whereas Energized Mile is a unit of measure that includes the use of existing underground facilities (spare conduit) that were cabled as part of the project(s). SPD understands that the work that SDG&E is performing is usually new work and so is confused as to how the energized mile only relates to existing work. Because of this, SPD is interpreting that the energized cost per mile is in addition to the trench cost per mile – and so understands that the full cost per mile of undergrounding is 1.930+2.379=$4.309 million per mile. If this is not correct, provide a diagram which shows the difference between energized miles and trench miles. | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 7/2/2025 7/16/2025 7/24/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf | 0 | N/A | N/A | SPD-SDGE-WMP2026-001 | N/A | N/A
114 | SPD | 2 | SPD-2 | 7 | SPD-2.7 | In response to SPD-SDGE-WMP2026-001 Question 2, SDG&E provided SPD with the file SDGE Response SPD-SDGE-WMP2026-001-Q02.b.Lifecycle Cost Dataset.xlsx. This Excel workbook includes the “lifecycle cost all territory” spreadsheet and each field in this spreadsheet is defined in the “metadata definition” spreadsheet. In the “metadata definition” spreadsheet of SDGE Response SPD-SDGE-WMP2026-001-Q02.b.Lifecycle Cost Dataset.xlsx it is explained that the field “total_if_ug_cost_per_mile”1 is calculated using the following formula: “total_ug_asset_cost_per_mile + total_ug_psps_cost_per_mile”. Additionally, the field “total_ug_asset_cost_per_mile” is calculated using the following formula: total_ug_inspection_cost_per_mile + total_ug_repair_cost_per_mile. a. Explain how SDG&E calculated values for each of the following fields: i. total_ug_inspection_cost_per_mile ii. total_ug_repair_cost_per_mile iii. total_ug_psps_cost_per_mile b. Explain why the total_ug_repair_cost_per_mile field includes a value of $247,280 for every feeder segment. c. Explain how each of the fields discussed in Question 7a. relate to corresponding values in the “Unit Cost” spreadsheet found in SDGE Response SPD-SDGE-WMP2026-001- Q02.b.Lifecycle Cost Dataset.xlsx. For instance, did SDG&E use the estimate of $1.43M/year for Total UG Inspection Cost in the “Unit Cost” Spreadsheet to inform total_ug_inspection_cost_per_mile field found in the “lifecycle cost all territory” spreadsheet. i. If not, explain why not. d. Provide any datasets that informed the calculation of the fields listed in Question 7a. e. Explain why Appendix G does not include separate spreadsheets for “UG Inspections”. f. For each of the fields listed in Question 7a., explain if the costs associated with that field fund a Mitigation or Control “Program” as defined in Row 28 of the RDF.2 i. Provide the page number in D.24-12-074 or its Appendices that discuss this Program and its costs. ii. Provide the page number in the Sempra 2024 Risk Spend Accountability Report (RSAR) that discusses this Program and its costs. 1. Provide an Excel version of the Sempra 2024 RSAR iii. Explain which budget code SDG&E used in its 2024 Test Year GRC to recover the costs presented in each field. iv. Explain if SDG&E intends to use a similar budget code to present these forecasted costs in its 2028 Test Year GRC. v. Explain which workpaper and cost center(s) SDG&E used in its 2024 Test Year GRC to recover the costs presented in this field. vi. Explain if SDG&E intends to use a workpaper and cost center(s) to present these forecasted costs in its 2028 Test Year GRC. g. In the “Unit Cost” spreadsheet for the SS10 Inspection (Subsurface) and AGI Inspection (Padmount) SDG&E has indicated that this would occur on a 10 and 5 year frequency, respectively. i. Explain how these frequencies comply with GO 165 inspection requirements. ii. Explain any other inspections and patrols that are required for undergrounded feeder segments by GO 165 that are not listed in the Unit Cost spreadsheet. 1. What are the costs associated with these inspections and patrols. h. For each location where SDG&E references “Historical Data” in Column H of the “Unit Cost” spreadsheet, provide SPD with said dataset. i. The name of each dataset must only include the name of the Activity (Column A) and timespan of the data. For instance, for the data referenced in cell H17, the dataset must be named “UG Repair and Replacement Capital 2020-2024.xlsx”. ii. For each dataset, explain why only 1 or 5 years of data were used. Footnote 1: This field is defined as the “total cost of combined covered conductor related cost divided by the length of the circuit miles of the given segment”. Footnote 2: D.24-05-064, Appendix A at A-19 – A-20. | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 7/2/2025 7/16/2025 7/24/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q7.f.ii_SDGE.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q7_Long-term%20Operational%20Mitigation%20Costs.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q7_Long-Term%20Operational%20Mitigation%20Unit%20Costs.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q7_PSPS%20Costs%20%282021-2024%29.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q7_Underground%20Inspection%20Costs%202024.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q7_Underground%20Repair%20Costs%20%282023-24%29.xlsx https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02_Q7_Vegetation%20Management%20Costs%20%282015-2023%29.xlsx | 0 | N/A | N/A | SPD-SDGE-WMP2026-001 | N/A | N/A
115 | SPD | 2 | SPD-2 | 8 | SPD-2.8 | In the “metadata definition” spreadsheet of SDGE Response SPD-SDGE-WMP2026-001-Q02.b.Lifecycle Cost Dataset.xlsx it is explained that the field “total_if_cc_cost_per_mile”3 is calculated using the following formula: “total_oh_asset_cost_per_mile + total_oh_veg_cost_per_mile + total_cc_psps_cost_per_mile + total_oh_peds_cost_per_mile + microgrid_cost_per_mile”. Additionally, the field “total_oh_asset_cost_per_mile” is calculated using the following formula: “total_oh_inspection_cost_per_mile + total_oh_repair_cost_per_mile + pole_replacement_cost_per_mile”. a. Explain how SDG&E calculated values for each of the following fields: i. total_oh_veg_cost_per_mile ii. total_cc_psps_cost_per_mile iii. total_oh_peds_cost_per_mile iv. microgrid_cost_per_mile v. total_oh_inspection_cost_per_mile vi. total_oh_repair_cost_per_mile vii. pole_replacement_cost_per_mile b. Explain how each of the fields discussed in Question 8a. relate to corresponding values in the “Unit Cost” spreadsheet found in SDGE Response SPD-SDGE-WMP2026-001-Q02.b.Lifecycle Cost Dataset.xlsx. For instance, did SDG&E use the estimate of $35.62M/year for OH Replacement Capital in the “Unit Cost” spreadsheet to inform the pole_replacement_cost_per_mile field found in the “lifecycle cost all territory” spreadsheet. i. If not, explain why not. c. Provide any datasets that informed the calculation of the fields listed in Question 8a. d. For each of the fields listed in Question 8a., explain if those seven fields are representative of, connected to and/or directly calculated from the costs listed in any of the spreadsheets in Appendix G of the 2026-2028 Base WMP? For instance, do the values found in the total_oh_veg_cost_per_mile field correspond to any of the cost fields (i.e. PV Total Cost Capital + O&M, Mitigation Annual Cost etc.) found in the Pole_Clearing, Fuel_Management, Trim_and_Removal, Off_Cycle_Partrol and/or Veg_Detail_Inspection spreadsheets found in Appendix G. Explain. i. If not, explain why not. e. For each of the fields listed in Question 8a., explain if the costs associated with that field fund a Mitigation or Control “Program” as defined in Row 28 of the RDF.4 i. Provide the page number in D.24-12-074 or its Appendices that discuss this Program and its costs. ii. Provide the page number in the Sempra 2024 Risk Spend Accountability Report (RSAR) that discusses this Program and its costs. iii. Explain which budget code SDG&E used in its 2024 Test Year GRC to recover the costs presented in each field. iv. Explain if SDG&E intends to use a similar budget code to present these forecasted costs in its 2028 Test Year GRC. v. Explain which workpaper and cost center(s) SDG&E used in its 2024 Test Year GRC to recover the costs presented in this field. vi. Explain if SDG&E intends to use a workpaper and cost center(s) to present these forecasted costs in its 2028 Test Year GRC. f. In the “Unit Cost” spreadsheet the Average Annual Cost (HFTD) for OH Replacement Capital is $35.62M. i. Explain why this value is $35.62M when $25,000/pole * 700 wood poles/year = $17.5M. ii. Explain why the Frequency of OH Replacement Capital is 700 wood poles/year, but in the notes it says “700 poles on average were replaced in the last 5 years”. iii. How many wood poles currently exist in SDG&E’s territory? iv. How many wood poles currently support covered conductor on SDG&E’s electric grid? v. Provide a dataset that demonstrates the distribution of the age of wood poles that currently exist in SDG&E’s territory. Include a variable in the dataset that designates wood poles that support covered conductor. vi. Regarding the forecast that 700 poles supporting covered conductor on average would be replaced each year, does SDG&E’s estimate of 700 wood poles per year for covered conductor include any other pole replacement programs related to the following issues: 1. deterioration, 2. overloading, and 3. emergencies. Footnote 3: This field is defined as the “total cost of undergrounding related cost divided by the length of the circuit miles after the given segment is undergrounded” Footnote 4: D.24-05-064, Appendix A at A-19 – A-20. | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 7/2/2025 7/16/2025 7/24/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02__Q8_f_iii-v.xlsx | 0 | N/A | N/A | PD-SDGE-WMP2026-001-Q02.b | N/A | N/A
116 | SPD | 2 | SPD-2 | 9 | SPD-2.9 | For every mitigation or control program spreadsheet5 found in Appendix G of the 2026-2028 Base WMP, explain the following: a. What is the capital investment associated with the “Capital Cost only in Year 0” field for this program b. What are the “Long-term Ongoing costs” for this program c. What are the “Additional Installation Cost (O&M) only in Year 0” for this program d. Explain why SDG&E does or does not calculate the risk reduction for the safety and reliability attributes for this program. e. Explain why SDG&E does or does not leave the “Mitigation Annual Cost (K$/year)” field empty for this program. f. Explain why the Present Value fields in Row 16 all include “Year 55” g. Explain why the Present Value fields in Row 20 all include “Year 40” h. Explain why the BCRs do or do not change across the three discount rate scenarios. | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 7/2/2025 7/16/2025 7/24/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf | 0 | N/A | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
117 | SPD | 2 | SPD-2 | 10 | SPD-2.10 | For the PV Risk Reduced and PV Total Cost fields in the mitigation and control program spread-sheets found in Appendix G of the 2026-2028 Base WMP, explain why SDG&E chose to estimate Present Value using the method found in the Inflation_and_Discount spreadsheet rather than to use the PV or Sequence functions that are native to Excel. a. Explain what are the values under WACC, Hybrid and Societal Discount rates in columns F, G, H on Rows 3-7 of the Inflation_and _Discount spreadsheet. | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 7/2/2025 7/16/2025 7/24/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf | 0 | N/A | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
118 | SPD | 2 | SPD-2 | 11 | SPD-2.11 | SDG&E’s underground cost is noticeably lower than that of other IOUs. SPD understands the contractors are paid at similar rates for the state of California. a. Describe any changes in the contracts, such as a longer-term contract that helps reduce the costs of undergrounding. i. In Appendix G of the 2026-2028 Base WMP, where would the costs of the longer-term contract be captured? b. Provide a high level cost analysis that includes consideration of structure installations, such as Manholes, Vaults, Pads, or any other structures required for the support of an undergrounding effort. i. Provide a cost analysis of each underground feeder segment submitted to Appendix G that in-cludes structure installations, such as Manholes, Vaults, Pads, or any other structures required for the support of an undergrounding effort. c. Provide a cost breakdown for a brand-new underground circuitry installed compared with a ret-rofit of an existing underground system. d. For spare conduits installed, do they meet the requirements for the new UG cable, and what would be the additional cost to replace the conduits. e. Provide relocation costs, if any, for both new and existing installation of UG circuitry. i. Explain whether or not relocation costs would also involve the upgrade of the existing structures to accommodate the addition of cable and equipment. f. If any of the UG structures contains third-party cables or equipment, what is the current process to relocate or retrofit the additional equipment/cable? i. What would be the added cost to relocate or retrofit the third-party equipment/cable? g. SPD understands that some costs of equipment are often centralized at company-wide level.6 For example, SPD understands that many companies buy distribution overhead transformers in bulk, so if a line were to be added, the cost of the project may not include the distribution overhead transformer as its supplied by the company. What (if any) of the costs associated with SDG&E’s undergrounding projects are centralized and therefore not included in the cost estimates? Footnote 6: See PG&E Response to Question 4 of TURN Data Request WMP-Discovery2026-2028_DR_TURN_003-Q004 and the workpaper WMP-Discovery2026-2028_DR_TURN_003-Q004Atch01.xlsx | OEIS issued an order rejecting SDG&E’s WMP and ordering that it be submitted by July 11th. In its order, OEIS pointed out specific “non-conforming elements, additional concerns, and non-substantive errata,” but also allowed SDG&E to make additional changes to its WMP. SDG&E is using this opportunity to review the entirety of its WMP. Given the issues raised in this data request, and to ensure SDG&E provides responses that align with its resubmitted WMP on July 11, the CPUC’s Safety Policy Division has granted SDG&E an extension to July 16 to provide responses to this data request. SDG&E’s July 16 response will be considered supplemental. | Edwin Schmitt | 2025-06-30 | 7/3/2025 7/16/2025 7/24/2025 | 2025-07-02 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20SPD-SDGE-WMP2026-02.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20_SPD-SDGE-WMP2026-02_.pdf | 0 | N/A | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
119 | OEIS | 12 | OEIS-12 | 1 | OEIS-12.1 | Regarding Public Resource Code Section 4292 Non-Exempt and Exempt Pole Clearing: a. Complete the table below regarding SDG&E’s pole clearing work in State Responsibility Areas (SRAs) located within the HFTD from 2022 to 2024: SRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics b. Complete the table below regarding SDG&E’s pole clearing work in Local Responsibility Areas (LRAs) located within the HFTD from 2022 to 2024: LRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics c. Complete the table below regarding SDG&E’s pole clearing work in Federal Responsibility Areas (FRAs) located within the HFTD from 2022 to 2024: FRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics | SDG&E is providing to the best of its ability the geographical location of its pole assets where clearing activities have occurred based on geospatial data and activity history. SDG&E notes that, for this data request, OEIS uses the term, “Cleared Poles”, while in a similar request for “OEIS-P-WMP_2025SDGE-11", OEIS uses the term, “Brushed Poles”. For clarity, SDG&E notes that these terms are interchangeable and identify the same activity. a. SRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics 2022 2023 2024 Total Number of Poles with PRC 4292 Exempt and Non-Exempt Equipment 32,561 32,568 32,097 Number of Poles with PRC 4292 Exempt Equipment 8,960 8,960 8,960 Number of Cleared Poles with PRC 4292 Exempt Equipment 7,475 7,561 7,621 Number of Poles with PRC 4292 Non-Exempt Equipment 23,601 23,608 23,137 Number of Cleared Poles with PRC 4292 Non-Exempt Equipment 20,917 20,867 20,781 b. LRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics 2022 2023 2024 Total Number of Poles with PRC 4292 Exempt and Non-Exempt Equipment 1,523 1,364 1,601 Number of Poles with PRC 4292 Exempt Equipment 624 624 624 Number of Cleared Poles with PRC 4292 Exempt Equipment 527 195 287 Number of Poles with PRC 4292 Non-Exempt Equipment 899 740 977 Number of Cleared Poles with PRC 4292 Non-Exempt Equipment 750 396 501 c. FRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics 2022 2023 2024 Total Number of Poles with PRC 4292 Exempt and Non-Exempt Equipment 1,847 1,918 1,806 Number of Poles with PRC 4292 Exempt Equipment 321 321 321 Number of Cleared Poles with PRC 4292 Exempt Equipment 259 252 259 Number of Poles with PRC 4292 Non-Exempt Equipment 1,526 1,597 1,485 Number of Cleared Poles with PRC 4292 Non-Exempt Equipment 1,517 1372 1,485 | Zhenying Shao | 2025-07-15 | 2025-07-18 | 7/18/2025 7/21/2025 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-12.pdf https://www.sdge.com/sites/default/files/regulatory/Amended%20SDGE%20Response%20to%20Question%201%20OEIS-P-WMP_2025-SDGE-02.pdf | 0 | No | N/A | 2022-2204 Public Resource Code Section 4292 Non-Exempt and Exempt Pole Clearing | N/A | N/A
120 | MGRA | 7 | MGRA-7 | 1 | MGRA-7.1 | Energy Safety Non-Conforming Element #3 states that SDG&E should address system wide risk reduction for its proposed hardening programs. Energy Safety Additional of Concern #1.b notes that SDG&E’s calculated risk reduction for its Combined Covered Conductor (CCC) and Strategic Undergrounding (SUG) programs is inconsistent with its estimate for ignition risk reduction for CCC and SUG. A comparison of SDG&E’s Table 8-1 estimated risk reduction in WMP R0 and R1 for its CCC and SUG programs, ostensibly showing per circuit and system wide risk reduction, is as follows: WMP R0 2026 2027 2028 Total Risk Reduction per Mile SUG Miles 0 0 50 50 CC Miles 50 50 30 130 SUG Risk Reduction 0 0 93.38% CCC Risk Reduction 23.8% 34.4% 43.9% WMP R1 SUG Miles 0 0 50 50 CC Miles 50 50 30 130 SUG Risk Reduction 0 0 4.05% 4.05% .081% CCC Risk Reduction 0.13% 0.40% 0.27% 0.80% .0062% a. Does this table accurately calculated SDG&E’s Table 8-1 estimations and results of Appendix G? If not please provide any corrections. b. In light of OEIS Additional Concern 1.b, how does SDG&E estimate that the amount of risk reduced per mile of SUG is 12X more than the amount of risk reduced by CCC? Please provide supporting technical documentation, calculations, and examples. | This table is accurately calculated in Appendix G for both WMP R0 and WMP R1. The key difference in the reported risk reductions lies in the scope of the baseline used. In WMP R0, risk reduction was calculated based on the feeder-segments included in the mitigation scope (tab CBR Summary by Risk, column H). In contrast, WMP R1 calculates risk reduction relative to the total service territory baseline risk (tab CBR Summary by Risk, column V), in alignment with the latest guidance from the OEIS.1 Risk reduction is driven by both baseline risk and mitigation effectiveness. SUG is modeled with a 98% mitigation effectiveness, making it generally more cost-effective on the riskiest portions of the system. In contrast, CCC, with a 61.7% effectiveness, is implemented on segments with comparatively lower risk. While the difference in mitigation effectiveness is close to 40%, SUG’s application to higher-risk areas results in a greater risk reduction per mile. | Joseph Mitchell | 2025-07-24 | 2025-07-29 | 2025-07-29 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-07.pdf | 0 | No | SDGE Table 8-1 | 8-1: Risk Event Rate with Pending Infractions 154 | N/A | N/A
121 | MGRA | 7 | MGRA-7 | 2 | MGRA-7.2 | Using neutral risk scaling rather than risk averse scaling, please provide: a. Table 8-1 entries for SUG and CCC hardening b. Appendix G with additional tabs showing neutral risk scaling for at least SUG and CCC hardening | a.Neutral risk scaling only affects the “% Risk Reduction <YEAR>” columns in table 8-1, as such, only these columns have been included. Neutral risk scaling is referred to as “NoAversion”: % Risk Reduction 2026 (NoAversion) % Risk Reduction 2027 (NoAversion) % Risk Reduction 2028 (NoAversion) Combined Covered Conductor 0.20% 0.37% 0.26% Strategic Undergrounding n/a (none scoped) n/a (none scoped) 2.52% b.See attached file titled “SDGE Response MGRA-2026-8-07_Q2_Appendix_G_WMP_BCR_NoAversion_2025_07_17_v4_Q2&Q3.xlsx.” This is a version of appendix G with NoAversion risk attitude. | Joseph Mitchell | 2025-07-24 | 2025-07-29 | 2025-07-29 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-07.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-07_Q2_Appendix_G_WMP_BCR_NoAversion_2025_07_17_v4_Q2%26Q3.xlsx | 1 | No | SDGE Table 8-1 | 8-1: Risk Event Rate with Pending Infractions 154 | N/A | N/A
122 | MGRA | 7 | MGRA-7 | 3 | MGRA-7.3 | Assuming that SDG&E entries for 2026, 2027, and 2028 assume a certain set of proposed circuits for mitigation using SUG and CCC, swap the 50 miles of circuits planned for CCC mitigation in 2026 (CCC tab 17-20) with the 50 miles of circuits planned for undergrounding in 2028 (SUG tab 17-23). This is to test the sensitivity of the risk reduction result to the circuits being selected. Provide both Appendix G tabs for CCC and SUG and Table 8-1 entries for SUG and CCC a. Using SDG&E’s risk averse scaling function b. Using risk neutral scaling | These comparisons are available in Appendix G available at https://www.sdge.com/2026-2028-wildfire-mitigation-plan. The raw comparison between the two at the feeder segment level can be found in the tab “SUG_vs_CCC,” as well as tabs “SUG_comp” and “CCC_comp.” Visual representations of the compared CBRs can be found in the “SUG_vs_CCC_plot” tab. There is one plot for each discount rate. Each orange square represents a feeder segment. The x axis measures the SUG CBR for the feeder segment, and the y axis measures the CCC CBR. The blue line denotes the point at which the SUG & CCC CBRs are equal. Points below the line indicate a higher SUG CBR and points above the line indicate a higher CCC CBR. These same resources can be found in the attached version of Appendix G that uses “NoAversion” risk attitude – as denoted in question 2. The plots can also be found below: | Joseph Mitchell | 2025-07-24 | 2025-07-29 | 2025-07-29 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-07.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-07_Q2_Appendix_G_WMP_BCR_NoAversion_2025_07_17_v4_Q2%26Q3.xlsx | 1 | No | SDGE Table 8-1 | 8-1: Risk Event Rate with Pending Infractions 154 | N/A | N/A
123 | MGRA | 8 | MGRA-8 | 1 | MGRA-8.1 | Regarding Appendix G and assignment of tranche to hardening work, and historical precedent. Please provide an Excel spreadsheet showing the circuit segments that were hardened as part of the SDG&E undergrounding program in the 2023-2025 period, including those planned but not completed in 2025, showing: a. Circuit feeder segment b. Number of miles mitigated c. Year(s) that mitigation was performed d. Quintile tranche ID assignment of circuit segment. e. HTM tranche ID assignment of circuit segment (if available) | SDG&E objects to the request to the extent it requires SDG&E to perform additional analyses and/or studies that do not currently exist, and is thus overly broad and unduly burdensome. SDG&E further objects to the request to the extent the request lacks relevance with respect to to SDG&E’s pending 2026-2028 WMP and is not reasonably calculated to lead the discovery of admissible evidence. Subject to and without waiving the foregoing objections, SDG&E responds as follows: See attached spreadsheet titled: “SDGE Response MGRA-2026-8-08_Q1and2_nb_output_TU_2025_07_30.xlsx” containing the circuit segments that were undergrounded as part of SDG&E’s Strategic Undergrounding program between January 1, 2023 and March 31, 2025. With respect to requests 1d and 1e, SDG&E is unable to provide tranche information (Quintile Tranche ID or HTM Tranche ID) for feeder segments in the 2023–2025 period. Tranche IDs are calculated based on baseline risk at the start of a planning period (i.e., 2023), and such calculations were not required for these segments at that time. However, as noted in Appendix G of SDG&E’s 2026-2028 WMP submission, each feeder segment is associated with a Tranche ID based on the updated 2025 baseline risk. | Joseph Mitchell | 2025-07-25 | 2025-07-30 | 2025-07-30 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-08.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-08_Q1and2_nb_output_TU_2025_07_30.xlsx | 1 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
124 | MGRA | 8 | MGRA-8 | 2 | MGRA-8.2 | Please provide an Excel spreadsheet showing the circuit segments that were hardened as part of the SDG&E covered conductor program in the 2023-2025 period, including those planned but not completed in 2025, showing: a. Circuit feeder segment b. Number of miles mitigated c. Year(s) that mitigation was performed d. Quintile tranche ID assignment of circuit segment. e. HTM tranche ID assignment of circuit segment (if available) | SDG&E objects to the request to the extent it requires SDG&E to perform additional analyses and/or studies that do not currently exist, and is thus overly broad and unduly burdensome. SDG&E further objects to the request to the extent the request lacks relevance with respect to to SDG&E’s pending 2026-2028 WMP and is not reasonably calculated to lead the discovery of admissible evidence. Subject to and without waiving the foregoing objections, SDG&E responds as follows: See attached spreadsheet titled “SDGE Response MGRA-2026-8-08_Q1and2_nb_output_TU_2025_07_30.xlsx” containing the circuit segments that were hardened as part of SDG&E’s Covered Conductor program between January 1, 2023 and March 31, 2025. With respect to requests 2d and 2e, SDG&E is unable to provide tranche information (Quintile Tranche ID or HTM Tranche ID) for feeder segments in the 2023–2025 period. Tranche IDs are calculated based on baseline risk at the start of a planning period (i.e., 2023), and such calculations were not required for these segments at that time. However, as noted in Appendix G of SDG&E’s 2026-2028 WMP, each feeder segment is associated with a Tranche ID based on the updated 2025 baseline risk. | Joseph Mitchell | 2025-07-25 | 2025-07-30 | 2025-07-30 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-08.pdf https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20MGRA-2026-8-08_Q1and2_nb_output_TU_2025_07_30.xlsx | 1 | No | Appendix G | Cost Benefit and Risk Reduction Supporting Data | N/A | N/A
125 | OEIS | 13 | OEIS-13 | 1 | OEIS-13.1 | Regarding SDG&E’s Pole Clearing Target WMP.512: SDG&E’s annual pole clearing target (WMP.512) in Revision 1 of its 2026–2028 Base WMP has decreased by 11,010 poles compared to its 2023–2025 Base WMP. However, Table 9-2 of the 2026–2028 Base WMP Revision 1 shows an increased estimated risk reduction benefit from this activity, increasing from 2.84%, as shown in the “x% Risk Impact” column of Table 8-14 in SDG&E’s 2023–2025 Base WMP, to 4.59% in the “% Risk Reduction” column of Table 9-2 in SDG&E’s 2026–2028 Base WMP Revision 1. a. Explain why the estimated risk reduction benefit from SDG&E’s pole clearing target (WMP.512) has increased in the 2026–2028 WMP cycle, despite the overall volume of work decreasing by 11,010 poles. | The difference of 11,010 poles in total targets between the 2023–2025 Base WMP and the 2026–2028 Base WMP is due to the exclusion of poles that are exempt from the vegetation clearance requirements of Public Resources Code 4292. The exemption is based on the presence of attached hardware defined as exempt by Cal Fire. Therefore, these poles are deemed to pose minimal fire risk. Additionally, note that the 2023–2025 Base WMP risk reductions are calculated using the Multi-Attribute Value Function (MAVF)1, while the 2026–2028 Base WMP Revision 1 risk reductions are based on a cost-benefit approach.2 These calculations are performed at different levels of granularity: the 2023–2025 WMP reductions are assessed at the Tier 2, Tier 3, and Non-HFTD levels, whereas the 2026–2028 WMP reductions are evaluated at the feeder-segment level. This shift in methodology and granularity resulted in a higher estimated risk reduction per unit of mitigation, with the effectiveness of pole clearing increasing by approximately 2.5 times in the 2026–2028 Base WMP Revision 1 compared to the earlier plan. 1 | Zhenying Shao | 2025-08-01 | 2025-08-06 | 2025-08-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-13.pdf | 0 | No | OEIS Table 9-2 | 9-2: Vegetation Inspections and Pole Clearing Targets by Year 208 | N/A | N/A
126 | OEIS | 13 | OEIS-13 | 2 | OEIS-13.2 | The Joint Study analyzed the effect of enhanced clearance distances using outages as a proxy for wildfire ignitions. This approach was used because the number of ignitions in the database is too small to draw robust conclusions. a. How many ignition datapoints are needed to conduct an analysis of the effect of enhanced clearances on the probability of ignition? i. Explain how this number was calculated. b. What data attributes are needed to perform this analysis? c. Does SDG&E already collect these attributes? i. If not, what attributes does SDG&E need to begin collecting? ii. If not, is SDG&E planning to collect these attributes? (1) If yes, when will SDG&E start collecting these attributes? (2) If not, why not? | a. SDG&E disagrees with the interpretation, “This approach was used because the number of ignitions in the database is too small to draw robust conclusions.” This data request does not include the citation from the White Paper or the third party’s assessment. As stated in the White Paper of the enhanced clearance study, the research results demonstrate that greater clearance reduces the probability of outages by a measurable amount. The study evaluates the impact of clearance on causing vegetation-bare conductor contacts and treats every vegetation-bare conductor contact as a heat event. The heat generated by such contact is one of the three factors that contribute to the probability of fire, as shown in the fire triangle figure. Because the purpose of the study is to evaluate the effectiveness of tree trimming clearance, measuring and modeling probability of vegetation contact is the correct method, whereas probability of ignition is not. Modeling probability of vegetation contact is equivalent to modeling probability of heat events caused by vegetation contact. When holding the other two factors (Oxygen and Fuel) consistent, a reduction in probability of heat event is a reduction in probability of fire or ignition. Such modeling in the study is the crucial part of modeling probability of fire or ignition caused by vegetation contact. Again, clearance is not the direct cause of fire. Therefore, the vegetation-caused ignition data points are not the data inputs needed for evaluating the effectiveness of tree trimming clearance. b. If the goal is to model the probability of fire or ignition caused by vegetation-bare conductor contact, the other two components required are the probability of fire due to the fuels condition (P fire), and probability of oxygen. Since it can be assumed that the probability of oxygen is 100% (=1), based on probability theorem, the probability of ignition given vegetation-bare conductor contact (P fire ¦ veg contact) is explained as follows: P(fire ∣ veg contact): Probability of fire given vegetation contact P(veg contact ∣ fire): Probability of vegetation contact given fire P(fire): Prior probability of fire due to fuels condition, regardless of the cause of the heat P(veg contact): Probability of vegetation contact The CPUC reportable ignition data are sufficient to calculate P (veg contact ∣ fire). The additional component left to evaluate is the probability of fire due to the fuels condition. This again confirms that the probability of ignition is not the right model for evaluating effectiveness of tree trimming since fuels conditions can change the probability of fire regardless of tree trimming. They are independent events. c.ii 1. SDG&E does not directly track or model fuels data internally. Instead, SDG&E partners with Technosylva, which provides annual updates to fuels maps and integrates fuel conditions into its fire behavior simulations. These maps incorporate surface and canopy fuel characteristics and are refreshed to reflect seasonal changes, disturbances, and regrowth. Technosylva uses this fuel layer, alongside weather, topography, and asset data to estimate site-specific fire spread conditions, which supports SDG&E’s operational and planning decision 2. SDG&E is not planning to collect data attributes because SDG&E receives fuels data from Technosylva. | Zhenying Shao | 2025-08-01 | 2025-08-06 | 2025-08-06 | https://www.sdge.com/sites/default/files/regulatory/SDGE%20Response%20OEIS-P-WMP_2025-SDGE-13.pdf | 0 | No | OEIS Table 9-2 | 9-2: Vegetation Inspections and Pole Clearing Targets by Year 208 | N/A | N/A

## WMP Sections (hidden)
| Section # | Section | Page #
1 Executive Summary ....................................................................................................................1 | 1 | 1 Executive Summary | 1
1.1 Primary Goal.................................................................................................................................. 2 | 1.1 | 1.1 Primary Goal. | 2
1.2 Objectives ...................................................................................................................................... 3 | 1.2 | 1.2 Objectives | 3
1.3 Framework for Development of the WMP ................................................................................... 4 | 1.3 | 1.3 Framework for Development of the WMP | 4
2 Responsible Persons ...................................................................................................................7 | 2 | 2 Responsible Persons . | 7
3 Overview of Base WMP ..............................................................................................................9 | 3 | 3 Overview of Base WMP | 9
3.1 Primary Goal.................................................................................................................................. 9 | 3.1 | 3.1 Primary Goal. | 9
3.2 Plan Objectives .............................................................................................................................. 9 | 3.2 | 3.2 Plan Objectives | 9
3.2.1 Public Safety Power Shutoff .................................................................................................. 9 | 3.2.1 | 3.2.1 Public Safety Power Shutoff | 9
3.2.2 Grid Design, Operations, and Maintenance ........................................................................ 10 | 3.2.2 | 3.2.2 Grid Design, Operations, and Maintenance | 10
3.2.3 Vegetation Management and Inspections .......................................................................... 10 | 3.2.3 | 3.2.3 Vegetation Management and Inspections | 10
3.3 Utility Mitigation Activity Tracking IDs ........................................................................................ 10 | 3.3 | 3.3 Utility Mitigation Activity Tracking IDs | 10
3.4 Prioritized List of Wildfire Risks and Risk Drivers ........................................................................ 11 | 3.4 | 3.4 Prioritized List of Wildfire Risks and Risk Drivers . | 11
3.5 Performance Metrics .................................................................................................................. 14 | 3.5 | 3.5 Performance Metrics . | 14
3.6 Projected Expenditures ............................................................................................................... 16 | 3.6 | 3.6 Projected Expenditures . | 16
3.7 Climate Change ........................................................................................................................... 16 | 3.7 | 3.7 Climate Change . | 16
4 Overview of the Service Territory .............................................................................................. 19 | 4 | 4 Overview of the Service Territory | 19
4.1 Service Territory .......................................................................................................................... 19 | 4.1 | 4.1 Service Territory . | 19
4.2 Catastrophic Wildfire History ...................................................................................................... 21 | 4.2 | 4.2 Catastrophic Wildfire History | 21
4.3 Frequently De-Energized Circuits ................................................................................................ 22 | 4.3 | 4.3 Frequently De-Energized Circuits | 22
5 Risk Methodology and Assessment ........................................................................................... 24 | 5 | 5 Risk Methodology and Assessment | 24
5.1 Methodology ............................................................................................................................... 24 | 5.1 | 5.1 Methodology . | 24
5.1.1 Overview ............................................................................................................................. 24 | 5.1.1 | 5.1.1 Overview | 24
5.2 Risk Analysis Framework ............................................................................................................. 29 | 5.2 | 5.2 Risk Analysis Framework | 29
5.2.1 Risk and Risk Component Identification ............................................................................. 30 | 5.2.1 | 5.2.1 Risk and Risk Component Identification | 30
5.2.1.1 WiNGS-Planning and WiNGS-Ops Models .................................................................. 33 | 5.2.1.1 | 5.2.1.1 WiNGS-Planning and WiNGS-Ops Models | 33
5.2.2 Risk and Risk Components Calculation ............................................................................... 34 | 5.2.2 | 5.2.2 Risk and Risk Components Calculation . | 34
5.2.2.1 Likelihood of Risk Event .............................................................................................. 37 | 5.2.2.1 | 5.2.2.1 Likelihood of Risk Event | 37
5.2.2.2 Consequence of Risk Event ......................................................................................... 37 | 5.2.2.2 | 5.2.2.2 Consequence of Risk Event | 37
5.2.2.3 Risk .............................................................................................................................. 40 | 5.2.2.3 | 5.2.2.3 Risk | 40
5.2.3 Key Assumptions and Limitations ....................................................................................... 43 | 5.2.3 | 5.2.3 Key Assumptions and Limitations . | 43
5.3 Risk Scenarios .............................................................................................................................. 46 | 5.3 | 5.3 Risk Scenarios . | 46
5.3.1 Design Basis Scenarios ........................................................................................................ 49 | 5.3.1 | 5.3.1 Design Basis Scenarios | 49
5.3.2 Extreme-Event/High Uncertainty Scenarios ....................................................................... 51 | 5.3.2 | 5.3.2 Extreme-Event/High Uncertainty Scenarios | 51
5.4 Summary of Risk Models ............................................................................................................. 53 | 5.4 | 5.4 Summary of Risk Models . | 53
5.5 Risk Analysis Results and Presentation ....................................................................................... 57 | 5.5 | 5.5 Risk Analysis Results and Presentation . | 57
5.5.1 Top Risk Areas within the HFRA .......................................................................................... 57 | 5.5.1 | 5.5.1 Top Risk Areas within the HFRA | 57
5.5.1.1 Geospatial Maps of Top-Risk Areas within the HFRA ................................................. 58 | 5.5.1.1 | 5.5.1.1 Geospatial Maps of Top-Risk Areas within the HFRA | 58
5.5.1.2 Proposed Updates to the HFTD .................................................................................. 59 | 5.5.1.2 | 5.5.1.2 Proposed Updates to the HFTD | 59
5.5.2 Top Risk-Contributing Circuits/Segments/Spans ................................................................ 60 | 5.5.2 | 5.5.2 Top Risk-Contributing Circuits/Segments/Spans | 60
5.6 Quality Assurance and Quality Control ....................................................................................... 60 | 5.6 | 5.6 Quality Assurance and Quality Control | 60
5.6.1 Independent Review ........................................................................................................... 60 | 5.6.1 | 5.6.1 Independent Review | 60
5.6.2 Model Controls, Design, and Review .................................................................................. 75 | 5.6.2 | 5.6.2 Model Controls, Design, and Review | 75
5.6.2.1 Modularization ............................................................................................................ 75 | 5.6.2.1 | 5.6.2.1 Modularization | 75
5.6.2.2 Reanalysis .................................................................................................................... 75 | 5.6.2.2 | 5.6.2.2 Reanalysis . | 75
5.6.2.3 Version Control ........................................................................................................... 75 | 5.6.2.3 | 5.6.2.3 Version Control . | 75
5.7 Risk Assessment Improvement Plan ........................................................................................... 76 | 5.7 | 5.7 Risk Assessment Improvement Plan | 76
5.7.1 Risk Assessment Methodology ........................................................................................... 76 | 5.7.1 | 5.7.1 Risk Assessment Methodology | 76
5.7.2 Design basis ......................................................................................................................... 76 | 5.7.2 | 5.7.2 Design basis . | 76
5.7.3 Risk Presentation ................................................................................................................ 77 | 5.7.3 | 5.7.3 Risk Presentation . | 77
5.7.4 Risk Event Tracking ............................................................................................................. 77 | 5.7.4 | 5.7.4 Risk Event Tracking | 77
5.7.5 Data Egineering Optimization ............................................................................................. 77 | 5.7.5 | 5.7.5 Data Egineering Optimization . | 77
6 Wildfire Mitigation Strategy ...................................................................................................... 81 | 6 | 6 Wildfire Mitigation Strategy | 81
6.1 Risk Evaluation ............................................................................................................................ 81 | 6.1 | 6.1 Risk Evaluation | 81
6.1.1 Approach ............................................................................................................................. 81 | 6.1.1 | 6.1.1 Approach | 81
6.1.2 Risk-Informed Prioritization ................................................................................................ 82 | 6.1.2 | 6.1.2 Risk-Informed Prioritization . | 82
6.1.2.1 Prioritized List of Risks ................................................................................................ 83 | 6.1.2.1 | 6.1.2.1 Prioritized List of Risks | 83
6.1.3 Activity Selection Process.................................................................................................... 85 | 6.1.3 | 6.1.3 Activity Selection Process. | 85
6.1.3.1 Identifying and Evaluating Mitigation Initiatives ........................................................ 86 | 6.1.3.1 | 6.1.3.1 Identifying and Evaluating Mitigation Initiatives | 86
6.1.3.2 Activity Prioritization ................................................................................................... 95 | 6.1.3.2 | 6.1.3.2 Activity Prioritization . | 95
6.1.3.3 Activity Scheduling .................................................................................................... 103 | 6.1.3.3 | 6.1.3.3 Activity Scheduling | 103
6.1.3.4 Key Stakeholders for Decision Making ...................................................................... 105 | 6.1.3.4 | 6.1.3.4 Key Stakeholders for Decision Making | 105
6.2 Wildfire Mitigation Strategy ...................................................................................................... 109 | 6.2 | 6.2 Wildfire Mitigation Strategy | 109
6.2.1 Anticipated Risk Reduction ............................................................................................... 109 | 6.2.1 | 6.2.1 Anticipated Risk Reduction | 109
6.2.1.1 Projected Overall Risk Reduction .............................................................................. 109 | 6.2.1.1 | 6.2.1.1 Projected Overall Risk Reduction | 109
6.2.1.2 Risk Impact of Activities ........................................................................................... 110 | 6.2.1.2 | 6.2.1.2 Risk Impact of Activities | 110
6.2.1.3 Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle | 6.2.1.3 | 6.2.1.3 Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle | cle
6.2.2 Interim Activities ............................................................................................................... 117 | 6.2.2 | 6.2.2 Interim Activities | 117
7 Public Safety Power Shutoff .................................................................................................... 119 | 7 | 7 Public Safety Power Shutoff . | 119
7.1 Overview ................................................................................................................................... 119 | 7.1 | 7.1 Overview | 119
7.2 Process for Initiating a PSPS De-Energization ........................................................................... 119 | 7.2 | 7.2 Process for Initiating a PSPS De-Energization | 119
7.3 PSPS Impact Redution on Frequently De-Energized Circuits .................................................... 122 | 7.3 | 7.3 PSPS Impact Redution on Frequently De-Energized Circuits | 122
7.4 Lessons Learned ........................................................................................................................ 123 | 7.4 | 7.4 Lessons Learned | 123
8 Grid Design, Operations, and Maintenance ............................................................................. 124 | 8 | 8 Grid Design, Operations, and Maintenance | 124
8.1 Targets....................................................................................................................................... 124 | 8.1 | 8.1 Targets. | 124
8.1.1 Qualitative Targets ............................................................................................................ 124 | 8.1.1 | 8.1.1 Qualitative Targets | 124
8.1.2 Quantitative Targets ......................................................................................................... 124 | 8.1.2 | 8.1.2 Quantitative Targets . | 124
8.2 Grid Design and System Hardening........................................................................................... 131 | 8.2 | 8.2 Grid Design and System Hardening | 131
8.2.1 Combined Covered Conductor Installation (WMP.455) ................................................... 131 | 8.2.1 | 8.2.1 Combined Covered Conductor Installation (WMP.455) | 131
8.2.1.1 Tracking ID ................................................................................................................. 131 | 8.2.1.1 | 8.2.1.1 Tracking ID | 131
8.2.1.2 | 8.2.1.2 | 8.2.1.2 | 1.2
8.2.1.3 Impact of the Activity on Wildfire Risk ...................................................................... 131 | 8.2.1.3 | 8.2.1.3 Impact of the Activity on Wildfire Risk . | 131
8.2.1.4 Impact of the Activity on Outage Program Risk ........................................................ 132 | 8.2.1.4 | 8.2.1.4 Impact of the Activity on Outage Program Risk . | 132
8.2.1.5 Updates to Activity .................................................................................................... 132 | 8.2.1.5 | 8.2.1.5 Updates to Activity | 132
8.2.1.6 Compatible Activities ................................................................................................ 132 | 8.2.1.6 | 8.2.1.6 Compatible Activities . | 132
8.2.2 Undergrounding of Electric Lines and/or Equipment (WMP.473) .................................... 132 | 8.2.2 | 8.2.2 Undergrounding of Electric Lines and/or Equipment (WMP.473) | 132
8.2.2.1 Tracking ID ................................................................................................................. 132 | 8.2.2.1 | 8.2.2.1 Tracking ID | 132
8.2.2.2 Overview of the Activity ............................................................................................ 133 | 8.2.2.2 | 8.2.2.2 Overview of the Activity | 133
8.2.2.3 Impact of the Activity on Wildfire Risk ...................................................................... 133 | 8.2.2.3 | 8.2.2.3 Impact of the Activity on Wildfire Risk | 133
8.2.2.4 Impact of the Activity on Outage Program Risk ........................................................ 133 | 8.2.2.4 | 8.2.2.4 Impact of the Activity on Outage Program Risk | 133
8.2.2.5 Updates to Activity .................................................................................................... 133 | 8.2.2.5 | 8.2.2.5 Updates to Activity | 133
8.2.2.6 Compatible Activities ................................................................................................ 134 | 8.2.2.6 | 8.2.2.6 Compatible Activities . | 134
8.2.3 Distribution Pole Replacements and Reinforcements ...................................................... 134 | 8.2.3 | 8.2.3 Distribution Pole Replacements and Reinforcements . | 134
8.2.3.1 Distribution Pole Replacement and Reinforcement Program .................................. 134 | 8.2.3.1 | 8.2.3.1 Distribution Pole Replacement and Reinforcement Program | 134
8.2.3.2 Strategic Pole Replacement Program (WMP.1189) .................................................. 135 | 8.2.3.2 | 8.2.3.2 Strategic Pole Replacement Program (WMP.1189) | 135
8.2.4 Transmission Pole/Tower Replacements and Reinforcements (WMP.472) ..................... 137 | 8.2.4 | 8.2.4 Transmission Pole/Tower Replacements and Reinforcements (WMP.472) | 137
8.2.4.1 Tracking ID ................................................................................................................. 137 | 8.2.4.1 | 8.2.4.1 Tracking ID | 137
8.2.4.2 Overview of the Activity ............................................................................................ 137 | 8.2.4.2 | 8.2.4.2 Overview of the Activity | 137
8.2.4.3 Impact of the Activity on Wildfire Risk ...................................................................... 137 | 8.2.4.3 | 8.2.4.3 Impact of the Activity on Wildfire Risk . | 137
8.2.4.4 Impact of the Activity on Outage Program Risk ........................................................ 137 | 8.2.4.4 | 8.2.4.4 Impact of the Activity on Outage Program Risk . | 137
8.2.4.5 Updates to Activity .................................................................................................... 137 | 8.2.4.5 | 8.2.4.5 Updates to Activity | 137
8.2.4.6 Compatible Activities ................................................................................................ 137 | 8.2.4.6 | 8.2.4.6 Compatible Activities . | 137
8.2.5 Traditional Overhead Hardening....................................................................................... 137 | 8.2.5 | 8.2.5 Traditional Overhead Hardening | 137
8.2.5.1 Distribution Overhead System Hardening (Traditional) (WMP.475) ........................ 137 | 8.2.5.1 | 8.2.5.1 Distribution Overhead System Hardening (Traditional) (WMP.475) | 137
8.2.5.2 Transmission System Hardening Program (WMP.543, WMP.545) ........................... 139 | 8.2.5.2 | 8.2.5.2 Transmission System Hardening Program (WMP.543, WMP.545) | 139
8.2.6 Emerging Grid Hardening Technology Installations and Pilots ......................................... 140 | 8.2.6 | 8.2.6 Emerging Grid Hardening Technology Installations and Pilots | 140
8.2.7 Microgrids (WMP.462) ...................................................................................................... 140 | 8.2.7 | 8.2.7 Microgrids (WMP.462) | 140
8.2.7.1 Tracking ID ................................................................................................................. 140 | 8.2.7.1 | 8.2.7.1 Tracking ID | 140
8.2.7.2 Overview of the Activity ............................................................................................ 140 | 8.2.7.2 | 8.2.7.2 Overview of the Activity | 140
8.2.7.3 Impact of the Activity on Wildfire Risk ...................................................................... 141 | 8.2.7.3 | 8.2.7.3 Impact of the Activity on Wildfire Risk | 141
8.2.7.4 Impact of the Activity on Outage Program Risk ........................................................ 141 | 8.2.7.4 | 8.2.7.4 Impact of the Activity on Outage Program Risk | 141
8.2.7.5 Updates to Activity .................................................................................................... 141 | 8.2.7.5 | 8.2.7.5 Updates to Activity | 141
8.2.7.6 Compatible Activities ................................................................................................ 141 | 8.2.7.6 | 8.2.7.6 Compatible Activities | 141
8.2.8 Installation of System Automation Equipment ................................................................. 141 | 8.2.8 | 8.2.8 Installation of System Automation Equipment | 141
8.2.8.1 Advanced Protection (WMP.463) ............................................................................. 141 | 8.2.8.1 | 8.2.8.1 Advanced Protection (WMP.463) | 141
8.2.9 Line Removal (in the HFTD) ............................................................................................... 144 | 8.2.9 | 8.2.9 Line Removal (in the HFTD) | 144
8.2.9.1 Tracking ID ................................................................................................................. 144 | 8.2.9.1 | 8.2.9.1 Tracking ID | 144
8.2.9.2 Overview of the Activity ............................................................................................ 144 | 8.2.9.2 | 8.2.9.2 Overview of the Activity | 144
8.2.9.3 Impact of the Activity on Wildfire Risk ...................................................................... 144 | 8.2.9.3 | 8.2.9.3 Impact of the Activity on Wildfire Risk | 144
8.2.9.4 Impact of the Activity on Outage Program Risk ........................................................ 144 | 8.2.9.4 | 8.2.9.4 Impact of the Activity on Outage Program Risk | 144
8.2.9.5 Updates to Activity .................................................................................................... 144 | 8.2.9.5 | 8.2.9.5 Updates to Activity | 144
8.2.9.6 Compatible Activities ................................................................................................ 144 | 8.2.9.6 | 8.2.9.6 Compatible Activities | 144
8.2.10 Other Grid Topology Improvements to Minimize Risk of Ignitions .................................. 144 | 8.2.10 | 8.2.10 Other Grid Topology Improvements to Minimize Risk of Ignitions | 144
8.2.11 Other Grid Topology Improvements to Mitigate or Reduce PSPS Events ........................ 145 | 8.2.11 | 8.2.11 Other Grid Topology Improvements to Mitigate or Reduce PSPS Events | 145
8.2.11.1 PSPS Sectionalizing Enhancement Program (WMP.461) .......................................... 145 | 8.2.11.1 | 8.2.11.1 PSPS Sectionalizing Enhancement Program (WMP.461) | 145
8.2.11.2 Standby Power Program (WMP.468) ........................................................................ 146 | 8.2.11.2 | 8.2.11.2 Standby Power Program (WMP.468) | 146
8.2.11.3 Customized Resiliency Assessments (WMP.1432) .................................................... 147 | 8.2.11.3 | 8.2.11.3 Customized Resiliency Assessments (WMP.1432) | 147
8.2.11.4 Generator Assistance Program (WMP.467) .............................................................. 148 | 8.2.11.4 | 8.2.11.4 Generator Assistance Program (WMP.467) | 148
8.2.12 Other Technologies and Systems not Listed Above .......................................................... 149 | 8.2.12 | 8.2.12 Other Technologies and Systems not Listed Above | 149
8.2.12.1 Ignition Management Program (WMP.558) ............................................................. 149 | 8.2.12.1 | 8.2.12.1 Ignition Management Program (WMP.558) | 149
8.2.13 Status Updates on Additional Technologies being Piloted ............................................... 149 | 8.2.13 | 8.2.13 Status Updates on Additional Technologies being Piloted | 149
8.3 Asset Inspections ...................................................................................................................... 150 | 8.3 | 8.3 Asset Inspections | 150
8.3.1 Distribution Overhead Detailed Inspections (WMP.478) ................................................. 153 | 8.3.1 | 8.3.1 Distribution Overhead Detailed Inspections (WMP.478) | 153
8.3.1.1 Overview ................................................................................................................... 153 | 8.3.1.1 | 8.3.1.1 Overview | 153
8.3.1.2 Frequency or Trigger ................................................................................................. 153 | 8.3.1.2 | 8.3.1.2 Frequency or Trigger | 153
8.3.1.3 Accomplishments, Roadblocks, and Updates ........................................................... 154 | 8.3.1.3 | 8.3.1.3 Accomplishments, Roadblocks, and Updates | 154
8.3.2 Transmission Overhead Detailed Inspections (WMP.479) ............................................... 155 | 8.3.2 | 8.3.2 Transmission Overhead Detailed Inspections (WMP.479) | 155
8.3.2.1 Overview ................................................................................................................... 155 | 8.3.2.1 | 8.3.2.1 Overview | 155
8.3.2.2 Frequency or Trigger ................................................................................................. 157 | 8.3.2.2 | 8.3.2.2 Frequency or Trigger | 157
8.3.2.3 Accomplishments, Roadblocks, and Updates ........................................................... 157 | 8.3.2.3 | 8.3.2.3 Accomplishments, Roadblocks, and Updates | 157
8.3.3 Transmission Infrared Inspections (WMP.482) ................................................................. 157 | 8.3.3 | 8.3.3 Transmission Infrared Inspections (WMP.482) | 157
8.3.3.1 Overview ................................................................................................................... 157 | 8.3.3.1 | 8.3.3.1 Overview | 157
8.3.3.2 Frequency or Trigger ................................................................................................. 158 | 8.3.3.2 | 8.3.3.2 Frequency or Trigger | 158
8.3.3.3 Accomplishments, Roadblocks, and Updates ........................................................... 159 | 8.3.3.3 | 8.3.3.3 Accomplishments, Roadblocks, and Updates | 159
8.3.4 Distribution Wood Pole Intrusive Inspections (WMP.483) ............................................... 159 | 8.3.4 | 8.3.4 Distribution Wood Pole Intrusive Inspections (WMP.483) | 159
8.3.4.1 Overview ................................................................................................................... 159 | 8.3.4.1 | 8.3.4.1 Overview | 159
8.3.4.2 Frequency or Trigger ................................................................................................. 160 | 8.3.4.2 | 8.3.4.2 Frequency or Trigger | 160
8.3.4.3 Accomplishments, Roadblocks, and Updates ........................................................... 161 | 8.3.4.3 | 8.3.4.3 Accomplishments, Roadblocks, and Updates | 161
8.3.5 Transmission Wood Pole Intrusive Inspections (WMP.1190) ........................................... 161 | 8.3.5 | 8.3.5 Transmission Wood Pole Intrusive Inspections (WMP.1190) | 161
8.3.5.1 Overview ................................................................................................................... 161 | 8.3.5.1 | 8.3.5.1 Overview | 161
8.3.5.2 Frequency or Trigger ................................................................................................. 161 | 8.3.5.2 | 8.3.5.2 Frequency or Trigger | 161
8.3.5.3 Accomplishments, Roadblocks, and Updates ........................................................... 161 | 8.3.5.3 | 8.3.5.3 Accomplishments, Roadblocks, and Updates | 161
8.3.6 Risk-Informed Drone Inspections (WMP.552) .................................................................. 162 | 8.3.6 | 8.3.6 Risk-Informed Drone Inspections (WMP.552) | 162
8.3.6.1 Overview ................................................................................................................... 162 | 8.3.6.1 | 8.3.6.1 Overview | 162
8.3.6.2 Frequency or Trigger ................................................................................................. 163 | 8.3.6.2 | 8.3.6.2 Frequency or Trigger | 163
8.3.6.3 Accomplishments, Roadblocks, and Updates ........................................................... 165 | 8.3.6.3 | 8.3.6.3 Accomplishments, Roadblocks, and Updates | 165
8.3.7 Distribution Overhead Patrol Inspections (WMP.488) ..................................................... 166 | 8.3.7 | 8.3.7 Distribution Overhead Patrol Inspections (WMP.488) | 166
8.3.7.1 Overview ................................................................................................................... 166 | 8.3.7.1 | 8.3.7.1 Overview | 166
8.3.7.2 Frequency or Trigger ................................................................................................. 166 | 8.3.7.2 | 8.3.7.2 Frequency or Trigger | 166
8.3.7.3 Accomplishments, Roadblocks, and Updates ........................................................... 167 | 8.3.7.3 | 8.3.7.3 Accomplishments, Roadblocks, and Update | 167
8.3.8 Transmission Overhead Patrol Inspections (WMP.489) ................................................... 167 | 8.3.8 | 8.3.8 Transmission Overhead Patrol Inspections (WMP.489) | 167
8.3.8.1 Overview ................................................................................................................... 167 | 8.3.8.1 | 8.3.8.1 Overview | 167
8.3.8.2 Frequency or Trigger ................................................................................................. 169 | 8.3.8.2 | 8.3.8.2 Frequency or Trigger | 169
8.3.8.3 Accomplishments, Roadblocks, and Updates ........................................................... 169 | 8.3.8.3 | 8.3.8.3 Accomplishments, Roadblocks, and Updates | 169
8.3.9 Substation Patrol Inspections (WMP.492) ........................................................................ 169 | 8.3.9 | 8.3.9 Substation Patrol Inspections (WMP.492) | 169
8.3.9.1 Overview ................................................................................................................... 169 | 8.3.9.1 | 8.3.9.1 Overview | 169
8.3.9.2 Frequency or Trigger ................................................................................................. 170 | 8.3.9.2 | 8.3.9.2 Frequency or Trigger | 170
8.3.9.3 Accomplishments, Roadblocks, and Updates ........................................................... 170 | 8.3.9.3 | 8.3.9.3 Accomplishments, Roadblocks, and Updates | 170
8.3.10 Discontinued Asset Inspection Programs ......................................................................... 171 | 8.3.10 | 8.3.10 Discontinued Asset Inspection Programs | 171
8.3.10.1 Distribution Infrared Inspections (WMP.481) ........................................................... 171 | 8.3.10.1 | 8.3.10.1 Distribution Infrared Inspections (WMP.481) | 171
8.3.10.2 Transmission 69 kV Tier 3 Visual Inspections (WMP.555) ........................................ 171 | 8.3.10.2 | 8.3.10.2 Transmission 69 kV Tier 3 Visual Inspections (WMP.555) | 171
8.3.11 Asset Inspection Pilot Programs ....................................................................................... 171 | 8.3.11 | 8.3.11 Asset Inspection Pilot Programs | 171
8.4 Equipment Maintenance and Repair (WMP.1130) ................................................................... 171 | 8.4 | 8.4 Equipment Maintenance and Repair (WMP.1130) | 171
8.4.1 Maintenance Strategies .................................................................................................... 171 | 8.4.1 | 8.4.1 Maintenance Strategies | 171
8.4.2 Timeframe for Remediation .............................................................................................. 174 | 8.4.2 | 8.4.2 Timeframe for Remediation | 174
8.4.3 Failure and Ignition Causes ............................................................................................... 176 | 8.4.3 | 8.4.3 Failure and Ignition Causes | 176
8.4.3.1 Failure Causes ........................................................................................................... 176 | 8.4.3.1 | 8.4.3.1 Failure Causes | 176
8.4.3.2 Ignition Causes .......................................................................................................... 176 | 8.4.3.2 | 8.4.3.2 Ignition Causes | 176
8.5 Quality Assurance and Quality Control ..................................................................................... 177 | 8.5 | 8.5 Quality Assurance and Quality Control | 177
8.5.1 Overview, Objectives, and Targets ................................................................................... 177 | 8.5.1 | 8.5.1 Overview, Objectives, and Targets | 177
8.5.2 QA and QC Procedures ...................................................................................................... 181 | 8.5.2 | 8.5.2 QA and QC Procedures | 181
8.5.2.1 Grid Design and System Hardening ........................................................................... 181 | 8.5.2.1 | 8.5.2.1 Grid Design and System Hardening | 181
8.5.2.2 Asset Inspections....................................................................................................... 181 | 8.5.2.2 | 8.5.2.2 Asset Inspections | 181
8.5.2.3 Equipment Maintenance and Repair ........................................................................ 182 | 8.5.2.3 | 8.5.2.3 Equipment Maintenance and Repair | 182
8.5.3 Sampling Plan .................................................................................................................... 182 | 8.5.3 | 8.5.3 Sampling Plan | 182
8.5.3.1 Grid Design and System Hardening ........................................................................... 182 | 8.5.3.1 | 8.5.3.1 Grid Design and System Hardening | 182
8.5.3.2 Asset Inspections....................................................................................................... 182 | 8.5.3.2 | 8.5.3.2 Asset Inspections | 182
8.5.3.3 Equipment Maintenance and Repair ........................................................................ 183 | 8.5.3.3 | 8.5.3.3 Equipment Maintenance and Repair | 183
8.5.4 Pass Rate Calculation ........................................................................................................ 183 | 8.5.4 | 8.5.4 Pass Rate Calculation | 183
8.5.4.1 Grid Design and System Hardening ........................................................................... 183 | 8.5.4.1 | 8.5.4.1 Grid Design and System Hardening | 183
8.5.4.2 Asset Inspections....................................................................................................... 184 | 8.5.4.2 | 8.5.4.2 Asset Inspections | 184
8.5.4.3 Equipment Maintenance and Repair ........................................................................ 185 | 8.5.4.3 | 8.5.4.3 Equipment Maintenance and Repair | 185
8.5.5 Other Metrics .................................................................................................................... 185 | 8.5.5 | 8.5.5 Other Metrics | 185
8.5.5.1 Grid Design and System Hardening ........................................................................... 185 | 8.5.5.1 | 8.5.5.1 Grid Design and System Hardening | 185
8.5.5.2 Asset Inspections....................................................................................................... 185 | 8.5.5.2 | 8.5.5.2 Asset Inspections | 185
8.5.5.3 Equipment Maintenance and Repair ........................................................................ 185 | 8.5.5.3 | 8.5.5.3 Equipment Maintenance and Repair | 185
8.5.6 Documentation of Findings ............................................................................................... 186 | 8.5.6 | 8.5.6 Documentation of Findings . | 186
8.5.6.1 Grid Design and System Hardening ........................................................................... 186 | 8.5.6.1 | 8.5.6.1 Grid Design and System Hardening | 186
8.5.6.2 Asset Inspections....................................................................................................... 186 | 8.5.6.2 | 8.5.6.2 Asset Inspections | 186
8.5.6.3 Equipment Maintenance and Repair ........................................................................ 187 | 8.5.6.3 | 8.5.6.3 Equipment Maintenance and Repair | 187
8.5.7 Changes to QA and QC Since Last WMP and Planned Improvements .............................. 187 | 8.5.7 | 8.5.7 Changes to QA and QC Since Last WMP and Planned Improvements | 187
8.5.7.1 Grid Design and System Hardening ........................................................................... 187 | 8.5.7.1 | 8.5.7.1 Grid Design and System Hardening | 187
8.5.7.2 Asset Inspections....................................................................................................... 188 | 8.5.7.2 | 8.5.7.2 Asset Inspections | 188
8.5.7.3 Equipment Maintenance and Repair ........................................................................ 188 | 8.5.7.3 | 8.5.7.3 Equipment Maintenance and Repair | 188
8.6 Work Orders .............................................................................................................................. 188 | 8.6 | 8.6 Work Orders . | 188
8.6.1 Procedures Documenting the Work Order Process .......................................................... 188 | 8.6.1 | 8.6.1 Procedures Documenting the Work Order Process | 188
8.6.2 Plan for Correcting Past Due Work Orders, if Applicable ................................................. 191 | 8.6.2 | 8.6.2 Plan for Correcting Past Due Work Orders, if Applicable | 191
8.6.3 Prioritization of Work Orders ............................................................................................ 191 | 8.6.3 | 8.6.3 Prioritization of Work Orders | 191
8.6.4 Procedure for Monitoring/Reinspecting Open Work Orders ........................................... 191 | 8.6.4 | 8.6.4 Procedure for Monitoring/Reinspecting Open Work Orders | 191
8.6.5 Open Work Order Trends .................................................................................................. 192 | 8.6.5 | 8.6.5 Open Work Order Trends | 192
8.7 Grid Operations and Procedures .............................................................................................. 194 | 8.7 | 8.7 Grid Operations and Procedures . | 194
8.7.1 Equipment Settings to Reduce Wildfire Risk ..................................................................... 194 | 8.7.1 | 8.7.1 Equipment Settings to Reduce Wildfire Risk | 194
8.7.1.1 Protective Equipment and Device Settings (WMP.991) ............................................ 194 | 8.7.1.1 | 8.7.1.1 Protective Equipment and Device Settings (WMP.991) | 194
8.7.1.2 Automatic Recloser Settings (WMP.1018) ................................................................ 195 | 8.7.1.2 | 8.7.1.2 Automatic Recloser Settings (WMP.1018) | 195
8.7.1.3 Settings of other Emerging Technologies ................................................................. 198 | 8.7.1.3 | 8.7.1.3 Settings of other Emerging Technologies | 198
8.7.2 Grid Response Procedures and Notifications ................................................................... 198 | 8.7.2 | 8.7.2 Grid Response Procedures and Notifications | 198
8.7.3 Personnel Work Procedures and Training in Conditions of Elevated Fire Risk ................. 199 | 8.7.3 | 8.7.3 Personnel Work Procedures and Training in Conditions of Elevated Fire Risk | 199
8.7.3.1 Work Procedures during Different Levels of Wildfire Risk ....................................... 199 | 8.7.3.1 | 8.7.3.1 Work Procedures during Different Levels of Wildfire Risk | 199
8.7.3.2 Procedures for Deployment of Fire Prevention and ignition Mitigation resources and Equipment…199 | 8.7.3.2 | 8.7.3.2 Procedures for Deployment of Fire Prevention and ignition Mitigation resources and Equipment | 199
8.8 Workforce Planning .................................................................................................................. 201 | 8.8 | 8.8 Workforce Planning | 201
9 Vegetation Management and Inspections ............................................................................... 206 | 9 | 9 Vegetation Management and Inspections | 206
9.1 Targets....................................................................................................................................... 207 | 9.1 | 9.1 Targets. | 207
9.1.1 Qualitative Targets ............................................................................................................ 207 | 9.1.1 | 9.1.1 Qualitative Targets | 207
9.1.2 Quantitative Targets ......................................................................................................... 207 | 9.1.2 | 9.1.2 Quantitative Targets . | 207
9.2 Vegetation Management Inspections ....................................................................................... 209 | 9.2 | 9.2 Vegetation Management Inspections . | 209
9.2.1 Detailed Inspections (WMP.494) ...................................................................................... 209 | 9.2.1 | 9.2.1 Detailed Inspections (WMP.494) | 209
9.2.1.1 Overview and Area Inspected ................................................................................... 209 | 9.2.1.1 | 9.2.1.1 Overview and Area Inspected | 209
9.2.1.2 Procedures ................................................................................................................ 209 | 9.2.1.2 | 9.2.1.2 Procedures . | 209
9.2.1.3 Clearance ................................................................................................................... 209 | 9.2.1.3 | 9.2.1.3 Clearance | 209
9.2.1.4 Fall-in Mitigation ....................................................................................................... 210 | 9.2.1.4 | 9.2.1.4 Fall-in Mitigation . | 210
9.2.1.5 Scheduling ................................................................................................................. 210 | 9.2.1.5 | 9.2.1.5 Scheduling . | 210
9.2.1.6 Updates ..................................................................................................................... 210 | 9.2.1.6 | 9.2.1.6 Updates . | 210
9.2.2 Off-Cycle Patrols (WMP.508) ............................................................................................ 210 | 9.2.2 | 9.2.2 Off-Cycle Patrols (WMP.508) | 210
9.2.2.1 Overview and Area Inspected ................................................................................... 210 | 9.2.2.1 | 9.2.2.1 Overview and Area Inspected | 210
9.2.2.2 Procedures ................................................................................................................ 210 | 9.2.2.2 | 9.2.2.2 Procedures . | 210
9.2.2.3 Clearance ................................................................................................................... 210 | 9.2.2.3 | 9.2.2.3 Clearance | 210
9.2.2.4 Fall-in Mitigation ....................................................................................................... 211 | 9.2.2.4 | 9.2.2.4 Fall-in Mitigation . | 211
9.2.2.5 Scheduling ................................................................................................................. 211 | 9.2.2.5 | 9.2.2.5 Scheduling . | 211
9.2.2.6 Updates ..................................................................................................................... 211 | 9.2.2.6 | 9.2.2.6 Updates . | 211
9.3 Pruning and Removal (WMP.501) ............................................................................................. 211 | 9.3 | 9.3 Pruning and Removal (WMP.501) | 211
9.3.1 Overview ........................................................................................................................... 211 | 9.3.1 | 9.3.1 Overview | 211
9.3.2 Procedures ........................................................................................................................ 211 | 9.3.2 | 9.3.2 Procedures | 211
9.3.3 Scheduling ......................................................................................................................... 211 | 9.3.3 | 9.3.3 Scheduling | 211
9.3.4 Updates ............................................................................................................................. 212 | 9.3.4 | 9.3.4 Updates . | 212
9.4 Pole Clearing (WMP.512) .......................................................................................................... 212 | 9.4 | 9.4 Pole Clearing (WMP.512) | 212
9.4.1 Overview ........................................................................................................................... 212 | 9.4.1 | 9.4.1 Overview | 212
9.4.2 Procedures ........................................................................................................................ 213 | 9.4.2 | 9.4.2 Procedures | 213
9.4.3 Scheduling ......................................................................................................................... 213 | 9.4.3 | 9.4.3 Scheduling | 213
9.4.4 Updates ............................................................................................................................. 213 | 9.4.4 | 9.4.4 Updates . | 213
9.5 Wood and Slash Management .................................................................................................. 214 | 9.5 | 9.5 Wood and Slash Management . | 214
9.5.1 Overview ........................................................................................................................... 214 | 9.5.1 | 9.5.1 Overview | 214
9.5.2 Procedures ........................................................................................................................ 214 | 9.5.2 | 9.5.2 Procedures | 214
9.5.3 Scheduling ......................................................................................................................... 214 | 9.5.3 | 9.5.3 Scheduling | 214
9.5.4 Updates ............................................................................................................................. 214 | 9.5.4 | 9.5.4 Updates . | 214
9.6 Defensible Space ....................................................................................................................... 214 | 9.6 | 9.6 Defensible Space | 214
9.6.1 Overview ........................................................................................................................... 214 | 9.6.1 | 9.6.1 Overview | 214
9.6.2 Procedures ........................................................................................................................ 215 | 9.6.2 | 9.6.2 Procedures | 215
9.6.3 Scheduling ......................................................................................................................... 215 | 9.6.3 | 9.6.3 Scheduling | 215
9.6.4 Updates ............................................................................................................................. 215 | 9.6.4 | 9.6.4 Updates . | 215
9.7 Integrated Vegetation Management: Fuels Management (WMP.497) .................................... 215 | 9.7 | 9.7 Integrated Vegetation Management: Fuels Management (WMP.497) | 215
9.7.1 Overview ........................................................................................................................... 215 | 9.7.1 | 9.7.1 Overview | 215
9.7.2 Procedures ........................................................................................................................ 215 | 9.7.2 | 9.7.2 Procedures | 215
9.7.3 Scheduling ......................................................................................................................... 215 | 9.7.3 | 9.7.3 Scheduling | 215
9.7.4 Updates ............................................................................................................................. 216 | 9.7.4 | 9.7.4 Updates . | 216
9.8 Partnerships .............................................................................................................................. 216 | 9.8 | 9.8 Partnerships | 216
9.8.1 Fire Safe Council of San Diego County .............................................................................. 217 | 9.8.1 | 9.8.1 Fire Safe Council of San Diego County | 217
9.8.1.1 Overview ................................................................................................................... 217 | 9.8.1.1 | 9.8.1.1 Overview | 217
9.8.1.2 Partnership History ................................................................................................... 217 | 9.8.1.2 | 9.8.1.2 Partnership History | 217
9.8.1.3 Future Projects .......................................................................................................... 217 | 9.8.1.3 | 9.8.1.3 Future Projects . | 217
9.8.2 Viejas Band of Kumeyaay Indians ..................................................................................... 218 | 9.8.2 | 9.8.2 Viejas Band of Kumeyaay Indians . | 218
9.8.2.1 Overview ................................................................................................................... 218 | 9.8.2.1 | 9.8.2.1 Overview | 218
9.8.2.2 Partnership History ................................................................................................... 218 | 9.8.2.2 | 9.8.2.2 Partnership History | 218
9.8.2.3 Future Projects .......................................................................................................... 218 | 9.8.2.3 | 9.8.2.3 Future Projects . | 218
9.8.3 Campo Band of Diegueno Mission Indians ....................................................................... 218 | 9.8.3 | 9.8.3 Campo Band of Diegueno Mission Indians | 218
9.8.3.1 Overview ................................................................................................................... 218 | 9.8.3.1 | 9.8.3.1 Overview | 218
9.8.3.2 Partnership History ................................................................................................... 219 | 9.8.3.2 | 9.8.3.2 Partnership History | 219
9.8.3.3 Future Projects .......................................................................................................... 219 | 9.8.3.3 | 9.8.3.3 Future Projects . | 219
9.8.4 San Diego Regional Fire & Emergency Services Foundation ............................................. 219 | 9.8.4 | 9.8.4 San Diego Regional Fire & Emergency Services Foundation . | 219
9.8.4.1 Overview ................................................................................................................... 219 | 9.8.4.1 | 9.8.4.1 Overview | 219
9.8.4.2 Partnership History ................................................................................................... 219 | 9.8.4.2 | 9.8.4.2 Partnership History | 219
9.8.4.3 Future Projects .......................................................................................................... 220 | 9.8.4.3 | 9.8.4.3 Future Projects . | 220
9.8.5 Inter-Tribal Long Term Recovery Foundation ................................................................... 220 | 9.8.5 | 9.8.5 Inter-Tribal Long Term Recovery Foundation | 220
9.8.5.1 Overview ................................................................................................................... 220 | 9.8.5.1 | 9.8.5.1 Overview | 220
9.8.5.2 Partnership History ................................................................................................... 220 | 9.8.5.2 | 9.8.5.2 Partnership History | 220
9.8.5.3 Future Projects .......................................................................................................... 220 | 9.8.5.3 | 9.8.5.3 Future Projects . | 220
9.8.6 San Diego County Fire ....................................................................................................... 220 | 9.8.6 | 9.8.6 San Diego County Fire | 220
9.8.6.1 Overview ................................................................................................................... 220 | 9.8.6.1 | 9.8.6.1 Overview | 220
9.8.6.2 Partnership History ................................................................................................... 221 | 9.8.6.2 | 9.8.6.2 Partnership History | 221
9.8.6.3 Future Projects .......................................................................................................... 221 | 9.8.6.3 | 9.8.6.3 Future Projects . | 221
9.9 Activities Based on Weather Conditions ................................................................................... 221 | 9.9 | 9.9 Activities Based on Weather Conditions . | 221
9.9.1 Overview ........................................................................................................................... 221 | 9.9.1 | 9.9.1 Overview | 221
9.9.2 Procedures ........................................................................................................................ 221 | 9.9.2 | 9.9.2 Procedures | 221
9.9.3 Scheduling ......................................................................................................................... 221 | 9.9.3 | 9.9.3 Scheduling | 221
9.9.4 Updates ............................................................................................................................. 222 | 9.9.4 | 9.9.4 Updates . | 222
9.10 Post-Fire Service Restoration .................................................................................................... 222 | 9.1 | 9.10 Post-Fire Service Restoration . | 222
9.10.1 Overview ........................................................................................................................... 222 | 9.10.1 | 9.10.1 Overview . | 222
9.10.2 Procedures ........................................................................................................................ 222 | 9.10.2 | 9.10.2 Procedures | 222
9.10.3 Scheduling ......................................................................................................................... 222 | 9.10.3 | 9.10.3 Scheduling | 222
9.10.4 Updates ............................................................................................................................. 222 | 9.10.4 | 9.10.4 Updates | 222
9.11 Quality Assurance and Quality Control of Vegetation Management (WMP.505) .................... 223 | 9.11 | 9.11 Quality Assurance and Quality Control of Vegetation Management (WMP.505) | 223
9.11.1 Overview, Objectives, and Targets ................................................................................... 223 | 9.11.1 | 9.11.1 Overview, Objectives, and Targets | 223
9.11.2 QA/QC Procedures ............................................................................................................ 225 | 9.11.2 | 9.11.2 QA/QC Procedures . | 225
9.11.3 Sample Sizes ...................................................................................................................... 225 | 9.11.3 | 9.11.3 Sample Sizes | 225
9.11.4 Pass Rate Calculation ........................................................................................................ 225 | 9.11.4 | 9.11.4 Pass Rate Calculation | 225
9.11.5 Other Metrics .................................................................................................................... 226 | 9.11.5 | 9.11.5 Other Metrics | 226
9.11.6 Documentation of Findings ............................................................................................... 226 | 9.11.6 | 9.11.6 Documentation of Findings | 226
9.11.7 Changes to QA/QC Since Last WMP and Planned Improvements .................................... 227 | 9.11.7 | 9.11.7 Changes to QA/QC Since Last WMP and Planned Improvements . | 227
9.12 Work Orders .............................................................................................................................. 227 | 9.12 | 9.12 Work Orders | 227
9.12.1 Priority Assignment ........................................................................................................... 227 | 9.12.1 | 9.12.1 Priority Assignment . | 227
9.12.2 Backlog Elimination ........................................................................................................... 227 | 9.12.2 | 9.12.2 Backlog Elimination . | 227
9.12.3 Trends ............................................................................................................................... 227 | 9.12.3 | 9.12.3 Trends . | 227
9.13 Workforce Planning (WMP.506) ............................................................................................... 229 | 9.13 | 9.13 Workforce Planning (WMP.506) | 229
9.13.1 Recruitment ...................................................................................................................... 232 | 9.13.1 | 9.13.1 Recruitment . | 232
9.13.2 Training and Retention...................................................................................................... 232 | 9.13.2 | 9.13.2 Training and Retention | 232
10 Situational Awareness and Forecasting ................................................................................... 234 | 10 | 10 Situational Awareness and Forecasting | 234
10.1 Targets....................................................................................................................................... 235 | 10.1 | 10.1 Targets | 235
10.1.1 Qualitative Targets ............................................................................................................ 235 | 10.1.1 | 10.1.1 Qualitative Targets . | 235
10.1.2 Quantitative Targets ......................................................................................................... 235 | 10.1.2 | 10.1.2 Quantitative Targets | 235
10.2 Environmental Monitoring Systems ......................................................................................... 237 | 10.2 | 10.2 Environmental Monitoring Systems . | 237
10.2.1 Existing Systems, Technologies, and Procedures .............................................................. 237 | 10.2.1 | 10.2.1 Existing Systems, Technologies, and Procedures . | 237
10.2.1.1 Weather Stations ...................................................................................................... 237 | 10.2.1.1 | 10.2.1.1 Weather Stations | 237
10.2.1.2 Air Quality Stations ................................................................................................... 237 | 10.2.1.2 | 10.2.1.2 Air Quality Stations . | 237
10.2.1.3 Fuel Moisture (WMP.1334) ....................................................................................... 238 | 10.2.1.3 | 10.2.1.3 Fuel Moisture (WMP.1334) | 238
10.2.2 Evaluation and Selection of New Systems ........................................................................ 238 | 10.2.2 | 10.2.2 Evaluation and Selection of New Systems | 238
10.2.3 Planned Improvements ..................................................................................................... 238 | 10.2.3 | 10.2.3 Planned Improvements | 238
10.2.4 Evaluating Activities .......................................................................................................... 239 | 10.2.4 | 10.2.4 Evaluating Activities | 239
10.3 Grid Monitoring Systems .......................................................................................................... 239 | 10.3 | 10.3 Grid Monitoring Systems | 239
10.3.1 Existing Systems, Technologies, and Procedures .............................................................. 239 | 10.3.1 | 10.3.1 Existing Systems, Technologies, and Procedures . | 239
10.3.2 Evaluation and Selection of New Systems ........................................................................ 242 | 10.3.2 | 10.3.2 Evaluation and Selection of New Systems | 242
10.3.3 Planned Improvements ..................................................................................................... 242 | 10.3.3 | 10.3.3 Planned Improvements | 242
10.3.4 Evaluating Activities .......................................................................................................... 242 | 10.3.4 | 10.3.4 Evaluating Activities | 242
10.4 Ignition Detection Systems ....................................................................................................... 243 | 10.4 | 10.4 Ignition Detection Systems . | 243
10.4.1 Existing Ignition Detection Sensors and Systems .............................................................. 243 | 10.4.1 | 10.4.1 Existing Ignition Detection Sensors and Systems | 243
10.4.1.1 Satellite Based Remote Sensing (WMP.971)............................................................. 243 | 10.4.1.1 | 10.4.1.1 Satellite Based Remote Sensing (WMP.971) | 243
10.4.1.2 Cameras (WMP.1343) ............................................................................................... 244 | 10.4.1.2 | 10.4.1.2 Cameras (WMP.1343) | 244
10.4.1.3 Fire Growth Potential Software ................................................................................ 245 | 10.4.1.3 | 10.4.1.3 Fire Growth Potential Software . | 245
10.4.2 Evaluation and Selection of New Detection Systems ....................................................... 246 | 10.4.2 | 10.4.2 Evaluation and Selection of New Detection Systems | 246
10.4.3 Planned Integration of New Ignition Detection Technologies .......................................... 246 | 10.4.3 | 10.4.3 Planned Integration of New Ignition Detection Technologies | 246
10.4.4 Evaluating Activities .......................................................................................................... 246 | 10.4.4 | 10.4.4 Evaluating Activities | 246
10.5 Weather Forecasting ................................................................................................................. 247 | 10.5 | 10.5 Weather Forecasting | 247
10.5.1 Existing Modeling Approach ............................................................................................. 247 | 10.5.1 | 10.5.1 Existing Modeling Approach | 247
10.5.1.1 Weather Research and Forecasting (WMP.541) ....................................................... 248 | 10.5.1.1 | 10.5.1.1 Weather Research and Forecasting (WMP.541) | 248
10.5.1.2 SAWTI (WMP.540)..................................................................................................... 248 | 10.5.1.2 | 10.5.1.2 SAWTI (WMP.540). | 248
10.5.2 Known Limitations of Existing Approach .......................................................................... 248 | 10.5.2 | 10.5.2 Known Limitations of Existing Approach . | 248
10.5.3 Planned Improvements ..................................................................................................... 248 | 10.5.3 | 10.5.3 Planned Improvements | 248
10.5.4 Evaluating Activities .......................................................................................................... 249 | 10.5.4 | 10.5.4 Evaluating Activities | 249
10.5.5 Weather Station Maintenance and Calibration ................................................................ 252 | 10.5.5 | 10.5.5 Weather Station Maintenance and Calibration . | 252
10.6 Fire Potential Index (WMP.450) ................................................................................................ 252 | 10.6 | 10.6 Fire Potential Index (WMP.450) | 252
10.6.1 Existing Calculation Approach and Use ............................................................................. 252 | 10.6.1 | 10.6.1 Existing Calculation Approach and Use | 252
10.6.2 Known Limitations of Existing Approach .......................................................................... 254 | 10.6.2 | 10.6.2 Known Limitations of Existing Approach . | 254
10.6.3 Planned Improvements ..................................................................................................... 254 | 10.6.3 | 10.6.3 Planned Improvements | 254
11 Emergency Preparedness, Collaboration, and Community Outreach ........................................ 255 | 11 | 11 Emergency Preparedness, Collaboration, and Community Outreach | 255
11.1 Targets....................................................................................................................................... 256 | 11.1 | 11.1 Targets | 256
11.1.1 Qualitative Targets ............................................................................................................ 256 | 11.1.1 | 11.1.1 Qualitative Targets . | 256
11.2 Emergency Preparedness and Recovery Plan ........................................................................... 258 | 11.2 | 11.2 Emergency Preparedness and Recovery Plan . | 258
11.2.1 Overview of Wildfire and PSPS Emergency Preparedness and Service Restoration ........ 258 | 11.2.1 | 11.2.1 Overview of Wildfire and PSPS Emergency Preparedness and Service Restoration | 258
11.2.1.1 Overview of Wildfire and PSPS Protocols, Policies, and Procedures ........................ 258 | 11.2.1.1 | 11.2.1.1 Overview of Wildfire and PSPS Protocols, Policies, and Procedures | 258
11.2.1.2 Key Personnel, Qualifications, and Training ............................................................. 261 | 11.2.1.2 | 11.2.1.2 Key Personnel, Qualifications, and Training | 261
11.2.1.3 Memorandum of Agreements .................................................................................. 262 | 11.2.1.3 | 11.2.1.3 Memorandum of Agreements | 262
11.2.2 Planning and Allocation of Resources ............................................................................... 263 | 11.2.2 | 11.2.2 Planning and Allocation of Resources | 263
11.3 External Collaboration and Coordination ................................................................................. 264 | 11.3 | 11.3 External Collaboration and Coordination | 264
11.3.1 Communication Strategy with Public Safety Partners ...................................................... 264 | 11.3.1 | 11.3.1 Communication Strategy with Public Safety Partners | 264
11.3.2 Collaboration on Local and Regional Wildfire Mitigation Planning .................................. 266 | 11.3.2 | 11.3.2 Collaboration on Local and Regional Wildfire Mitigation Planning . | 266
11.3.3 Collaboration with Tribal Governments ............................................................................ 268 | 11.3.3 | 11.3.3 Collaboration with Tribal Governments | 268
11.4 Public Communication, Outreach, and Education Awareness.................................................. 270 | 11.4 | 11.4 Public Communication, Outreach, and Education Awareness | 270
11.4.1 Protocols for Emergency Communications ....................................................................... 271 | 11.4.1 | 11.4.1 Protocols for Emergency Communications . | 271
11.4.2 Messaging ......................................................................................................................... 273 | 11.4.2 | 11.4.2 Messaging | 273
11.4.3 Outreach and Education Awareness Activities ................................................................. 274 | 11.4.3 | 11.4.3 Outreach and Education Awareness Activities . | 274
11.4.4 Engagement with Access and Functional Needs Populations .......................................... 276 | 11.4.4 | 11.4.4 Engagement with Access and Functional Needs Populations | 276
11.4.4.1 Summary of Key AFN Demographics ........................................................................ 276 | 11.4.4.1 | 11.4.4.1 Summary of Key AFN Demographics | 276
11.4.4.2 Evaluation of Challenges and Needs during a Wildfire or PSPS Event ...................... 277 | 11.4.4.2 | 11.4.4.2 Evaluation of Challenges and Needs during a Wildfire or PSPS Event | 277
11.4.4.3 Plans to Address Needs of the AFN Customer Base ................................................. 277 | 11.4.4.3 | 11.4.4.3 Plans to Address Needs of the AFN Customer Base | 277
11.4.5 Engagement with Tribal Nations ....................................................................................... 277 | 11.4.5 | 11.4.5 Engagement with Tribal Nations . | 277
11.4.6 Current Gaps and Limitations ........................................................................................... 278 | 11.4.6 | 11.4.6 Current Gaps and Limitations | 278
11.5 Customer Support in Wildfire and PSPS Emergencies .............................................................. 279 | 11.5 | 11.5 Customer Support in Wildfire and PSPS Emergencies | 279
11.5.1 Outage Reporting .............................................................................................................. 279 | 11.5.1 | 11.5.1 Outage Reporting . | 279
11.5.2 Support for Low-Income Customers ................................................................................. 279 | 11.5.2 | 11.5.2 Support for Low-Income Customers . | 279
11.5.3 Billing Adjustments ........................................................................................................... 280 | 11.5.3 | 11.5.3 Billing Adjustments . | 280
11.5.4 Deposit Waivers ................................................................................................................ 280 | 11.5.4 | 11.5.4 Deposit Waivers | 280
11.5.5 Extended Payment Plans ................................................................................................... 280 | 11.5.5 | 11.5.5 Extended Payment Plans . | 280
11.5.6 Suspension of Disconnection and Nonpayment Fees ....................................................... 280 | 11.5.6 | 11.5.6 Suspension of Disconnection and Nonpayment Fees | 280
11.5.7 Repair Processing and Timing ........................................................................................... 280 | 11.5.7 | 11.5.7 Repair Processing and Timing | 280
11.5.8 Community Assistance Locations and Services ................................................................. 280 | 11.5.8 | 11.5.8 Community Assistance Locations and Services . | 280
11.5.9 Medical Baseline Support Services ................................................................................... 282 | 11.5.9 | 11.5.9 Medical Baseline Support Services | 282
11.5.10 Access to Electrical Corporation Representatives ........................................................ 282 | 11.5.10 | 11.5.10 Access to Electrical Corporation Representatives | 282
12 Enterprise Systems ................................................................................................................. 284 | 12 | 12 Enterprise Systems . | 284
12.1 | 12.1 | 12.1 | 2.1
12.1.1 Qualitative Targets ............................................................................................................ 284 | 12.1.1 | 12.1.1 Qualitative Targets . | 284
12.2 Summary of Enterprise Systems ............................................................................................... 286 | 12.2 | 12.2 Summary of Enterprise Systems . | 286
13 Lessons Learned ..................................................................................................................... 289 | 13 | 13 Lessons Learned . | 289
13.1 Description and Summary of Lessons Learned ......................................................................... 295 | 13.1 | 13.1 Description and Summary of Lessons Learned . | 295
13.1.1 Feedback from Government Agencies and Stakeholders ................................................. 295 | 13.1.1 | 13.1.1 Feedback from Government Agencies and Stakeholders | 295
13.1.2 Collaboration with Other Electrical Corporations and Industry Experts .......................... 295 | 13.1.2 | 13.1.2 Collaboration with Other Electrical Corporations and Industry Experts | 295
13.1.3 PSPS or Outage Events ...................................................................................................... 295 | 13.1.3 | 13.1.3 PSPS or Outage Events | 295
13.1.4 Outcomes from Previous WMP Cycles ............................................................................. 296 | 13.1.4 | 13.1.4 Outcomes from Previous WMP Cycles | 296
13.1.5 Areas for Continued Improvement ................................................................................... 296 | 13.1.5 | 13.1.5 Areas for Continued Improvement | 296
13.2 Working Group Meetings .......................................................................................................... 296 | 13.2 | 13.2 Working Group Meetings | 296
13.2.1 PSPS Working Group ......................................................................................................... 296 | 13.2.1 | 13.2.1 PSPS Working Group | 296
13.2.2 Risk Modeling Working Group .......................................................................................... 296 | 13.2.2 | 13.2.2 Risk Modeling Working Group . | 296
13.2.3 Grid Hardening Working Groups ....................................................................................... 296 | 13.2.3 | 13.2.3 Grid Hardening Working Groups | 296
13.2.4 Enhanced Vegetation Management Working Group ........................................................ 297 | 13.2.4 | 13.2.4 Enhanced Vegetation Management Working Group | 297
13.3 Discontinued Activities .............................................................................................................. 298 | 13.3 | 13.3 Discontinued Activities | 298
OEIS Table 3-1: List of Risks and Risk Drivers to Prioritize .......................................................................... 11 | OEIS Table 3-1 | 3-1: List of Risks and Risk Drivers to Prioritize 11
OEIS Table 3-2: Self-Identified Performance Metrics Table ........................................................................ 14 | OEIS Table 3-2 | 3-2: Self-Identified Performance Metrics Table . 14
OEIS Table 3-3: Summary of Projected WMP Expenditures ....................................................................... 16 | OEIS Table 3-3 | 3-3: Summary of Projected WMP Expenditures 16
OEIS Table 4-1: High-Level Service Territory Components ......................................................................... 19 | OEIS Table 4-1 | 4-1: High-Level Service Territory Components .. 19
OEIS Table 4-2: Catastrophic Electrical Corporation Wildfires ................................................................... 21 | OEIS Table 4-2 | 4-2: Catastrophic Electrical Corporation Wildfires . 21
OEIS Table 4-3: Frequently De-energized Circuits ...................................................................................... 23 | OEIS Table 4-3 | 4-3: Frequently De-energized Circuits 23
OEIS Table 5-1: Risk Modeling Assumptions and Limitations ..................................................................... 43 | OEIS Table 5-1 | 5-1: Risk Modeling Assumptions and Limitations 43
OEIS Table 5-2: Summary of Design Scenarios ........................................................................................... 49 | OEIS Table 5-2 | 5-2: Summary of Design Scenarios .. 49
OEIS Table 5-3: Summary of Extreme-Event Scenarios .............................................................................. 52 | OEIS Table 5-3 | 5-3: Summary of Extreme-Event Scenarios 52
OEIS Table 5-4: Summary of Risk Models ................................................................................................... 53 | OEIS Table 5-4 | 5-4: Summary of Risk Models .. 53
OEIS Table 5-5: Summary of Top-Risk Circuits, Segments, or Spans .......................................................... 60 | OEIS Table 5-5 | 5-5: Summary of Top-Risk Circuits, Segments, or Spans 60
OEIS Table 5-6: Utility Risk Assessment Improvement Plan ....................................................................... 79 | OEIS Table 5-6 | 5-6: Utility Risk Assessment Improvement Plan 79
OEIS Table 6-1: List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk ................................................................................................................................................... 84 | OEIS Table 6-1 | 6-1: List of Prioritized Areas in an Electrical Corporations Service Territory Based on Overall Utility Risk 84
OEIS Table 6-2: Stakeholder Roles and Responsibilities in the Decision-Making Process ........................ 106 | OEIS Table 6-2 | 6-2: Stakeholder Roles and Responsibilities in the Decision-Making Process 106
OEIS Table 6-3: Risk Impact of Activities ................................................................................................... 111 | OEIS Table 6-3 | 6-3: Risk Impact of Activities .. 111
OEIS Table 6-4: Summary of Risk Reduction for Top-Risk Circuits ............................................................ 116 | OEIS Table 6-4 | 6-4: Summary of Risk Reduction for Top-Risk Circuits .. 116
OEIS Table 8-1: Grid Design, Operations, and Maintenance Targets by Year .......................................... 126 | OEIS Table 8-1 | 8-1: Grid Design, Operations, and Maintenance Targets by Year 126
OEIS Table 8-2: Asset Inspection Frequency, Method, and Criteria ......................................................... 151 | OEIS Table 8-2 | 8-2: Asset Inspection Frequency, Method, and Criteria .. 151
OEIS Table 8-3: Grid Design, Asset Inspections, and Maintenance QA and QC Program Objectives ....... 177 | OEIS Table 8-3 | 8-3: Grid Design, Asset Inspections, and Maintenance QA and QC Program Objectives . 177
OEIS Table 8-4: Grid Design, Asset Inspections, and Maintenance QA and QC Activity Targets .............. 179 | OEIS Table 8-4 | 8-4: Grid Design, Asset Inspections, and Maintenance QA and QC Activity Targets 179
OEIS Table 8-5: Number of Past Due Asset Work Orders Categorized by Age ......................................... 193 | OEIS Table 8-5 | 8-5: Number of Past Due Asset Work Orders Categorized by Age .. 193
OEIS Table 8-6: Number of Past Due Asset Work Orders Categorized by Age for Priority Levels ............ 194 | OEIS Table 8-6 | 8-6: Number of Past Due Asset Work Orders Categorized by Age for Priority Levels . 194
OEIS Table 8-7: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years ........................... 194 | OEIS Table 8-7 | 8-7: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years 194
OEIS Table 8-8: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years ........................... 196 | OEIS Table 8-8 | 8-8: Top Ten Impacted Circuits from Changes to PEDS in the Past 3 Years 196
OEIS Table 9-1: Vegetation Management Targets by Year (Non-inspection Targets) .............................. 207 | OEIS Table 9-1 | 9-1: Vegetation Management Targets by Year (Non-inspection Targets) 207
OEIS Table 9-2: Vegetation Inspections and Pole Clearing Targets by Year ............................................. 208 | OEIS Table 9-2 | 9-2: Vegetation Inspections and Pole Clearing Targets by Year 208
OEIS Table 9-3: Vegetation Management Inspection Frequency, Method, and Criteria ......................... 209 | OEIS Table 9-3 | 9-3: Vegetation Management Inspection Frequency, Method, and Criteria . 209
OEIS Table 9-4: Partnerships in Vegetation Management ....................................................................... 216 | OEIS Table 9-4 | 9-4: Partnerships in Vegetation Management 216
OEIS Table 9-5: Vegetation Management QA and QC Program Objectives ............................................. 224 | OEIS Table 9-5 | 9-5: Vegetation Management QA and QC Program Objectives 224
OEIS Table 9-6: Vegetation Management QA and QC Activity Targets .................................................... 224 | OEIS Table 9-6 | 9-6: Vegetation Management QA and QC Activity Targets .. 224
OEIS Table 9-7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier ................................................................................................................................................... 228 | OEIS Table 9-7 | 9-7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier 228
OEIS Table 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels ............................................................................................................................................ 228 | OEIS Table 9-8 | 9-8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels . 228
OEIS Table 9-9: Vegetation Management Qualifications and Training ..................................................... 229 | OEIS Table 9-9 | 9-9: Vegetation Management Qualifications and Training 229
OEIS Table 10-1: Situational Awareness Targets by Year ......................................................................... 235 | OEIS Table 10-1 | 10-1: Situational Awareness Targets by Year .. 235
OEIS Table 10-2: Environmental Monitoring Systems .............................................................................. 237 | OEIS Table 10-2 | 10-2: Environmental Monitoring Systems 237
OEIS Table 10-3: Grid Operation Monitoring Systems .............................................................................. 239 | OEIS Table 10-3 | 10-3: Grid Operation Monitoring Systems 239
OEIS Table 10-4: Ignition Detection Systems Currently Deployed ............................................................ 243 | OEIS Table 10-4 | 10-4: Ignition Detection Systems Currently Deployed .. 243
OEIS Table 10-5: Fire Potential Features .................................................................................................. 253 | OEIS Table 10-5 | 10-5: Fire Potential Features . 253
OEIS Table 11-1: Emergency Preparedness and Community Outreach Targets by Year .......................... 256 | OEIS Table 11-1 | 11-1: Emergency Preparedness and Community Outreach Targets by Year .. 256
OEIS Table 11-2: Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan ......................................................................................................................................... 263 | OEIS Table 11-2 | 11-2: Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan . 263
OEIS Table 11-3: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners ..................................................................................................................................................... 265 | OEIS Table 11-3 | 11-3: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners 265
OEIS Table 11-4: Gaps and Limitations in Communication Coordination with Public Safety Partners .... 266 | OEIS Table 11-4 | 11-4: Gaps and Limitations in Communication Coordination with Public Safety Partners . 266
OEIS Table 11-5: Collaboration in Local and Regional Wildfire Mitigation Planning ................................ 267 | OEIS Table 11-5 | 11-5: Collaboration in Local and Regional Wildfire Mitigation Planning 267
OEIS Table 11-6: Key Gaps and Limitations in Collaborating on Local and Regional Wildfire Mitigation Planning .................................................................................................................................................... 268 | OEIS Table 11-6 | 11-6: Key Gaps and Limitations in Collaborating on Local and Regional Wildfire Mitigation Planning . 268
OEIS Table 11-7: Collaboration with Tribal Agencies ................................................................................ 268 | OEIS Table 11-7 | 11-7: Collaboration with Tribal Agencies .. 268
OEIS Table 11-8: Key Gaps and Limitations in Collaborating with Tribal Agencies ................................... 270 | OEIS Table 11-8 | 11-8: Key Gaps and Limitations in Collaborating with Tribal Agencies 270
OEIS Table 11-9: Protocols for Emergency Communication to Stakeholder Groups ............................... 272 | OEIS Table 11-9 | 11-9: Protocols for Emergency Communication to Stakeholder Groups . 272
OEIS Table 11-10: List of Target Communities .......................................................................................... 274 | OEIS Table 11-1 | 11-10: List of Target Communities . 274
OEIS Table 11-11: Key Gaps and Limitations in Public Emergency Communication Strategy .................. 278 | OEIS Table 11-1 | 11-11: Key Gaps and Limitations in Public Emergency Communication Strategy .. 278
OEIS Table 12-1: Enterprise Systems Targets ........................................................................................... 284 | OEIS Table 12-1 | 12-1: Enterprise Systems Targets .. 284
OEIS Table 13-1: Lessons Learned ............................................................................................................. 290 | OEIS Table 13-1 | 13-1: Lessons Learned . 290
OEIS Table 13-2: Lessons Learned from Discontinued Activities .............................................................. 299 | OEIS Table 13-2 | 13-2: Lessons Learned from Discontinued Activities . 299
SDGE Table 5-1: CoRE Attributes and Dollar Equivalencies ........................................................................ 27 | SDGE Table 5-1 | 5-1: CoRE Attributes and Dollar Equivalencies . 27
SDGE Table 5-2: Safety Sub-Attributes, Values, and Dollar Equivalencies ................................................. 28 | SDGE Table 5-2 | 5-2: Safety Sub-Attributes, Values, and Dollar Equivalencies .. 28
SDGE Table 5-3: Risk Components for LoRE ............................................................................................... 37 | SDGE Table 5-3 | 5-3: Risk Components for LoRE . 37
SDGE Table 5-4: Attributes for Wildfire Consequence ............................................................................... 38 | SDGE Table 5-4 | 5-4: Attributes for Wildfire Consequence . 38
SDGE Table 5-5: Attributes for PSPS Consequence ..................................................................................... 39 | SDGE Table 5-5 | 5-5: Attributes for PSPS Consequence . 39
SDGE Table 5-6: Attributes for PEDS Consequence .................................................................................... 40 | SDGE Table 5-6 | 5-6: Attributes for PEDS Consequence 40
SDGE Table 5-7: Pre-Mitigation Wildfire, PSPS, PEDS, and Overall Utility Risk estimates for the Service Territory ...................................................................................................................................................... 42 | SDGE Table 5-7 | 5-7: Pre-Mitigation Wildfire, PSPS, PEDS, and Overall Utility Risk estimates for the Service Territory . 42
SDGE Table 5-8: WiNGS-Planning Third Party Recommendations ............................................................. 62 | SDGE Table 5-8 | 5-8: WiNGS-Planning Third Party Recommendations 62
SDGE Table 5-9: WiNGS-Ops Risk Modeling Updates ................................................................................. 66 | SDGE Table 5-9 | 5-9: WiNGS-Ops Risk Modeling Updates 66
SDGE Table 6-1: Potential Mitigation Activities for Risk Drivers included in List of Prioritized Circuit Segments ..................................................................................................................................................... 89 | SDGE Table 6-1 | 6-1: Potential Mitigation Activities for Risk Drivers included in List of Prioritized Circuit Segments 89
SDGE Table 6-2: Interim Mitigations Initiatives ........................................................................................ 117 | SDGE Table 6-2 | 6-2: Interim Mitigations Initiatives .. 117
SDGE Table 8-1: Risk Event Rate with Pending Infractions ....................................................................... 154 | SDGE Table 8-1 | 8-1: Risk Event Rate with Pending Infractions 154
SDGE Table 8-2: Maintenance and Replacement Strategies .................................................................... 172 | SDGE Table 8-2 | 8-2: Maintenance and Replacement Strategies .. 172
SDGE Table 8-3: Timeframe for Remediation of Distribution Findings .................................................... 174 | SDGE Table 8-3 | 8-3: Timeframe for Remediation of Distribution Findings .. 174
SDGE Table 8-4: Timeframe for Remediation of Transmission Findings .................................................. 175 | SDGE Table 8-4 | 8-4: Timeframe for Remediation of Transmission Findings 175
SDGE Table 8-5: Ignition Rate and Failure Rate ........................................................................................ 177 | SDGE Table 8-5 | 8-5: Ignition Rate and Failure Rate .. 177
SDGE Table 8-6: Faults by HFTD Tier and Weather Condition .................................................................. 197 | SDGE Table 8-6 | 8-6: Faults by HFTD Tier and Weather Condition 197
SDGE Table 8-7: 5-Year Average Ignition Rate .......................................................................................... 197 | SDGE Table 8-7 | 8-7: 5-Year Average Ignition Rate . 197
SDGE Table 8-8: Estimated Faults and Ignitions Avoided ......................................................................... 197 | SDGE Table 8-8 | 8-8: Estimated Faults and Ignitions Avoided .. 197
SDGE Table 8-9: Workforce Planning, Asset Inspections .......................................................................... 201 | SDGE Table 8-9 | 8-9: Workforce Planning, Asset Inspections 201
SDGE Table 8-10: Workforce Planning, Grid Hardening ........................................................................... 203 | SDGE Table 8-10 | 8-10: Workforce Planning, Grid Hardening . 203
SDGE Table 8-11: Workforce Planning, Risk Event Inspection .................................................................. 205 | SDGE Table 8-11 | 8-11: Workforce Planning, Risk Event Inspection 205
SDGE Table 9-1: Fire Safe Council of San Diego County Project History .................................................. 217 | SDGE Table 9-1 | 9-1: Fire Safe Council of San Diego County Project History 217
SDGE Table 9-2: Viejas Band of Kumeyaay Indians Project History .......................................................... 218 | SDGE Table 9-2 | 9-2: Viejas Band of Kumeyaay Indians Project History 218
SDGE Table 9-3: Campo Band of Diegueno Mission Indians ..................................................................... 219 | SDGE Table 9-3 | 9-3: Campo Band of Diegueno Mission Indians 219
SDGE Table 9-4: San Diego County Fire Project History ........................................................................... 221 | SDGE Table 9-4 | 9-4: San Diego County Fire Project History . 221
SDGE Table 10-1: Five-Year Average Ignition Rate (2019-2023) .............................................................. 254 | SDGE Table 10-1 | 10-1: Five-Year Average Ignition Rate (2019-2023) . 254
SDGE Table 11-1: CRC Locations and Services .......................................................................................... 281 | SDGE Table 11-1 | 11-1: CRC Locations and Services . 281
Figure 1-1: 2026-2028 Expected Risk Reduction .......................................................................................... 3 | Figure 1-1 | 1-1: 2026-2028 Expected Risk Reduction . 3
Figure 1-2: Long-Term Risk Reduction Approach ......................................................................................... 4 | Figure 1-2 | 1-2: Long-Term Risk Reduction Approach 4
Figure 1-3: Enterprise Risk Management Framework for Development of the WMP ................................. 5 | Figure 1-3 | 1-3: Enterprise Risk Management Framework for Development of the WMP . 5
Figure 3-1: Summary of Projected WMP Expenditures .............................................................................. 16 | Figure 3-1 | 3-1: Summary of Projected WMP Expenditures 16
Figure 4-1: Utility Service Territory of the Enterprise Risk Management Framework ............................... 19 | Figure 4-1 | 4-1: Utility Service Territory of the Enterprise Risk Management Framework . 19
Figure 4-2: Service Territory (polygons) and Distribution of Customers Served ........................................ 20 | Figure 4-2 | 4-2: Service Territory (polygons) and Distribution of Customers Served . 20
Figure 4-3: Frequently De-energized Circuits ............................................................................................. 22 | Figure 4-3 | 4-3: Frequently De-energized Circuits . 22
Figure 5-1: Enterprise Risk Management Framework ................................................................................ 26 | Figure 5-1 | 5-1: Enterprise Risk Management Framework .. 26
Figure 5-2: Enterprise CoRE Attributes and Sub-Attributes ........................................................................ 27 | Figure 5-2 | 5-2: Enterprise CoRE Attributes and Sub-Attributes . 27
Figure 5-3: Risk Identification Step of the Enterprise Risk Management Framework ................................ 31 | Figure 5-3 | 5-3: Risk Identification Step of the Enterprise Risk Management Framework 31
Figure 5-4: Enterprise Utility Risk Overview ............................................................................................... 32 | Figure 5-4 | 5-4: Enterprise Utility Risk Overview . 32
Figure 5-5: Risk Analysis Step of the Enterprise Risk Management Framework ........................................ 34 | Figure 5-5 | 5-5: Risk Analysis Step of the Enterprise Risk Management Framework . 34
Figure 5-6: WiNGS-Planning and Ops Calculation Schematic ..................................................................... 36 | Figure 5-6 | 5-6: WiNGS-Planning and Ops Calculation Schematic 36
Figure 5-7: SDG&E Convex Risk Aversion Function ..................................................................................... 42 | Figure 5-7 | 5-7: SDG&E Convex Risk Aversion Function . 42
Figure 5-8: HFTD Risk Including Risk Aversion Attitude .............................................................................. 43 | Figure 5-8 | 5-8: HFTD Risk Including Risk Aversion Attitude 43
Figure 5-9: WiNGS-Ops Fire Visualization Platform Screenshot ................................................................. 48 | Figure 5-9 | 5-9: WiNGS-Ops Fire Visualization Platform Screenshot .. 48
Figure 5-10: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ......... 57 | Figure 5-10 | 5-10: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework . 57
Figure 5-11: Higher-Risk Urban Areas in Relation to HFTD ......................................................................... 58 | Figure 5-11 | 5-11: Higher-Risk Urban Areas in Relation to HFTD .. 58
Figure 5-12: Map of Service Territory with HFTD Circuit-Segments Categorized by Mean Overall Risk (as of 2025) ....................................................................................................................................................... 59 | Figure 5-12 | 5-12: Map of Service Territory with HFTD Circuit-Segments Categorized by Mean Overall Risk (as of 2025) .. 59
Figure 5-13: Independent Review Process ................................................................................................. 61 | Figure 5-13 | 5-13: Independent Review Process 61
Figure 6-1: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ........... 82 | Figure 6-1 | 6-1: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework 82
Figure 6-2: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk .................................. 100 | Figure 6-2 | 6-2: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk .. 100
Figure 6-3: Risk Mitigation Plan Development & Documentation Step of the Enterprise Risk Management Framework ................................................................................................................................................ 109 | Figure 6-3 | 6-3: Risk Mitigation Plan Development & Documentation Step of the Enterprise Risk Management Framework 109
Figure 6-4: Wildfire Hardening Targets ..................................................................................................... 110 | Figure 6-4 | 6-4: Wildfire Hardening Targets . 110
Figure 6-5: Estimated Wildfire Risk Reduction 2007-2037 ....................................................................... 110 | Figure 6-5 | 6-5: Estimated Wildfire Risk Reduction 2007-2037 110
Figure 7-1: PSPS Decision-Making Framework ......................................................................................... 121 | Figure 7-1 | 7-1: PSPS Decision-Making Framework 121
Figure 8-1: Risk-Informed Investment decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework .................................................................................................................. 124 | Figure 8-1 | 8-1: Risk-Informed Investment decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework . 124
Figure 8-2: Distribution Detailed Overhead Inspections Process Flow ..................................................... 153 | Figure 8-2 | 8-2: Distribution Detailed Overhead Inspections Process Flow 153
Figure 8-3: Transmission Detailed Overhead Inspections Process Flow ................................................... 156 | Figure 8-3 | 8-3: Transmission Detailed Overhead Inspections Process Flow . 156
Figure 8-4: Transmission Infrared Inspections Process Flow .................................................................... 158 | Figure 8-4 | 8-4: Transmission Infrared Inspections Process Flow .. 158
Figure 8-5: Wood Pole Intrusive Inspections Process Flow (Transmission and Distribution) ................... 160 | Figure 8-5 | 8-5: Wood Pole Intrusive Inspections Process Flow (Transmission and Distribution) 160
Figure 8-6: Risk-Informed Drone Inspections Process Flow ..................................................................... 163 | Figure 8-6 | 8-6: Risk-Informed Drone Inspections Process Flow 163
Figure 8-7: RIDI Inspection Prioritization Model ....................................................................................... 165 | Figure 8-7 | 8-7: RIDI Inspection Prioritization Model . 165
Figure 8-8: Distribution Patrol Inspections Process Flow ......................................................................... 166 | Figure 8-8 | 8-8: Distribution Patrol Inspections Process Flow .. 166
Figure 8-9: Transmission Overhead Patrol Inspections Process Flow ...................................................... 168 | Figure 8-9 | 8-9: Transmission Overhead Patrol Inspections Process Flow . 168
Figure 8-10: Substation Patrol Inspection Workflow ................................................................................ 170 | Figure 8-10 | 8-10: Substation Patrol Inspection Workflow .. 170
Figure 8-11: Asset Criticality and Maintenance/Replacement Strategies ................................................ 172 | Figure 8-11 | 8-11: Asset Criticality and Maintenance/Replacement Strategies . 172
Figure 8-12: Open Work Orders: Corrective Maintenance ....................................................................... 190 | Figure 8-12 | 8-12: Open Work Orders: Corrective Maintenance 190
Figure 8-13: Annual Percentage of Deferred Work Orders ...................................................................... 193 | Figure 8-13 | 8-13: Annual Percentage of Deferred Work Orders . 193
Figure 8-14: Work Orders by Number of Days Past Due .......................................................................... 193 | Figure 8-14 | 8-14: Work Orders by Number of Days Past Due 193
Figure 8-15: Results of Reclosure Protocols in Fault Avoidance ............................................................... 198 | Figure 8-15 | 8-15: Results of Reclosure Protocols in Fault Avoidance 198
Figure 10-1: Smoke Detection Image Identified by AI Smoke Detection Algorithm ................................. 245 | Figure 10-1 | 10-1: Smoke Detection Image Identified by AI Smoke Detection Algorithm . 245
Figure 10-2: Historical Major Wildfire Correlation to FPI ......................................................................... 249 | Figure 10-2 | 10-2: Historical Major Wildfire Correlation to FPI .. 249
Figure 10-3: SAWTI Across Time and Incidences of Major Wildfires ........................................................ 250 | Figure 10-3 | 10-3: SAWTI Across Time and Incidences of Major Wildfires . 250
Figure 10-4: Wind Gust Machine Learning Validation for West Alpine .................................................... 251 | Figure 10-4 | 10-4: Wind Gust Machine Learning Validation for West Alpine .. 251
Figure 10-5: Example of Machine Learning Gust Forecast Model Output ............................................... 251 | Figure 10-5 | 10-5: Example of Machine Learning Gust Forecast Model Output 251
Figure 11-1: EOC Activation Levels ........................................................................................................... 259 | Figure 11-1 | 11-1: EOC Activation Levels .. 259
Figure 11-2: Wildfire and PSPS Emergency Response Phases .................................................................. 260 | Figure 11-2 | 11-2: Wildfire and PSPS Emergency Response Phases 260
Figure 13-1: Monitoring & Review Step of the Enterprise Risk Management Framework ...................... 289 | Figure 13-1 | 13-1: Monitoring & Review Step of the Enterprise Risk Management Framework 289
Appendix A: Definitions | Appendix A | Definitions
Appendix B: Supporting Documentation for Risk Methodology and Assessment | Appendix B | Supporting Documentation for Risk Methodology and Assessment
Appendix C: Additional Maps | Appendix C | Additional Maps
Appendix D: Areas for Continued Improvement | Appendix D | Areas for Continued Improvement
Appendix E: Referenced Regulations, Codes, and Standards | Appendix E | Referenced Regulations, Codes, and Standards
Appendix F: Tables | Appendix F | Tables
Appendix G: Cost Benefit and Risk Reduction Supporting Data | Appendix G | Cost Benefit and Risk Reduction Supporting Data
Appendix H: 2025 Plan to Support Populations with Access and Functional Needs During Public Safety Power Shutoffs | Appendix H | 2025 Plan to Support Populations with Access and Functional Needs During Public Safety Power Shutoffs

## DR Count (hidden)
Data Requests
#REF! | #REF! | #REF! | Count = | #REF! | *Check Range When Updating*
#REF! | #REF! | #REF!
#REF! | #REF! | #REF! | Jan | 0
#REF! | #REF! | #REF! | Feb | 0
#REF! | #REF! | #REF! | Mar | #REF!
#REF! | #REF! | #REF! | Apr | #REF!
#REF! | #REF! | #REF! | May | 3
#REF! | #REF! | #REF! | Jun | 2
#REF! | #REF! | #REF! | Jul
#REF! | #REF! | #REF! | Aug
#REF! | #REF! | #REF! | Sep
#REF! | #REF! | #REF!
#REF! | #REF! | #REF! |  | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
OEIS-2 | OEIS-2 | 2025-05-09
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
MGRA-3 | MGRA-3 | 2025-05-12
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-3 | OEIS-3 | 2025-05-13
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-4 | OEIS-4 | 2025-05-15
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-5 | OEIS-5 | 2025-05-16
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-6 | OEIS-6 | 2025-05-20
OEIS-7 | OEIS-7 | 2025-05-23
OEIS-7 | OEIS-7 | 2025-05-23
OEIS-7 | OEIS-7 | 2025-05-23
OEIS-7 | OEIS-7 | 2025-05-23
SPD-1 | SPD-1 | 2025-05-27
SPD-1 | SPD-1 | 2025-05-27
SPD-1 | SPD-1 | 2025-05-27
SPD-1 | SPD-1 | 2025-05-27
SPD-1 | SPD-1 | 2025-05-27
SPD-1 | SPD-1 | 2025-05-27
SPD-1 | SPD-1 | 2025-05-27
SPD-1 | SPD-1 | 2025-05-27
MGRA-5 | MGRA-5 | 2025-05-30
MGRA-5 | MGRA-5 | 2025-05-30
OEIS-8 | OEIS-8 | 2025-05-30
OEIS-8 | OEIS-8 | 2025-05-30
OEIS-8 | OEIS-8 | 2025-05-30
OEIS-8 | OEIS-8 | 2025-05-30
OEIS-8 | OEIS-8 | 2025-05-30
MGRA-6 | MGRA-6 | 2025-06-06
OEIS-9 | OEIS-9 | 2025-06-06
OEIS-10 | OEIS-10 | 2025-06-24
OEIS-11 | OEIS-11 | 2025-06-24
OEIS-11 | OEIS-11 | 2025-06-24
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
SPD-2 | SPD-2 | 2025-06-30
OEIS-12 | OEIS-12 | 2025-07-15
MGRA-7 | MGRA-7 | 2025-07-24
MGRA-7 | MGRA-7 | 2025-07-24
MGRA-7 | MGRA-7 | 2025-07-24
MGRA-8 | MGRA-8 | 2025-07-25
MGRA-8 | MGRA-8 | 2025-07-25
OEIS-13 | OEIS-13 | 2025-08-01
OEIS-13 | OEIS-13 | 2025-08-01
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
0 | 0 | 0

## Analytics (hidden)
|  | 2024 WMP Data Requests (Case Related) |  | 2024 WMP Data Requests (Non-Case Related) |  | Party | Non-Case DR Name | Question #
# of Questions
Row Labels | Count of Data Requests | # of DRs | 1 | # of DRs | 52
0 | 171 | # of DR Questions | #REF! | # of DR Questions | 176
Grand Total | 171
|  | # of Requests per Party | 0 | # of Requests per Party | 52
|  | CalPA | 0 | CalPA | 3
|  | MGRA | 0 | MGRA | 1
|  | OEIS | 0 | SPD | 0
|  | GPI | 0 | OEIS | 8
|  | SPD | 0 | IE | 40
|  |  |  | 4LEAF | Ask Shaun G
|  | # of Questions per Party | 342
|  | CalPA | 342 | # of Questions per Party | 176
|  | MGRA | 0 | CalPA | 20
|  | OEIS | 0 | MGRA | 7
|  | GPI | 0 | SPD | 0
|  | SPD | 0 | OEIS | 106
|  |  |  | IE | 43
|  | 2024-06-24 |  | 4LEAF | Ask Shaun G
|  | Count Check |  | 2024-06-24
|  | # of DRs | #REF! | Manually Input
|  | # of DR Questions | 126