## 2025
*Log Begins August 8, 2025*
Trans Bay Cable LLC
2026-2028 WMP Data Request Log
As of October 30, 2025
Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Response | Requestor | Date Received | Final Due Date | Date Sent | Links | No. of Attachments | NDA Required | WMP Section | Category | Subcategory | Confidential
1 | OEIS | P-WMP_2025-TBC | 001 | 1 | Q01 | Regarding TBC’s Converter Maintenance Practices: a. Provide the latest version of TBC’s Converter Maintenance Practices (TBC-MP-001). | Trans Bay Cable (TBC) provides the current version of its Converter Maintenance Practices (TBC-MP-001) as a confidential attachment to this data request. TBC requests confidentiality for TBC-MP-001, and requests that the Office of Energy Infrastructure Safety not disclose TBC-MP-001 or the information contained therein to the public or any third party. Confidential treatment of TBC-MP-001 by the Energy Safety is appropriate pursuant to: • U.S. Code Title 16, Section 824o-1, and regulations promulgated thereunder by the Federal Energy Regulatory Commission (“FERC”) (18 C.F.R. § 388.113) prohibiting disclosure of critical electric infrastructure information; • Section 6254(k) of the California Government Code, which specifies that a state agency is not required to disclose “records, the disclosure of which is exempted or prohibited pursuant to federal or state law, including, but not limited to, provisions of the Evidence code relating to privilege;” and • Section 1040 of the California Evidence Code, which specifies that a public entity has a privilege to refuse to disclose information acquired in confidence by a public employee in the course of his or her duty and not open, or officially disclosed, to the public prior to the time the claim of privilege is made, when disclosure is forbidden by an act of Congress of the United States or a statute of this state. | Johan Im | 2025-08-07 | 2025-08-12 | 2025-08-12 |  | 1 |  | Various | Various | Various | Yes
2 | OEIS | P-WMP_2025-TBC | 002 | 1 | Q01 | Regarding Enterprise System Internal Procedures a. On page 192 of the TBC 2026-2028 Base WMP, TBC says that “[m]aintenance, vegetation and asset management tasks are inputted, tracked, and monitored in AMP.” i. Please provide the internal procedures for updating the various enterprise systems used in vegetation and asset management tasks, any planned updates, and the ability to migrate data across systems. ii. Please provide the internal processes used to ensure data integrity, accessibility, and retention for the enterprise systems used in vegetation and asset management tasks. | i. AMP is a custom-built, in-house asset management program which is utilized by all NextEra Energy affiliates, including TBC. AMP is managed at the corporate level by NextEra Energy’s Power Delivery business unit and its dedicated IT department. As such any changes, updates, etc. are directed, managed, and controlled at the corporate level. ii. AMP is the only enterprise system that TBC utilizes for vegetation and asset management tasks. As noted in the response above, AMP is managed at the corporate level by NextEra Energy’s Power Delivery business unit and its dedicated IT department. | Johan Im | 2025-08-15 | 2025-08-20 | 2025-08-20 |  |  |  | 12.2 | Enterprise Systems | Summary of Enterprise Systems | No
3 | CPUC Safety Policy Division | SPD-TBC-WMP2026 | 002 | 1 | 1 | Does TBC have any PSPS protocols when a PSPS event is triggered? If so, provide a copy of these protocols. If not, explain TBC’s responsibilities if a PG&E initiated PSPS event creates a shutoff of TBC infrastructure. | Given TBC’s limited scope and scale of operations, distribution system, no distribution or retail customers, TBC does not have specific PSPS protocols. TBC expects that PG&E doctrine regarding PSPS that impacts the PG&E Pittsburg Substation would be the prevailing driver of any PSPS impacts on TBC’s operational area. Any PSPS issued by PG&E that impacted TBC’s Pittsburg Converter Station to the extent that TBC’s interconnection would be de-energized would take the Trans Bay System offline. The quantitative description of such a PSPS implementation for TBC is effectively binary, being either online or offline due to a PG&E issued PSPS whereby the Trans Bay System would not be energized and therefore poses minimal to no fire risk to the public. As TBC is under the operational control of the CAISO and interconnected with PG&E, TBC would coordinate any PG&E PSPS-driven outage and restoration with those entities. | Tyler Dunaway | 2025-08-28 | 2025-09-03 | 2025-09-03 |  |  |  | 11.2 | Emergency Preparedness, Collaboration and Community Outreach | Emergency Preparedness and Recovery Plan | No
4 | CPUC Safety Policy Division | SPD-TBC-WMP2026 | 002 | 2 | 2 | Provide proposed / actual WMP expenditure data from 2023 – 2025 (through August 15th) | Year Proposed (in thousands of $USD Actual (in thousands of $USD 2023 $280 $209.1 2024 $0 $35.8 2025 (year to Aug. 15) $0 $0 | Tyler Dunaway | 2025-08-28 | 2025-09-03 | 2025-09-03 |  |  |  | N/A | N/A | N/A | No
5 | OEIS | P-WMP_2025-TBC | 003 | 1 | Q01 | Regarding SA-02 and SA-06 Activities: a. In the 2026-2028 Base WMP Revision 1, Table 10-1 on pages 140 and 142 show the same activities for SA-02 and SA-06 “Evaluation of Optos/Firecaster performance”. i. Provide an explanation and further information on the usage of the different tracking numbers for the same activity. 1. If this is a typo, please indicate as such and describe the steps being taken to correct. | i. Optos/Firecaster has both environmental monitoring components and risk index features. Evaluation of the performance of various inputs to Firecaster may be separate from evaluation of overall output of the wildfire risk index model. As such although the title of the task is the same for SA-02 and SA-06, different aspects of the Optos/Firecaster tool will be evaluated. | Johan Im | 2025-09-23 | 2025-09-26 | 2025-09-26 |  |  |  | 10.1 | Situational Awareness and Forecasting | Targets | No
6 | OEIS | P-WMP_2025-TBC | 003 | 2 | Q02 | Regarding TBC’s Planned Migration from AMP to Elements: a. In the TBC 2026-2028 Base WMP Revision 1, Table 12-1 on page 191 show “N/A” for initiatives related to Section 12: Enterprise systems. However, in the narrative section on page 193 states, “However, there is a corporate-directed plan to transition to Elements (a custom-build, in-house asset management program), the upgraded version of AMP, during this timeframe." i. Provide the following information related to the transition from AMP to Elements during the 2026-2028 WMP cycle: 1. Narrative information on the timing, milestones, and status of the transition to Elements. 2. Explanation of why this transition plan is not included in the initiatives for Section 12: Enterprise systems of the WMP. | 1. The corporate transition from AMP to Elements is planned for completion by mid-2026. As part of the transition process, assets, work tasks, and functions are being verified and crosschecked in the test environment to ensure continuity of operations and compliance with existing maintenance workflows in AMP. Confirmation of functionality will be verified in the production environment and job-aids and training provided to users in connection with project completion planned for mid-2026. 2. Exclusion of the transition plan as an initiative in Section 12 was an oversight, as it should have been included in the most recent revision of TBC’s Base 2026-2028 WMP to sync with the revised language added in the narrative on page 193. A subsequent revision to TBC’s Base 2026-2028 WMP will be submitted to correct the oversight. | Johan Im | 2025-09-23 | 2025-09-26 | 2025-09-26 |  |  |  | 12.1 | Enterprise Systems | Targets | No
7 | OEIS | P-WMP_2025-TBC | 004 | 1 | Q01 | Regarding General Housekeeping during the Monthly Inspection of Watch: a. On page 37 of its 2026-2028 base WMP, TBC states, “TBC Operations and Maintenance Technicians (O&M Techs) perform monthly systems inspections in accordance with TBC’s Monthly Inspection of Watch procedure (TBC-MP-004), which includes general checks, visual inspections, general housekeeping, and a review of maintenance equipment.” i. What activities are completed as part of “general housekeeping”? ii. As part of the monthly systems inspections, do O&M Techs visually inspect the converter stations for combustible materials, trash, and/or other hazardous materials? 1. If yes; is this inspection task listed on the Monthly Inspection of Watch Maintenance Procedure? a) If yes, please provide the page number and location of this item. b) If no, how do O&M Techs record and track this information? 2. If no; why is this not a necessary item to track for inspections? Additionally, what do O&M Techs do if they discover combustible materials, trash, and/or other hazardous materials during their inspection? | i. General housekeeping implies a visual check as the inspection is in progress for any deficiencies or off normal conditions which would include the presence of combustible materials or trash outside of designated receptacle or storage areas in the wrong spot (for example trash in the vicinity of energized equipment) ii. Yes, O&M Techs visually inspect the converter stations for combustible materials, trash, and/or other hazardous materials. 1. This type of general housekeeping is not identified as an inspection task in the monthly inspection. See response to # 2 below. a. N/A b. Any off normal condition that cannot be remediated immediately is noted in the inspection notes for follow up action/remediation. 2. Activities connected to site cleanliness, storage of combustible and/or hazardous materials are more appropriately addressed under TBC’s Health and Safety program, led by TBC’s Sr. Health & Safety Specialist, and associated procedures. If an O&M tech discovered combustible materials, trash, and/or other hazardous materials during the inspection then the condition is remediated immediately by the inspecting O&M Tech or reported to Operations manager or Sr. Health & Safety Specialist for appropriate remediation. | Johan Im | 2025-10-17 | 2025-10-22 | 2025-10-22 |  |  |  | 5.1 | Risk Methodology and Assessment | Methodology | No
8 | OEIS | P-WMP_2025-TBC | 004 | 2 | Q02 | Regarding Monthly Inspection of Watch document: a. Provide the monthly Inspection of Watch tracking form completed by O&M Techs during their inspection. i. Provide a blank version of the document and the most recently completed version of the document for the TBC Pittsburg Converter station. | Trans Bay Cable (TBC) provides a blank version of the Monthly Inspection of Watch document and the most recently completed inspection dated, September 9, 2025, as confidential attachments to this data request. TBC requests confidentiality for both documents, and requests that the Office of Energy Infrastructure Safety not disclose either document or the information contained therein to the public or any third party. | Johan Im | 2025-10-17 | 2025-10-22 | 2025-10-22 |  | 1 |  | N/A | N/A | N/A | Yes