## Cover
Policy 001
MAINTENANCE INTERVALS FOR APPARATUS, RELAYS, METERS,
LINE PATROL/INSPECTIONS, WIRES EQUIPMENT AND COMMUNICATIONS EQUIPMENT
PacifiCorp Asset Maintenance and Compliance Policy 001
Date | Revision # | Notes
2009-10-30 | 17 | Add security system, clarify switchgear CB maintenance
2010-10-01 | 18 | Revise labor estimates and clarify transmission LTC's w/filter overhaul schedule
2011-08-01 | 19 | Revise maintenance procedure list for communications equipment, add line recloser and SVC maintenance plans for apparatus equipment, add SVC relay equipment
…
2017-12-08 | 36 | Updated maintenance ID for Meters M4, M5 and M6. On Relay tab added new Throwover, Autosource transfer and Air cooled Xfmr maintenance tasks; and removed V1-VBE and S2 maintenance activity. On Apparatus tab added synchronous condenser testing; updated OFIN-xxx; cycle is to be determined; also, updated TNOS-002 added Pacific Power BMMx-036 minor maintenance. On Comm tab modified equipment information.
2018-08-08 | 37 | Updated California Visual Assurance (Patrol) inspections to meet new requirements, corrected Hold Down Inspection policy inspection to Policy 337 from incorrect 377
2018-12-14 | 38 | Line Inspec tab: Updated CA UG detail inspection note; added CA visual inspection to 1 year for Tier 1, 2 & 3; added Fuse Saver. Meter tab: Added CAISO/EIM meter intervals.
2019-05-14 | 39 | Updated Relay Equipment Description for B1_B2 and U1_U2 to include "Monitored and Alarming to Scada", and correcting Maintenance Task for BR2 to "Minor". Correcting CA visual Tier notes.
2020-03-24 | 40 | Maintenance Basis tab added note 3) regarding maintenance cycles less than 1 year. Apparatus tab added new line items for CKB, CAP, TRF and XRT for RMP only Warranty Inspections. Relay tab updated equipment description to "Electromechanical" for B5_B6 maintenance; added BR1 and BR2 to "Montitored alarming to scada" and add new plans BR3 and BR4 for recloser relays "Not Monitored"; also included Sudden Press in BR1, BR3 and BR4 notes. Line tab added Weather station 6 month inspections for RMP. Updated Recloser battery replacment model to 351R2 for RCBT(apc) and DRCL(line). Added FHCA new inspection cycles on Line tab. Added new maintenance activity OTN on Comm tab.
2021-06-21 | 0-PP | First version of Policy 001 specific to Pacific Power. Updated Communications man hours. Removed WMA maintenance task.
2022-06-20 | 1-PP | Added local transmission infrared line inspections (wires tab); RAS SPS1 maintenance interval changed from four years to six years (relay tab). Added B1_B2 maintenance to RAS SPS1 maintenance tasks (relay tab). Updated to include distribution breaker overhaul plans for large customers (apparatus tab). Added grid resilience equipment/storage facility inspection and maintenance task (apparatus tab).
2023-06-30 | 2-PP | Added non-FHCA Transmission Line Infrared Inspections for OR/WA (wires tab, line 15); Added non-NERC remedial action scheme maintenance items (relay tab, line 37 & 41).
2020-10-13 | 0-RMP | First version of Policy 001 specific to Rocky Mountain Power.
2020-12-22 | 1-RMP | Revision to update the policy on new transformer baseline DGA cycles.
2021-02-12 | 2-RMP | Revision to updated the policy on HVAC wall and window units and DGA and WARR on spare transformers; updated DCAP cycle.
2021-09-20 | 3-RMP | Removed "window" from HVAC maintenance; Combined the DGA on Spare transformers with the Designated/Strategic Spares. Removed MWA and updated TOW hours and notes from Communications tab. Added Synchronous Condenser 5-year & monthly maintenance and 5-year operating validation. Removed 4-month XROS and OFIN plans.
2022-02-09 | 4-RMP | Updated maintenance basis explanation for non-WECC apparatus and relay work orders. Added synchronous condenser PRC-019 maintenance requirements. Changed RAS maintenance plan cycle from 4 to 6 years per PRC-005. Added MWA and Alarm GMP plans on Communication tab.
2023-02-09 | 5-RMP | Updated weather station maintenance plan cycle from 6 months to 1 year. Updated weather station maintenance plan type from EML4 to EML8. Updated cap bank interval from 2 and 4 years to 1 year on GE.
2023-09-18 | 6-RMP | Added RAS Component maintenance B1_B2; in addition add maintenace for any potential Non-WECC/NERC RAS systems and their components. Removing TNOS specific Plan; noting TROS and XROS plans are to begin 2 months after commissioning. Added DRCL Siemens CMR maintenance. Additional maintennace added for GE SCAP and Sync Condensors. Added STATCOM Maintenance
2024-01-19 | 7-RMP | Wires tab: Added infrared Inspections to FHCA transmission lines. Added annual inspections on underground transmission lines. Distribution PTT and UG Detail Inspection cycles change from 20-year to 10-year. Adding switchgear infrared inspections. Add SEL AR360 fault indicator unit replacement.
2024-11-04 | 41 | Combined Pacific Power and Rocky Mountain Power Policy 001. Update Maintenance Basis with Actual Finish Dates disclaimer. Added Syn Conderson MIN mtc for Goshen. Added PRC-027 Setting requirements, under relay. Separated out Wires Inspections and Equipment into two tabs. DRCL-MAJ added to Wires Equipment tab. Separated out Wires Inspections by State from wires equipment.
2025-04-30 | 42 | Added FAA Inspections on Wires Equipment tab. Pacific Power UGIN cycle change. Pacific Power CA & WA PTT cycle change to 10yr. WA UG Detail cycle change to 10yr.
2025-12-03 | 43 | Added DTSW-SUB on Apparatus tab. Updated the maintenance basis for FAC-501 equipment to allow approval of specific maintenance deferral. Added ceramic to Hold Down Inspections. Added DCAP inspections for PP on Wires Equipment tab. Added DGA sampling for vault transformers on Lines Equipment tab. Add increased inspections for CA Tier 3 and added DRONE inspections on Lines Inspections tab. Added "include mobiles" for specific maintenance on Apparatus and Relay tabs. Updated TROS to annual PM and TCOS to 6 month PMs.
2025-12-11 | 44 | Removing drone transmission inspections for OR, WA, UT, ID and WY; on wires line inspection tab; put on by mistake. Updated DTSW to DTSS on apparatus tab. Adding BXRT requirements for PMs on apparatus tab.
Author: Various Contributors; Updated by Mindy Curnes
Approval: Eddie Summit
Authoring Department: Asset Maintenance & Compliance
Approved Location: J:\Publications\FPP\DIS\POL
File Number-Name: Policy 001-Maintenance Intervals Rev0.xlsx
Revision number: 44
Revision date: 12/11/2025
* between 10/31/20 and 11/4/24 there was a separate Rocky Mountain Power version of this policy. Between 6/21/21 and 11/4/24 there was a separate Pacific Power version of this policy. As of 11/4/24 the policy has been reintegrated as a single PacifiCorp document.
The most current version of this document is posted to engineering's policy websites.
Revisions to this document must be made by the authoring department and posted by engineering publications (eampub@pacificorp.com)

## Maintenance Basis
Maintenance Basis
Apparatus | Apparatus maintenance intervals for PacifiCorp are based on a combination of manufacturer's recommendations, failure and corrective maintenance history and experience and the opinions of PacifiCorp subject matter experts. The maintenance intervals are time based, are based on operations counts or based on other triggers.
The following pertains to apparatus equipment designated as a component of a NERC FAC-501 critical path: 1) Time intervals are developed assuming the required preventative maintenance work will be performed within the calendar year the order is generated with the stated interval being defined as calendar years. 2) For work on equipment that is triggered by an operational counter, the work shall be performed within the calendar year following the counter trigger date. 3) For time intervals less than one year (i.e. 3 months, 4 months, etc.) the preventative maintenance work will be performed within the cycle time period.
Testing or maintenance activities that call for operation of the equipment may be satisfied if an actual real-time operation of that device can be documented during the last maintenance cycle.
Maintenance intervals and requirements are reviewed on a periodic basis and adjusted based on failure or maintenance issues, industry trends and manufacturer's recommendations.
Maintenance Deferral for NERC Equipment | Maintenance due in a given calendar year for apparatus equipment designated NERC in Maximo may be deferred if an approved capital replacement project for the equipment is scheduled for the following calendar year or if materials, parts or required expertise are unavailable, delaying work, or if there are other valid concerns as approved by the director of asset maintenance and compliance. The maintenance order will be closed when the replaced equipment is placed in-service and a new maintenance plan will be assigned to the replaced equipment. NERC relay maintenance must be completed within caledar year due and cannot be deferred for any NERC in-service equipment.
Maintenance Deferral for Non-NERC Equipment | Work orders and maintenance for non-NERC equipment may be deferred due to operational priorities, approved capital projects or maintenance projects.
Maintenance Actual Finish Dates | Work orders Actual Finish Dates can differentiate from completion date on form due to the new system functionality.
New or Revised Maintenance Policies | Upon creation or revision of a maintenance policy, the determination of when the new maintenance activity will commence on an individual piece of equipment will be determined by PacifiCorp Asset Management. Equipment will not be considered non-compliant with the new or revised maintenance policy interval if the work required per this policy is completed within the calendar year of the initial call date that was assigned to that equipment by PacifiCorp Asset Management.

## Apparatus
Site | Equipment Type | Equipment Description | Equipment Use | Manufacturer | Model Number(s) | Operating Ratings | Maintenance Task | Asset Type | Job Plan ID | Interval Years (Months) | Interval Months | Counters (Ops/Fault) | Notes | Policy Effective Date/Year (If Known) | Master PM or Job Plan (Templates refer to Reference Sheets ) | Prerequisite (Job Plan) | Sub Type (Job Plan) | Crew (Asset) | Use Last Work Orders Start Date (Master PM or PM) | Leadtime Days (Master PM or PM) | Scheduling Date
PP & RMP | Battery | Vented or NiCad | NERC - Bulk Electrical System | All | All | N/A | Battery Inspection | BATTERY | BTTI | 4 Months | 4 | N/A | Battery inspection. |  | 2154 PD-S-NERC-BTTI-004:NERC Battery Inspection 2233 PD-S-NERC-BTTI-004-PP:NERC Battery Inspection PP | Yes | BATTERYMAINT | APP | Yes | 4 | xx/01/xxxx See Referece Sheets for Months
PP & RMP | Battery | Valve Regulated | NERC - Bulk Electrical System | All | All | N/A | Battery Maintenance | BATTERY | BTTM | 4 Months | 4 | N/A | Battery impedance test. |  | 2155 PD-S-NERC-BTTM-004:NERC Battery Impedance-VALVE 2247 PD-S-NER-BTTM-004-PP:NERC Battry Impedance PP | Yes | BATTERYMAINT | APP | Yes | 4 | xx/01/xxxx See Referece Sheets for Months
PP & RMP | Battery | Vented or NiCad | NERC - Bulk Electrical System | All | All | N/A | Battery Maintenance | BATTERY | BTTM | 18 Months | 18 | N/A | Battery impedance test. |  | 2156 PD-S-NERC-BTTM-018:NERC Battery Impedance 2249 PD-S-NERC-BTTM-018-PP:NERC Battery Impedance PP | Yes | BATTERYMAINT | APP | Yes | 4 | Start-up Month/Year (xx/01/xxxx)
PP & RMP | Battery | Vented, NiCad or Valve | Transmission and Distribution (Non-NERC, including Mobiles) | All | All | N/A | Battery Maintenance | BATTERY | BTTM | 2 | 24 | N/A | Battery impedance test. |  | 2116 PD-S-BTTM-024:Battery Impedance 2251 PD-S-BTTM-024-PP:Battery Impendance PP | Yes | BATTERYMAINT | APP | No | 0 | Start-up Date
PP & RMP | Battery | Sodium Nickel | All | All | All | N/A | N/A | BATTERY | N/A | N/A | N/A | N/A | No maintenance required on these batteries | 2024 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
RMP | Battery Energy Storage System | BESS Site |  | All | All | N/A | Annual Inspection | N/A | BESS | 1 | 12 | N/A | Annual inspection of BESS site as indicated on the maintenance form (Panguitch Solar Battery Site). | 2020 | 2144 - Job Plan BESS | Yes | SUBINSPECTION | APP | Yes | 4 | 1/1/xxxx
RMP | Battery Energy Storage System | UPS Battery |  | All | All | N/A | Battery Replacement | BAT_UPS | UPS BATTERY | 3 | 36 | N/A | Replace UPS batteries. | 2020 | 2029 - Job Plan UPS BATTERY | No | BATTERYMAINT | APP | No | 0 | Start-up Date
RMP | Battery Energy Storage System | Fire Suppression System |  | All | All | N/A | Inspection | FSS | FSS | 6 Months | 6 | N/A | Inspection to be completed by a third party. | 2020 | 2019 - Job Plan FIRE SYSTEM | No | SPECIALPROJECT | APP | Yes | 4 | 1/1/xxxx
RMP | Battery Energy Storage System | Solar Panels |  | All | All | N/A | Infrared Testing by Drone | N/A | SINF-DRONE | 1 | 12 | N/A | Infrared testing of solar panels with the use of a drone. | 2020 | 2025 - Job Plan SINF-DRONE | Yes | IRINSPECTION | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Circuit Breakers | Breaker Battery | All (including mobiles) | All w/UPS | All w/UPS | N/A | Circuit Breaker Battery Replacement | BREAKER | BKBT | 3 | 36 | N/A | Circuit breaker battery replacement. |  | 2092 PD-S-BKBT-036:CKB Battery Replacement | No | BATTERYMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | Recloser Battery |  | All (except Hydraulic - see Notes column) | All | N/A | Recloser Battery Replacement | RECLOSER | RCBT | 3 | 36 | N/A | Recloser battery replacement. Hydraulic reclosers do not have batteries, and do not need maintenance plans. |  | 2166 PD-S-RCBT-036:Sub Recloser Battery Replacement | No | BATTERYMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | Recloser Battery |  | G&W Viper | with SEL-351R Controllers | N/A | Recloser Battery Replacement | RECLOSER | RCBT | 2 | 24 | N/A | Recloser battery replacement. |  | 2165 PD-S-RCBT-024:Sub Recloser Battery Replacement | No | BATTERYMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6, Vacuum and Oil |  | All | All | All Voltages | Warranty Inspection | BREAKER | WARR | 4 | 48 | N/A | Inspect equipment for warranty problems. Schedule based on manufacture date. One time only plan. |  | 2199 PD-S-WARR-048:Warranty Inspection Master PM | No | WARRINSP | APP | Yes | 0 | Construction Year 1/1/xxxx
PP & RMP | Circuit Breakers | SF6, Vacuum and Oil (including mobiles) | Except Transformer Low Side Circuit Breaker with no Bypass, or 35kV and Below Cap Bank and Others as Approved by Asset Management | All | All | All Voltages | Exercise Breaker | BREAKER OR RECLOSER | BIOA | 1 | 12 | N/A | Yearly operational test. May be fulfilled by documentation of an actual operation. |  | 2091 PD-S-BIOA-012:CKB Inspect and Operate | No | BREAKERINSPECT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6, Vacuum and Oil | NERC - FAC-501 Critical Path | All | All | All Voltages | Exercise Breaker | BREAKER OR RECLOSER | BIOA | 1 | 12 | N/A | Yearly operational test. May be fulfilled by documentation of an actual operation. |  | 2151 PD-S-NERC-BIOA-012:NERC CKB Inspect and Operate | No | BREAKERINSPECT | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Circuit Breakers | Air | Tertiary Fed Reactor, Cap Bank, Station Service, Synchronous Condenser | All | All | 12kV to 34.5kV | Overhaul | BREAKER | BOHA | 6 | 72 | N/A |  |  | 2102 PD-S-BOHA-072:CKB Overhaul Air | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Air | Breakers selected by Pacific Power Asset Management (LGCU) | All | All | All Voltages | Minor Maintenance | BREAKER | BMMA | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed. |  | 2093 PD-S-BMMA-036:CKB Minor Maintenance Air | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Air | Breakers selected by Pacific Power Asset Management (LGCU) | All | All | All Voltages | Overhaul | BREAKER | BOHA | 9 | 108 |  |  |  | 2103 PD-S-BOHA-108:CKB Overhaul Air | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Air | All applications except bus, cap and low side transformer | All | All | 35kV and Below | Overhaul | BREAKER | BOHA | 0 | Counter Based | 50-Fault | Counters applied per Asset Management. |  | 2104 PD-S-BOHA-CTR:CKB Overhaul Air | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | SF6 gas | Breakers selected by Pacific Power Asset Management (LGCU) | All | All | All Voltages | Minor Maintenance | BREAKER | BMMS | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed. |  | 2096 PD-S-BMMS-036:CKB Minor Maintenance SF6 Bottle | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas | Capacitor or Reactor Without Zero Crossing Controls | All | All | 40kV and Above | Minor Maintenance | BREAKER | BMMS | 8 | 96 |  | Time/Ductor inspect mechanism. |  | 2099 PD-S-BMMS-096:CKB Minor Maintenance SF6 | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas | Reactor with Zero Crossing Controls | All | All | 40kV and Above | Minor Maintenance | BREAKER | BMMS | 6 | 72 | N/A | Time/Ductor inspect mechanism. |  | 2098 PD-S-BMMS-072:CKB Minor Maintenance SF6 | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas | Reactor with Zero Crossing Controls | All | All | 40kV and Above | Control System Download | BREAKER | BXRT | 2 | 24 | N/A | Meter/Relay to download oscillography data and forward to Apparatus Tech Support for review of proper timing. Submit to Asset Maintenance | 2020-09-03 | 2117 PD-S-BXRT-024:CKB Control System Download | Yes | CBCNTLDOWN | REL | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas | Capacitors with Zero Crossing Controls | Asea-Brown Boveri Mitsubishi | All | 40kV and Above | Control System Download | BREAKER | BXRT | 2 | 24 | N/A | Meter/Relay to download oscillography data and forward to Apparatus Tech Support for review of proper timing. Submit to Asset Maintenance | 2026 | 2117 PD-S-BXRT-024:CKB Control System Download | Yes | CBCNTLDOWN | REL | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas | Relay packages protecting Reactor or Capacitors | Asea-Brown Boveri Mitsubishi General Electric | SCU or SCS SSC Visimax or DT1-245P-F3 | All | Control System Download | BREAKER | BXRT | 2 | 24 | N/A | Meter/Relay to download oscillography data and forward to Apparatus Tech Support for review of proper timing. Submit to Asset Maintenance | 2026 | 2117 PD-S-BXRT-024:CKB Control System Download | Yes | CBCNTLDOWN | REL | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas | Reactors or Capacitors | All | All | 230KV and Above | Control System Download | BREAKER | BXRT | 2 | 24 | N/A | Meter/Relay to download oscillography data and forward to Apparatus Tech Support for review of proper timing. Submit to Asset Maintenance | 2026 | 2117 PD-S-BXRT-024:CKB Control System Download | Yes | CBCNTLDOWN | REL | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas Puffer | Line, Transformer, Bus | All | All | 40kV and Above | Minor Maintenance | BREAKER | BMMS | 10 | 120 | N/A |  |  | 2100 PD-S-BMMS-120:CKB Minor Maintenance SF6 Puffer | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas, Dual Pressure | Line, Transformer, Bus | All (except for mfg and models listed below) | All (except for mfg and models listed below) | 40kV and Above | Minor Maintenance | BREAKER | BMMS | 4 | 48 | N/A | Time/Ductor inspect mechanism. |  | 2097 PD-S-BMMS-048:CKB Minor Maintenance SF6 Dual Pressure | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas, Dual Pressure |  | ITE | GA | 230kV- 500kV | Overhaul | BREAKER | BOHS | 6 | 72 | N/A | These models have overhauls only, no minor maintenance. |  | 2107 PD-S-BOHS-072:CKB Overhaul Dual Pressure | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | SF6 Gas, Dual Pressure |  | Westinghouse | 2300-SF-15000 | 230kV | Overhaul | BREAKER | BOHS | 6 | 72 | N/A | These models have overhauls only, no minor maintenance. |  | 2107 PD-S-BOHS-072:CKB Overhaul Dual Pressure | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | SF6 Gas, Dual Pressure |  | Westinghouse | SFA | 230kV- 500kV | Overhaul | BREAKER | BOHS | 8 | 96 |  | These models have overhauls only, no minor maintenance. |  | 2108 PD-S-BOHS-096:CKB Overhaul Dual Pressure | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | SF6 gas bottles | Breakers selected by Pacific Power Asset Management (LGCU) |  |  |  | Minor Maintenance | BREAKER | BMMS | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed. |  | 2096 PD-S-BMMS-036:CKB Minor Maintenance SF6 Bottle | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP | Circuit Breakers | SF6 gas | Breakers selected by Pacific Power Asset Management (LGCU) |  |  |  | Overhaul | BREAKER | BOHS | 9 | 108 |  |  |  | 2109 PD-S-BOHS-108:CKB Overhaul SF6 Bottle | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | SF6 gas bottles (sealed module) | All applications except bus, cap and low side transformer |  |  | 35kV and below | Overhaul | BREAKER | BOHS | 0 | Counter Based | 50-Fault | Counters applied per Asset Management. Pacific Power ONLY. |  | 2110 PD-S-BOHS-CTR:CKB Overhaul SF6 Bottle | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | Oil | Capacitor or Reactor | All | All | 40kV and Above | Minor Maintenance | BREAKER | BMMO | 6 | 72 |  |  |  | 2095 PD-S-BMMO-072:CKB Minor Maintenance Oil | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | Oil | Line, Transformer, Bus | All | All | 40kV and Above | Minor Maintenance | BREAKER | BMMO | 6 | 72 | N/A |  |  | 2095 PD-S-BMMO-072:CKB Minor Maintenance Oil | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Oil | Breakers selected by Pacific Power Asset Management (LGCU) |  |  |  | Minor Maintenance | BREAKER | BMMO | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed. |  | 2094 PD-S-BMMO-036:CKB Minor Maintenance Oil | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Oil | Breakers selected by Pacific Power Asset Management (LGCU) |  |  |  | Overhaul | BREAKER | BOHO | 6 | 72 |  |  |  | 2105 PD-S-BOHO-072:CKB Overhaul Oil | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Oil | All applications except bus, cap and low side transformer |  |  | 35kV and below | Overhaul | BREAKER | BOHO | 0 | Counter Based | 30-Fault | Counters applied per Asset Management. |  | 2106 PD-S-BOHO-CTR:CKB Overhaul Oil | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | Vacuum | Tertiary Fed Reactor, Cap Bank | All | All | 12kV to 34.5kV | Overhaul | BREAKER OR RECLOSER | BOHV | 8 | 96 | N/A |  |  | 2112 PD-S-BOHV-096:CKB Overhaul Vacuum | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | Vacuum | Tertiary Fed SVC, Wind Site Breakers. | All | All | 12kV to 34.5kV | Overhaul | BREAKER OR RECLOSER | BOHV | 10 | 120 | N/A |  |  | 2114 PD-S-BOHV-120:CKB Overhaul Vacuum | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Breakers | Vacuum | Synchronous Condenser | All | All | 12kV to 34.5kV | Overhaul | BREAKER OR RECLOSER | BOHV | 6 | 72 | N/A |  |  | 2111 PD-S-BOHV-072:CKB Overhaul Vacuum | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Vacuum | Breakers selected by Pacific Power Asset Management (LGCU) |  |  |  | Minor Maintenance | BREAKER OR RECLOSER | BMMV | 3 | 36 |  | Exercise breaker. Inspect, clean and lubricate operating mechanism. Install or relocate cabinet heater as needed. |  | 2101 PD-S-BMMV-036:CKB Minor Maintenance Vacuum | Yes | BREAKERMAINT | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Vacuum | Breakers selected by Pacific Power Asset Management (LGCU) |  |  |  | Overhaul | BREAKER OR RECLOSER | BOHV | 9 | 108 |  |  |  | 2113 PD-S-BOHV-108:CKB Overhaul Vacuum | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP | Circuit Breakers | Vacuum | All applications (including mobiles) except bus, cap and low side transformer |  |  | 35kV and below | Overhaul | BREAKER OR RECLOSER | BOHV | 0 | Counter Based | 50-Fault | Counters applied per Asset Management. |  | 2115 PD-S-BOHV-CTR:CKB Overhaul Vacuum | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Switcher | Gas | Reactive Switching, Line Switching or Transformer Protection (including mobiles) | S&C Electric Siemens Allis | Type G, Mark Series Linebacker | 100kV or Above | Inspect & Operate | CIRSWR | CSIO | 5 | 60 | N/A | Inspect and test. |  | 2118 PD-S-CSIO-060:CSIO Inspect and Operate | Yes | BREAKERINSPECT | APP | No | 0 | Start-up Date
PP & RMP | Circuit Switcher | Gas | NERC - FAC-501 Critical Path | S&C Electric Siemens Allis | Type G, Mark Series Linebacker | 100kV or Above | Inspect & Operate | CIRSWR | CSIO | 5 | 60 | N/A | Inspect and test. |  | 2157 PD-S-NERC-CSIO-060:NERC CSIO Inspect and Operate | Yes | BREAKERINSPECT | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Circuit Switcher | Gas | No Physical Counter | All | All (exclude Transrupters) | All Voltages | Overhaul | CIRSWR | CSOH | 8 | 96 | N/A |  |  | 2119 PD-S-CSOH-096:CSW Overhaul | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Switcher | Gas | All Applications (including mobiles) | S&C Electric | 2000 Series | All Voltages | Overhaul | CIRSWR | CSOH | N/A | Counter Based | 3,000-Ops |  |  | 2122 PD-S-CSOH-CTR-3000:CSW Overhaul | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Switcher | Gas | All Applications (including mobiles) | S&C Electric Siemens Allis Southern States | Type G, Mark Series (Mark V - 1984 or newer) Linebacker, CPV2 CSV | All Voltages | Overhaul | CIRSWR | CSOH | N/A | Counter Based | 1,500-Ops |  |  | 2121 PD-S-CSOH-CTR-1500:CSW Overhaul | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Circuit Switcher | Gas | All Applications (including mobiles) | S&C Electric | Mark V - 1983 or older | All Voltages | Overhaul | CIRSWR | CSOH | N/A | Counter Based | 1,000-Ops |  |  | 2120 PD-S-CSOH-CTR-1000:CSW Overhaul | Yes | BREAKEROVERHAUL | APP | No | 0 | Start-up Date
PP & RMP | Fuse | All Spare Power Transformer Fuses |  | S&C Electric SMD Fuses |  | N/A | Air Flow Test | N/A | FUSE | 5 | 60 | N/A | Air flow test. |  | 2128 PD-S-FUSE-060:Fuse Air Flow Test on Spare TRF fuses | No | FUSEAFTEST | APP | No | 0 | Start-up Date
PP & RMP | Generator | Emergency |  | All | All | N/A | Annual Inspection | GENERATOR | EPUA | 1 | 12 | N/A |  |  | 2127 PD-S-EPU-012:Emergency Generator Inspection | No | EMGENINSP | APP | Yes | 4 | 1/1/xxxx
RMP | Generator | Mobile | Terminal | All | All | N/A | Start-up & Inspect | GENERATOR | MOGN | Monthly | 1 | N/A | Monthly start-up and inspection on mobile generators on Barron oil trailers. |  | 2145 PD-S-MOGN-001:Mobile Generator Start-up & Inspection | No | MOBGENINSP | APP | Yes | 4 | x/x/xxxx
PP | GRID RESILIENCE STORAGE FACILITY | Grid resilience facility |  |  |  |  | GR Equipment/Bldg Inspection | N/A | GRID | 4 Months | 4 | N/A | Inspection of grid resilience equipment and storage facility |  | 2216 PD-S-GRID-003:Grid Resilience Inspection | Yes | SPAREINSP | APP | Yes | 4 | x/x/xxxx
PP & RMP | HVAC | Air Conditioning/Heating Systems | Excluding Wall Units | All | All | N/A | Inspect & Operate | HVAC | HVAC | 1 | 12 | N/A |  |  | 2130 PD-S-HVAC-012:HVAC Maintenance | No | HVACINSP | APP | Yes | 4 | 1/1/xxxx
RMP | HVAC | Wall Units |  | Bard Mitsubishi | All All | N/A | Inspect & Operate | HVAC | HVAC | 1 | 12 | N/A |  | 2021 | 2130 PD-S-HVAC-012:HVAC Maintenance | No | HVACINSP | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Reactors | All Types, including Spares | All Applications | All | All | All Voltages | Warranty Inspection | REACTOR | WARR | 4 | 48 | N/A | Inspect equipment for warranty problems. Schedule based on manufacture date. One time only plan. |  | 2199 PD-S-WARR-048:Warranty Inspection Master PM | No | WARRINSP | APP | Yes | 4 | Construction Year 1/1/xxxx
PP & RMP | Reactors | Oil Filled, including Spares | All Applications | All | All | All Voltages | DGA & Oil Quality Tests | REACTOR | XROS | 1 | 12 | N/A | DGA and oil quality for reactor tank. Initial order to be called 2 months after commissioning of asset to obtain the baseline DGA; orders to be called annully thereafter. |  | 2202 PD-S-XROS-012:Reactor DGA and Oil Quality Test 2254 PD-S-XROS-012-PP:Reactor DGA and Oil Quality Test PP | No | DGAOILTEST | APP | Yes | 4 | 1/1/xxxx
PP | Reactors | Oil Filled, including Spares |  | ABB |  | 345kV, 500kV | DGA and Oil Quality Tests | REACTOR | XROS | 4 Months | 4 | N/A | DGA and oil quality for reactor tank. NOTE: Work orders generated every 4 months, a minimum of 2 tests shall be performed in a calendar year. |  | 2271 PD-S-XROS-004-PP:Reactor DGA and Oil Quality Test PP | No | DGAOILTEST | APP | Yes | 4 | x/x/xxxx
PP & RMP | Regulator LTC | All (Excluding Non-Vacuum w/Separate LTC Tank on 3 Phase Regulator) |  | All | All | N/A | DGA Tests | REGLTC | TCOS | 6 Months | 6 | N/A | DGA for LTC tank. | 2026 | tbd | No | DGAOILTEST | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Regulator LTC | Non Vacuum with Separate LTC Tank on 3 Phase Regulator |  | General Electric Cooper Power Westinghouse | MLT32 550BLS and SVR URS, URT and UTT | N/A | DGA Tests | REGLTC | TCOS | 4 Months | 4 | N/A | DGA for LTC tank. NOTE: Work orders are generated every 4 months, a minimum of 2 tests shall be performed in a calendar year. |  | 2189 PD-S-TCOS-004:LTC DGA Test 2269 PD-S-TCOS-004-PP:LTC DGA Test PP | No | DGAOILTEST | APP | Yes | 4 | (Jan, May, Sep)
PP & RMP | Regulator LTC | 3 Phase with Non Vacuum LTC |  | All | All | All Voltages | Overhaul | REGLTC | RGOH | 4 | 48 | N/A | Inspect contacts & filter oil. |  | 2167 PD-S-RGOH-048:Regulator LTC Overhaul | Yes | REGOVH | APP | No | 0 | Start-up Date
PP & RMP | Regulator LTC | 3 Phase with Vacuum LTC |  | Cooper Power | V2A | All Voltages | Overhaul | REGLTC | RGOH | 8 | 96 | N/A | Inspect contacts & filter oil. |  | 2168 PD-S-RGOH-096:Regulator LTC Overhaul | Yes | REGOVH | APP | No | 0 | Start-up Date
PP & RMP | Regulators | 3 Phase with LTC in Tank |  | Allis Chalmers General Electric | AFR and SFR TMLT32 | All Voltages | DGA & Oil Quality Tests | REGULATOR | RGOS | 4 Months | 4 | N/A | DGA and oil quality for regulator main tank. NOTE: Work orders are generated every 4 months, a minimum of 2 tests shall be performed in a calendar year. |  | 2169 PD-S-RGOS-004:Regulator DGA and Oil Quality Test 2248 PD-S-RGOS-004-PP:Regulator DGA and Oil Quality Test PP | No | DGAOILTEST | APP | Yes | 4 | (Jan, May, Sep)
PP & RMP | Regulators | 3 Phase with LTC in Separate Tank |  | General Electric Cooper Power Westinghouse | MLT32 550BLS and SVR URS, URT and UTT | All Voltages | DGA & Oil Quality Tests | REGULATOR | RGOS | 1 | 12 | N/A | DGA and oil quality for a regulator's main tank. |  | 2170 PD-S-RGOS-012:Regulator DGA and Oil Quality Test 2252 PD-S-RGOS-012-PP:Regulator DGA and Oil Quality Test PP | No | DGAOILTEST | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Series Capacitor | Under 10 years old |  | All (exclude GE) | All | All Voltages | Inspection | CAPBANK | SCIN | 4 | 48 | N/A | On platform equipment |  | 2172 PD-S-SCIN-048:Series Capacitor Inspections | Yes | SERIESCAPINSP | APP | No | 0 | Start-up Date
PP & RMP | Series Capacitor | Over 10 years old |  | All (exclude GE) | All | All Voltages | Inspection | CAPBANK | SCIN | 2 | 24 | N/A | On platform equipment |  | 2171 PD-S-SCIN-024:Series Capacitor Inspections | Yes | SERIESCAPINSP | APP | No | 0 | Start-up Date
PP & RMP | Series Capacitor | All Years |  | General Electric | All | All Voltages | Inspection | CAPBANK | SCIN | 1 (sequence with SCMT) | 12 | N/A | On platform equipment | April 2023 (GE SCIN updated to 1 year) | 2277 PD-S-SCIN-SCMT GE Series Capacitor Inspections | Yes | SERIESCAPINSP | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Series Capacitor | All Years |  | General Electric | All | All Voltages | Maintenance | CAPBANK | SCMT | 5 (sequence with SCIN) | 60 | N/A | On platform equipment | May 2023 (GE SCMT added and sequenced with SCIN) | 2277 PD-S-SCIN-SCMT GE Series Capacitor Inspections | Yes | SERIESCAPMTC | APP | Yes | 4 | 1/1/xxxx
PP | Series Capacitor | With air gap trigger |  | N/A | N/A | N/A | Air Gap Injection | CAPBANK | ARGP | 0 | Counter Based | 25 Operations | Burns Reactor Sub only |  | Job Plan: 13320 - ARGP | No | SPECIALPROJECT | APP | Yes | 0 | Start-up Date
RMP | Shunt Capacitor | All Types |  | All | All | 40kV and Above | Warranty Inspection | CAPBANK | WARR | 4 | 48 | N/A | Inspect equipment for warranty problems. Schedule based on the manufacture date. One time only plan. |  | 2199 PD-S-WARR-048:Warranty Inspection Master PM | No | WARRINSP | APP | Yes | 4 | Construction Year 1/1/xxxx
PP & RMP | Spare Equipment | Strategic Spare Equipment Located in Tech Ops Yard/Bldg. |  | All | All | All Voltages | Spare Equipment Inspection | N/A | SPAR | 4 Months | 4 | N/A | Inspection of strategic spares in yard. |  | 2176 PD-S-SPAR-004:Spare Equipment Inspection 2273 PD-S-SPAR-004-PP:Spare Equipment Inspection PP | No | SPAREINSP | APP | Yes | 4 | (Jan, May, Sep)
RMP | STATCOM | Statcom System |  | All | All | All Voltages | Inspection | N/A | STATCOM-INSP | 1 Month | 1 | N/A | Monthly inspection to be completed 8 times per year; same months as substation inspections | 2023 | 2245 PD-S-STATCOM-SEASON: STATCOM Inspection | Yes | SUBINSPECTION | APP | Yes | 4 | (Jan, Mar, Apr, Jun, Jul, Sept, Oct, Dec)
RMP | STATCOM | Statcom System |  | All | All | All Voltages | PM | N/A | STATCOM-PM | 1 Year | 12 | N/A | Annual inspection to be completed by Contractor | 2023 | 2244 PD-S-STATCOM-012: STATCOM PM | Yes | SPECIALPROJECT | APP | Yes | 4 | 1/1/xxxx
RMP | Substation | NERC TMIP Facility Pertaining to FAC-501 Critical Path Standard |  | N/A | N/A | All Voltages | Facility Safety/Operational Inspection | N/A | SBIN-MIN and SBIN-MAJ | Monthly | 1 | N/A | Periodic substation security and operational inspection, load and counter reads / minor / major scope performed periodically. NOTE: For substations associated with NERC critical paths (FAC-501) a minimum of 10 monthly inspections shall be performed annually, with three of these monthly inspections being the more detailed "Major" inspection. |  | 2209 PD-S-SBIN-RMP-MAJ:Substation Inspection *AND* 2210 PD-S-SBIN-RMP-MIN:Substation Inspection | Yes | SUBINSPECTION | APP | Yes | 4 | x/1/xxxx (See Reference Sheets for Months)
PP | Substation | NERC TMIP Facility Pertaining to FAC-501 Critical Path Standard |  | N/A | N/A | All Voltages | Facility Safety/Operational Inspection | N/A | SBIN-MIN, SBIN-MAJ and SECURITY | Monthly | 1 | N/A | Periodic substation security and operational inspection, load and counter reads/minor/major scope performed periodically. NOTE: Substations associated with NERC critical paths (FAC-501), a minimum of 10 monthly inspections shall be performed annually, with 3 of these monthly inspections being the more detailed "major." |  | 2208 PD-S-NERC-SBIN-PP-MAJ:Substation Inspection *AND* 2284 PD-S-NERC-SBIN-PP-MIN:Substation Inspection | Yes | SUBINSPECTION | APP | Yes | 4 | x/1/xxxx (See Reference Sheets for Months)
PP | Substation | Substations − Oregon |  | N/A | N/A | All Voltages | Facility Safety/Operational Inspection | N/A | SBIN-MIN, SBIN-MAJ and SECURITY | Monthly | 1 | N/A | Periodic substation security and operational inspection, load and counter reads/minor/major scope performed periodically. NOTE: Inspections shall be performed monthly, with no longer than 45 calendar days between consecutive inspections. |  | 2213 PD-S-SBIN-PP-MAJ:Substation Inspection *AND* 2214 PD-S-SBIN-PP-MIN:Substation Inspection *AND* 2215 PD-S-SBIN-PP-SECURITY:Substation Inspection | Yes | SUBINSPECTION | APP | Yes | 4 | x/1/xxxx (See Reference Sheets for Months)
RMP | Substation | Non-NERC All Facilities Including Mobiles |  | N/A | N/A | All Voltages | Facility Safety/Operational Inspection | N/A | SBIN-MIN and SBIN-MAJ | Monthly (8 times per year) | 1 | N/A | Periodic substation security and operational inspection, load and counter reads / minor / major scope performed periodically. |  | 2212 PD-S-SBIN-SEASON-RMP-MIN:Substation Inspection *AND* 2211 PD-S-SBIN-SEASON-RMP-MAJ:Substation Inspection | Yes | SUBINSPECTION | APP | Yes | 4 | x/1/xxxx (See Reference Sheets for Months)
PP | Substation | Non-NERC All Facilities - California & Washington Including Mobiles |  | N/A | N/A | All Voltages | Facility Safety/Operational Inspection | N/A | SBIN-MIN and SBIN-MAJ | Monthly (8 times per year) | 1 | N/A | Periodic substation security and operational inspection, load and counter reads / minor / major scope performed periodically. |  | 2213 PD-S-SBIN-PP-MAJ:Substation Inspection *AND* 2214 PD-S-SBIN-PP-MIN:Substation Inspection | Yes | SUBINSPECTION | APP | Yes | 4 | x/1/xxxx (See Reference Sheets for Months)
RMP | Substation | All Pole Mount Sites; Facility with No Electrical Exposure/Fence Requirement |  | N/A | N/A | All Voltages | Facility Safety/Operational Inspection | N/A | SBIN-MAJ | 1 | 12 | N/A | Inspect pole mounts, collector sites or other facilities with no electrical exposure / fence requirement. |  | 2222 PD-S-SBIN-012-RMP:Substation Inspection | No | SUBINSPECTION | APP | Yes | 4 | x/1/xxxx (See Reference Sheets for Months)
PP | Substation | Pole mount/other facility with no electrical exposure, fence requirement. Excludes FII sites. |  | N/A | N/A | All Voltages | Facility Safety/Operational Inspection | N/A | OFIN | VARIES | N/A | N/A | Interval determined by Asset Management. Inspect pole mounts, collector sites (4 months) or other facilities with no electrical exposure/fence requirement. |  | 2265 PD-S-OFIN-001-PP:Other Facility Inspection PP 2263 PD-S-OFIN-004-PP:Other Facility Inspection PP | No | SUBINSPECTION | APP | Yes | 4 | xx/xx/xxxx
PP & RMP | Substation | Distribution Facility, FII, Pole Mount |  | N/A | N/A | All Voltages | Infrared Testing | N/A | SINF | 2 | 24 | N/A | Infrared testing of substation bus, switches & major equipment. |  | 2175 PD-S-SINF-024:Substation Infrared 2262 PD-S-SINF-024-PP:Substation Infrared PP | Yes | IRINSPECTION | APP | No | 0 | Start-up Date
PP & RMP | Substation | Transmission Facility | FAC-501 NERC Locations and All Transmission Locations | N/A | N/A | All Voltages | Infrared Testing | N/A | SINF | 1 | 12 | N/A | Infrared testing of substation bus, switches & major equipment. |  | 2174 PD-S-SINF-012:Substation Infrared 2259 PD-S-SINF-012-PP:Substation Infrared PP | Yes | IRINSPECTION | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Substation | Substation Security System |  | N/A | N/A | All Voltages | Inspection | N/A | SSS | 3 | 36 | N/A | AVTEC contracted to inspect the substation security system. Company required to chaperone AVTEC during the inspection. Compliance identifies security sites. |  | 2177 PD-S-SSS-036:Substation Security Inspection | Yes | SSSINSP | APP | No | 0 | Start-up Date
PP | Substation | Wood Poles |  | N/A | N/A | All Voltages | Detail, Pole Test & Treat | MISC | WOOD | 10 | 120 | N/A | Wood pole within substation fence will be inspected, tested or treated per company's PTT policies. Inspections completed by OSMOSE and coordinated with sub-operations staff. |  | 2200 PD-S-WOOD-120:Test and Treat Poles in Sub - Escort Contractor | No | SPECIALPROJECT | APP | Yes | 0 | 1/1/xxxx
RMP | Synchronous Condenser | Standpipe Sub |  | N/A | N/A | N/A | Major Maintenance | CONDENSER | SYNMAJ | 5 (sequenced with ANN) | 60 | N/A | Standpipe Major and Annual maintenance are sequenced. | 2024 | 2283 PD-S-SYNANN-MAJ: SYNC CONDENSER MAINTENANCE | Yes | BREAKERMAINT | APP | Yes | 4 | 1/1/xxxx
RMP | Synchronous Condenser | Standpipe Sub |  | N/A | N/A | N/A | Annual Maintenance | CONDENSER | SYNANN | 1 (sequenced with MAJ) | 12 | N/A | Standpipe Major and Annual maintenance are sequenced. | 2024 | 2283 PD-S-SYNANN-MAJ: SYNC CONDENSER MAINTENANCE | Yes | BREAKERMAINT | APP | Yes | 4 | 1/1/xxxx
RMP | Synchronous Condenser | Goshen Sub |  | N/A | N/A | N/A | Major Maintenance | CONDENSER | SYNMAJ | 5 (sequenced with MIN) | 60 | N/A |  | 2024 | 2285 PD-S-SYNMIN-MAJ: SYNC CONDENSER MAINTENANCE | Yes | BREAKERMAINT | APP | Yes | 4 | 1/1/xxxx
RMP | Synchronous Condenser | Goshen Sub |  | N/A | N/A | N/A | Minor Maintenance | CONDENSER | SYNMIN | 5 (sequenced with MAJ) | 60 | N/A |  | 2024 | 2285 PD-S-SYNMIN-MAJ: SYNC CONDENSER MAINTENANCE | Yes | BREAKERMAINT | APP | Yes | 4 | 1/1/xxxx
RMP | Synchronous Condenser | Goshen and Standpipe Subs |  | N/A | N/A | N/A | Inspection | CONDENSER | SYNMON | Monthly | 1 | N/A | Monthly Inspection; complete form | 2021 | 2100 - Job Plan SYNM | Yes | BREAKERINSPECT | APP | Yes | 4 | x/1/xxxx
RMP | Synchronous Condenser | Goshen and Standpipe Subs | NERC | N/A | N/A | N/A | Verify Relay Setting Orders; If Changed, Coordination Study Required | CONDENSER | PRC19 | 5 | 60 | N/A | 5 Year Setting Order Verification; If study is required, an EMS3 order will be created; order must be completed within the year | 2022 | 2043 - Job Plan PRC19 | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
RMP | Synchronous Condenser | Goshen and Standpipe Subs | NERC | N/A | N/A | N/A | Verify Operating at Nameplate Capacity | CONDENSER | MOD25 | 5 | 60 | N/A | 5 Year Verification |  | 2002 - Job Plan MOD25 | Yes | BREAKERINSPECT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | Synchronous Var Controller (SVC) | Thyristor Switched |  | All | All | All Voltages | Inspection/Checkout | SVC | SVCI | 2 | 24 | N/A | De-energized inspection/checkout per SVC maintenance checklist. |  | 2178 PD-S-SVC-024:Synchronous Var Controller (SVC) Inspection | Yes | SVCINSP | APP | No | 0 | Start-up Date
PP & RMP | Tank | Oil/Fuel Storage Tank |  | All | All | N/A | Inspection | FTANK or OTANK | TKIN | 1 | 12 | N/A | Inspection of oil or fuel storage and trailer mounted tanks. |  | 2192 PD-S-TKIN-012:Storage Tank Oil/Fuel Inspection | Yes | OILFUELTNKCINSP | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Tank | Oil/Fuel Storage Tank, Above Ground |  | All | All | N/A | Certified Tank Inspection | FTANK or OTANK | TKTS | 20 | 240 | N/A | Certified tank inspection performed by STI certified tank inspector per PacifiCorp policy 216 & Steel Tank Institute (STI) document SP001 Section 4. |  | 2193 PD-S-TKTS-240:Storage Tank Oil/Fuel Certified Inspection | Yes | OILFUELTNKCINSP | APP | No | 0 | Start-up Date
PP & RMP | Tank | SF6 Cylinder Trailers/Carts |  | All | All | N/A | Inspection | FTANK or OTANK | SF6C | 5 | 60 | N/A | Hammer or ring test SF6 cylinders on handcart and trailers. |  | 2173 PD-S-SF6C-060:SF6 Cylinder Hammer or Ring Test | No | SF6CYLNDRINSP | APP | No | 0 | Start-up Date
PP & RMP | Transfer Switch | DTSW In Substations |  | All | All | N/A | Operate Motor Operator and Replace Battery | DTSW-SUB | tbd | 3 | 36 | N/A | Work coordinated by Sub Ops; involved Wires if necessary | 2026 | tbd | Yes | BATTERYMAINT | APP | No | 0 | Start-up Date
PP & RMP | Transformer | 1 Phase and 3 Phase |  | All | All | 40kV and Above (High Side) | Warranty Inspection | PTRANSFORMER | WARR | 4 | 48 | N/A | Inspect equipment for warranty problems. Schedule based on manufacture date. One time only plan. |  | 2199 PD-S-WARR-048:Warranty Inspection Master PM | No | WARRINSP | APP | Yes | 4 | Construction Year 1/1/xxxx
PP & RMP | Transformer | All | All energized transformers, mobiles & non-energized spares | All | All | All | DGA & Oil Quality Tests | PTRANSFORMER | TROS | 1 | 12 | N/A | DGA and oil quality for transformer tank. Initial order to be called 2 months after commissioning of asset to obtain the baseline DGA; orders to be called annully thereafter. | 2026 | tbd | No | DGAOILTEST | APP | No | 0 | Start-up Date
PP & RMP | Transformer | Spare |  | All | All | All Voltages | Warranty Inspection | PTRANSFORMER | WARR | 4 | 48 | N/A | Inspect equipment for warranty problems. Schedule based on manufacture date. One time only plan. | 2021 | 2199 PD-S-WARR-048:Warranty Inspection Master PM | No | WARRINSP | APP | Yes | 4 | Construction Year 1/1/xxxx
PP & RMP | Transformer LTC | All |  | All | All | N/A | DGA Tests | TRFLTC | TCOS | 6 Months | 6 | N/A | DGA for load tap changer only. | 2026 | tbd | No | DGAOILTEST | APP | Yes | 4 | 1/1/xxxx
PP & RMP | Transformer LTC | Reactive or Resistive |  | All | All | N/A | DGA Tests | TRFLTC | TCOS | 4 Months | 4 | N/A | DGA for load tap changer only NOTE: Work orders generated every 4 months, a minimum of 2 tests shall be performed in a calendar year. |  | 2189 PD-S-TCOS-004:LTC DGA Test 2269 PD-S-TCOS-004-PP:LTC DGA Test PP | No | DGAOILTEST | APP | Yes | 4 | (Jan, May, Sept)
PP & RMP | Transformer LTC | Reactive With or Without Filter | All Applications and Mobiles | Federal Pacific McGraw Edison | TC-525 and 546 550 | N/A | Overhaul LTC | TRFLTC | TCOH | 3 | 36 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2183 PD-S-TCOH-036:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Reactive Without Filter | All Applications and Mobiles | Westinghouse Allis Chalmers Maloney McGraw Edison General Electric | UTT, URT and URS TLH-21 MA 496B LRT32 | N/A | Overhaul LTC | TRFLTC | TCOH | 3 | 36 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2183 PD-S-TCOH-036:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Reactive With Filter | Distribution Applications and Mobiles | Westinghouse Allis Chalmers Maloney McGraw Edison General Electric | UTT, URT and URS TLH-21 MA 496B LRT32 | N/A | Overhaul LTC | TRFLTC | TCOH | 6 | 72 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2184 PD-S-TCOH-072:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Reactive With Filter | Transmission Applications and Mobiles | Westinghouse Allis Chalmers Maloney McGraw Edison General Electric | UTT, URT and URS TLH-21 MA 496B LRT32 | N/A | Overhaul LTC | TRFLTC | TCOH | 3 | 36 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2183 PD-S-TCOH-036:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Resistive Without Filter | All Applications and Mobiles | Allis Chalmers Reinhausen | UZD,UZE and UZF TYPE-M or T | N/A | Overhaul LTC | TRFLTC | TCOH | 6 | 72 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2184 PD-S-TCOH-072:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Resistive With Filter | Distribution Applicaton and Mobiles | Allis Chalmers Reinhausen | UZD,UZE and UZF TYPE-M or T | N/A | Overhaul LTC | TRFLTC | TCOH | 9 | 108 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2186 PD-S-TCOH-108:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Resistive With Filter | Transmission Applications and Mobiles | Allis Chalmers Reinhausen | UZD,UZE and UZF TYPE-M or T | N/A | Overhaul LTC | TRFLTC | TCOH | 6 | 72 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2184 PD-S-TCOH-072:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Vacuum | All Applications and Mobiles | Reinhausen Cooper | RMV V1 and V2 | N/A | Overhaul LTC | TRFLTC | TCOH | 12 | 144 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2187 PD-S-TCOH-144:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Vacuum | All Applications and Mobiles | Reinhausen | VR | N/A | Overhaul LTC | TRFLTC | TCOH | N/A | N/A | 300,000 Ops | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2188 PD-S-TCOH-CTR:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date
PP & RMP | Transformer LTC | Vacuum | All Applications and Mobiles | Cooper | LRT-200 and LRT-500 | N/A | Overhaul LTC | TRFLTC | TCOH | 8 | 96 | N/A | NOTE: Intervals shown are baseline intervals for LTC equipment. Actual intervals may change per maintenance procedures based on analysis performed on the individual pieces of equipment. |  | 2185 PD-S-TCOH-096:LTC Overhaul | Yes | LTCOVH | APP | No | 0 | Start-up Date

## Relay
Site | Equipment Type | Equipment Description | Maintenance Task | Job Plan ID | Interval Years | Procedures | Notes | Policy Effective Date/Year (If Known) | Master PM or Job Plan (No Templates available) | Prerequisite (Job Plan) | Sub Type (Job Plan) | Crew (Asset) | Use Last Work Orders Start Date (Master PM or PM) | Leadtime Days (Master PM or PM) | Scheduling Date
PP & RMP | NERC Bulk Electrical System | Microprocessor Relay Protection System Monitored and Alarming to SCADA | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | B1-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B2 Equip Code. B2 is scheduled first - 6 years after commissioning. |  | 2146 PD-S-NERC-B1-B2:NERC Relay Microprocessor Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Microprocessor Relay Protection System Monitored and Alarming to SCADA | Minor: Settings, Test Auxiliary's and Verify Inputs | B2-MIN | 12 (sequenced) | MIN | Verify inputs and settings, download history - maintain non-monitored relays per procedures, trip coils if 2 coils present. NOTE: Maintenance shall be scheduled 6 years offset from B1 Equip Code. B2 is scheduled first - 6 years after commissioning. |  | 2146 PD-S-NERC-B1-B2:NERC Relay Microprocessor Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Microprocessor Relay Protection System Not Monitored | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | B3-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, auxiliary relays, control wiring per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B4 Equip Code. B4 is scheduled first - 6 years after commissioning. |  | 2147 PD-S-NERC-B3-B4:NERC Relay Microprocessor NOT Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Microprocessor Relay Protection System Not Monitored | Major: Test & Calibrate Relays, Auxiliaries and Verify Inputs | B4-MAJ | 12 (sequenced) | MAJ (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, auxiliary relays, per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B3 Equip Code. B4 is scheduled first - 6 years after commissioning. |  | 2147 PD-S-NERC-B3-B4:NERC Relay Microprocessor NOT Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Primary Microprocessor with Electromechanical or Electronic Backup Relay | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | B5-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, auxiliary relays, control wiring per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B6 Equip Code. B6 is scheduled first - 6 years after commissioning. |  | 2148 PD-S-NERC-B5-B6:NERC Relay Primary Micro Backup Electro | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Primary Microprocessor with Electromechanical or Electronic Backup Relay | Major: Test & Calibrate Relays, Auxiliaries and Verify Inputs | B6-MAJ | 12 (sequenced) | MAJ (INSRVC) | Test overall protection package including sudden press if present, CT/ PT's, auxiliary relays, per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B5 Equip Code. B6 is scheduled first - 6 years after commissioning. |  | 2148 PD-S-NERC-B5-B6:NERC Relay Primary Micro Backup Electro | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Electronic or Electromechanical Relay Protection System | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | B7-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, auxiliary relays, control wiring per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B8 Equip Code. B8 is scheduled first - 6 years after commissioning; |  | 2149 PD-S-NERC-B7-B8:NERC Relay Electromechanical | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Electronic or Electromechanical Relay Protection System | Major: Test & Calibrate Relays, Auxiliaries and Verify Inputs | B8-MAJ | 12 (sequenced) | MAJ (INSRVC) | Test overall protection package including sudden press if present, CT/ PT's, auxiliary relays, per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B7 Equip Code. B8 is scheduled first - 6 years after commissioning. |  | 2149 PD-S-NERC-B7-B8:NERC Relay Electromechanical | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Programmable Logic Controller (PLC) Based Protection Systems for Series Capacitor Banks or Other Devices | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | B9-MAJ/CTRL | 6 | MAJ/CTRL | Test overall protection package, CT/PT's, auxiliary relays, control wiring per procedures, trip coils if 2 present. |  | 2150 PD-S-NERC-B9:NERC Relay Programmable Logic Cntlr | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Protection with Reclosing Relay Per PRC-005 Monitored and Alarming to SCADA | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | BR1-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from BR2 Equip Code. BR2 is scheduled first - 6 years after commissioning. |  | 2152 PD-S-NERC-BR1-BR2:NERC Relay Reclosing Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Protection with Reclosing Relay Per PRC-005 Monitored and Alarming to SCADA | Minor: Settings, Test Auxiliary's and Verify Inputs | BR2-MIN | 12 (sequenced) | MIN | Verify inputs and settings, download history - Maintain non-monitored relays per procedures, trip coils if 2 coils present NOTE: Maintenance shall be scheduled 6 years offset from BR1 Equip Code. BR2 is scheduled first - 6 years after commissioning. |  | 2152 PD-S-NERC-BR1-BR2:NERC Relay Reclosing Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Protection with Reclosing Relay Per PRC-005 Not Monitored | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | BR3-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from BR2 Equip Code. BR4 is scheduled first - 6 years after commissioning. |  | 2153 PD-S-NERC-BR3-BR4:NERC Relay Reclosing NOT Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | Protection with Reclosing Relay Per PRC-005 Not Monitored | Major: Test & Calibrate Relays, Auxiliaries and Verify Inputs | BR4-MAJ | 12 (sequenced) | MAJ (INSRVC) | Test overall relay package including sudden press if present, CT/ PT's, auxiliary relays, per procedures, trip coils if 2 coils present and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from BR3 Equip Code. BR4 is scheduled first - 6 years after commissioning. |  | 2153 PD-S-NERC-BR3-BR4:NERC Relay Reclosing NOT Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Bulk Electrical System | BES Settings Review PRC-027 | Review BES relay settings | PRC-027 | 6 | N/A | P&C Engineer will review settings on BES relay, one year prior to the BES scheduled maintenance. NOTE: There may be relay packages that are not BES relays, but are part of PRC-005 RAS systems which will have the "B" maintenance activity as the PM, but will not require the PRC-027 maintenance. | 2025 | 2294 PD-S-PRC27: Relay Setting Review by Engineering | Yes | PRC27SETTING | ENGR | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Under Frequency and Under Voltage | Microprocessor Relay Protection System Monitored and Alarming to SCADA | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | U1-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL (INSRVC) | Test overall relay package, CT/ PT's, alarm path, auxiliary relays, control wiring per procedures and verify settings. NOTE: Maintenance shall be scheduled 6 years offset from U2 Equip Code. U2 is scheduled first - 6 years after commissioning. |  | 2160 PD-S-NERC-U1-U2:NERC UF-UV Relay Microprocessor Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Under Frequency and Under Voltage | Microprocessor Relay Protection System Monitored and Alarming to SCADA | Minor: Settings, Test Auxiliary's and Verify Inputs | U2-MIN | 12 (sequenced) | MIN | Verify inputs and settings, download history - Maintain non-monitored auxiliary relays per procedures. NOTE: Maintenance shall be scheduled 6 years offset from U1 Equip Code. U2 is scheduled first - 6 years after commissioning. |  | 2160 PD-S-NERC-U1-U2:NERC UF-UV Relay Microprocessor Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Under Frequency and Under Voltage | Microprocessor Relay Protection System Not Monitored | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | U3-MAJ/CTRL | 6 | MAJ/CTRL (INSRVC) | Test overall relay package, CT/PT's and control wiring. |  | 2161 PD-S-NERC-U3:NERC UF-UV Relay Microprocessor NOT Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC Under Frequency and Under Voltage | Electronic or Electromechanical Relay Protection System-Load Shed | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | U4-MAJ/CTRL | 6 | MAJ/CTRL (INSRVC) | Test overall relay package, CT/PT's and control wiring. |  | 2162 PD-S-NERC-U4:NERC UF-UV Relay Electromechanical | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | Transmission (Non-NERC) (including mobiles) | Microprocessor Relay Protection System | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | T1-MAJ/CTRL | 12 (sequenced) | MAJ/CTRL | Functional test overall relay package, operate lockouts if feasible. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes. NOTE: Maintenance shall be scheduled 6 years offset from T2 Equip Code. T2 is scheduled first - 6 years after commissioning. |  | 2179 PD-S-T1-T2:Transmission Relay Microprocessor | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Transmission (Non-NERC) (including mobiles) | Microprocessor Relay Protection System | Minor: Settings, Test Auxiliary's and Verify Inputs | T2-MIN | 12 (sequenced) | MIN | Verify inputs and settings, download history - maintain non-monitored relays per procedures, NOTE: Maintenance shall be scheduled 6 years offset from T1 Equip Code. T2 is scheduled first - 6 years after commissioning. |  | 2179 PD-S-T1-T2:Transmission Relay Microprocessor | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Transmission (Non-NERC) (including mobiles) | Primary Microprocessor with Electromechanical or Electronic Backup Relay | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | T3-MAJ/CTRL | 6 | MAJ/CTRL | MP diagnostic, perform relay functional test and element testing of EM/EE relays, operate lockouts if feasible. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes. |  | 2180 PD-S-T3:Transmission Relay Primary Micro BU Electro | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Transmission (Non-NERC) (including mobiles) | Electromechanical or Electronic Relay Protection System | Major & Control: Test & Calibrate Overall Relay Package, Control Circuitry, CT's and PT's and Control Circuitry | T4-MAJ/CTRL | 6 | MAJ/CTRL | Perform relay functional test and element testing of EM/EE relays, operate lockouts if feasible. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes. |  | 2181 PD-S-T4:Transmission Relay Electromechanical | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Transmission (Non-NERC) | Auto - Throwover | Perform Relay Functional Test and Decouple and Operate Motor Operators | T5-ATOS | 6 | ATOS | Not subject to PRC-005 standard requirements |  | 2182 PD-S-T5:Transmission Auto Throwover | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Distribution (Non-NERC) | Microprocessor Relay Protection System | Test & Calibrate Relay Package and Components | D1-MAJ/CTRL | 12 | MAJ/CTRL | Functional test overall relay package. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes. |  | 2123 PD-S-D1:Distribution Relay Microprocessor | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Distribution (Non-NERC) | Electromechanical or Electronic Relay Protection System | Test & Calibrate Relay Package and Components | D3-MAJ/CTRL | 12 | MAJ/CTRL | Functional test overall relay package. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes. |  | 2124 PD-S-D3:Distribution Relay Electromechanical | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Distribution (Non-NERC) | Fuse Protected, Transformer | Test & Calibrate Relays / Devices | D4-CTRL | 12 | CTRL | Test Thermal / Other Relays |  | 2125 PD-S-D4:Distribution Relay TRF Fuse Protected | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | Distribution (Transformer) (Non-NERC) | Electromechanical or Electronic Relay with Capacitive Components Protection System on Transformer | Test & Calibrate Relay Package and Components | D5-MAJ/CTRL | 6 | MAJ/CTRL | Perform relay element testing of EM/EE relays / test auxiliary relays. NOTE: See maintenance procedures for detailed control circuitry testing and auxiliary relay testing requirements for individual equipment codes. |  | 2126 PD-S-D5:Distribution Relay TRF Electromechanical | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | HMI | Automated Substation | Replace CPU Battery | S3-HMI | 5 | N/A | Replace CPU battery. |  | 2129 PD-S-HMI-S3:HMI Relay Replace CPU Battery | Yes | RELAYMAINT | REL | No | 0 | Start-up Date
PP & RMP | NERC REMEDIAL ACTION SCHEME | Remedial Action System Components | Remedial Action Scheme Functional Testing | SPS1 | 6 | Functional Testing | Maintain per PRC-005-RAS requirements including functional test. Note: If components exist in SPS1 package; B1_B2 maintenace will also be present on all relay packages for the RAS. Only 1 SPS1 plan per RAS, usually the PM is placed on the Substation that the RAS is named after, if not refer to the annual Transmission Planning RAS spreadsheet or to Scott Hillis. | change from 4 yr cycle to 6 yr cyle 1/2022 | 2217 PD-S-SPS1-072:SPS Relay Maintenance | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC REMEDIAL ACTION SCHEME | Remedial Action System Components | Major and Control: test and calibrate overall relay package, control circuitry, CTs, PTs and control circuitry | B1-MAJ/CTRL | 12 | MAJ/CTRL (INSRVC) | Test overall relay package including sudden pressure if present, CT/ PTs, alarm path, auxiliary relays, control wiring per procedures, trip coils if 2 coils present, verify settings. NOTE: Maintenance shall be scheduled 6 years offset from B2 Equip Code. B2 is scheduled first, 6 years after commissioning. | 3/2023 Added to cover Components only installed for protection of the RAS | 2146 PD-S-NERC-B1-B2:NERC Relay Microprocessor Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP & RMP | NERC REMEDIAL ACTION SCHEME | Remedial Action System Components | Minor: settings, test auxiliaries, verify inputs | B2-MIN | 12 | MIN | Verify inputs and settings, download history. Maintain non-monitored relays per procedures, trip coils if 2 coils present. NOTE: Maintenance shall be scheduled 6 years offset from B1 Equip Code. B2 is scheduled first, 6 years after commissioning. | 3/2023 Added to cover Components only installed for protection of the RAS | 2146 PD-S-NERC-B1-B2:NERC Relay Microprocessor Monitored | Yes | RELAYMAINT | REL | Yes | 4 | 1/1/xxxx
PP | Relay - Doble Test Equip | Doble F6150 test equipment | Test and calibrate relay test set | TEST | 1 | N/A | Perform annual calibration of Doble F6150 |  | 2191 PD-S-TEST:Test Equipment Inspection | Yes | SPECIALPROJECT | REL | Yes | 4 | 1/1/xxxx

## Meter
Site | Equipment | Equipment Types | NERC / CAISO / Non-NERC | Equipment Use | Witness | Form(s) to Submit | Interval Years | Job Plan ID | Notes | Policy Effective Date/Year (if known) | Master PM or Job Plan (MTR) (No Templates available) | Master PM or Job Plan (REL) (No Templates available)2 | Prerequisite (Job Plan) | Sub Type (Job Plan) | Crew (Asset) | Use Last Work Orders Start Date (Master PM or PM) | Leadtime Days (Master PM or PM) | Scheduling Date
PP & RMP | Meter Package | Intertie Meters (Interchange Meter as Defined by NERC BAL-005) | NERC or NERC/CAISO | PAC-Owned | YES | Form 129F | 2 | M1-MTR or M1-REL | Test Document 129F must have the NERC/WECC portion populated on at least one meter in the package. |  | 2158 PD-S-NERC-M1-024-MTR:NERC BAL-005 Meter Intertie PAC Owned Witness | 2159 PD-S-NERC-M1-024-REL:NERC BAL-005 Meter Intertie PAC Owned Witness | Yes | INTERCHNGMTRMNT | MTR or REL | Yes | 4 | 1/1/xxxx
PP & RMP | Meter Package | Intertie Meters (Interchange Meter as Defined by NERC BAL-005) | CAISO | Foreign-Owned | YES | Foreign Utility Test Form & Form 130F | Varies | M2-MTR or M2-REL | Interval determined by other utility. |  | 2312 PD-S-CAISO-M2-036-MTR:BAL-005 Meter Intertie Foreign Owned Witness | 2311 PD-S-CAISO-M2-024-REL:BAL-005 Meter Intertie Foreign Owned Witness | Yes | INTERCHNGMTRMNT | MTR or REL | Yes | 4 | 1/1/xxxx
PP & RMP | Meter Package | Borderline or PAC Gen Meters | CAISO | PAC-Owned | YES | Form 129F | 2 | M3-MTR or M3-REL |  |  | 2313 PD-S-CAISO-M3-024-MTR:Meter Borderline/PAC Gen Witness | 2314 PD-S-CAISO-M3-024-REL:Meter Borderline/PAC Gen Witness | Yes | INTERCHNGMTRMNT | MTR or REL | Yes | 4 | 1/1/xxxx
PP & RMP | Meter Package | Borderline or Cust Gen Meters | CAISO | Foreign-Owned | YES | Foreign Utility Test Form & Form 130F | Varies | M4-MTR or M4-REL | Interval determined by other utility. |  | 2315 PD-S-CAISO-M4-024-MTR:Meter Borderline/Cust Gen Witness | tbd | Yes | INTERCHNGMTRMNT | MTR or REL | Yes | 4 | 1/1/xxxx
PP & RMP | Meter Package | Borderline, Gen Retail, PAC Gen or Load Meters | CAISO | PAC-Owned | NO | Form 129F | 2 | M5-MTR or M5-REL | Load - Meters used for retail loads that provide SCADA to the EMS. |  | 2316 PD-S-CAISO-M5-024-MTR:Meter Borderline/Gen Retail/PAC Gen/Load | 2317 PD-S-CAISO-M5-024-REL:Meter Borderline/Gen Retail/PAC Gen/Load | Yes | INTERCHNGMTRMNT | MTR or REL | Yes | 4 | 1/1/xxxx
PP & RMP | Meter Package | Intertie Meters (Interchange Meter as Defined by NERC BAL-005) | Non-NERC | Foreign-Owned | YES | Foreign Utility Test Form & Form 130F | Varies | M2-MTR or M2-REL | Interval determined by other utility. |  | 2131 PD-S-M2-024-MTR:BAL-005 Meter Intertie Foreign Owned Witness | 2132 PD-S-M2-024-REL:BAL-005 Meter Intertie Foreign Owned Witness | Yes | INTERCHNGMTRMNT | MTR or REL | No | 0 | Start-up Date
PP & RMP | Meter Package | Borderline or PAC Gen Meters | Non-NERC | PAC-Owned | YES | Form 129F | 2 | M3-MTR or M3-REL |  |  | 2135 PD-S-M3-024-MTR:Meter Borderline/PAC Gen Witness | 2136 PD-S-M3-024-REL:Meter Borderline/PAC Gen Witness | Yes | INTERCHNGMTRMNT | MTR or REL | No | 0 | Start-up Date
PP & RMP | Meter Package | Borderline or Cust Gen Meters | Non-NERC | Foreign-Owned | YES | Foreign Utility Test Form & Form 130F | Varies | M4-MTR or M4-REL | Interval determined by other utility. |  | 2137 PD-S-M4-024-MTR:Meter Borderline/Cust Gen Witness | 2138 PD-S-M4-024-REL:Meter Borderline/Cust Gen Witness | Yes | INTERCHNGMTRMNT | MTR or REL | No | 0 | Start-up Date
PP & RMP | Meter Package | Borderline, Gen Retail, PAC Gen or Load Meters | Non-NERC | PAC-Owned | NO | Form 129F | 2 | M5-MTR or M5-REL | Load - Meters used for retail loads that provide SCADA to the EMS. |  | 2141 PD-S-M5-024-MTR:Meter Borderline/Gen Retail/PAC Gen/Load | 2142 PD-S-M5-024-REL:Meter Borderline/Gen Retail/PAC Gen/Load | Yes | INTERCHNGMTRMNT | MTR or REL | No | 0 | Start-up Date
PP & RMP | Meter Package | Check or Stateline Meters | Non-NERC | PAC-Owned | NO | Form 129F | 5 | M6-MTR or M6-REL |  |  | 2143 PD-S-M6-060-MTR:Meter Check/Stateline | 2144 PD-S-M6-060-REL:Meter Check/Stateline | Yes | INTERCHNGMTRMNT | MTR or REL | No | 0 | Start-up Date
PP & RMP | Meter Package | Retail | Non-NERC | PAC-Owned Non-NERC | NO | None | Varies | Maintained in CSS | Retail - Meter used for retail load outside of a substation. |  | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a

## Lines Inspections by State
BU | Equipment Type | Equipment Description | Equipment Use | State(s) | Maintenance Task | CURRENT Sequenced Maintenance (example) | Equipment Code (Tech ID) | Maintenance ID (XXX = DST, LOC or MGT) | Interval Calendar Year | Notes | Policy Effective Date/Year (if known) | Template | Master PM or Job Plan | Plan Type | Order Type | MAT's | Main Work Center | Shift Factor Late | Shift Factor Early | Call Horizon | Scheduling Period | Scheduling Type | Completion Requirement | Scheduling Indictor (Time) | Scheduling Date
PP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | CA | Visual Assurance Inspection (V) | V-V-V-V-D&V-V-V-V-V-PTT | Map String | Standing Order | 1 | NOTE: CA PUC maximum interval is 2 years plus 3 calendar months from the previous inspection for Non-Tier and Tier 1 areas. Change from 2 year cycle to 1 year cycle (effective 1/1/2025) | 2025 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | CA | Detail Inspection (D) | D&V-V-V-V-V-PTT-V-V-V-V | Map String | Standing Order | 5 | NOTE: CA PUC maximum interval is 5 years plus 3 calendar months from the previous detail inspection. Note: Detail is combined with PTT on PTT years |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | CA | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Map String | Standing Order | 10 | NOTE: If detail and PTT are combined in one task, per CA PUC the combined inspection must be performed no later than 5 years and 3 months from the previous detail inspection. Maximum interval between PTT inspection is 20 calendar years. Cycle change from 20 year to 10 year, effective in 2026. | 2026 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA; Tier 2 | CA | Visual Assurance Inspection (V) | V-V-V-V-D&V-V-V-V-V-PTT | Map String | Standing Order | 1 | NOTE: CA PUC maximum interval is 1 year plus 3 calendar months from the previous inspection for Tier 2 areas in CA. FHCA Tier 2 must have at least one (1) inspection completed by June 30th, effective in 2026. | 2019 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA; Tier 2 | CA | Detail Inspection (D) | D&V-V-V-V-V-PTT-V-V-V-V | Map String | Standing Order | 5 | NOTE: CA PUC maximum interval is 5 years plus 3 calendar months from the previous detail inspection. Note: Detail is combined with PTT on PTT years FHCA Tier 2 must have at least one (1) inspection completed by June 30th, effective in 2026. | 2019 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA; Tier 3 Only | CA | Visual Assurance Inspection (V) | V-D-V-D-V-D-V-D-V-PTT | Map String | Standing Order | 1 | Due to the increase of detail inspection in Tier 3, the visual will now sequence every 2 years with the more in-depth detail inspection. NOTE: CA PUC maximum interval is 1 year plus 3 calendar months from the previous inspection for Tier 3 areas in CA. FHCA Tier 3 must have at least one (1) inspection completed by June 30th, effective in 2026. | 2027 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA; Tier 3 Only | CA | Detail Inspection (D) | D-V-D-V-D-V-D-V-D-PTT | Map String | Standing Order | 2 | Increasing Tier 3 detail inspections to every 2 years, sequencying with a visual. NOTE: CA PUC maximum interval is 2 years plus 3 calendar months from the previous inspection for Tier 3 areas in CA. FHCA Tier 3 must have at least one (1) inspection completed by June 30th, effective in 2026. | 2027 (Pilot in 2025) | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA; Tier 2/3 | CA | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Map String | Standing Order | 10 | NOTE: If detail and PTT are combined in one task, per CA PUC the combined inspection must be performed no later than 5 years and 3 months from the previous detail inspection. Maximum interval between PTT inspection is 20 calendar years. *** Tier 3 must have at least one (1) inspection completed by June 30th. Cycle change from 20 year to 10 year, effective in 2026. FHCA Tier 2/3 must have at least one (1) inspection completed by June 30th, effective in 2026. | 2026 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA, Tier 2 | CA | Drone Inspection | n/a | Mapstring | Standing Order | 5 | The inspections are performed 2 years before the next scheduled detail or DPTT inspection. | 2026
PP | Distribution Circuit | Overhead Distribution Circuit | Tier 3 | CA | Drone Inspection | n/a | Mapstring | Standing Order | 2 | The inspections are performed on the off-cycle detailed inspection year. | 2026
PP | Distribution Circuit | Underground Distribution Circuit | All | CA | Visual Assurance Inspection (V) | V-D-V-D | Map String | Standing Order | 2 | NOTE: CA PUC maximum interval is 2 years plus 3 calendar months from the previous inspection. |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Underground Distribution Circuit | All | CA | Detail Inspection (D) | D-V-D-V | Map String | Standing Order | 4 | Cabinets shall be opened and visually inspected (CA and OR only) Note: CA PUC maximum interval is 5 years plus 3 calendar months from previous inspection. |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | OR | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Map String | Standing Order | 1 | Change from 2 year cycle to 1 year cycle (effective 1/1/2025). | 2025 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | OR | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Map String | Standing Order | 10 |  |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | OR | Visual Assurance Inspection (V) | V-V-V-V-D&V-V-V-V-V-PTT | Map String | Standing Order | 1 |  | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | OR | Detail Inspection (D) | D&V-V-V-V-V-PTT-V-V-V-V | Map String | Standing Order | 5 | Note: Detail is combined with PTT on PTT years | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | OR | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Map String | Standing Order | 10 | NOTE: If Detail and PTT are combined in one task, the combined inspection must be performed no later than 5 years. Maximum interval between PTT inspection is 10 calendar years. Note: Detail and PTT is combined on PTT years | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | OR | Drone Inspection | n/a | Mapstring | Standing Order | 5 | The inspections are performed 2 years before the next scheduled detail or DPTT inspection. | 2026
PP | Distribution Circuit | Underground Distribution Circuit | All | OR | Detail Inspection (D) | n/a | Map String | Standing Order | 10 | Cabinets shall be opened and visually inspected (CA and OR only) |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | WA | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Map String | Standing Order | 1 | Change from 2 year cycle to 1 year cycle (effective 1/1/2025). | 2025 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | WA | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Map String | Standing Order | 10 | Cycle change from 20 year to 10 year, effective in 2026. Note: From 2020 to 2025 Detail was sequenced with PTT. | 2026 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WA | Visual Assurance Inspection (V) | V-V-V-V-D&V-V-V-V-V-PTT | Map String | Standing Order | 1 |  | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WA | Detail Inspection (D) | D&V-V-V-V-V-PTT-V-V-V-V | Map String | Standing Order | 5 | Note: Detail is combined with PTT on PTT years | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WA | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Map String | Standing Order | 10 | Note: Detail and PTT is combined on PTT years Cycle change from 20 year to 10 year, effective in 2026. | 2026 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WA | Drone Inspection | n/a | Mapstring | Standing Order | 5 | The inspections are performed 2 years before the next scheduled detail or DPTT inspection. | 2026
PP | Distribution Circuit | Underground Distribution Circuit | All | WA | Detail Inspection (D) | n/a | Map String | Standing Order | 10 | Cycle change from 20 year to 10 year, effective in 2026. | 2026 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | ID | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Map String | Standing Order | 1 | Change from 2 year cycle to 1 year cycle (effective 1/1/2025). | 2025 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | ID | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Map String | Standing Order | 10 | Changed from 20 year cycle to 10 year (effective 1/1/2024). | 2024 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | ID | Visual Assurance Inspection (V) | V-V-V-V-D-V-V-V-V-PTT&V | Map String | Standing Order | 1 | Note: As of 2024 there are no FHCA areas identified in Idaho |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | ID | Detail Inspection (D) | D-V-V-V-V-PTT&V-V-V-V-V | Map String | Standing Order | 5 | Note: As of 2024 there are no FHCA areas identified in Idaho Note: Detail is combined with PTT on PTT years |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | ID | Detail Pole Test and Treat (PTT) | PTT&V-V-V-V-V-D-V-V-V-V | Map String | Standing Order | 10 | Note: As of 2024 there are no FHCA areas identified in Idaho Note: Detail and PTT is combined on PTT years. |  | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | ID | Drone Inspection | n/a | Mapstring | Standing Order | 5 | Note: As of 2024 there are no FHCA areas identified in Idaho The inspections are performed 2 years before the next scheduled detail or DPTT inspection | 2026
RMP | Distribution Circuit | Underground Distribution Circuit | All | ID | Detail Inspection (D) | n/a | Map String | Standing Order | 10 | Changed from 20 year cycle to 10 year (effective 1/1/2024). | 2024 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | UT | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Map String | Standing Order | 1 | Change from 2 year cycle to 1 year cycle (effective 1/1/2025). | 2025 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | UT | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Map String | Standing Order | 10 | Changed from 20 year cycle to 10 year (effective 1/1/2024). | 2024 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | UT | Visual Assurance Inspection (V) | V-V-V-V-D-V-V-V-V-PTT&V | Map String | Standing Order | 1 |  | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | UT | Detail Inspection (D) | D-V-V-V-V-PTT&V-V-V-V-V | Map String | Standing Order | 5 | Note: Detail is combined with PTT on PTT years | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | UT | Detail Pole Test and Treat (PTT) | PTT&V-V-V-V-V-D-V-V-V-V | Map String | Standing Order | 10 | Note: Detail and PTT is combined on PTT years. | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | UT | Drone Inspection | n/a | Mapstring | Standing Order | 5 | The inspections are performed 2 years before the next scheduled detail or DPTT inspection. | 2026
RMP | Distribution Circuit | Underground Distribution Circuit | All | UT | Detail Inspection (D) | n/a | Map String | Standing Order | 10 | Changed from 20 year cycle to 10 year (effective 1/1/2024). | 2024 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | WY | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Map String | Standing Order | 1 | Change from 2 year cycle to 1 year cycle (effective 1/1/2025). | 2025 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | Non-FHCA | WY | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Map String | Standing Order | 10 | Changed from 20 year cycle to 10 year (effective 1/1/2024). | 2024 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WY | Visual Assurance Inspection (V) | V-V-V-V-D-V-V-V-V-PTT&V | Map String | Standing Order | 1 |  | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WY | Detail Inspection (D) | D-V-V-V-V-PTT&V-V-V-V-V | Map String | Standing Order | 5 | Note: Detail is combined with PTT on PTT years | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WY | Detail Pole Test and Treat (PTT) | PTT&V-V-V-V-V-D-V-V-V-V | Map String | Standing Order | 10 | Note: Detail and PTT is combined on PTT years. | 2020 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
RMP | Distribution Circuit | Overhead Distribution Circuit | FHCA | WY | Drone Inspection | n/a | Mapstring | Standing Order | 5 | The inspections are performed 2 years before the next scheduled detail or DPTT inspection. | 2026
RMP | Distribution Circuit | Underground Distribution Circuit | All | WY | Detail Inspection (D) | n/a | Map String | Standing Order | 10 | Changed from 20 year cycle to 10 year (effective 1/1/2024). | 2024 | tbd | tbd | n/a | EM06 by District | tbd | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
PP | Local Transmission Line | Overhead Transmission Line | All | CA | Infrared Inspection | n/a | Plant Locality Number | LOC-IR FHCA | 1 |  |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | All | CA | Visual Assurance Inspection (V) | V-V-V-V-D&V-V-V-V-V-PTT | Plant Locality Number | LOC-ISA | 1 |  |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | All, excluding Tier 3 | CA | Detail Inspection (D) | D&V-V-V-V-V-PTT-V-V-V-V | Plant Locality Number | LOC-IFA | 5 | Note: Sequenced with PTT Note: Detail is combined with PTT on PTT years |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Tier 3 Only | CA | Detail Inspection (D) | D-V-D-V-PTT-V-D-V-D | Plant Locality Number | LOC-IFA-024 | 2 | Increasing detail inspection cycle to 2 years for Tier 3 only Note: Sequenced with Visual and PTT Note: Detail is combined with PTT on PTT years | 2026 | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | All | CA | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Tier 3 | CA | Drone Inspection | n/a | Plant Locality Number | LOC-DRONE-024 | 2 | The inspections are scheduled in the off-cycle detail inspection year. | 2026
PP | Local Transmission Line | Overhead Transmission Line | FHCA, Tier 2 | CA | Drone Inspection | n/a | Plant Locality Number | LOC-DRONE-060 | 5 | The inspections are performed 2 years before the next scheduled detail or DPTT inspection. | 2026
PP | Local Transmission Line | Overhead Transmission Line | Polymer & Glass Insulators | CA | Hold Down Inspection | n/a | Plant Locality Number | LOC-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction. |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Glass ONLY Insulators | CA | Hold Down Inspection | n/a | Plant Locality Number | LOC-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | OR | Infrared Inspection | n/a | Plant Locality Number | LOC-IR FHCA | 1 |  |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | OR | Infrared Inspection | n/a | Plant Locality Number | LOC-IR-024 | 2 |  |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | OR | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT&V | Plant Locality Number | LOC-ISA | 1 | All Local Transmission Lines now on annual cycle, beginning 2025 | 2025 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | OR | Detail Pole Test and Treat (PTT) | PTT&V-V-V-V-V-V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 |  |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | OR | Visual Assurance Inspection (V) | n/a | Plant Locality Number | LOC-ISA | 1 |  |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | OR | Detail Inspection (D) | D&V-V-V-V-V-PTT-V-V-V-V | Plant Locality Number | LOC-IFA | 5 | Note: Sequenced with PTT Note: Detail is combined with PTT on PTT years |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | OR | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Polymer & Glass Insulators | OR | Hold Down Inspection | n/a | Plant Locality Number | LOC-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction. |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Glass/Ceramic ONLY Insulators | OR | Hold Down Inspection | n/a | Plant Locality Number | LOC-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | WA | Infrared Inspection | n/a | Plant Locality Number | LOC-IR FHCA | 1 | Note: As of 2024 there are no FHCA areas identified in Washington |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | WA | Infrared Inspection | n/a | Plant Locality Number | LOC-IR-024 | 2 |  |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | WA | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Plant Locality Number | LOC-ISA | 1 | All Local Transmission Lines now on annual cycle, beginning 2025 Note: Sequenced with PTT | 2025 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | WA | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Visual |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | WA | Visual Assurance Inspection (V) | n/a | Plant Locality Number | LOC-ISA | 1 | Note: As of 2024 there are no FHCA areas identified in Washington |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | WA | Detail Inspection (D) | D&V-V-V-V-V-PTT-V-V-V-V | Plant Locality Number | LOC-IFA | 5 | Note: As of 2024 there are no FHCA areas identified in Washington Note: Sequenced with PTT Note: Detai is combined with PTT on PTT years |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | FHCA | WA | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: As of 2024 there are no FHCA areas identified in Washington Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Polymer & Glass Insulators | WA | Hold Down Inspection | n/a | Plant Locality Number | LOC-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction. |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Local Transmission Line | Overhead Transmission Line | Glass ONLY Insulators | WA | Hold Down Inspection | n/a | Plant Locality Number | LOC-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | ID | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Plant Locality Number | LOC-ISA | 1 | All Local Transmission Lines now on annual cycle, beginning 2025 Note: Sequenced with PTT | 2025 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | ID | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Visual |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | ID | Infrared Inspection | n/a | Plant Locality Number | LOC-IRFHCA | 1 | Note: As of 2024 there are no FHCA areas identified in Idaho | 2024 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | ID | Visual Assurance Inspection (V) | V-V-V-V-D-V-V-V-V-PTT&V | Plant Locality Number | LOC-ISA | 1 | Note: As of 2024 there are no FHCA areas identified in Idaho |  | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | ID | Detail Inspection (D) | D-V-V-V-V-PTT&V-V-V-V-V | Plant Locality Number | LOC-IFA | 5 | Note: As of 2024 there are no FHCA areas identified in Idaho Note: Sequenced with PTT Note: Detail is combined with PTT on PTT years |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | ID | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-D&V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: As of 2024 there are no FHCA areas identified in Idaho Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | UT | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Plant Locality Number | LOC-ISA | 1 | All Local Transmission Lines now on annual cycle, beginning 2025 Note: Sequenced with PTT | 2025 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | UT | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Visual |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | UT | Visual Assurance Inspection (V) | V-V-V-V-D-V-V-V-V-PTT&V | Plant Locality Number | LOC-ISA | 1 |  | 2020 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | UT | Detail Inspection (D) | D-V-V-V-V-PTT&V-V-V-V-V | Plant Locality Number | LOC-IFA | 5 | Note: Sequenced with PTT Note: Detail is combined with PTT on PTT years |  | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | UT | Detail Pole Test and Treat (PTT) | PTT&V-V-V-V-V-D-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | UT | Infrared Inspection | n/a | Plant Locality Number | LOC-IRFHCA | 1 |  | 2024 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | WY | Visual Assurance Inspection (V) | V-V-V-V-V-V-V-V-V-PTT | Plant Locality Number | LOC-ISA | 1 | All Local Transmission Lines now on annual cycle, beginning 2025 Note: Sequenced with PTT | 2025 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | Non-FHCA | WY | Detail Pole Test and Treat (PTT) | PTT-V-V-V-V-V-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Visual |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | WY | Visual Assurance Inspection (V) | V-V-V-V-D-V-V-V-V-PTT&V | Plant Locality Number | LOC-ISA | 1 |  | 2020 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | WY | Detail Inspection (D) | D-V-V-V-V-PTT&V-V-V-V-V | Plant Locality Number | LOC-IFA | 5 | Note: Sequenced with PTT Note: Detail is combined with PTT on PTT years | 2020 | tbd | tbd | M3 | EML4 | 840 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | WY | Detail Pole Test and Treat (PTT) | PTT&V-V-V-V-V-D-V-V-V-V | Plant Locality Number | LOC-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 843 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Overhead Transmission Line | FHCA | WY | Infrared Inspection | n/a | Plant Locality Number | LOC-IRFHCA | 1 |  | 2024 | tbd | tbd | M3 | EML4 | 841 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Underground Transmission Line | All | UT | Detail Inspection | n/a | Plant Locality Number | LOC-UGIN-003 | 3 Months | Inspection is only on one UG transmission line PL#071003. |  | tbd | tbd | M3 | EML4 | 840 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | Set Schedule (Jan, Mar & Sep)
RMP | Local Transmission Line | Underground Transmission Line | All | UT | Major Detail Inspection (MAJ) | MAJ-MIN-MAJ-MIN | Plant Locality Number | LOC-UGIN-MAJ | 2 | Inspection done on specific lines, which have UG points, by UG crews. NOTE: Maintenance shall be scheduled 2 years offset from Minor Detail Inspection. Minor is scheduled first. | 2024 | tbd | tbd | M3 | EML8 | 840 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Local Transmission Line | Underground Transmission Line | All | UT | Minor Detail Inspection (MIN) | MIN-MAJ-MIN-MAJ | Plant Locality Number | LOC-UGIN-MIN | 2 | Inspection done on specific lines, which have UG points, by UG crews. NOTE: Maintenance shall be scheduled 2 years offset from Major Detail Inspection. Minor is scheduled first. | 2024 | tbd | tbd | M3 | EML8 | 840 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | CA | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | CA | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | CA | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | CA | Infrared Inspection | n/a | Plant Locality Number | MGT-IR FHCA | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Tier 3 | CA | Drone Inspection | n/a | Plant Locality Number | MGT-DRONE-024 | 2 | The inspections are scheduled in the off-cycle detail inspection year. | 2026
PP | Main Grid Transmission Line | Overhead Transmission Line | FHCA, Tier 2 | CA | Drone Inspection | n/a | Plant Locality Number | MGT-DRONE-024 | 2 | The inspections are scheduled in the off-cycle detail inspection year. | 2026
PP | Main Grid Transmission Line | Overhead Transmission Line | Polymer & Glass Insulators | CA | Hold Down Inspection | n/a | Plant Locality Number | MGT-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction. |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Glass ONLY Insulators | CA | Hold Down Inspection | n/a | Plant Locality Number | MGT-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction. |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | OR | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | OR | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | OR | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | OR | Infrared Inspection | n/a | Plant Locality Number | MGT-IR FHCA | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Non-FHCA | OR | Infrared Inspection | n/a | Plant Locality Number | MGT-IR-024 | 2 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Polymer & Glass Insulators | OR | Hold Down Inspection | n/a | Plant Locality Number | MGT-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction. |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Glass/Ceramic ONLY Insulators | OR | Hold Down Inspection | n/a | Plant Locality Number | MGT-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction. |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | WA | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | WA | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | All | WA | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | WA | Infrared Inspection | n/a | Plant Locality Number | MGT-IR FHCA | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Non-FHCA | WA | Infrared Inspection | n/a | Plant Locality Number | MGT-IR-024 | 2 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Polymer & Glass Insulators | WA | Hold Down Inspection | n/a | Plant Locality Number | MGT-HOLD-012 | 1 | Inspect per Policy 337. Interval annual on hold down structures utilizing polymer and glass insulators in their construction. |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Main Grid Transmission Line | Overhead Transmission Line | Glass ONLY Insulators | WA | Hold Down Inspection | n/a | Plant Locality Number | MGT-HOLD-024 | 2 | Inspect per Policy 337. Interval every two years on hold down structures utilizing glass ONLY insulators in their construction. |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | AZ | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | AZ | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | AZ | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | AZ | Infrared Inspection | n/a | Plant Locality Number | MGT-IRFHCA | 1 | Note: As of 2024 there are no FHCA areas in Arizona | 2024 | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | CO | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | CO | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | CO | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | CO | Infrared Inspection | n/a | Plant Locality Number | MGT-IRFHCA | 1 | Note: As of 2024 there are no FHCA areas in Colorado | 2024 | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | ID | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | ID | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | ID | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | ID | Infrared Inspection | n/a | Plant Locality Number | MGT-IRFHCA | 1 | Note: As of 2024 there are no FHCA areas in Idaho | 2024 | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | MT | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | MT | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | MT | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | MT | Infrared Inspection | n/a | Plant Locality Number | MGT-IRFHCA | 1 | Note: As of 2024 there are no FHCA areas in Montana | 2024 | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | NM | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | NM | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | NM | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | NM | Infrared Inspection | n/a | Plant Locality Number | MGT-IRFHCA | 1 | Note: As of 2024 there are no FHCA areas in New Mexico | 2024 | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | UT | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | UT | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | UT | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | UT | Infrared Inspection | n/a | Plant Locality Number | MGT-IRFHCA | 1 |  | 2024 | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | WY | Visual Assurance Inspection (V) | n/a | Plant Locality Number | MGT-AIR | 1 |  |  | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | WY | Detail Inspection (D) | D-D-D-D-D-PTT | Plant Locality Number | MGT-PAT | 2 | Note: Sequenced with PTT |  | tbd | tbd | M3 | EML4 | 880 | LCRxxxDE | 0% | 0% | 99% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | All | WY | Detail Pole Test and Treat (PTT) | PTT-D-D-D-D-D | Plant Locality Number | MGT-PTT | 10 | Note: Sequenced with Detail |  | tbd | tbd | M3 | EML4 | 883 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Main Grid Transmission Line | Overhead Transmission Line | FHCA | WY | Infrared Inspection | n/a | Plant Locality Number | MGT-IRFHCA | 1 |  | 2024 | tbd | tbd | M3 | EML4 | 881 | LCRxxxDE | 0% | 0% | 98% | 140 | MON | No | Key Date | 1/1/xxxx

## Lines & Vaults Equipment
BU | Equipment Type | Equipment Description | Equipment Use | Equipment Manufacturer or Model | State(s) | Maintenance Task | Equipment Code (Tech ID) | Maintenance ID (XXX = DST, LOC or MGT) | Interval Calendar Year | Notes | Policy Effective Date/Year (if known) | Template | Master PM or Job Plan | Plan Type | Order Type | MAT's | Main Work Center | Shift Factor Late | Shift Factor Early | Call Horizon | Scheduling Period | Scheduling Type | Completion Requirement | Scheduling Indictor (Time) | Scheduling Date
PP & RMP | Recloser/Protection Devices | Distribution Transfer Switch U/G | All | All | All | Operate Motor Operator and Replace Battery | DTSW | DST-DTSW-060 | 5 | Work coordinated by Wires; involved Sub Ops if necessary |  | tbd | tbd | M3 | EML8 | 522 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP | Recloser/Protection Devices | Distribution Recloser Controller | Circuits | All (excluding G&W Viper w/SEL-351R Controllers) | All | Recloser Battery Replacement & Setting Download | DRCL | DST-DRCL-036 | 3 | Line reclosers maintained by Substation Operations. |  | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP | Recloser/Protection Devices | Distribution Recloser Controller | Circuits | G&W Viper with SEL-351R Controllers | All | Recloser Battery Replacement & Setting Download | DRCL | DST-DRCL-024 | 2 | Line reclosers maintained by Substation Operations. |  | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
RMP | Recloser/Protection Devices | Distribution Recloser Controller | Circuits | All (excluding G&W Viper w/SEL-351R Controllers) | All | Recloser Battery Replacement | DRCL | DST-DRCL-MIN-036 | 3 | Line reclosers maintained by Substation Operations. Note: Sequenced with DRCL-MAJ PM | 2025 | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
RMP | Recloser/Protection Devices | Distribution Recloser Controller | Circuits | G&W Viper with SEL-351R Controllers | All | Recloser Battery Replacement | DRCL | DST-DRCL-MIN-024 | 2 | Line reclosers maintained by Substation Operations. Note: Sequenced with DRCL-MAJ PM | 2025 | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
RMP | Recloser/Protection Devices | Distribution Recloser Controller | Circuits | All | All | Recloser Settings | DRCL | DST-DRCL-MAJ-072 | 6 | Settings downloaded for review by Tech Ops and replace battery. Note: Sequenced with DRCL-MIN 2 year and 3 year PMs | 2025 | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP & RMP | Recloser/Protection Devices | Distribution Recloser Controller | Circuits | Siemens CMR | All | Recloser Battery Replacement | DRCL | DST-DRCL-120 | 10 | Line reclosers maintained by Substation Operations. | 2023 | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP & RMP | Recloser/Protection Devices | Distribution Fuse Saver | Circuits | All | All | Battery Replacement | FSV | DST-FSBT-060 | 5 | Work coordinated by Wires. |  | tbd | tbd | M3 | EML4 | 522 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
RMP | Recloser/Protection Devices | Distribution Switchgear | Circuits | All | ID, UT & WY | Infrared Inspection | DSWG | DST-DSWG-120 | 10 | Specific assets on distribution circuit; standing order per area per year. Assets tracked in GIS. | 2024 | tbd | tbd | M3 | EML4 | 522 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
RMP | Recloser/Protection Devices | Trident Switchgear | Circuits | All | UT | Trident Switchgear Battery Replacement | TSWG | DST-TSWG-MIN-036 | 3 | Trident switchgear maintained by Substatio Operations. Note: Sequenced with TSWG-MAJ 6 year PM | 2026 | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
RMP | Recloser/Protection Devices | Trident Switchgear | Circuits | All | UT | Trident Switchgear Settings | TSWG | DST-TSWG-MAJ-072 | 6 | Settings downloaded for review by Tech Ops and replace battery. Note: Sequenced with TSWG-MIN 3 year PM | 2026 | tbd | tbd | M3 | EML8 | 522 | RECxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP | Underground Vaults | Vault, Network | All | N/A | OR | Vault Inspection | Plant Locality Number | DST-UGIN-006 | 6 Months | As recommended by Operations Manager or Asset Management. |  | tbd | tbd | M3 | EML8 | 512 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | Set Schedule (Jan & Jul)
PP | Underground Vaults | Vault, Non-Network | All | N/A | OR | Vault Inspection | Plant Locality Number | DST-UGIN-024 | 2 | As recommended by Operations Manager or Asset Management. Change cycle from annual to 2 years, effective 2025. | 2025 | tbd | tbd | M3 | EML8 | 512 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Underground Vaults | Vault, Air Cooled Transformers | All | All | OR | Air-Cooled Transformers Cleaned and Tested | Plant Locality Number | DST-UGTC-084 | 7 |  |  | tbd | tbd | M3 | EML4 | 512 | UGCXXXDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP | Underground Vaults | Vault Transformers | All | All | OR | DGA Sampling on Vault Transformers | TRF | DST-VDGA-036 | 3 | DGA and oil quality for transformer tank. | 2026 | tbd | tbd | M3 | EML4 | 512 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | Underground Vaults | n/a | All | N/A | OR | River Crossing Sign Inspection | Plant Locality Number | DST-UGRC-001 | monthly | Monthly inspection completed by UG personnel of the river crossing sign, required by City of Portland. |  | tbd | tbd | M3 | EML4 | 512 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
RMP | Underground Vaults | Vault | All | N/A | UT | Vault Inspection | Plant Locality Number | DST-UGIN-006 | 6 Months | As recommended by Operations Manager or Asset Management. |  | tbd | tbd | M3 | EML8 | 512 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | Set Schedule (Jan & Jul)
RMP | Underground Vaults | Vault | All | N/A | UT | Vault Inspection | Plant Locality Number | DST-UGIN-003 | 3 Months | As recommended by Operations Manager or Asset Management. |  | tbd | tbd | M3 | EML8 | 512 | UGCXXXDE | 0% | 0% | 100% | 140 | MON | No | Key Date | Set Schedule (Jan, Mar & Sep)
PP & RMP | FAA Light | FAA Light | Circuits and Transmission Lines | All | All | FAA Light Inspection | FAAI | XXX-FAAI-012 | 1 | Add only to structures (Trans or Distr) that the Federal Aviation Administration (FAA) has requested a FAA Light be installed. Right of Way will file with the FAA and notify Asset Management of any new FAA equipment requirements. | 2025 | tbd | tbd | M3 | EML4 | 521 - Dist 841 - LOC Trans 881 - MG Trans | LCRxxxDE | 0% | 0% | 100% | 240 | MON | No | Time | 1/1/XXXX
PP & RMP | Fault Indicators | Fault Indicators | Circuits and Transmission Lines | Joslyn or Fisher Pierce | All | Fault Indicator Battery Replacement | FCI | XXX-FIBT-108 | 9 | Add to only Overhead Fault Indicators; excluding Underground and Communicating Fault Indicators. |  | tbd | tbd | M3 | EML4 | 522 812 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
RMP | Fault Indicators | Fault Indicators | Circuits and Transmission Lines | Navigator or Unknown | ID, UT & WY | Fault Indicator Battery Replacement | FCI | XXX-FIBT-048 | 4 | Add to only Overhead Fault Indicators; excluding Underground and Communicating Fault Indicators. |  | tbd | tbd | M3 | EML4 | 522 812 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP | Fault Indicators | Fault Indicators | Circuits and Transmission Lines | Navigator or Unknown | CA, OR & WA | Fault Indicator Battery Replacement | FCI | XXX-FIBT-096 | 8 | Add to only Overhead Fault Indicators; excluding Underground and Communicating Fault Indicators. |  | tbd | tbd | M3 | EML4 | 522 812 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP & RMP | Fault Indicators | Fault Indicators | Circuits and Transmission Lines | SEL AR360 | All | Fault Indicator Unit Replacement | FCI | XXX-FIBT-120 | 10 | Replace Fault Indictor | 2024 | tbd | tbd | M3 | EML4 | 522 812 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP & RMP | Distribution Capacitors | Capacitors | Circuits | All | All PP and UT & WY | Capacitor Inspection | DCAP | XXX-DCAP-072 | 6 |  | 1/1/2021 PP 1/1/2026 | tbd | tbd | M3 | EML4 | 522 812 | LCRxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP & RMP | Transmission High Voltage Switches | Transmission High Voltage Switches | Transmission Lines | Motor Operator Switches | All | High Voltage Switch Battery Replacement | THVS | XXX-THVS-036 | 3 | Motor operated high voltage switches batteries replaced by Substation Operations. (Task List under SWBT). |  | tbd | tbd | M3 | EML4 | 522 812 | APCxxxDE | 100% | 100% | 100% | 140 | MON | Yes | Time | 6/1/xxxx
PP | FII SUBSTATION INSPECTIONS | Field Ops Sub | N/A | N/A | OR | Facility Safety/Operational Inspection | FII-SBIN | XXX-FII-SBIN-001 | monthly | Periodic security and operational inspection. NOTE: Inspections shall be performed monthly, with no longer than 45 calendar days between consecutive inspections. |  | tbd | tbd | M3 | EML4 | 522 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP | FII SUBSTATION INSPECTIONS | Field Ops Sub | N/A | N/A | CA & WA | Facility Safety/Operational Inspection | FII-SBIN | XXX-FII-SBIN-001 | monthly | Periodic security and operational inspection. NOTE: Inspections be performed no more than 120 days between consecutive monthly or 180 days between the more detail major inspections. |  | tbd | tbd | M3 | EML4 | 522 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx
PP & RMP | Weather Stations | Weather Stations | Circuits and Transmission Lines | All | All | Inspection, Calibration, Check Battery, and Remove Ground Sensors | WEA | XXX-WSIN-012 | 1 | Inspect and clean weather station for damage and calibrate wind, temp, RH and precipitation gages. Check battery and replace if necessary. Remove ground sensor sticks and install a secondary box over ground rod. | Fall 2019 | tbd | tbd | M3 | EML8 | 522 812 | LCRxxxDE | 0% | 0% | 100% | 140 | MON | No | Key Date | 1/1/xxxx

## Telecom & SCADA
BU | Equip Code | Equipment Type | Equipment Description | Requires Commissioning (See Note 4) | Equipment Use | Equipment Model Examples | Maintenance Task | Maintenance ID | Interval Calendar Year | Labor Hours | Notes | EC PM MAT | EC Repair MAT | MG/LOC PM MAT | MG/LOC Repair MAT
PP & RMP | ASR | Antenna Structure Registration | FCC number attached to a tower and cleared with the FAA | No | Non-BES | Number attached to the tower | Check tower for FCC antenna registration number | GMP6004 | 4 | 1 | Antenna structure meets FAA and FCC requirements. | CSM 579 | CSR 580 | CSM 887 | CSR 888
PP & RMP | BAS | Base Radio | Mobile Radio System Base Station | Yes | Non-BES | TAIT | Testing | GMP6301 | 1 | 8 | Radio meets FCC requirements. | RDM 585 | RDR 586 | RDM 895 | RDR 896
PP & RMP | BAS/MCL | Base Radio Control Link | Point to Point Mobile Radio System | Yes | Non-BES |  | Testing | GMP6301 | 2 | 5 | Radio meets FCC requirements. | RDM 585 | RDR 586 | RDM 895 | RDR 896
PP & RMP | BAT | Power Supply | Battery & Charger | Yes | Non-BES | All non BES | Inspect & Maintain | GMP6502 | 1 | 5 | Battery impedance test. | BAM 588 | BAF 589 | BAM 828 | BAF 829
PP & RMP | BAT | Lines Cabinet Power Supply | Battery | Yes | Non-BES | All non BES | Inspect & Replace Battery | GMP6003 | 3 | 5 | Inspect and replace battery. Effective 1/2025 | BAM 588 | BAF 589 | BAM 828 | BAF 829
PP & RMP | BAT | Substation Site/Vented Lead Acid | Battery & Charger | Yes | BES (WECC) | Alcad, Fiamm, Hoppecke | Battery Inspection | GMP6504 | 4 month | 5 | Battery inspection test. | BAM 588 | BAF 589 | BAM 828 | BAF 829
PP & RMP | BAT | Substation Site/Valve Regulated | Battery & Charger | Yes | BES (WECC) | East Penn, C&D | Battery Maintenance | GMP6503 | 4 month | 5 | Battery impedance test. | BAM 588 | BAF 589 | BAM 828 | BAF 829
PP & RMP | BAT | Substation Site/Vented Lead Acid | Battery & Charger | Yes | BES (WECC) | Alcad, Fiamm, Hoppecke | Battery Maintenance | GMP6505 | 18 month | 5 | Battery impedance test. | BAM 588 | BAF 589 | BAM 828 | BAF 829
PP & RMP | DCS | Digital Cross Connect System | Digital Cross Connect System | Yes | Non-BES | DNX-88, Titan 532L, V4150 | Testing | GMP6450 | 1 | 3 | Verify high speed module protection. | DCM 608 | DCR 609 | DCM 908 | DCR 910
PP & RMP | EPUy | Generator (Comm.) | LP Gas Engine Generator | Yes | Non-BES | Generac, Onan, Kohler | Inspect & Maintain | GMP6512 | 1 | 6 | Pre-winter LOF and inspection. | GPM 596 | GPR 597 | GPM 834 | GPR 835
PP & RMP | EPUm | Generator (Comm.) | Diesel generator only | Yes | Non-BES | Caterpillar | Inspect | GMP6513 | 1 month | 1 | Monthly startup / inspection. Diesel only. | GPM 596 | GPR 597 | GPM 834 | GPR 835
PP & RMP | FAC | Communication Site | Property & Equipment | No | Non-BES | Various | Inspection | GMP6001 | 6 month | 6 | Semi-annual check of facility and peripheral equipment. | CSM 579 | CSR 580 | CSM 887 | CSR 888
PP & RMP | FAC | Communication Site | Alarms | No | Non-BES | Various | Verification | GMP6006 | 1 | 2 | Verify alarms on Monarch for PLC and tone relay equipment
PP & RMP | FOT | Fiber Optics Terminal | FO Multiplex Equipment | Yes | Non-BES | Larus FT2, ATT DDM 1000, NEC RC28D, DMXplore | Test & Maintain | GMP6402 | 4 | 4 | Perform tests. | FOM 602 | FOR 603 | FOM 830 | FOR 831
PP & RMP | DMX FOT | DMX Fiber Optics Terminal | FO Multiplex Equipment | Yes | Non-BES | DMX, DMXtend | Inspect | GMP6403 | 1 | 4 | Change filter. | FOM 602 | FOR 603 | FOM 830 | FOR 831
PP & RMP | MAS | Radio (MAS) Master All / Transmission only for remotes | SCADA Radio | Yes | Non-BES | Darcomm, MDS, Alligator | Testing | GMP6332 | 1 | 4 | Perform tests. Radio meets FCC requirements. | RDM 585 | RDR 586 | RDM 895 | RDR 896
PP & RMP | MAS/MCL | MAS Radio Control Link | Point to Point SCADA Radio System | Yes | Non-BES | Darcomm, Alligator, Optaphone | Testing | GMP6332 | 1 | 4 | Perform tests. Radio meets FCC requirements. | RDM 585 | RDR 586 | RDM 895 | RDR 896
PP & RMP | MWA | Radio (Analog) | Analog Microwave | Yes | Non-BES | FAS-6000 | Testing | GMP6322 | 1 | 4 | Perform tests on Analog MW.
PP & RMP | MWD | Radio (Digital) | Digital Microwave | Yes | Non-BES | Alcatel MDR-6706, Harris Constellation, IRU600 | Testing | GMP6312 | 1 | 4 | Perform tests on Digital MW. | CTM 590 | CTR 591 | CTM 898 | CTR 899
PP & RMP | OTN | Optical Transport Network | Fiber | Yes | Non-BES | Ciena 6500 | Testing | GMP6405 | 1 | 3 | Perform tests.
PP & RMP | PLC | Power Line Carrier | On/Off PLC Terminal | Yes | BES (WECC) | Westinghouse TC10B | Inspect | GMP6104 | 4 month | 4 | Function verification. | PLM 593 | PLR 594 | PLM 832 | PLR 833
PP & RMP | PLC | Power Line Carrier | PLC Terminal | Yes | BES (WECC) | GE Type 51, 61, 71, TCF-10B | Maintenance | GMP6102 | 2 see note 3 | 7 | Check levels & operate. Perform test. | PLM 593 | PLR 594 | PLM 832 | PLR 833
PP & RMP | RTU | Remote Terminal Unit/Transmission only | SCADA Remote | Yes | Non-BES, except Jim Bridger SEL RTU's | Harris D-20, L&G 5700 | Inspection | GMP6342 | 1 | 4 | Inspect. | RTR 583 | RTR 584 | RTM 893 | RTR 894
PP & RMP | RTU | GE N60 | Logic Controller | Yes | CIP | GE N60 | Test | GMP6345 | 5 | 8 | Perform tests. | RTR 583 | RTR 584 | RTM 893 | RTR 894
PP & RMP | RCC | Monarch Comm. Channels | SCADA | No | Non-BES | Monarch | Inspection | GMP6343 | 4 month | 3 | PCC and SCC communications channel switchover. | RTR 583 | RTR 584 | RTM 893 | RTR 894
PP & RMP | TON | Tone Relay | Tone Relay Terminal | Yes | BES (WECC) | GE Type 30, GE Type 40, RFL 6745 | Test & Maintain | GMP6202 | 1 see note 1 | 5 | Check levels & operate. Perform test. | TOM 598 | TOR 599 | TOM 836 | TOR 837
PP & RMP | TON | Tone Relay | Tone Relay Terminal | Yes | BES (WECC) | 9745 | Test & Maintain | GMP6204 | 4 see note 2 | 5 | Check levels & operate. Perform test. | TOM 598 | TOR 599 | TOM 836 | TOR 837
PP & RMP | TOWg | Tower (Guyed) | Tower | Yes | Non-BES | All | Inspecting & Maintain | GMP6005 | 3 | 4 | Contracted inspection of guyed towers. | CSM 579 | CSR 580 | CSM 887 | CSR 888
PP & RMP | TOWs | Tower(Steel) | Tower | Yes | Non-BES | Sabre, Microflect, Valmont | Inspecting & Maintain | GMP6002 | 5 | 21 | Internal crews inspection of steel towers. | CSM 579 | CSR 580 | CSM 887 | CSR 888
1) Interval shown is the preferred interval. Work orders will be generated every calendar year with a PM performed no longer than 18 calendar months between consecutive tests.
2) Interval shown is the preferred interval. Work orders will be generated every 4 calendar years with a PM performed no longer than 60 calendar months between consecutive tests.
3) Interval shown is the preferred interval. Work orders will be generated every 2 calendar years with an interval of no longer than 36 calendar months between consecutive tests.
4) Other equipment requiring commissioning would include HVAC, digital mux, charger, DRI, DFI, fiber optic cable, network equipment, satellite equipment and telemetry equipment.