## 2025
*Log Begins August 8, 2025*
Horizon West Transmission
2026-2028 WMP Data Request Log
As of January 22, 2026
Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Response | Requestor | Date Received | Final Due Date | Date Sent | Links | No. of Attachments | NDA Required | WMP Section | Category | Subcategory | Confidential
1 | OEIS | P-WMP_2025-HWT | 001 | 1 | Q01 | Regarding Defensible Space (VM-02) Weed Abatement Frequency: On page 119 of its 2026-2028 Base WMP, HWT states that its "primary vegetation management activity consists of weed control which occurs once per year with supplemental treatments up to four times per year." However, on page 99 of its 2023-2025 Base WMP, HWT states that it performs weed abatement six times per year, "bimonthly during winter and spring, and quarterly during summer and fall." a. Explain why HWT reduced its Defensible Space (VM-02) target from six treatments per year, to one with up to four treatments per year (e.g., resource use efficiency, treatments have become more effective over time, etc.). b. Explain how defensible space treatments one to four times per year will reduce the average annual fuel loading as effectively as six treatments. c. State the time of year that HWT plans to perform weed abatement to achieve its target of one treatment per year (e.g., late spring, early summer, fall, etc.). | a. The Suncrest Substation and the fuel modification zone around the substation are both hardscaped with rock which provides limited opportunity for vegetative fuels to grow. HWT’s field engineers conduct monthly vegetation inspections to assess the existence and growth of weeds and other low lying vegetation within Suncrest’s operational space. Limited weed abatement treatments have been effective in inhibiting the growth and existence of weeds both within the substation and the fuel modification zone. As a result, HWT elected to revise the cadence of weed abatement to better align with historically observed existence/growth of vegetation within the substation and fuel modification zone and best practices for optimal use/best practices associated with herbicide treatments. b. Given the fact the both the Suncrest Substation and the fuel modification zone around the substation are both hardscaped with rock, there is limited growth of weeds and other low lying vegetation within Suncrest’s operational space. As Suncrest was a new facility which went operational in 2020, HWT did not have an operational history upon which to base its cadence of weed abatement treatments and initially established a program of six treatments. Over the course of 5 years of monthly vegetation inspections by field engineers and periodic weed abatement activities conducted by contracted vendors, the field engineers have been able to observe the growth of vegetation and the effectiveness of weed abatements. Additionally considering recommendations from contracted vendor and best practices for use of herbicides and vegetation management techniques, HWT has determined that a minimum one year treatment, with up to three additional treatments, dependent on vegetation growth driven by observed rainfall, will be sufficiently effective for address the limited vegetative fuels that may exist in and around the Suncrest Substation. c. Target treatment will occur in the spring before peak fire risk months. | Johan Im | 2025-08-12 | 2025-08-15 | 2025-08-15 |  |  |  | 9.6 | Defensible Space | Scheduling | No
2 | OEIS | P-WMP_2025-HWT | 001 | 2 | Q02 | Regarding Quality Assurance and Quality Control Record Keeping: On page 134 of its 2026-2028 Base WMP HWT describes its documentation of quality assurance and quality control findings. HWT states that "asset management and inspection tasks are tracked and reported as complete in HWT’s asset management program, AMP. Field engineers review results of monthly equipment inspections. Any identified issues which need further mitigation will be discussed and addressed with the appropriate subject matter expert (SME) or the supervisor as required. Issues are documented and monitored by entering corresponding work tasks in the database." a. Does HWT’s field engineer also verify that its vegetation management and inspection contractor completed work and then record that the work is complete in its asset management program? i. If yes, provide an example of conditions the field engineer records when performing a quality check (e.g., no vegetation within the Suncrest Facility walls, no vegetation within 5 feet outside of the Suncrest Facility walls, etc.). ii. If no, describe how HWT tracks the results of its quality checks and, as in (i.) above, provide an example of conditions the field engineer records. | a. An HWT field engineer perform the monthly vegetation inspections as part of the monthly WMP Condition Assessment (WCA) and mark the task complete in AMP. Any vegetation need identified is communicated to the vegetation management contractor. Field engineers document vegetation management works by the contractor as complete via an AMP task after the work is completed (See screenshot below). The WCA which occurs subsequent to the vegetation management works by the contractor functions as the assessment of the conditions observed by the field engineer and includes follow-up/after action items if needed. Two WCAs (OEIS-P-WMP_2025-HWT-001_ Attachment _WCA_20240425 and OEIS-P-WMP_2025-HWT-001_ Attachment _WCA_20250129) are provided as confidential attachments. Figure 1. AMP record of completed Weed Abatement Activity conducted by contractor in 2024 | Johan Im | 2025-08-12 | 2025-08-15 | 2025-08-15 |  | 2 |  | 9.11 | Quality Assurance and Quality Control | Documentation of Findings | Yes
3 | OEIS | P-WMP_2025-HWT | 002 | 1 | Q01 | Regarding Drone in a Box Aerial Inspections: a. On page 84 of its 2026-2028 base WMP R0, HWT states, “HWT will also utilize a drone in the box for aerial inspections to supplement the visual inspections performed by field personnel, however visual ground inspections will remain the primary means of asset inspection.” i. Will an aerial inspection using the Drone in a Box be performed during every monthly inspection? 1. If not, how often will it be performed? 2. Provide an explanation of the rationale for determining the frequency of aerial inspections. | 1. Yes, an aerial inspection using the Drone in a Box will be performed as supplemental to the visual ground inspections by the field engineers which will remain the primary means of asset inspection. Additionally, the drone will be utilized to supplement the annual FLIR and riser pole inspection. 2. Please see response to #1 above. Additional flights may be conducted to support further testing, development and refinement of processes and procedures and product capabilities. | Johan Im | 2025-08-13 | 2025-08-18 | 2025-08-18 |  |  |  | 8.3 | Asset Inspection | Substation Inspection | No
4 | OEIS | P-WMP_2025-HWT | 002 | 2 | Q02 | Regarding a Second Water Tank: b. On page 18 of its 2026-2028 base WMP R0, HWT states that one of the proposed mitigation initiatives for the 2026-2028 WMP cycle is, “Notional plans to improve stationed firefighting resources by constructing a second water tank near the Suncrest Substation.” i. Provide information in one of the following two categories: 1. If the water tank is to be installed: a) Provide a timeline for when a second water tank will be installed. 2. If the water tank is to be considered: a) Provide a timeline for when a decision will be made. b) Provide the criteria for how it will be determined if a second water tank should be installed. | i. The notion to explore the potential to install a second water tank at the Suncrest Station was a conceptual idea raised in late Q2 2025. As the concept is a recent development, HWT has not yet initiated the process to ascertain the feasibility of the additional water tank, and any associated permitting, environmental, engineering assessments, etc. or developed a timeline. HWT anticipates commencing this process by Q4 2025 and will update its 2026-2028 WMP and/or requisite quarterly/annual reporting to document any material progress or decision-making associated with this potential project. | Johan Im | 2025-08-13 | 2025-08-18 | 2025-08-18 |  |  |  | 3.2 | Plan Objectives |  | No
4 | OEIS | P-WMP_2025-HWT | 002 | 2 | Q02 | Regarding a Second Water Tank: b. On page 18 of its 2026-2028 base WMP R0, HWT states that one of the proposed mitigation initiatives for the 2026-2028 WMP cycle is, “Notional plans to improve stationed firefighting resources by constructing a second water tank near the Suncrest Substation.” i. Provide information in one of the following two categories: 1. If the water tank is to be installed: a) Provide a timeline for when a second water tank will be installed. 2. If the water tank is to be considered: a) Provide a timeline for when a decision will be made. b) Provide the criteria for how it will be determined if a second water tank should be installed. | This supplement response is to clarify that HWT will provide an update in its 2027 Update to its 2026-2028 Base WMP to document any material progress or decision-making associated with the potential Second Water Tank project. | Johan Im | 2025-08-13 | 2025-08-18 | 2025-08-22 |  |  |  | 3.2 | Plan Objectives |  | No
5 | OEIS | P-WMP_2025-HWT | 003 | 1 | Q01 | Regarding HWT’s Usage of AMP As Its Asset and Maintenance Management Program: On page 195, HWT states that they utilize “AMP as its asset and maintenance management program and SharePoint for document storage.” a. Please provide further information on HWT’s use of AMP as its asset and maintenance management program. i. Provide a list and description of each type of data stored in AMP for the asset and maintenance management program. ii. For each type of data stored, explain how long is the data stored in the system of record. iii. Does HWT plan any integration of new software for asset management in the 2026-2028 Base WMP years? 1. If yes, provide a list and description of each new software planned, and a timeframe for when HWT plans to integrate it. 2. If not, provide a description of HWT’s plans to update its current software, in order to shift to a more risk-based asset management program. | i. AMP is used to store transmission and substation equipment data, plus pending and completed inspection/maintenance/trouble tasks. ii. All data is retained for the operational life of the assets and applicable regulatory retention periods at a minimum. iii. AMP is a custom-built, in-house asset management program which is utilized by all NextEra Energy affiliates, including HWT. AMP is managed at the corporate level by NextEra Energy’s Power Delivery business unit and its dedicated IT department. As such any changes, updates, etc. are directed, managed, and controlled at the corporate level. There is no current plan for any integration of new software for AMP in the 2026-2028 WMP years. However, there is a plan to transition to Elements (custom-build, in-house asset management program), the upgraded version of AMP, during this timeframe. | Johan Im | 2025-08-19 | 2025-08-22 | 2025-08-22 |  |  |  | 12.1 | Enterprise Systems | Targets | No
6 | OEIS | P-WMP_2025-HWT | 004 | 1 | Q01 | Regarding SA-02 and SA-06 Activities: a. In the 2026-2028 Base WMP Revision 1, Table 10-1 on pages 142 and 144 show the same activities for SA-02 and SA-06 “Evaluation of Optos/Firecaster performance”. i. Provide an explanation and further information on the usage of the different tracking numbers for the same activity. 1. If this is a typo, please indicate as such and describe the steps being taken to correct. | i. Optos/Firecaster has both environmental monitoring components and risk index features. Evaluation of the performance of various inputs to Firecaster may be separate from evaluation of overall output of the wildfire risk index model. As such although the title of the task is the same for SA-02 and SA-06, different aspects of the Optos/Firecaster tool will be evaluated. | Johan Im | 2025-09-23 | 2025-09-26 | 2025-09-26 |  |  |  | 10.1 | Situational Awareness and Forecasting | Targets | No
7 | OEIS | P-WMP_2025-HWT | 004 | 2 | Q02 | Regarding HWT’s Planned Migration from AMP to Elements: a. In the HWT 2026-2028 Base WMP Revision 1, Table 12-1 on page 195 show “N/A” for initiatives related to Section 12: Enterprise systems. However, in the narrative section on page 196 states, “However, there is a corporate-directed plan to transition to Elements (a custom-build, in-house asset management program), the upgraded version of AMP, during this timeframe." i. Provide the following information related to the transition from AMP to Elements during the 2026-2028 WMP cycle: 1. Narrative information on the timing, milestones, and status of the transition to Elements. 2. Explanation of why this transition plan is not included in the initiatives for Section 12: Enterprise systems of the WMP. | 1. The corporate transition from AMP to Elements is planned for completion by mid-2026. As part of the transition process, assets, work tasks, and functions are being verified and crosschecked in the test environment to ensure continuity of operations and compliance with existing maintenance workflows in AMP. Confirmation of functionality will be verified in the production environment and job-aids and training provided to users in connection with project completion planned for mid-2026. 2. Exclusion of the transition plan as an initiative in Section 12 was an oversight, as it should have been included in the most recent revision of HWT’s Base 2026-2028 WMP to sync with the revised language added in the narrative on page 196. A subsequent revision to HWT’s Base 2026-2028 WMP will be submitted to correct the oversight. | Johan Im | 2025-09-23 | 2025-09-26 | 2025-09-26 |  |  |  | 12.1 | Enterprise Systems | Targets | No
8 | OEIS | P-WMP_2025-HWT | 005 | 1 | Q01 | Regarding General Housekeeping during the Monthly Wildfire Mitigation Condition Assessment Procedure: a. On page 37 of its 2026-2028 base WMP, HWT states, “Field engineers perform monthly substation inspections in accordance with HWT’s Wildfire Mitigation Condition Assessment Procedure, which includes general checks, visual inspections, general housekeeping, vegetation control, and a review of maintenance equipment.” i. What activities are completed as part of “general housekeeping”? ii. As part of the monthly substation inspections, do field engineers visually inspect the substations for combustible materials, trash, and/or other hazardous materials? 1. If yes; is this inspection task listed on the Wildfire Mitigation Condition Assessment Procedure? a) If yes, please provide the page number and location of this item. b) If no, how do field engineers record and track this information? 2. If no; why is this not a necessary item to track for inspections? Additionally, what do field engineers do if they discover combustible materials, trash, and/or other hazardous materials during their inspection? | Field engineers visually inspect areas for vegetation, wildlife, obstructions/debris, vandalism, and off normal conditions as performance of ‘general housekeeping’ as part of the monthly wildfire and equipment condition assessments. ii. Yes. The corresponding inspection items are listed in the Wildfire Mitigation Condition Assessment Procedure and accounted for in the associated inspection form(s). a) Page numbers and locations in the Wildfire Mitigation Condition Assessment Procedure Page 4 to 8 – Section 4.1 and 4.2. Subsections address assessing and maintaining appropriate site conditions. | Johan Im | 2025-10-17 | 2025-10-22 | 2025-10-22 |  |  |  | 5.1 | Risk Methodology and Assessment | Methodology | No
9 | OEIS | P-WMP_2025-HWT | 005 | 2 | Q02 | Regarding Fire Department Connection to Water Tank: a. On page 10 of the Wildfire Mitigation Condition Assessment, effective date October 24, 2019 (V1.1), HWT identifies the location of the, “10,000 Gallon Water Tank with Fire Dept. Connection.” i. Provide a narrative description of how local fire suppression agencies can assess the water tank. List all departments and agencies that have access. ii. Provide relevant documents demonstrating communication with local fire suppression agencies that confirms access to the water tank. | i. The water tank is located proximate to the Suncrest substation but outside the substation walls. The fire stations closest to Suncrest that would have access to water tank would be San Diego County Fire Station 44 (Pine Valley) and San Diego County Fire Station 45 (Descanso). ii. HWT hosted members of San Diego County Fire Station 45 (Descanso) at the Suncrest Substation on April 24, 2025, for a site tour and discussion which included access to the water tank. A copy of the calendar invitation for the meeting is provided as an attachment to this response. | Johan Im | 2025-10-17 | 2025-10-22 | 2025-10-22 |  | Yes |  | N/A | N/A | N/A | No