## SDGE Table 5-1
Attributes | Sub-Attributes | 2023 Dollar Equivalency | 2025 Dollar Equivalency
Safety | Fatality | $15.2 million per fatality | $15.97 million per fatality
Safety | Serious Injury | $3.84 million per serious injury | $4.03 million per serious injury
Safety | Minor Injury | $45,000 per minor injury | $45,000 per minor injury
Electric Reliability (SDG&E Only) | n/a | $3.67 per CMI* | $3.85 per CMI*
Gas Reliability | Gas Meter Experiencing Outage | 3382 | 3553
Financial | US Dollar | 1 | 1
*Customer Minutes Interrupted (CMI) is measure for electric outages that includes the number of customers affected and duration

## SDGE Table 5-2
Safety Sub-Attributes | Relative Value | 2023 Dollar Equivalency | 2025 Dollar Equivalency
Fatality | 1 | $15.2 million | $15.97 million
Serious Injury | 0.253 | $3.84 million | $4.03 million
Minor Injury | 0.003 | $0.045 million | $0.047 million

## SDGE Table 5-3
Risk Component | Description
Wildfire Likelihood | Simulates annual frequency of ignition event occurrences leading to potential wildfires, leveraging probabilistic PoI values and simulated wind speeds.
Other Equipment & Foreign Object Probability of Failure | Estimates the likelihood and frequency of other equipment and foreign object failure (e.g, fuse damages, animal interference, vandalism, etc.) at every span in the service territory.
Vegetation Probability of Failure | Estimates the likelihood and frequency of a vegetation failure (i.e., tree strike causing a wire down) at every span in the service territory.
Conductor Probability of Failure | Estimates the likelihood and frequency of a conductor failure (i.e., wire down) at every span in the service territory.
Vehicle Contact Probability of Failure | Estimates the likelihood and frequency of a vehicle contact failure at every pole in the service territory.
Pole/Span Conditional Probability of Ignition | Estimates the likelihood and frequency of an electrical outage leading to an ignition within the service territory.
PSPS Likelihood | Estimates the probability that a given feeder-segment would be proactively de-energized due to PSPS on a given high-fire day. For WiNGS-Ops, a PSPS Likelihood of 1 is assumed.
Burn Likelihood | Subject matter expertise is used to select a representation of the worst fire weather days in the service territory. The burn probability is assumed to be 100% for these days.
PEDS Outage Likelihood | Simulates annual frequency of PEDS outage event impact occurrences in a specific location of the grid.

## SDGE Table 5-4
Risk Component | Wildfire Consequence
Safety | Equivalent Safety Serious Injuries and Fatalities (SIF) are calculated based on Technosylva estimates of structures destroyed. Assumption: To estimate the total number of equivalent fatalities per structure destroyed a 0.00617 factor is assumed. This factor is estimated based on an internal analysis conducted on the CAL FIRE dataset.
Reliability | Subject matter expert conservative assumption to estimate Customer Minutes Interrupted (CMI) values based on estimates of outage duration and assumed restoration duration. These CMI estimates are subsequently monetized using the $/CMI value provided in SDG&E Table 5-1. Assumption: Restoration time is 24 hours
Financial | Subject matter expert conservative assumption to translate buildings destroyed and acres impacted estimated by Technosylva simulations to financial dollars. Assumptions: Suppression and restoration cost: $2,350/acres burned; Structure Destroyed cost: $1,000,000/structure destroyed

## SDGE Table 5-5
Risk Attribute | PSPS Consequence
Safety | Subject matter expert conservative assumption to estimate the potential number of Serious Injuries and Fatalities (SIF) created by a PSPS de-energization. Assumption: 1 fatality per 10 billion customer minutes de-energized. Estimated based on a review of historical PSPS de-energizations in California (2018-2021).
Reliability | Customer Minutes Interrupted (CMI) estimates are calculated directly from the number of customers impacted at each feeder segment with varying event durations based on historical and projected durations of PSPS de-energizations. Assumption: CMI estimates are subsequently monetized using the $/CMI value provided in SDGE Table 5-1.
Financial | Subject matter expert conservative assumption to estimate the potential financial loss experienced by customers affected by a PSPS de-energization. Assumption: For residential customers a $482 cost per event is calculated using the per diem rates applicable to San Diego, California, as of September 2024, with the assumption of accommodating four family members per customer meter. For C&I customers, a $1,446 cost per event* is estimated.
*Financial values as of February 2025. A factor of three is assumed for C&I customers: https://www.federalpay.org/perdiem/2025/california/san-diego

## SDGE Table 5-6
Risk Attribute | PEDS Consequence
Safety | Subject matter expert conservative assumption to estimate the potential number of Serious Injuries and Fatalities (SIF) created by a PEDS reliability outage event. Assumption: 1 fatality per 10 billion customer minutes de-energized. This assumption is estimated based on a review of historical PSPS de-energizations in California (2018-2021).
Reliability | Customer Minutes Interrupted (CMI) estimates are calculated directly from the number of customers impacted at each feeder segment, with varying event durations based on historical and projected durations of PEDS de-energizations. Assumption: CMI estimates are subsequently monetized using the $/CMI value provided in SDGE Table 5-1.
Financial | Subject matter expert conservative assumption to estimate the potential financial loss by a PEDS de-energization event. Assumption: Based on historical overhead line patrol costs during elevated or extreme fire weather conditions. Whether conducted on foot or by helicopter, a 10% ratio of the expected reliability cost is assumed.

## SDGE Table 5-7
Percentiles | Annual Return Period (Years) | Wildfire Millions $ | PSPS Millions $ | PEDS Millions $ | Overall Utility Risk Millions $
P50 | 20 | 14.02 | 62.52 | 5.25 | 171.2
P98 | 50 | 36164.84 | 785.26 | 16.34 | 36304.72
P99 | 100 | 52108.23 | 865.94 | 18.1 | 52244.82
P100 | --- | 210980.47 | 2875.66 | 38.91 | 211824.59
AAL | 1 | 2891.82 | 134.77 | 5.9 | 3032.48

## SDGE Table 5-8
ID | Recommendation Name | Description | Severity Level and Impact | Target Deadline (EOY) | Status
1 | Data Ownership | Ensure that there is an integrated function, such that communication from specific data owners is cohesive and timely. This would ensure the communication of definitions, use, bounds for validity, and decisions on changes. Data owners would also be responsible for ensuring that the data is up to date and accessible. | Severity Level: Medium – lack of communication from data owners may result in unexpected changes and diminished data integrity. The data owner is accountable for the use, quality and protection of a dataset. | 2027 | In progress
2 | Calculation Ownership | Assign owners of specific constants (e.g., PSPS risks) and calculation methodologies such that their definitions and approaches are agreed, documented and uniform across the business. This is to ensure that any colloquial terms used for aggregated data assets are consistent such that an output like “miles of span in HFTD in one group’s calculation is the same as another’s. | Severity Level: Low – a calculation owner will be accountable for ensuring calculation methodologies are clearly defined and are used appropriately and consistently. | 2027 | In progress
3 | Model Value | In order to quantify the value the model brings to the business, define a measurable metric that clearly shows what benefit the model is providing in order to evaluate if the value offsets the costs. A potential metric could be tracking the percent Electric System Hardening (ESH) deviates from the model recommendations. | Severity Level: Low – while not directly affecting the model output, it is best practice to regularly evaluate the value a model brings to a business to determine future growth and investment. | 2027 | In progress
4 | Initiation Stage Documentation | Document the initiation stage in order to capture critical elements of the initial planning stage. This includes defining what problem this model will solve, what is the feasibility of the model, who are the end users and how do they want to ingest the model outputs, who are the subject matter experts and what is their ability to participate in the model development, who will be the business owner of the model, what are the initial assumptions and how were they determined, and confirmation that all relevant business areas have taken full sponsorship of the project. Additional details on why certain decisions were made with respect to model generation are also critical to document in the initiation process. | Severity Level: Medium – due to the lack of documentation from the initiation of the WiNGS-Planning model, there are several assumptions and decisions that were made that cannot be explained now that the original stakeholders are no longer with the company. | 2026 | In progress
5 | Data Documentation and Dictionaries | Document for all input data, which should include the data owner, the context of the data, data collection methodology, structure and organization of the data, data validation and quality assurance steps, data manipulations from raw data, and data confidentiality, access and use conditions. If applicable, it should also include any calculations used to derive any of the fields, data dictionary of input data into those calculations, assumptions, references to methodologies or assumptions, and any limitations of the data. This will ensure a detailed understanding of the data that can be referenced as needed. Additionally, develop data dictionaries for all input data, which should list all the data fields. Each data field listing should include a description, data type, acceptable numerical ranges or classification values if applicable, units, if mandatory, null or missing value definition, effective date, and update information (including date of update, by who, what was updated, and why). This will ensure a thorough understanding of each data field, as well as a reference for data validation steps. | Severity Level: Low – not having documentation or data dictionaries do not prevent the model from running, however, there is a risk of misunderstanding the data, or if there is turnover on the data science team, new team members will have a more challenging time referencing and understand the data inputs. | 2026 | In progress
6 | Data Input Validation | Implement an automated data validation check for every data input to look for outliers, errors, text control, contradictions, etc. Each of these validation checks should have associated documentation that includes what to do when data is missing or anomalous. Examples of how outliers, errors, contradictions, etc. are detected and how corrections are performed in a demonstratable way should be provided if necessary. | Severity Level: Medium – there is currently a lot of reliance on source data owners to validate their data, which can lead to errors and reduce data quality. | 2026 | In progress
7 | LiDAR Tree Data | Update tree locations based on available LiDAR data to present a more accurate count of strikes per mile input for the circuit segments. | Severity Level: Medium – updating tree locations will likely change the tree strike potentials for circuit segments. | 2027 | Not Started
8 | Derived Data Validation | In line with recommendation R3.2, incorporate data validation steps when new fields are derived to ensure the generated data is explainable, and include documentation that explains the validation steps taken and what to do when data is missing or anomalous. Provide examples of how flagged data is detected and how corrections are performed in a demonstratable way if necessary. | Severity Level: Medium – validating derived data is an important step for ensuring the most accurate model outputs. Some values are valid on their own which allows them to make it through the initial data ingest validation step, but when put in context with another value, it may indicate the data is an outlier. | 2026 | In progress
9 | Mean Value Assessment | Conduct a detailed assessment of the instances where mean values are utilized in the calculations in order to determine if the approach would correctly account for outliers, potentially presenting a less risky situation than is accurate. | Severity Level: Medium – if it is determined that using mean values does not correctly account for outliers and a decision to use something other than mean values is made, then the data will change, which will result in a change to the risk score. | 2027 | In progress
10 | Stakeholder Involved Sensitivity Analysis | Conduct a more robust sensitivity analysis at a regular cadence (as outlined in ASTM E 1355 Section 10). Business stakeholders should be made aware of this sensitivity analysis and should be invited to participate in choosing the variables and their value ranges. The business users should then be involved in all output reviews and have the suggested changes/remediation actions presented to them, such that the impacts may be fully understood and agreed with. | Severity Level: Medium – a sensitivity analysis will provide the end users a better understanding of how different values affect the model as well as help identify which values are influencing the model the most. This will allow the end users to make more informed decisions when determining if they need to deviate from the model results. | 2028 | In progress
11 | Customer Type Multiplier Sensitivity Analysis | Perform a sensitivity analysis on the results of the customer type weight multipliers to evaluate if any unintended bias has resulted by adding weights to certain types of customers. This could include understanding the distribution of medical baseline and urgent customers relative to certain areas that may result in a decreased hardening priority. | Severity Level: Medium – if the results of the study indicate that the different customer type multipliers have the potential to adversely impact certain communities or demographics and the multiplier values are adjusted, that will result in changes to the CoRE model outputs and may change the mitigation rank for certain segments. | 2028 | In progress
12 | Formalize Model Validation Process | Devise and document formal process for validating the overall model outputs. This can be completed by comparing the run’s results with previous iterations' outputs as well as identifying outputs that appear erroneous. It is also recommended to engage the end users to incorporate any additional thoughts or checks they have into the validation process. | Severity Level: Low – a formalized model validation process will instill greater trust by end users by knowing how the model results are validated prior to receiving the outputs, and can reference any generated validation reports. | 2027 | In progress
13 | Formalize External Feedback Management Process | Create formalized demand management process for external parties to provide feedback and request adjustments to the models. This will ensure that as the team, model, and user base continue to grow, there is a robust mechanism through which updates may be requested, tracked, and implemented in the Cloud environment. | Severity Level: Low – this will not directly affect the model outputs; however, this is an important validation step between model developers and end users to continue to facilitate model development, accuracy, and value to the business. | 2026 | In progress
14 | Standardize Model Notifications | Create a standardized approach for how model update notifications are delivered and work with end users to capture the correct granularity and details that they would need to understand the changes. | Severity Level: Low – this recommendation will not have any effect on the model output, but ensures that the appropriate level of communication is delivered between the development team and the end users. | 2028 | In progress
15 | Unit Testing | Incorporate unit testing to ensure all functions are performing as expected. | Severity Level: Low – this recommendation will only affect the model if any functions are not performing as they should. | 2026 | Completed
16 | Aws Billing Limits | Introduce billing limits for certain sandbox/development activities such that there is not a risk of an unintended spike in cloud costs for a development error. | Severity Level: Low – this recommendation is to ensure that model costs are monitored and meet the set budget. | 2026 | In progress
17 | AWA Access Control | Review access control principles, focused on two areas, review the default access periods so access is revoked if someone doesn’t access for a given period of time and consider enabling row or column-level security to ensure users only access certain subsets of data most relevant and appropriate to them, which will become more necessary in the WiNGS-Planning visualization tool. | Severity Level: Low – following the security pillar from the 6 pillars of the AWS Well-Architected Framework will ensure the confidentiality and integrity of the data, and prevent unauthorized access and changes to the model and systems. | 2026 | In progress
18 | Single Cloud Vendor Consolidation | In the future, consolidate services under one cloud provider for ease of use, integration, and billing. This can ensure that future updates to any of the cloud services are always made in a way to keep compatibility and seamless integration with the other developed components. | Severity Level: Low – this recommendation has no impact on the output of the WiNGS-Planning model, but would allow for greater efficiency in use of cloud services. | 2026 | Not Started
19 | AWS Athena Consolidation | With improved Governance of the data, create only one instance of AWS Athena, with the GIS and Flat File data combined into the Data Mesh layer. With the data available in the Data Mesh, appropriate ownership and controls must be established such that any shared data is used within the bounds of its intended purpose. | Severity Level: Low – reducing from multiple instances of AWS Athena down to one would ensure efficiency of use and a lower overhead to manage, monitor, and maintain. | 2026 | In progress
20 | Separate Access On AWS | Create separation in the access to Cloud workspaces as the products mature. | Severity Level: Low – this would allow more control over access control, budget planning, and spend tracking for the separate groups. | 2026 | In progress

## SDGE Table 5-9
ID | Recommendation Name | Description | Severity Level | Target Deadline (EOY) | Status
1 | Data Owner Communication | Ensure that there is an integrated function, such that communication from specific data owners is cohesive and timely. Definitions, use, bounds for validity, and decisions on potential changes would be communicated. Data owners would also ensure that data is up to date and accessible. | Severity Level: Medium – lack of communication from data owners may result in unexpected changes and diminished data integrity. | 2026 | In Progress
2 | Calculation Ownership | Assign owners of specific constants (e.g., PSPS risks) and calculation methodologies such that their definitions and approaches are agreed, documented and uniform across the business. This is to ensure that any colloquial terms used for aggregated data assets are consistent such that an output like “miles of span in HFTD in one group’s calculation is the same as another’s. | Severity Level: Low – a calculation owner will be accountable for ensuring calculation methodologies are clearly defined and are used appropriately and consistently. | 2026 | In progress
3 | Model Ownership | Implement broader model ownership in the form of a board/ group with regular meeting cadence to agree to higher-level changes and adjustments, reviewing output of sensitivity analysis and changes prior to implementation. This would ensure that the direction of overall model enhancements and improvements is agreed amongst the Developers, Wildfire Mitigation team, and the Business users. | Severity Level: Low – without regular communication between all stakeholders, the direction and prioritization of model development and improvements can be missed. | 2027 | In Progress
4 | EAMP Data Experts | Onboard an internal team to share subject matter expertise responsibility for EAMP/Asset 360. EAMP/Asset 360 provides a rich asset data source used in modeling. The data itself is a clean and curated version of GIS and Asset Management data. Currently, the program is operated by external contractors who also remain as the data source subject matter experts. The source, including all dictionaries and implemented manipulations, should also be fully documented such that any new user may easily gain a complete understanding of the data and its use. | Severity Level: Medium – with a continued reliance on external parties for this critical data source, the team will not gain full ownership, understanding, and control over the underlying data. Internal subject matter expertise in the data source will ensure a robust and future-proof mechanism for data understanding, questions, and data updates. | 2025 | Complete
5 | OIR Requirements | Build and maintain a formalized report that tracks OIR requirements and how they were carried out in order to ensure that all Order Instituting Rulemaking (OIR) requirements are met and prevent possible violations. Having this existing documentation will not only confirm what the requirements are and if and how they were completed but will also be ready to pass along to the OIR as appropriate. | Severity Level: Low – this will help prevent potential violations from the OIR by tracking all the requirements and how they were completed. | 2026 | In Progress
6 | Model Change Documentation | Create a formal process through which requirements for model changes are captured, tracked, and completed against. This will ensure that changes are understood and captured correctly and will allow success criteria to be defined and assessed against by the end users in their approval of model changes. | Severity Level: Low – without a documented process, requirements and requested changes may be incorrectly implemented or the end users may not have an easy mechanism for change approval. | 2026 | In Progress
7 | Initiation Stage Documentation | Document the initiation stage in order to capture critical elements of the initial planning stage. This includes defining what problem this model will solve, what is the feasibility of the model, who are the end users and how do they want to ingest the model outputs, who are the subject matter experts and what is their ability to participate in the model development, who will be the business owner of the model, what are the initial assumptions and how were they determined, and confirmation that all relevant business areas have taken full sponsorship of the project. Additional details on why certain decisions were made with respect to model generation are also critical to document in the initiation process. | Severity Level: Low – without this documentation in place, future developers and end users may have a more difficult time understanding the decisions and assumptions that were made, which subject matter experts to turn to for input, how the model will be measured for success, or the original problem and objectives. | 2026 | In Progress
8 | Data Input Validation | Implement an automated data validation check for every data input to look for outliers, errors, text control, contradictions, etc. Each of these validation checks should have associated documentation that includes what to do when data is missing or anomalous. This should be implemented in the inference pipeline and should be consistent with data validation performed by the WiNGS-Ops data science team during their exploratory data analysis process. | Severity Level: Medium – there is currently a lot of reliance on source data owners to validate their data, which can lead to errors and reduce data quality. | 2026 | In Progress
9 | SAIDIDAT Data Ingestion | Perform a direct query of SAIDIDAT data from its source database. This eliminates the reliance on individuals and prevents potential human error. | Severity Level: Low – manual data request and transfers are reliant on the requestor to ask for the information. Automating the request process may be a better way to obtain updated outage history data on a scheduled basis rather than on an as-requested basis. | 2026 | In Progress
10 | Alternative Land Use Data Source | Work closely with the SANGIS team to incorporate service territory areas currently not covered in their existing coverage data, as well as request more frequent than annual data updates. This would ensure the models have access to the same information as the rest of San Diego County and are up to date during a red flag warning event. | Severity Level: Low – models run on data which has not been recently refreshed or on imputed data based on mean values may provide inaccurate outputs. This may cause a model to under-represent the potential consequence of an ignition due to a missing at-risk land use. | 2026 | Not Started
11 | Model Improvement Limitations | Do not develop or incorporate additional features to the models. Due to the time pressures and resource constraints, the team does not have the capacity to further improve models in this manner. | Severity Level: Low –impact would be minimal due to the models’ existing satisfactory performance but might represent a missed opportunity for continued model improvements and enhancement. | 2026 | In Progress
12 | Class Imbalance Approaches | Test other approaches to handling class imbalanced data, including up-sampling, SMOTE, and ADASYN, in order to determine the most applicable method for each model. | Severity Level: Medium – down-sampling excludes significant amounts of data which may result in an unrepresentative data sample being used for training and testing the model. | 2026 | In Progress
13 | Algorithm Testing | Test other algorithms to ensure that the most suitable algorithm is used to solve the problem, balancing complexity of understanding and training with accuracy of modeling outputs. | Severity Level: Low – without validating that there isn’t a more suitable algorithm for the model, the team cannot be certain that they have built the most suitable model for the specific application. | 2026 | In Progress
14 | Conductor Model Retrain | Retrain the conductor model based on data from 2015 to present, utilizing the 2022 data for testing and validation. This will ensure the most representative data is utilized in construction and training to create the most accurate and useful modeling outputs. | Severity Level: Medium – based on the most recent data used for validation, the model under-represented the potential risk due to conductor failure. Re-training this model would generate a more representative output. | 2026 | In Progress
15 | Same Data Sources | Train the models on the same data sources that would be utilized for inference in production such that the resulting outputs are most relevant and applicable. | Severity Level: Medium – as the models were trained on different source data, the learned data relationships may not be representative of what would be seen in the EOC. As a result, outputs of the models may not be as accurate as if the data used for training was the same source as used in inference. | 2026 | In Progress
16 | GIS Cleaning | Consider a larger program of GIS data cleaning, validating, and improvement and investigate if existing GIS red lining processes can be leveraged to ensure the GIS system of record for assets represents the most accurate view of assets in the service territory. This would ensure that any modeling application or activation event would consider that most accurate understanding when making data-driven decisions. | Severity Level: Low – it is critical that decisions in the EOC are made based upon the most accurate representation of the assets in the field. | 2027 | Not Started
17 | Hyper-parameter Tuning | Implement the approach used for tuning hyper-parameters in the foreign object model, GridSearchCV, for tuning hyper-parameters in the vehicle contact model. | Severity Level: Low – consistent use of techniques across models ensures that the quality and robustness of each model is uniform and contributes to an optimal output. | 2026 | Not Started
18 | Brier Score | Use the full Brier score such that the outputs are unaffected by population size. This will enable Brier scores to be compared across different versions of a model to allow model improvements to be validated. | Severity Level: Low – a modified Brier score might be inadvertently used to compare models with different sample sizes. This would give an inaccurate view of the performance comparison and could result in an incorrect modeling decision. | 2027 | Not Started
19 | Class Imbalance Validation Methodology | For the vehicle contact model, incorporate a nested cross validation where one fold is an out-of-period imbalanced data split for the final validation and the other fold is split for training and testing on balanced sampled data set. This would provide an additional method for validating the accuracy of the model. Ensure the right metric is used for the evaluation, as some metrics are better for evaluation when there is class balance (ROC AUC) and others are better for when there is class imbalance (Precision-Recall AUC). | Severity Level: Medium – validating imbalanced data with this approach checks performance of the model against real class distribution. | 2027 | Not Started
20 | Uniform Model Testing | Establish a consistent and agreed approach for model testing across the team such that each member may be sure of the optimal model and be in agreement when training is complete. This will ensure consistency across models and build credibility with the end users. | Severity Level: Low – models may have differing levels of robustness without a uniform, defined, and agreed upon approach to testing. | 2026 | In Progress
21 | Data Documentation | Provide detailed documentation for all data that is ingested into the models The documentation is the responsibility of the data owners and should contain pertinent information such as the data owner, data collection methodology, data dictionary, structure of the data, data validation and quality assurance steps taken, data manipulations from the raw data, and confidentiality, access and use conditions. This will ensure a detailed understanding of the data that can be reference as needed, critical for ground truth data. | Severity Level: Low – without detailed documentation, there is a risk the data can be misinterpreted, or if there is turnover or new hires on the WiNGS-Ops Data Science or Advanced Analytics teams, they may have a more challenging time referencing and understanding the data inputs. | 2026 | In Progress
22 | Back-casting Model Validation Process | Create a more holistic and reliable model validation process to allow automated back-casting for each model change. This would allow for greater confidence in the updated version of each model. Given the snapshots of data are now maintained in the cloud, this ensures that this process would be simpler to perform. | Severity Level: Low – without an automated and uniform approach to model output validation, validating each new model release will be a time-consuming and inconsistent process. | 2026 | In Progress
23 | Back-casting Data Capture | Ensure that all necessary data and calculation components are captured, including the network configuration, at the time of a PSPS activation to help streamline future back-casting exercises. | Severity Level: Low – implementing this would allow for the automated and uniform approach mentioned in R7.1 and could be enacted for model back-casting. | 2027 | In Progress
24 | End User Formalized Validation Process | Establish a formalized validation process by the end users that will establish consistency in the validation approach and also build credibility with OEIS by demonstrating the results are reviewed in a specific and systematic way. | Severity Level: Low – without a formalized validation process, there is the potential for end users to validate the model differently every time a new model version is released. This may result in missing an important check, or reviewing an output that differs from a previous model version. | 2026 | In Progress
25 | Centralize Models | Migrate the conductor training model and PSPS model scripts to Azure DevOps Repos. This will ensure development on local machines are version controlled, tracked appropriately, and accessible by the team. This will also allow models to leverage cloud compute capabilities, meaning that more advanced models may be produced. Additionally, the PSPS model should be passed to the inference team such that the entire WiNGS-Ops model can be executed through the inference pipeline. | Severity Level: Medium – current processes limiting version control and access could introduce errors and confusion in the correct version that should be run in production. Full cloud migration would limit the risk of this issue. | 2027 | In Progress
26 | Profiler | Run a profiler to help understand the resource consumption of the various operations in the model. This can potentially resolve performance bottlenecks and help the model execute faster. | Severity Level: Low – this recommendation does not affect the model output but may improve the runtime performance of the model. | 2027 | In Progress
27 | Unit Testing | Incorporate unit testing to ensure all functions are performing as intended and errors are more easily isolated when they occur. Unit tests also check that the code still functions as expected after making changes, which builds code stability. | Severity Level: Medium – Without unit testing, there is no assurance that the code will function correctly and that there are no undiscovered bugs. This can lead to poor quality modeling results and wasted time and resources spent debugging. | 2027 | In Progress
28 | Docstrings | Ensure all python functions have docstrings, which will ensure that all functions are correctly documented and definitions, descriptions, and decision point reasoning are captured. Docstring best practice for a function includes a brief description of what the function is and what it is used for, any arguments that are passed, labeling what is required and what is optional, and determining any restrictions on when the function can be called or any exceptions that are raised. | Severity Level: Low – this recommendation will not affect the model outputs, but is a best practice to follow when writing code. | 2027 | In Progress
29 | Internal Resources Embedded into Each Team | Ensure there is a skilled and knowledgeable base of internal resources involved in each aspect of the WiNGS-Ops modeling process such that reliance on external parties is reduced. | Severity Level: Low – the Advanced Analytics team is skilled and knowledgeable so there is minimal risk to the model outputs at this stage. | 2027 | In Progress
30 | Cloud Consolidation | Consolidate services under one cloud provider for ease of use, integration, and billing. This can ensure that future updates to any of the cloud services are always made in a way to keep compatibility and seamless integration with the other developed components. | Severity Level: Low – this recommendation has no impact on the output of the WiNGS-Ops model but would allow for greater efficiency in use of cloud services. Although cloud services may work together across different vendors, they are optimized to work most effectively when combined with services belonging to one single cloud provider. | 2027 | Not Started
31 | Pipeline Deployment Documentation | Create robust and granular documentation of the deployment pipeline, which would ensure a lower reliance on the experience of resources. | Severity Level: Medium – without this documentation, a continued reliance on external resources would be mandatory as there would be no straightforward mechanism through which internal resources could inform themselves on the finer details of the inference pipeline. | 2027 | In Progress
32 | Limitations Documentations | Document the limitations of the models that underpin the WiNGS-Ops outputs and ensure that these are fully understood by the business users. This will ensure that any decisions made based on the result of the WiNGS-Ops model are made from the most informed position. | Severity Level: Medium – without understanding the limitations of the model, sub-optimal decisions may be made due to a misinterpretation of the results. | 2026 | In Progress
33 | Full Model Lifecycle Documentation | Document the full lifecycle of each model in training and in inference such that the knowledge, skills and experience of the team is captured for future use. This would also enable training and onboarding of new resources to be more straightforward and regulatory filings to be completed more swiftly. Example pieces to include in this documentation are the problem formulation process, all decision points and reasonings, and future plans and intentions. | Severity Level: Low – the team is knowledgeable in the models they have constructed so any risk is reduced. In most cases there is only one team member with discrete knowledge of the specific model. | 2027 | In Progress
34 | Weather Sanitization Ownership Update | Update the technical ownership of the weather sanitization repository and any other repositories that may have changed ownership. | Severity Level: Medium – the script is well understood by multiple parties, however there is no single owner to drive decisions or improvements. | 2026 | In Progress
35 | Missing Data Outputs | Correct data issues such that all segments have an outputted value from the WiNGS-Ops model. Failing that, provide full communication and explanation to the end users for those segments where a WiNGS-Ops output was unable to be generated. This would ensure that awareness of these missing values is gained and decisions are not based on the omission of those segments in the model outputs. | Severity Level: Medium – while the PSPS de-energization decision takes other inputs aside from WiNGS-Ops, without a complete model output for every segment, it is conceivable that the decision maker will lose trust with WiNGS-Ops model if a PSPS de-energization decision would need to be made for a segment that has no WiNGS-Ops output. | 2026 | In Progress
36 | Cold Storage | Consider the use of cold storage for long-term storage of snapshots or model runs which do not need to be accessed regularly. This would reduce the overall costs of the cloud infrastructure, which will become more important as the models and data sets mature and grow in size. | Severity Level: Low – as the size of files being stored currently is not large, use of cold storage would have a minimal effect on the cost of cloud services, though remains a best practice recommendation. | 2027 | Not Started
37 | Error Monitoring Dashboard | Develop a monitoring dashboard that provides real-time error monitoring and a view of the model runs such that issues may be highlighted and resolved in a timely manner. | Severity Level: Low – existing monitoring allow for errors to be identified; however, advanced monitoring would allow a more streamlined process for error identification and remediation. | 2026 | In Progress
38 | Global ID Cleaning | Clean the data such that all Global IDs are valid and the amount of feeders without output results due to invalid global IDs decreases. This will prevent situations where the WiNGS-Ops model is unable to produce risk scores. | Severity Level: Medium – having up to 10% of feeders without risk scores could cause a loss of credibility within the organization when the model is needed to provide data driven insights for PSPS de-energization decision making. | 2026 | In Progress
39 | Issue Reporting Process | Create a formalized process for issue reporting from the end users to the development teams. This should be simple and streamlined such that any issues may be raised, quantified, and remediated quickly. | Severity Level: Low – currently there is no prescribed process, which could lead to confusion as to the point of escalation for issues. This may result in a delay to any remediation activity and impact the quality of outputs. | 2026 | In Progress
40 | Action & Tasks Log | Document meetings and create a backlog for actions/tasks so they can be prioritized, tracked, and completed against. This will ensure that all tasks are captured and implemented as intended and miscommunication is avoided. | Severity Level: Low – without a formalized process of documentation and action tracking, there may be more instances of misunderstanding of intention between teams, which might result in a sub-optimal outcome or re-work in remediating the concern. | 2027 | In Progress
41 | Questions and Model Changes Tracking | Create a formalized process for questions and model changes ahead of each activation event. In addition, track changes to model code and outputs through formal version control. This will mean that the decision points and actions taken are formally documented and easily explainable if a reference is required, which may aid answering regulatory questions or post-event report preparation. | Severity Level: Low – the current process will result in a more time-consuming post-activation event reporting process. This may mean a period of potential re-work to establish the reasoning behind certain tweaks and decisions taken in the model pre-event. | 2027 | In Progress
42 | WiNGS-Ops Overall Versioning Process | Create an overall WiNGS-Ops model versioning process such that changes or updates to any component of WiNGS-Ops results in a version iteration. This ensures that users have a clear indication of when a model methodology has changed. This may help the users understand which models may be easily compared. | Severity Level: Low – the current versioning methodology may result in inaccurate comparisons being made by end users across models. | 2027 | In Progress

## SDGE Table 6-1
Risk Driver (from OEIS Table 6-1) | Initiative | Activity | Tracking ID | Activity Effectiveness | Expected Implementation Cost (K$) | CapEx | O&M | Uncertainties/Potential Impacts | Implementation Schedule
Contact from Object | Grid Design and System Hardening | Strategic Undergrounding | WMP.473 | 99.2% | 435575 | 430561 | 5014 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Grid Design and System Hardening | Combined Covered Conductor | WMP.455 | 59% | 212401 | 208317 | 4084 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Grid Design and System Hardening | Advance Protection | WMP.463 | 8% | 6354 | 5793 | 561 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Grid Design and System Hardening | Early Fault Detection | WMP.1195 | 16% | 7613 | 7604 | 9 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Public Safety Power Shutoff | PSPS | n/a | n/a | n/a** | n/a** | n/a** | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Grid Operations and Procedures | Sensitive Relay Profile | n/a | n/a | n/a*** | n/a*** | n/a*** | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Distribution Overhead Detailed Inspections | WMP.478 | 29% | 3004 | 0 | 3004 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Distribution Wood Pole Intrusive Inspections | WMP.483 | 29% | 2536 | 0 | 2536 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Risk-Informed Done Inspections | WMP.522 | 29% | 104208 | 70625 | 33583 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Distribution Overhead Patrol Inspections | WMP.488 | 29% | 852 | 0 | 852 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Transmission Overhead Detailed Inspections | WMP.479 | 28% | 3425 | 3380 | 45 | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Transmission Infrared Inspections | WMP.482 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Transmission Wood Pole Intrusive Inspections | WMP.1190 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Contact from Object | Asset Inspections | Transmission Overhead Patrol Inspections | WMP.489 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Grid Design and System Hardening | Strategic Undergrounding | WMP.473 | 99.2% | 435575 | 430561 | 5014 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Grid Design and System Hardening | Combined Covered Conductor | WMP.455 | 59% | 212401 | 208317 | 4084 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Vegetation Management and Inspections | Off-cycle patrol | WMP.508 | 1% | 4399 | 0 | 4399 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Vegetation Management and Inspections | Prune and Removal | WMP.501 | 1% | 91017 | 0 | 91017 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Public Safety Power Shutoff | PSPS | n/a | n/a | n/a** | n/a** | n/a** | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Grid Operations and Procedures | Sensitive Relay Profile | n/a | n/a | n/a*** | n/a*** | n/a*** | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Distribution Overhead Detailed Inspections | WMP.478 | 29% | 3004 | 0 | 3004 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Distribution Wood Pole Intrusive Inspections | WMP.483 | 10% | 2536 | 0 | 2536 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Risk-Informed Done Inspections | WMP.552 | 29% | 104208 | 70625 | 33583 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Distribution Overhead Patrol Inspections | WMP.488 | 10% | 852 | 0 | 852 | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Transmission Overhead Detailed Inspections | WMP.479 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Transmission Infrared Inspections | WMP.482 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Transmission Wood Pole Intrusive Inspections | WMP.1190 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Vegetation Contact | Asset Inspections | Transmission Overhead Patrol Inspections | WMP.489 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Grid Design and System Hardening | Strategic Undergrounding | WMP.473 | 99.2% | 435575 | 430561 | 5014 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Grid Design and System Hardening | Combined Covered Conductor | WMP.455 | 59% | 212401 | 208317 | 4084 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Grid Design and System Hardening | Advance Protection | WMP.463 | 8% | 6354 | 5793 | 561 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Grid Design and System Hardening | Early Fault Detection | WMP.1195 | 16% | 7613 | 7604 | 9 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Distribution Overhead Detailed Inspections | WMP.478 | 29% | 3004 | 0 | 3004 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Transmission Overhead Detailed Inspections | WMP.479 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Risk-Informed Done Inspections | WMP.552 | 29% | 104208 | 70625 | 33583 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Distribution Wood Pole Intrusive Inspections | WMP.483 | 29% | 2536 | 0 | 2536 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Distribution Overhead Patrol Inspections | WMP.488 | 29% | 852 | 0 | 852 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Transmission Infrared Inspections | WMP.482 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Transmission Wood Pole Intrusive Inspections | WMP.1190 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Asset Inspections | Transmission Overhead Patrol Inspections | WMP.489 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Grid Design and System Hardening | Strategic Pole Replacement | WMP.1189 | 39% | 18996 | 18492 | 504 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Grid Design and System Hardening | Traditional Hardening | WMP.475 | 39.43% | 11618 | 9559 | 2059 | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Public Safety Power Shutoff | PSPS | n/a | n/a | n/a** | n/a** | n/a** | See Section 6.1.3.1.4 | 2026-2028
Equipment / facility failure or damage | Grid Operations and Procedures | Sensitive Relay Profile | n/a | n/a | n/a*** | n/a*** | n/a*** | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Grid Design and System Hardening | Traditional Hardening | WMP.475 | 39.43% | 0 | 0 | 0 | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Grid Design and System Hardening | Strategic Undergrounding | WMP.473 | 99.2% | 435575 | 430561 | 5014 | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Grid Design and System Hardening | Combined Covered Conductor | WMP.455 | 59% | 212401 | 208317 | 4084 | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Public Safety Power Shutoff | PSPS | n/a | n/a | n/a** | n/a** | n/a** | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Grid Operations and Procedures | Sensitive Relay Profile | n/a | n/a | n/a*** | n/a*** | n/a*** | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Distribution Overhead Detailed Inspections | WMP.478 | 29% | 3004 | 0 | 3004 | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Distribution Wood Pole Intrusive Inspections | WMP.483 | 29% | 2536 | 0 | 2536 | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Risk-Informed Done Inspections | WMP.552 | 29% | 104208 | 70625 | 33583 | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Distribution Overhead Patrol Inspections | WMP.488 | 29% | 852 | 0 | 852 | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Transmission Overhead Detailed Inspections | WMP.479 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Transmission Infrared Inspections | WMP.482 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Transmission Wood Pole Intrusive Inspections | WMP.1190 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Wire-to-wire contact | Asset Inspections | Transmission Overhead Patrol Inspections | WMP.489 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Contamination | Grid Design and System Hardening | Strategic Undergrounding | WMP.473 | 99.2% | 435575 | 430561 | 5014 | See Section 6.1.3.1.4 | 2026-2028
Contamination | Grid Design and System Hardening | Combined Covered Conductor | WMP.455 | 59% | 212401 | 208317 | 4084 | See Section 6.1.3.1.4 | 2026-2028
Contamination | Public Safety Power Shutoff | PSPS | n/a | n/a | n/a** | n/a** | n/a** | See Section 6.1.3.1.4 | 2026-2028
Contamination | Grid Operations and Procedures | Sensitive Relay Profile | n/a | n/a | n/a*** | n/a*** | n/a*** | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Distribution Overhead Detailed Inspections | WMP.478 | 29% | 3004 | 0 | 3004 | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Distribution Wood Pole Intrusive Inspections | WMP.483 | 29% | 2536 | 0 | 2536 | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Risk-Informed Done Inspections | WMP.552 | 29% | 104208 | 70625 | 33583 | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Distribution Overhead Patrol Inspections | WMP.488 | 29% | 852 | 0 | 852 | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Transmission Overhead Detailed Inspections | WMP.479 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Transmission Infrared Inspections | WMP.482 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Transmission Wood Pole Intrusive Inspections | WMP.1190 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Contamination | Asset Inspections | Transmission Overhead Patrol Inspections | WMP.489 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Distribution Overhead Detailed Inspections | WMP.478 | 29% | 3004 | 0 | 3004 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Distribution Wood Pole Intrusive Inspections | WMP.483 | 29% | 2536 | 0 | 2536 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Distribution Overhead Patrol Inspections | WMP.488 | 29% | 852 | 0 | 852 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Transmission Overhead Detailed Inspections | WMP.479 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Transmission Wood Pole Intrusive Inspections | WMP.1190 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Transmission Overhead Patrol Inspections | WMP.489 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Transmission Infrared Inspections | WMP.482 | 28% | n/a* | n/a* | n/a* | See Section 6.1.3.1.4 | 2026-2028
Unknown | Asset Inspections | Risk-Informed Done Inspections | WMP.552 | 29% | 104208 | 70625 | 33583 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Grid Design and System Hardening | Strategic Undergrounding | WMP.473 | 99.2% | 435575 | 430561 | 5014 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Grid Design and System Hardening | Combined Covered Conductor | WMP.455 | 59% | 212401 | 208317 | 4084 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Grid Design and System Hardening | Early Fault Detection | WMP.1195 | 16% | 7613 | 7604 | 9 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Grid Design and System Hardening | Advance Protection | WMP.463 | 8% | 6354 | 5793 | 561 | See Section 6.1.3.1.4 | 2026-2028
Unknown | Public Safety Power Shutoff | PSPS | n/a | n/a | n/a** | n/a** | n/a** | See Section 6.1.3.1.4 | 2026-2028
Unknown | Grid Operations and Procedures | Sensitive Relay Profile | n/a | n/a | n/a*** | n/a*** | n/a*** | See Section 6.1.3.1.4 | 2026-2028
* Transmission only activities are funded by FERC
** PSPS costs cannot be projected
*** For Sensitive Relay Profile, see Grid Operations and Procedures initiatives

## SDGE Table 6-2
Interim Mitigation Initiative | Interim Risk | Goal of Interim Mitigation | Frequency of Occurrence and Potential Consequences of Risk Event(s) Addressed by the Improvement/Initiative
Microgrids (WMP.462) | Some customers have a higher potential to be affected by PSPS de-energizations | Decrease the number of customers affected by a PSPS de-energization | More customers will have a higher risk of PSPS de-energizations and higher PSPS impacts.
Sensitive Relay Profile (SRP) | The high amount of energy available when faults occur during times of extreme fire risk could lead to ignitions | Change settings to reduce fault energy and fire risk | There will be a greater risk of equipment/facility failure or damage, wire to wire contact, contact due to objects or vegetation, and unknown contamination.
Strategic Pole Replacement Program (WMP.1189) | Poles nearing the end of their useful life have a higher failure potential | Replace high-risk equipment | Increase in risk events from equipment/facility failure or damage
PSPS Sectionalizing Enhancements (WMP.461) | Large customer counts between sectionalizing devices result in more customers with an increased risk of PSPS de-energizations | Decrease the number of customers affected by a PSPS de-energization | More customers will have a higher risk of PSPS de-energizations and higher PSPS impacts.
Standby Power Program (WMP.468) | Customers in rural areas have a higher potential to be affected by PSPS de-energization | Reduce PSPS impacts on rural, backcountry customers by providing backup power generation during a PSPS de-energization | More customers will have a higher risk of PSPS de-energizations and higher PSPS impacts.
Generator Assistance Program (WMP.467) | Some customers have a higher potential to be affected by PSPS de-energization | Provide rebates for portable generators to enhance customer preparedness for PSPS de-energization | More customers will have a higher risk of PSPS de-energizations and higher PSPS impacts.
Automatic Recloser Settings (WMP.1018) | High amount of energy available when faults occur during times of extreme fire risk | Reduce the potential for unwanted energy release after fault has occurred | There will be a greater risk of equipment/facility failure or damage, wire to wire contact, contact due to objects or vegetation, and unknown contamination.
Contracted Fire Resources (CFRs) | Electric crews risk events while performing work during elevated and extreme conditions | Suppress an ignition before it can grow | There will be a greater risk of an ignition propagation and therefore greater wildfire consequences.
PSPS | High wind events and high fire potential | Reduce the potential for asset-caused ignitions during extreme weather events | There will be a greater risk of equipment/facility failure or damage, wire to wire contact, contact due to objects or vegetation, and unknown contamination.
Corrective Maintenance Program (WMP.1433) | Equipment failure or contact from objects could cause an ignition or fault | Reduce the risk of equipment failure from issues found during asset inspections | There will be an increase in the likelihood of faults or ignitions.
Prune and Removal (Clearance) (WMP.501) | Contact from vegetation could cause an ignition or fault | Reduce the risk of ignitions or faults due to vegetation contact | There will be an increase in the likelihood of faults or ignitions.
Pole Clearing (WMP.512) | Non-exempt equipment may spark, arc, and/or fail, causing hot particles to fall to the base of the pole and potentially cause an ignition | Reduce the consequence of an ignition | There will be a greater risk of an ignition propagation and therefore greater wildfire consequences.

## SDGE Table 8-1
Risk Event Type | 9-Year Total | Annual Average
Risk events with wildfire related pending infractions | 7 | 0.78
Total equipment risk events | 1148 | 128
Risk event rate with pending infractions | 0.61% | 0.61%
Wildfire Infractions Repaired | 35598 | 3955

## SDGE Table 8-2
Maintenance/Replacement Strategy | Definition | Equipment Type | WMP Initiative (or other)
Reactive | This strategy is utilized to maintain or replace an asset or equipment when an asset or equipment is operated until it stops functioning per its specifications. This is a reactionary strategy since the asset or equipment is only replaced when it fails. It is used for lower risk assets that do not impact public safety. | All equipment,* when needed | Asset Inspections: WMP.478; WMP.479; WMP.482; WMP.483; WMP.1190; WMP.488; WMP.489; WMP.492
Time-based (Interval-based) | This strategy is utilized to repair or replace an asset or equipment that does not meet acceptance criteria found during a routine, cyclical inspection. The inspection cycle may be determined by regulatory mandates, equipment manufacturer recommendation, or industry best practice. | All equipment* as required | Asset Inspections: WMP.478; WMP.479; WMP.482; WMP.483; WMP.488; WMP.489; WMP.492; WMP.1190; WMP.1433
Condition-based Monitoring | This strategy is utilized to maintain or replace an asset or equipment when certain attributes of the asset or equipment exceed the defined thresholds as alerted by a continuous monitoring system. This strategy requires continuous monitoring and analysis of key health data of an asset such as age, location, gassing, number of operations, electrical loading, and temperature. | Conductors | Early Fault Detection WMP.1195
Risk-based | This strategy is utilized to maintain or replace an asset or equipment based on the probability and consequence of failure. While the automated condition-based strategy considers the health of the asset, which is often a proxy for the likelihood of failure, the risk-based strategy considers the consequence of failure of the assets in addition to the health of the asset. | Poles/Towers Conductor Insulators Shield Wire Hardware | Grid Hardening Initiatives: WMP.455; WMP.473; WMP.1189; WMP.543; WMP.545 Risk-based inspections WMP.552
* All equipment includes capacitors, circuit breakers, connectors, including hotline clamps, conductor, including covered conductor, fuses, including expulsion fuses, distribution pole, lightning arrestors, reclosers, splices, transmission poles/towers, transformers, non-exempt equipment, pre-GO 95 legacy equipment, and other equipment not listed.

## SDGE Table 8-3
Condition | Severity | Priority Level | Timeframe for Remediation*
Damaged/Missing Pole Hardware | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged/Missing Pole Hardware | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
SDG&E Leaning Pole or Potential Overload | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
SDG&E Leaning Pole or Potential Overload | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Private Property Caused Pole Inaccessible | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Private Property Caused Pole Inaccessible | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
SDG&E/Vegetation Caused Pole Inaccessible or Cannot Locate | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
SDG&E/Vegetation Caused Pole Inaccessible or Cannot Locate | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Open/Damaged Ground | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Open/Damaged Ground | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged Arrestor/Insulator/Dead-end | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged Arrestor/Insulator/Dead-end | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Oil Leak | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Oil Leak | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged Crossarm | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged Crossarm | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged Switch | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged Switch | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged Switch Gang Operator Mechanism | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged Switch Gang Operator Mechanism | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Corrosion - OH Transformer | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Corrosion - OH Transformer | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
SDG&E Pole/ Stub Pole Damaged or Broken | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
SDG&E Pole/ Stub Pole Damaged or Broken | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
SDG&E Insufficient Clearance | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
SDG&E Insufficient Clearance | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Avian Protection Damaged | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Avian Protection Damaged | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Private Property Hazardous Condition | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Private Property Hazardous Condition | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Foreign Objects | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Foreign Objects | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged Capacitor | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged Capacitor | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Slack Conductors | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Slack Conductors | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged Conductors | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged Conductors | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Guy Grounded | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Guy Grounded | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Slack Anchor Guy | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Slack Anchor Guy | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged / Missing Guying | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Damaged / Missing Guying | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Slack Span Guy | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Slack Span Guy | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Infraction - No Applicable Code | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Infraction - No Applicable Code | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Trees/Veg in Proximity to Primary | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Trees/Veg in Proximity to Primary | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Trees/Veg. Contacting Open Wire | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Trees/Veg. Contacting Open Wire | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Secondary (SSC/Aerial Cable) - Trim | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Secondary (SSC/Aerial Cable) - Trim | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Secondary (SSC/Aerial Cable) - Guard | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Secondary (SSC/Aerial Cable) - Guard | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Secondary (SSC/Aerial Cable) - Reroute | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Secondary (SSC/Aerial Cable) - Reroute | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Service - Guard | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Service - Guard | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Service - Slack | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Service - Slack | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Service - Reroute | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Service - Reroute | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Service - Trim | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Service - Trim | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Veg in Guy - Heavy Strain or Abrasion | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Veg in Guy - Heavy Strain or Abrasion | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Pole replacement from POIN | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Pole replacement from POIN | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Restoration Recommended, Special Reject | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Restoration Recommended, Special Reject | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Restoration Rejected Replace,Special Reject | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Restoration Rejected Replace,Special Reject | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Restoration Rejected, Replace | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Restoration Rejected, Replace | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Restoration Recommended, Steel Rein | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Restoration Recommended, Steel Rein | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 or Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
*Timeframe is determined by GO 95, Rule 18

## SDGE Table 8-4
Condition | Severity | Priority Level | Timeframe for Remediation*
Balloon-Mylar | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Balloon-Mylar | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Assessment Required | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Cracked | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Cracked | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Woodpecker Hole(S) | Critical issues that present an imminent hazard to public safety, including fire risk, that require immediate action to either correct or make safe | Level 1 | 7 days, or as soon as practical
Woodpecker Hole(S) | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
3 Guys-1Rod | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Backed Out-Off | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Bent | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Bird Droppings | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Bird Nest | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Birdcaged | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Blackening | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Blown | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Broken | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Chipped | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Clearance-Insufficient | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Corona Damage | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Covered With | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Cracked | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Damaged | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Deterioration | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Disconnected | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Drainage | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Evidence Of Tracking | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Exposed | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Faded | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Fire Damage | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Flashed | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Foreign Object (Bird's Nest) | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Foreign Object (Specify) | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Greasing Needed | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Ground Line Insp Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Grounding Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Grounding Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Gunshot | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Heat Damage | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Improper Sag | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Installation Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Installation Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Installation-Improper | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Installation-Non Standard | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Isolating Insulators-Remove | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Kite | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Leaning-Tilted | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Loaded Improperly | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Loose | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Maintenance Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Mis-Aligned-Pulled | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Missing | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Moved-Slid | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Not Fully Closed | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Not Seated | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Not Sheared | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Open | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Out Of Adjustment | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Out Of Lay | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Painting Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Painting Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Reinforcing Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Reinforcing Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Removal Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Removal Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Replacement Assessment Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Replacement Needed | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Rotten | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Rust (Heavy) | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Rust (Medium) | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Split | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Submerged | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Tagging Required | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Twisted | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Unreadable | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Unwrapping | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Vibration | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Vines | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Washed Out | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Washing Needed | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Wire Contact | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Woodpecker Hole(S) | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Worn | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Wrong Size | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 2 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Danger Sign Components - Sign Warning (With Man) | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Signs-Danger | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Signs-High Voltage-At Top | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
Aerial Number Bracket | Infraction issues that pose a moderate or low potential hazard to public safety, employee safety, or fire risk; issues that present a nonconformance with GO 95 requirements or specifications | Level 3 | 6 months in Tier 3 12 months in Tier 2 36-60 months in non-HFTD
*Timeframe is determined by GO 95, Rule 18

## SDGE Table 8-5
Equipment Type | Distribution Failure Rate* | Distribution Ignition Rate** | Transmission Failure Rate* | Transmission Ignition Rate**
Capacitors | 0.5249% | 0% | 0% | 0%
Circuit Breakers | 0.128% | n/a | 0.2506% | n/a
Connectors | 0.1688% | 5.357% | 0% | 0%
Conductor | 0.01113% | 1.485% | 0.01241% | 0%
Transformers | 0.06413% | 0.8333% | 0% | 0%
Fuses+cutouts | 0.08013% | 3.846% | 0% | 0%
Distribution pole | 0.03073% | 0% | n/a | n/a
Lightning arrestors/Insulator/bushing | 0.08185% | 0.1862% | 0.00374% | 0%
Reclosers | 0.1312% | 0% | 0% | 0%
Splices | 0% | 0% | n/a | 0%
Transmission poles/towers | n/a | n/a | 0.005109% | 0%
Anchor/Guy | 0.01083% | 0.2041% | 0.005414% | 0%
Switch | 0.04453% | 14.29% | 0% | 0%
Crossarm | 0.01836% | 0% | 0.01022% | 0%
Note: 2022-2024 historical data
* Failure Rate: Failed equipment resulting in faults
** Ignition Rate: Total ignitions caused by actual failures that lead to faults

## SDGE Table 8-6
HFTD Tier | FPI Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 5-Year Average
Non-HFTD | Normal | 151 | 137 | 188 | 149 | 165 | 158
Non-HFTD | Elevated | 23 | 59 | 53 | 29 | 14 | 36
Non-HFTD | Extreme | 1 | 3 | 0 | 0 | 0 | 1
Tier 2 | Normal | 51 | 41 | 38 | 36 | 55 | 44
Tier 2 | Elevated | 39 | 38 | 47 | 27 | 11 | 32
Tier 2 | Extreme | 2 | 1 | 0 | 5 | 0 | 2
Tier 3 | Normal | 43 | 31 | 45 | 24 | 40 | 37
Tier 3 | Elevated | 41 | 57 | 31 | 19 | 15 | 33
Tier 3 | Extreme | 1 | 0 | 0 | 2 | 0 | 1

## SDGE Table 8-7
Tier | Normal | Elevated | Extreme
Tier 2 | 2.26% | 3.37% | 22.22%
Tier 3 | 1.37% | 5.38% | 14.29%

## SDGE Table 8-8
Avoidance Type | HFTD Tier | FPI Rating | 2019 | 2020 | 2021 | 2022 | 2023 | 5-Year Average
Estimated Faults Avoided | Tier 2 | Normal | 102 | 82 | 76 | 72 | 110 | 88.4
Estimated Faults Avoided | Tier 2 | Elevated | 78 | 76 | 94 | 54 | 22 | 64.8
Estimated Faults Avoided | Tier 2 | Extreme | 4 | 2 | 0 | 10 | 0 | 3.2 | `
Estimated Faults Avoided | Tier 3 | Normal | 86 | 62 | 90 | 48 | 80 | 73.2
Estimated Faults Avoided | Tier 3 | Elevated | 82 | 114 | 62 | 38 | 30 | 65.2
Estimated Faults Avoided | Tier 3 | Extreme | 2 | 0 | 0 | 4 | 0 | 1.2
Estimated Ignitions Avoided | Tier 2 | n/a | 5.8 | 4.9 | 4.9 | 5.7 | 3.2 | 4.8926
Estimated Ignitions Avoided | Tier 3 | n/a | 5.9 | 7 | 4.6 | 3.3 | 2.7 | 4.6821
Estimated Ignitions Avoided | Total | n/a | 11.6982 | 11.8414 | 9.454 | 8.9426 | 5.9374 | 9.5747
Estimated Ignition Avoided

## SDGE Table 8-9
Asset Type | Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | Reference to Electrical Corporation Training/ Qualification Programs
Distribution | Line Inspector | Successful completion of 6-month Overhead Detailed Inspection training program; IBEW status in good standing; Valid California driver’s license | Overhead and underground Inspection Training | Overhead CMP Detailed Inspection Training (STU EL310)
Distribution | Distribution Lineman | Journeyman Lineman having completed an accredited apprenticeship program; International Brotherhood of Electrical Workers (IBEW) Journeyman Lineman status in good standing; Class A California Driver’s License | Qualified electrical worker (QEW), Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program
Distribution | Fault Finding Specialist | Journeyman Lineman having completed an accredited apprenticeship program; IBEW Journeyman Lineman status in good standing; 4-week Relief Fault Finder (RFF) class completed and associated written and practical exams passed | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program RFF Course
Distribution | Electric Troubleshooter | Journeyman Lineman having completed an accredited apprenticeship program; IBEW Journeyman Lineman status in good standing; Complete 7-week Relief Trouble Shooter (RETS) class and pass written and practical exams | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program
Distribution | Working Foreman | Journeyman Lineman having completed an accredited apprenticeship program; IBEW Journeyman Lineman status in good standing; 6 months’ experience in both overhead and underground electric during the past three years; Construction Standards and Practices tests passed | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program
Distribution | Distribution Construction Supervisor | 6+ years construction and maintenance experience | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program Essentials of Supervision
Distribution | Inspection and Treatment Foreman | Pesticide handler training; Valid class C driver’s license; First aid/CPR qualified | n/a | n/a
Distribution | Auditor | Demonstrated education or experience to audit the work as appropriate. Training on the use of audit software or processes and awareness training on scope of audit and schedule deadlines. | n/a | n/a
Transmission | Transmission Lineman | Journeyman Lineman having completed an accredited apprenticeship program; IBEW Journeyman Lineman status in good standing; Class A California Driver’s License | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program
Transmission | Transmission Patroller | Journeyman Lineman having completed an accredited apprenticeship program; IBEW Journeyman Lineman status in good standing; Class A California Driver’s License; 18 months experience in overhead and underground transmission construction and maintenance within the past 3 years | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program
Transmission | Working Foreman- Electric Transmission | Journeyman Lineman having completed an accredited apprenticeship program; IBEW Journeyman Lineman status in good standing; Valid California Class A driver's license; Class A Medical Certificate; 18 months’ experience in transmission construction and Energized High Voltage hotline maintenance within the past 5 years | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program
Transmission | Thermographer | Part 107 drone license or must obtain within first year; Level I Infrared Certification or must obtain within first year | Thermography certificate; QEW or Electrician | n/a
Transmission | Senior Thermographer | Part 107 drone license or must obtain within first year; Level III Infrared Certification or must obtain within first year | Thermography certificate; QEW or Electrician | n/a
Transmission | Transmission Construction Supervisor | 6+ years construction and maintenance experience | QEW, Overhead and/or Underground Inspection Training | Line Assistant and Apprenticeship Program
Transmission | Inspection and Treatment Foreman | Pesticide handler training; Valid class C driver’s license; First aid / CPR qualified | n/a | Essentials of Supervision
Substation | Substation Inspector | Substation Electrician Journeyman having completed electrician apprenticeship program; Valid California Class A driver's license | QEW | Electrician Apprenticeship Program
Substation | Substation Construction Supervisor | Journeyman with 5+ years experience | QEW | Electrician Apprenticeship Program; Essentials of Supervision

## SDGE Table 8-10
Transmission or Distribution | Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | Reference to Electrical Corporation Training/ Qualification Programs
Distribution | Apprentice Lineman | 9 months’ experience as Line Assistant; Valid California driver’s license; Must have held previous position for at least 9 months | No special certification required | Line Assistant and Apprenticeship Program
Distribution | Cable Splicer | Journeyman Lineman | No special certification required | Line Assistant and Apprenticeship Program; Essentials of Supervision
Distribution | Construction Manager-Electric | Bachelor’s Degree or equivalent experience; 8 years’ experience | No special certification required | Essentials of Supervision
Distribution | Construction Supervisor-Electric | High School Diploma or GED; 6 years’ experience; Complete 2-day program at Skills Training Center or complete outside program | No special certification required | Line Assistant and Apprenticeship Program; Essentials of Supervision
Distribution | District Manager | High School Diploma or GED; 10 years’ experience | No special certification required | Essentials of Supervision
Distribution | Electric Troubleshooter | Complete 7-week RETS class and pass written and practical exams | Journeyman Lineman | Line Assistant and Apprenticeship Program; RETS Training
Distribution | Fault Finder | Complete 4-week RFF class and pass written and practical exams | Journeyman Lineman | Line Assistant and Apprenticeship Program; RFF Training
Distribution | Field Construction Advisor (FCA) | Journeyman Lineman | QEW | Line Assistant and Apprenticeship Program
Distribution | Foreman | Journeyman Lineman | QEW | Line Assistant and Apprenticeship Program
Distribution | Foreman (Splicing) | Journeyman Lineman | QEW | Line Assistant and Apprenticeship Program
Distribution | Groundman | n/a | No special certification required | n/a
Distribution | Journeyman Lineman | Journeyman Lineman | QEW | Line Assistant and Apprenticeship Program
Distribution | Line Assistant (non QEW) | Successfully pass Company administered aptitude and skills tests; Valid California Class A driver's license; Pass a DMV physical examination and DOT drug screen; Must have held previous position for at least 9 months | No special certification required | Line Assistant and Apprenticeship Program
Distribution | Distribution Lineman | Complete the minimum 3-year 6000-hour Lineman Apprentice program at the Skills Training Center and assigned Districts; Complete a 3-year, 480-hour college-level program to be qualified to take the Journeyman Lineman’s test; Pass the Journeyman Lineman test | QEW | Line Assistant and Apprenticeship Program
Distribution | Working Foreman-Electric Distribution | 6 months’ experience in both overhead and underground electric during the past 3 years; Valid California Class A driver's license; Class A Medical Certificate; Must have held previous position for at least 9 months | QEW | Line Assistant and Apprenticeship Program
Transmission | Construction Manager-Electric | Bachelor’s Degree or equivalent experience; 8 years’ experience | QEW | Essentials of Supervision
Transmission | Construction Supervisor-Electric | High School Diploma or GED; 6 years’ experience | No special certification required | Line Assistant and Apprenticeship Program; Essentials of Supervision
Transmission | Line Assistant (non QEW) | Successfully pass Company administered aptitude and skills tests; Valid California Class A driver's license; Pass a DMV physical examination and DOT drug screen; Must have held previous position for at least 9 months | No special certification required | Line Assistant and Apprenticeship Program
Transmission | Supv II - E Trans As Plg & Ops | Bachelor’s Degree or equivalent experience; 5 years’ experience; Professional Engineer License | No special certification required | n/a
Transmission | Transmission Lineman | Complete the minimum 3-year 6000-hour Lineman Apprentice program at the Skills Training Center and assigned Districts; Complete a 3-year, 480-hour college-level program to be qualified to take the Journeyman Lineman’s test; Pass the Journeyman Lineman test | QEW | Line Assistant and Apprenticeship Program
Transmission | Transmission Patroller | Valid California Class A driver's license; Class A Medical Certificate; 18 months experience in overhead and underground transmission construction and maintenance within the past 3 years; Must reside within the service territory | QEW | Line Assistant and Apprenticeship Program
Transmission | Working Foreman-Electric Transmission | Valid California Class A driver's license; Class A Medical Certificate; 18 months’ experience in transmission construction and EHV hotline maintenance within the past 5 years; Must have held previous position for at least 9 months | QEW | Line Assistant and Apprenticeship Program; Essentials of Supervision
Transmission | Field Construction Advisor (FCA) | Journeyman Lineman | QEW | Line Assistant and Apprenticeship Program
Transmission | Apprentice Lineman | n/a | No special certification required | n/a
Transmission | Journeyman Lineman | Journeyman Lineman | QEW | Line Assistant and Apprenticeship Program
Transmission | Groundman | n/a | No special certification required | n/a
Transmission | Operator | Crane license if operating a crane | No special certification required | n/a

## SDGE Table 8-11
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | Reference to Electrical Corporation Training/ Qualification Programs
Electric Troubleshooter | Journeyman Lineman who completed an accredited apprenticeship program; IBEW Journeyman Lineman status in good standing; Complete 7-week RETS class and pass the associated written and practical exams | QEW | RETS Training; Line Assistant and Apprenticeship Program

## SDGE Table 9-1
Year | Amount | Projects | Acres | Homes | Miles | Poles/Towers
2021 | $500K | 1 | 200 | 105 | 0 | 120
2022 | $1.1M | 2 | 398 | 133 | 4 | 103
2023 | $1.2M | 2 | 279 | 183 | 0 | 233
2024 | $1.5M | 2 | 189 | 408 | 24 | 438
2025 | $1M | 2 | TBD* | TBD* | TBD* | TBD*
*Project scopes for 2025 have not been determined

## SDGE Table 9-2
Year | Amount | Projects | Acres | Homes | Miles | Poles/Towers
2019 | $27K | 2 | 35 | 94 | 0 | 114
2020 | $24K | 2 | 55 | 94 | 4 | 114
2021 | $50K | 2 | 97 | 94 | 0 | 94
2022 | $20K | 2 | 0 | 0 | 24 | 29
2023 | $75K | 2 | 97 | 94 | 3 | 94
2024 | $90K | 2 | 97 | 94 | 3 | 94
2025 | 0 | TBD* | TBD* | TBD* | TBD* | TBD*
*Project scopes for 2025 have not been determined

## SDGE Table 9-3
Year | Amount | Projects | Acres | Homes | Miles | Poles/Towers
2010 | $53K | 1 | 43 | 0 | 2 | 7
2012 | $36K | 1 | 43 | 0 | 2 | 7
2016 | $33K | 1 | 43 | 0 | 2 | 7
2018 | $26K | 1 | 20 | 0 | 0.5 | 7
2020 | $19K | 1 | 43 | 0 | 2 | 7
2023 | $22K | 1 | 43 | 0 | 2 | 7
2025 | 0 | TBD* | TBD* | TBD* | TBD* | TBD*
*Project scopes for 2025 have not been determined

## SDGE Table 9-4
Year | Amount | Projects | Miles | Poles/Towers
2019 | $50K | 1 | 3.5 | 47
2021 | $50K | 1 | 23.4 | 270
2022 | $80K | 1 | 3.5 | 47
2023 | $60K | 1 | 3.5 | 47
2024 | 0 | 0 | 0 | 0
2025 | 0 | 0 | 0 | 0

## SDGE Table 10-1
Location | Normal FPI | Elevated FPI | Extreme FPI | All FPI
Non-HFTD | 0.6617% | 2.162% | 0% | 0.9247%
Tier 2 | 2.257% | 3.349% | 22.22% | 2.817%
Tier 3 | 1.379% | 5.385% | 11.11% | 3.064%
System | 1.063% | 3.448% | 10% | 1.733%
HFTD (Tier 2 and Tier 3) | 1.862% | 4.332% | 16.67% | 2.931%

## SDGE Table 11-1
Community Resource Center | Area Served | Facility Name | Location | Site Description | Services Offered
Boulevard CRC | Boulevard | Boulevard Community Center | 39919 Ribbonwood Rd Boulevard, CA 91916 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Descanso CRC | Descanso | Descanso County Library | 9545 River Dr Descanso, CA 91916 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Dulzura CRC | Dulzura | Dulzura Community Development Center | 1136 Community Building Rd Dulzura, CA 91917 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Fallbrook CRC | Fallbrook | Fallbrook Branch Library | 124 S Mission Rd Fallbrook, CA 92028 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Julian CRC | Julian | Whispering Winds Catholic Camp | 17606 Harrison Park Rd Julian, CA 92036 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Lake Morena CRC | Lake Morena | Lake Morena Community Church | 29765 Oak Dr Campo, CA 91906 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Pine Valley CRC | Pine Valley | Pine Valley Improvement Club | 28890 Old Hwy 80 Pine Valley, CA 91962 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Potrero CRC | Potrero | Potrero Community Center | 24550 Highway 94 Potrero, CA 91963 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Ramona CRC | Ramona | Ramona Branch Library | 1275 Main Street Ramona, CA 92065 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Valley Center CRC | Valley Center | Valley Center Branch Library | 29200 Cole Grade Rd Valley Center, CA 92082 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information
Warner Springs CRC | Warner Springs | Warner Springs Community Resource Center | 30950 Highway 79 Warner Springs, CA 92086 | Brick & Mortar | Water, WiFi, Medical Device Charging, Snacks, Phone Charging, Ice, Water for livestock, Car Power Inverter, Battery Bank, and Up-to-Date Outage Information